## Heat Load of Room
Heat Load Calculator (Estimation by Area)
Room Size
Room Length | 100 | ft
Room Width | 10 | ft
Heat Load per sqft | 65 | btu/h/sqft
Heat Load to cover Area | 65000 | btu/h
Human
Heat Load per human | 500 | btu/h/pax
Heat Load Occupancy (pax) | 2 | pax
Human Heat Load | 1000 | btu/h
Solar
Window Length | 2 | ft
Window Width | 2 | ft
Heat Load per sqft of Window | 80 | btu/h/sqft
Solar Heat Load | 320 | btu/h
Other Heat Load
Equipment/Lighting/Processs Heat Load | 3.5 | kW
| 11942.49 | btu/h
Total Room Heat Load | 78262.49 | btu/h
Refrigerant Tonneage, RT | 6.5219 | TR
CFM/RT | 350 | CFM/RT
Airflow, CFM | 2282.656 | CFM

## Cooling Load of AC
Cooling Load Calculator (or Heat introduced by System)
Airflow (CFM) | 8800 | CFM
% OA (%) | 10 | %
% RA (%) | 90 | %
Offcoil Setting/Leaving Air Component (LA)
Offcoil Temperature, (°F) | 52.9 | °F
Offcoil RH (%) | 98 | %
Offcoil Enthalpy, hLA (btu/lb) | 21.7298 | btu/lb
Outdoor Air Component (OA)
Outdoor Air Temperature, OAT (°F) * | 50.9 | °F
Outdoor Air RH (%) ** | 98 | %
Outdoor Air Enthalpy, hOA (btu/lb) *** | 20.5914 | btu/lb
Return Air Component (RA)
Room Setpoint/Return Air Temperature, RAT (°F) | 73.4 | °F
Room/Return Air RH (%) | 55 | %
Room/Return Air Enthalpy, hRA (btu/lb) | 28.1479 | btu/lb
Mixed Air Component (MA)
Mixed Air Temperature, MAT (°F) | 71.15 | °F
Mixed Air RH (%) | 59.3 | %
Mixed Air Enthalpy, hMA (btu/lb) | 27.3922 | btu/lb
* OAT can also be Precooler Output Temperature
** Outdoor Air RH can also be Precooler Output RH
*** hOA can also be Precooler Output Air Enthalpy
Grand Total Heat, GTH (btu/h) | 221739.9502 | btu/h
Total Sensible Heat, TSH (btu/h) | 173448 | btu/h
Grand Sensible Heat Factor, GSHF | 0.78221
Room Total Heat, RTH (btu/h) | 251331.1641 | btu/h
Room Sensible Heat, RSH (btu/h) | 194832 | btu/h
Room Sensible Heat Factor, RSHF | 0.7752