## Sheet1
SR4-2 Transition, Pyramidal, Supply Air Systems
Transition Length, L |  | 500 | mm
Incoming (Pre-Transition)
Duct Width |  | 600 | mm
Duct Height |  | 550 | mm
Air Flow (CFM) |  | 4083
Duct Velocity (FPM) |  | 1149.8817
VP |  | 0.082433
Outgoing (Post-Transition)
Duct Width |  | 550 | mm
Duct Height |  | 500 | mm
Air Flow (CFM) |  | 4083
Duct Velocity (FPM) |  | 1379.8581
VP |  | 0.1187
θ1 (Side) |  | 5.7241 | °
θ2 (Top) |  | 5.7241 | °
A1/A |  | 1.2
θ (Max) |  | 5.7241 | °
C |  | 0.023084
Frictional Loss |  | 0.0027402 | " WG
Table 14-12A Coefficient C (See Note 7)
A0 /A1 |  | θ
| 0 | 10 | 15 | 20 | 30 | 45 | 60 | 90 | 120 | 150 | 180 | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 41 | 42 | 43 | 44 | 45 | 46 | 47 | 48 | 49 | 50 | 51 | 52 | 53 | 54 | 55 | 56 | 57 | 58 | 59 | 60 | 61 | 62 | 63 | 64 | 65 | 66 | 67 | 68 | 69 | 70 | 71 | 72 | 73 | 74 | 75 | 76 | 77 | 78 | 79 | 80 | 81 | 82 | 83 | 84 | 85 | 86 | 87 | 88 | 89 | 90 | 91 | 92 | 93 | 94 | 95 | 96 | 97 | 98 | 99 | 100 | 101 | 102 | 103 | 104 | 105 | 106 | 107 | 108 | 109 | 110 | 111 | 112 | 113 | 114 | 115 | 116 | 117 | 118 | 119 | 120 | 121 | 122 | 123 | 124 | 125 | 126 | 127 | 128 | 129 | 130 | 131 | 132 | 133 | 134 | 135 | 136 | 137 | 138 | 139 | 140 | 141 | 142 | 143 | 144 | 145 | 146 | 147 | 148 | 149 | 150 | 151 | 152 | 153 | 154 | 155 | 156 | 157 | 158 | 159 | 160 | 161 | 162 | 163 | 164 | 165 | 166 | 167 | 168 | 169 | 170 | 171 | 172 | 173 | 174 | 175 | 176 | 177 | 178 | 179 | 180
0.1 | 0 | 0.05 | 0.05 | 0.05 | 0.05 | 0.07 | 0.08 | 0.19 | 0.29 | 0.37 | 0.43
0.17 | 0 | 0.05 | 0.05 | 0.05 | 0.04 | 0.06 | 0.07 | 0.18 | 0.28 | 0.36 | 0.42
0.25 | 0 | 0.06 | 0.05 | 0.05 | 0.04 | 0.06 | 0.07 | 0.17 | 0.27 | 0.35 | 0.41
0.5 | 0 | 0.06 | 0.07 | 0.07 | 0.05 | 0.06 | 0.06 | 0.12 | 0.18 | 0.24 | 0.26
1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 0 | 0.6 | 0.84 | 1 | 1.2 | 1.32 | 1.32 | 1.32 | 1.28 | 1.24 | 1.2
4 | 0 | 4 | 5.76 | 7.2 | 8.32 | 9.28 | 9.92 | 10.24 | 10.24 | 10.24 | 10.24
10 | 0 | 30 | 50 | 53 | 64 | 75 | 84 | 89 | 91 | 91 | 88
16 | 0 | 76.8 | 138.24 | 135.68 | 166.4 | 197.12 | 225.28 | 243.2 | 250.88 | 250.88 | 250.88
0.1 | 0 | 0.05 | 0.05 | 0.05 | 0.05 | 0.07 | 0.08 | 0.19 | 0.29 | 0.37 | 0.43 | 0 | 0.005 | 0.01 | 0.015 | 0.02 | 0.025 | 0.03 | 0.035 | 0.04 | 0.045 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.051333 | 0.052667 | 0.054 | 0.055333 | 0.056667 | 0.058 | 0.059333 | 0.060667 | 0.062 | 0.063333 | 0.064667 | 0.066 | 0.067333 | 0.068667 | 0.07 | 0.070667 | 0.071333 | 0.072 | 0.072667 | 0.073333 | 0.074 | 0.074667 | 0.075333 | 0.076 | 0.076667 | 0.077333 | 0.078 | 0.078667 | 0.079333 | 0.08 | 0.083667 | 0.087333 | 0.091 | 0.094667 | 0.098333 | 0.102 | 0.10567 | 0.10933 | 0.113 | 0.11667 | 0.12033 | 0.124 | 0.12767 | 0.13133 | 0.135 | 0.13867 | 0.14233 | 0.146 | 0.14967 | 0.15333 | 0.157 | 0.16067 | 0.16433 | 0.168 | 0.17167 | 0.17533 | 0.179 | 0.18267 | 0.18633 | 0.19 | 0.19333 | 0.19667 | 0.2 | 0.20333 | 0.20667 | 0.21 | 0.21333 | 0.21667 | 0.22 | 0.22333 | 0.22667 | 0.23 | 0.23333 | 0.23667 | 0.24 | 0.24333 | 0.24667 | 0.25 | 0.25333 | 0.25667 | 0.26 | 0.26333 | 0.26667 | 0.27 | 0.27333 | 0.27667 | 0.28 | 0.28333 | 0.28667 | 0.29 | 0.29267 | 0.29533 | 0.298 | 0.30067 | 0.30333 | 0.306 | 0.30867 | 0.31133 | 0.314 | 0.31667 | 0.31933 | 0.322 | 0.32467 | 0.32733 | 0.33 | 0.33267 | 0.33533 | 0.338 | 0.34067 | 0.34333 | 0.346 | 0.34867 | 0.35133 | 0.354 | 0.35667 | 0.35933 | 0.362 | 0.36467 | 0.36733 | 0.37 | 0.372 | 0.374 | 0.376 | 0.378 | 0.38 | 0.382 | 0.384 | 0.386 | 0.388 | 0.39 | 0.392 | 0.394 | 0.396 | 0.398 | 0.4 | 0.402 | 0.404 | 0.406 | 0.408 | 0.41 | 0.412 | 0.414 | 0.416 | 0.418 | 0.42 | 0.422 | 0.424 | 0.426 | 0.428 | 0.43
0.15 | 0 | 0.05 | 0.05 | 0.05 | 0.042857 | 0.062857 | 0.072857 | 0.18286 | 0.28286 | 0.36286 | 0.42286 | 0 | 0.005 | 0.01 | 0.015 | 0.02 | 0.025 | 0.03 | 0.035 | 0.04 | 0.045 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.049286 | 0.048571 | 0.047857 | 0.047143 | 0.046429 | 0.045714 | 0.045 | 0.044286 | 0.043571 | 0.042857 | 0.04419 | 0.045524 | 0.046857 | 0.04819 | 0.049524 | 0.050857 | 0.05219 | 0.053524 | 0.054857 | 0.05619 | 0.057524 | 0.058857 | 0.06019 | 0.061524 | 0.062857 | 0.063524 | 0.06419 | 0.064857 | 0.065524 | 0.06619 | 0.066857 | 0.067524 | 0.06819 | 0.068857 | 0.069524 | 0.07019 | 0.070857 | 0.071524 | 0.07219 | 0.072857 | 0.076524 | 0.08019 | 0.083857 | 0.087524 | 0.09119 | 0.094857 | 0.098524 | 0.10219 | 0.10586 | 0.10952 | 0.11319 | 0.11686 | 0.12052 | 0.12419 | 0.12786 | 0.13152 | 0.13519 | 0.13886 | 0.14252 | 0.14619 | 0.14986 | 0.15352 | 0.15719 | 0.16086 | 0.16452 | 0.16819 | 0.17186 | 0.17552 | 0.17919 | 0.18286 | 0.18619 | 0.18952 | 0.19286 | 0.19619 | 0.19952 | 0.20286 | 0.20619 | 0.20952 | 0.21286 | 0.21619 | 0.21952 | 0.22286 | 0.22619 | 0.22952 | 0.23286 | 0.23619 | 0.23952 | 0.24286 | 0.24619 | 0.24952 | 0.25286 | 0.25619 | 0.25952 | 0.26286 | 0.26619 | 0.26952 | 0.27286 | 0.27619 | 0.27952 | 0.28286 | 0.28552 | 0.28819 | 0.29086 | 0.29352 | 0.29619 | 0.29886 | 0.30152 | 0.30419 | 0.30686 | 0.30952 | 0.31219 | 0.31486 | 0.31752 | 0.32019 | 0.32286 | 0.32552 | 0.32819 | 0.33086 | 0.33352 | 0.33619 | 0.33886 | 0.34152 | 0.34419 | 0.34686 | 0.34952 | 0.35219 | 0.35486 | 0.35752 | 0.36019 | 0.36286 | 0.36486 | 0.36686 | 0.36886 | 0.37086 | 0.37286 | 0.37486 | 0.37686 | 0.37886 | 0.38086 | 0.38286 | 0.38486 | 0.38686 | 0.38886 | 0.39086 | 0.39286 | 0.39486 | 0.39686 | 0.39886 | 0.40086 | 0.40286 | 0.40486 | 0.40686 | 0.40886 | 0.41086 | 0.41286 | 0.41486 | 0.41686 | 0.41886 | 0.42086 | 0.42286
0.17 | 0 | 0.05 | 0.05 | 0.05 | 0.04 | 0.06 | 0.07 | 0.18 | 0.28 | 0.36 | 0.42 | 0 | 0.005 | 0.01 | 0.015 | 0.02 | 0.025 | 0.03 | 0.035 | 0.04 | 0.045 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.049 | 0.048 | 0.047 | 0.046 | 0.045 | 0.044 | 0.043 | 0.042 | 0.041 | 0.04 | 0.041333 | 0.042667 | 0.044 | 0.045333 | 0.046667 | 0.048 | 0.049333 | 0.050667 | 0.052 | 0.053333 | 0.054667 | 0.056 | 0.057333 | 0.058667 | 0.06 | 0.060667 | 0.061333 | 0.062 | 0.062667 | 0.063333 | 0.064 | 0.064667 | 0.065333 | 0.066 | 0.066667 | 0.067333 | 0.068 | 0.068667 | 0.069333 | 0.07 | 0.073667 | 0.077333 | 0.081 | 0.084667 | 0.088333 | 0.092 | 0.095667 | 0.099333 | 0.103 | 0.10667 | 0.11033 | 0.114 | 0.11767 | 0.12133 | 0.125 | 0.12867 | 0.13233 | 0.136 | 0.13967 | 0.14333 | 0.147 | 0.15067 | 0.15433 | 0.158 | 0.16167 | 0.16533 | 0.169 | 0.17267 | 0.17633 | 0.18 | 0.18333 | 0.18667 | 0.19 | 0.19333 | 0.19667 | 0.2 | 0.20333 | 0.20667 | 0.21 | 0.21333 | 0.21667 | 0.22 | 0.22333 | 0.22667 | 0.23 | 0.23333 | 0.23667 | 0.24 | 0.24333 | 0.24667 | 0.25 | 0.25333 | 0.25667 | 0.26 | 0.26333 | 0.26667 | 0.27 | 0.27333 | 0.27667 | 0.28 | 0.28267 | 0.28533 | 0.288 | 0.29067 | 0.29333 | 0.296 | 0.29867 | 0.30133 | 0.304 | 0.30667 | 0.30933 | 0.312 | 0.31467 | 0.31733 | 0.32 | 0.32267 | 0.32533 | 0.328 | 0.33067 | 0.33333 | 0.336 | 0.33867 | 0.34133 | 0.344 | 0.34667 | 0.34933 | 0.352 | 0.35467 | 0.35733 | 0.36 | 0.362 | 0.364 | 0.366 | 0.368 | 0.37 | 0.372 | 0.374 | 0.376 | 0.378 | 0.38 | 0.382 | 0.384 | 0.386 | 0.388 | 0.39 | 0.392 | 0.394 | 0.396 | 0.398 | 0.4 | 0.402 | 0.404 | 0.406 | 0.408 | 0.41 | 0.412 | 0.414 | 0.416 | 0.418 | 0.42
0.2 | 0 | 0.05375 | 0.05 | 0.05 | 0.04 | 0.06 | 0.07 | 0.17625 | 0.27625 | 0.35625 | 0.41625 | 3.4694e-18 | 0.005375 | 0.01075 | 0.016125 | 0.0215 | 0.026875 | 0.03225 | 0.037625 | 0.043 | 0.048375 | 0.05375 | 0.053 | 0.05225 | 0.0515 | 0.05075 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.049 | 0.048 | 0.047 | 0.046 | 0.045 | 0.044 | 0.043 | 0.042 | 0.041 | 0.04 | 0.041333 | 0.042667 | 0.044 | 0.045333 | 0.046667 | 0.048 | 0.049333 | 0.050667 | 0.052 | 0.053333 | 0.054667 | 0.056 | 0.057333 | 0.058667 | 0.06 | 0.060667 | 0.061333 | 0.062 | 0.062667 | 0.063333 | 0.064 | 0.064667 | 0.065333 | 0.066 | 0.066667 | 0.067333 | 0.068 | 0.068667 | 0.069333 | 0.07 | 0.073542 | 0.077083 | 0.080625 | 0.084167 | 0.087708 | 0.09125 | 0.094792 | 0.098333 | 0.10187 | 0.10542 | 0.10896 | 0.1125 | 0.11604 | 0.11958 | 0.12312 | 0.12667 | 0.13021 | 0.13375 | 0.13729 | 0.14083 | 0.14437 | 0.14792 | 0.15146 | 0.155 | 0.15854 | 0.16208 | 0.16562 | 0.16917 | 0.17271 | 0.17625 | 0.17958 | 0.18292 | 0.18625 | 0.18958 | 0.19292 | 0.19625 | 0.19958 | 0.20292 | 0.20625 | 0.20958 | 0.21292 | 0.21625 | 0.21958 | 0.22292 | 0.22625 | 0.22958 | 0.23292 | 0.23625 | 0.23958 | 0.24292 | 0.24625 | 0.24958 | 0.25292 | 0.25625 | 0.25958 | 0.26292 | 0.26625 | 0.26958 | 0.27292 | 0.27625 | 0.27892 | 0.28158 | 0.28425 | 0.28692 | 0.28958 | 0.29225 | 0.29492 | 0.29758 | 0.30025 | 0.30292 | 0.30558 | 0.30825 | 0.31092 | 0.31358 | 0.31625 | 0.31892 | 0.32158 | 0.32425 | 0.32692 | 0.32958 | 0.33225 | 0.33492 | 0.33758 | 0.34025 | 0.34292 | 0.34558 | 0.34825 | 0.35092 | 0.35358 | 0.35625 | 0.35825 | 0.36025 | 0.36225 | 0.36425 | 0.36625 | 0.36825 | 0.37025 | 0.37225 | 0.37425 | 0.37625 | 0.37825 | 0.38025 | 0.38225 | 0.38425 | 0.38625 | 0.38825 | 0.39025 | 0.39225 | 0.39425 | 0.39625 | 0.39825 | 0.40025 | 0.40225 | 0.40425 | 0.40625 | 0.40825 | 0.41025 | 0.41225 | 0.41425 | 0.41625
0.25 | 0 | 0.06 | 0.05 | 0.05 | 0.04 | 0.06 | 0.07 | 0.17 | 0.27 | 0.35 | 0.41 | 0 | 0.006 | 0.012 | 0.018 | 0.024 | 0.03 | 0.036 | 0.042 | 0.048 | 0.054 | 0.06 | 0.058 | 0.056 | 0.054 | 0.052 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.049 | 0.048 | 0.047 | 0.046 | 0.045 | 0.044 | 0.043 | 0.042 | 0.041 | 0.04 | 0.041333 | 0.042667 | 0.044 | 0.045333 | 0.046667 | 0.048 | 0.049333 | 0.050667 | 0.052 | 0.053333 | 0.054667 | 0.056 | 0.057333 | 0.058667 | 0.06 | 0.060667 | 0.061333 | 0.062 | 0.062667 | 0.063333 | 0.064 | 0.064667 | 0.065333 | 0.066 | 0.066667 | 0.067333 | 0.068 | 0.068667 | 0.069333 | 0.07 | 0.073333 | 0.076667 | 0.08 | 0.083333 | 0.086667 | 0.09 | 0.093333 | 0.096667 | 0.1 | 0.10333 | 0.10667 | 0.11 | 0.11333 | 0.11667 | 0.12 | 0.12333 | 0.12667 | 0.13 | 0.13333 | 0.13667 | 0.14 | 0.14333 | 0.14667 | 0.15 | 0.15333 | 0.15667 | 0.16 | 0.16333 | 0.16667 | 0.17 | 0.17333 | 0.17667 | 0.18 | 0.18333 | 0.18667 | 0.19 | 0.19333 | 0.19667 | 0.2 | 0.20333 | 0.20667 | 0.21 | 0.21333 | 0.21667 | 0.22 | 0.22333 | 0.22667 | 0.23 | 0.23333 | 0.23667 | 0.24 | 0.24333 | 0.24667 | 0.25 | 0.25333 | 0.25667 | 0.26 | 0.26333 | 0.26667 | 0.27 | 0.27267 | 0.27533 | 0.278 | 0.28067 | 0.28333 | 0.286 | 0.28867 | 0.29133 | 0.294 | 0.29667 | 0.29933 | 0.302 | 0.30467 | 0.30733 | 0.31 | 0.31267 | 0.31533 | 0.318 | 0.32067 | 0.32333 | 0.326 | 0.32867 | 0.33133 | 0.334 | 0.33667 | 0.33933 | 0.342 | 0.34467 | 0.34733 | 0.35 | 0.352 | 0.354 | 0.356 | 0.358 | 0.36 | 0.362 | 0.364 | 0.366 | 0.368 | 0.37 | 0.372 | 0.374 | 0.376 | 0.378 | 0.38 | 0.382 | 0.384 | 0.386 | 0.388 | 0.39 | 0.392 | 0.394 | 0.396 | 0.398 | 0.4 | 0.402 | 0.404 | 0.406 | 0.408 | 0.41
0.3 | 0 | 0.06 | 0.054 | 0.054 | 0.042 | 0.06 | 0.068 | 0.16 | 0.252 | 0.328 | 0.38 | 0 | 0.006 | 0.012 | 0.018 | 0.024 | 0.03 | 0.036 | 0.042 | 0.048 | 0.054 | 0.06 | 0.0588 | 0.0576 | 0.0564 | 0.0552 | 0.054 | 0.054 | 0.054 | 0.054 | 0.054 | 0.054 | 0.0528 | 0.0516 | 0.0504 | 0.0492 | 0.048 | 0.0468 | 0.0456 | 0.0444 | 0.0432 | 0.042 | 0.0432 | 0.0444 | 0.0456 | 0.0468 | 0.048 | 0.0492 | 0.0504 | 0.0516 | 0.0528 | 0.054 | 0.0552 | 0.0564 | 0.0576 | 0.0588 | 0.06 | 0.060533 | 0.061067 | 0.0616 | 0.062133 | 0.062667 | 0.0632 | 0.063733 | 0.064267 | 0.0648 | 0.065333 | 0.065867 | 0.0664 | 0.066933 | 0.067467 | 0.068 | 0.071067 | 0.074133 | 0.0772 | 0.080267 | 0.083333 | 0.0864 | 0.089467 | 0.092533 | 0.0956 | 0.098667 | 0.10173 | 0.1048 | 0.10787 | 0.11093 | 0.114 | 0.11707 | 0.12013 | 0.1232 | 0.12627 | 0.12933 | 0.1324 | 0.13547 | 0.13853 | 0.1416 | 0.14467 | 0.14773 | 0.1508 | 0.15387 | 0.15693 | 0.16 | 0.16307 | 0.16613 | 0.1692 | 0.17227 | 0.17533 | 0.1784 | 0.18147 | 0.18453 | 0.1876 | 0.19067 | 0.19373 | 0.1968 | 0.19987 | 0.20293 | 0.206 | 0.20907 | 0.21213 | 0.2152 | 0.21827 | 0.22133 | 0.2244 | 0.22747 | 0.23053 | 0.2336 | 0.23667 | 0.23973 | 0.2428 | 0.24587 | 0.24893 | 0.252 | 0.25453 | 0.25707 | 0.2596 | 0.26213 | 0.26467 | 0.2672 | 0.26973 | 0.27227 | 0.2748 | 0.27733 | 0.27987 | 0.2824 | 0.28493 | 0.28747 | 0.29 | 0.29253 | 0.29507 | 0.2976 | 0.30013 | 0.30267 | 0.3052 | 0.30773 | 0.31027 | 0.3128 | 0.31533 | 0.31787 | 0.3204 | 0.32293 | 0.32547 | 0.328 | 0.32973 | 0.33147 | 0.3332 | 0.33493 | 0.33667 | 0.3384 | 0.34013 | 0.34187 | 0.3436 | 0.34533 | 0.34707 | 0.3488 | 0.35053 | 0.35227 | 0.354 | 0.35573 | 0.35747 | 0.3592 | 0.36093 | 0.36267 | 0.3644 | 0.36613 | 0.36787 | 0.3696 | 0.37133 | 0.37307 | 0.3748 | 0.37653 | 0.37827 | 0.38
0.35 | 0 | 0.06 | 0.058 | 0.058 | 0.044 | 0.06 | 0.066 | 0.15 | 0.234 | 0.306 | 0.35 | 0 | 0.006 | 0.012 | 0.018 | 0.024 | 0.03 | 0.036 | 0.042 | 0.048 | 0.054 | 0.06 | 0.0596 | 0.0592 | 0.0588 | 0.0584 | 0.058 | 0.058 | 0.058 | 0.058 | 0.058 | 0.058 | 0.0566 | 0.0552 | 0.0538 | 0.0524 | 0.051 | 0.0496 | 0.0482 | 0.0468 | 0.0454 | 0.044 | 0.045067 | 0.046133 | 0.0472 | 0.048267 | 0.049333 | 0.0504 | 0.051467 | 0.052533 | 0.0536 | 0.054667 | 0.055733 | 0.0568 | 0.057867 | 0.058933 | 0.06 | 0.0604 | 0.0608 | 0.0612 | 0.0616 | 0.062 | 0.0624 | 0.0628 | 0.0632 | 0.0636 | 0.064 | 0.0644 | 0.0648 | 0.0652 | 0.0656 | 0.066 | 0.0688 | 0.0716 | 0.0744 | 0.0772 | 0.08 | 0.0828 | 0.0856 | 0.0884 | 0.0912 | 0.094 | 0.0968 | 0.0996 | 0.1024 | 0.1052 | 0.108 | 0.1108 | 0.1136 | 0.1164 | 0.1192 | 0.122 | 0.1248 | 0.1276 | 0.1304 | 0.1332 | 0.136 | 0.1388 | 0.1416 | 0.1444 | 0.1472 | 0.15 | 0.1528 | 0.1556 | 0.1584 | 0.1612 | 0.164 | 0.1668 | 0.1696 | 0.1724 | 0.1752 | 0.178 | 0.1808 | 0.1836 | 0.1864 | 0.1892 | 0.192 | 0.1948 | 0.1976 | 0.2004 | 0.2032 | 0.206 | 0.2088 | 0.2116 | 0.2144 | 0.2172 | 0.22 | 0.2228 | 0.2256 | 0.2284 | 0.2312 | 0.234 | 0.2364 | 0.2388 | 0.2412 | 0.2436 | 0.246 | 0.2484 | 0.2508 | 0.2532 | 0.2556 | 0.258 | 0.2604 | 0.2628 | 0.2652 | 0.2676 | 0.27 | 0.2724 | 0.2748 | 0.2772 | 0.2796 | 0.282 | 0.2844 | 0.2868 | 0.2892 | 0.2916 | 0.294 | 0.2964 | 0.2988 | 0.3012 | 0.3036 | 0.306 | 0.30747 | 0.30893 | 0.3104 | 0.31187 | 0.31333 | 0.3148 | 0.31627 | 0.31773 | 0.3192 | 0.32067 | 0.32213 | 0.3236 | 0.32507 | 0.32653 | 0.328 | 0.32947 | 0.33093 | 0.3324 | 0.33387 | 0.33533 | 0.3368 | 0.33827 | 0.33973 | 0.3412 | 0.34267 | 0.34413 | 0.3456 | 0.34707 | 0.34853 | 0.35
0.4 | 0 | 0.06 | 0.062 | 0.062 | 0.046 | 0.06 | 0.064 | 0.14 | 0.216 | 0.284 | 0.32 | 0 | 0.006 | 0.012 | 0.018 | 0.024 | 0.03 | 0.036 | 0.042 | 0.048 | 0.054 | 0.06 | 0.0604 | 0.0608 | 0.0612 | 0.0616 | 0.062 | 0.062 | 0.062 | 0.062 | 0.062 | 0.062 | 0.0604 | 0.0588 | 0.0572 | 0.0556 | 0.054 | 0.0524 | 0.0508 | 0.0492 | 0.0476 | 0.046 | 0.046933 | 0.047867 | 0.0488 | 0.049733 | 0.050667 | 0.0516 | 0.052533 | 0.053467 | 0.0544 | 0.055333 | 0.056267 | 0.0572 | 0.058133 | 0.059067 | 0.06 | 0.060267 | 0.060533 | 0.0608 | 0.061067 | 0.061333 | 0.0616 | 0.061867 | 0.062133 | 0.0624 | 0.062667 | 0.062933 | 0.0632 | 0.063467 | 0.063733 | 0.064 | 0.066533 | 0.069067 | 0.0716 | 0.074133 | 0.076667 | 0.0792 | 0.081733 | 0.084267 | 0.0868 | 0.089333 | 0.091867 | 0.0944 | 0.096933 | 0.099467 | 0.102 | 0.10453 | 0.10707 | 0.1096 | 0.11213 | 0.11467 | 0.1172 | 0.11973 | 0.12227 | 0.1248 | 0.12733 | 0.12987 | 0.1324 | 0.13493 | 0.13747 | 0.14 | 0.14253 | 0.14507 | 0.1476 | 0.15013 | 0.15267 | 0.1552 | 0.15773 | 0.16027 | 0.1628 | 0.16533 | 0.16787 | 0.1704 | 0.17293 | 0.17547 | 0.178 | 0.18053 | 0.18307 | 0.1856 | 0.18813 | 0.19067 | 0.1932 | 0.19573 | 0.19827 | 0.2008 | 0.20333 | 0.20587 | 0.2084 | 0.21093 | 0.21347 | 0.216 | 0.21827 | 0.22053 | 0.2228 | 0.22507 | 0.22733 | 0.2296 | 0.23187 | 0.23413 | 0.2364 | 0.23867 | 0.24093 | 0.2432 | 0.24547 | 0.24773 | 0.25 | 0.25227 | 0.25453 | 0.2568 | 0.25907 | 0.26133 | 0.2636 | 0.26587 | 0.26813 | 0.2704 | 0.27267 | 0.27493 | 0.2772 | 0.27947 | 0.28173 | 0.284 | 0.2852 | 0.2864 | 0.2876 | 0.2888 | 0.29 | 0.2912 | 0.2924 | 0.2936 | 0.2948 | 0.296 | 0.2972 | 0.2984 | 0.2996 | 0.3008 | 0.302 | 0.3032 | 0.3044 | 0.3056 | 0.3068 | 0.308 | 0.3092 | 0.3104 | 0.3116 | 0.3128 | 0.314 | 0.3152 | 0.3164 | 0.3176 | 0.3188 | 0.32
0.45 | 0 | 0.06 | 0.066 | 0.066 | 0.048 | 0.06 | 0.062 | 0.13 | 0.198 | 0.262 | 0.29 | 0 | 0.006 | 0.012 | 0.018 | 0.024 | 0.03 | 0.036 | 0.042 | 0.048 | 0.054 | 0.06 | 0.0612 | 0.0624 | 0.0636 | 0.0648 | 0.066 | 0.066 | 0.066 | 0.066 | 0.066 | 0.066 | 0.0642 | 0.0624 | 0.0606 | 0.0588 | 0.057 | 0.0552 | 0.0534 | 0.0516 | 0.0498 | 0.048 | 0.0488 | 0.0496 | 0.0504 | 0.0512 | 0.052 | 0.0528 | 0.0536 | 0.0544 | 0.0552 | 0.056 | 0.0568 | 0.0576 | 0.0584 | 0.0592 | 0.06 | 0.060133 | 0.060267 | 0.0604 | 0.060533 | 0.060667 | 0.0608 | 0.060933 | 0.061067 | 0.0612 | 0.061333 | 0.061467 | 0.0616 | 0.061733 | 0.061867 | 0.062 | 0.064267 | 0.066533 | 0.0688 | 0.071067 | 0.073333 | 0.0756 | 0.077867 | 0.080133 | 0.0824 | 0.084667 | 0.086933 | 0.0892 | 0.091467 | 0.093733 | 0.096 | 0.098267 | 0.10053 | 0.1028 | 0.10507 | 0.10733 | 0.1096 | 0.11187 | 0.11413 | 0.1164 | 0.11867 | 0.12093 | 0.1232 | 0.12547 | 0.12773 | 0.13 | 0.13227 | 0.13453 | 0.1368 | 0.13907 | 0.14133 | 0.1436 | 0.14587 | 0.14813 | 0.1504 | 0.15267 | 0.15493 | 0.1572 | 0.15947 | 0.16173 | 0.164 | 0.16627 | 0.16853 | 0.1708 | 0.17307 | 0.17533 | 0.1776 | 0.17987 | 0.18213 | 0.1844 | 0.18667 | 0.18893 | 0.1912 | 0.19347 | 0.19573 | 0.198 | 0.20013 | 0.20227 | 0.2044 | 0.20653 | 0.20867 | 0.2108 | 0.21293 | 0.21507 | 0.2172 | 0.21933 | 0.22147 | 0.2236 | 0.22573 | 0.22787 | 0.23 | 0.23213 | 0.23427 | 0.2364 | 0.23853 | 0.24067 | 0.2428 | 0.24493 | 0.24707 | 0.2492 | 0.25133 | 0.25347 | 0.2556 | 0.25773 | 0.25987 | 0.262 | 0.26293 | 0.26387 | 0.2648 | 0.26573 | 0.26667 | 0.2676 | 0.26853 | 0.26947 | 0.2704 | 0.27133 | 0.27227 | 0.2732 | 0.27413 | 0.27507 | 0.276 | 0.27693 | 0.27787 | 0.2788 | 0.27973 | 0.28067 | 0.2816 | 0.28253 | 0.28347 | 0.2844 | 0.28533 | 0.28627 | 0.2872 | 0.28813 | 0.28907 | 0.29
0.5 | 0 | 0.06 | 0.07 | 0.07 | 0.05 | 0.06 | 0.06 | 0.12 | 0.18 | 0.24 | 0.26 | 0 | 0.006 | 0.012 | 0.018 | 0.024 | 0.03 | 0.036 | 0.042 | 0.048 | 0.054 | 0.06 | 0.062 | 0.064 | 0.066 | 0.068 | 0.07 | 0.07 | 0.07 | 0.07 | 0.07 | 0.07 | 0.068 | 0.066 | 0.064 | 0.062 | 0.06 | 0.058 | 0.056 | 0.054 | 0.052 | 0.05 | 0.050667 | 0.051333 | 0.052 | 0.052667 | 0.053333 | 0.054 | 0.054667 | 0.055333 | 0.056 | 0.056667 | 0.057333 | 0.058 | 0.058667 | 0.059333 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.062 | 0.064 | 0.066 | 0.068 | 0.07 | 0.072 | 0.074 | 0.076 | 0.078 | 0.08 | 0.082 | 0.084 | 0.086 | 0.088 | 0.09 | 0.092 | 0.094 | 0.096 | 0.098 | 0.1 | 0.102 | 0.104 | 0.106 | 0.108 | 0.11 | 0.112 | 0.114 | 0.116 | 0.118 | 0.12 | 0.122 | 0.124 | 0.126 | 0.128 | 0.13 | 0.132 | 0.134 | 0.136 | 0.138 | 0.14 | 0.142 | 0.144 | 0.146 | 0.148 | 0.15 | 0.152 | 0.154 | 0.156 | 0.158 | 0.16 | 0.162 | 0.164 | 0.166 | 0.168 | 0.17 | 0.172 | 0.174 | 0.176 | 0.178 | 0.18 | 0.182 | 0.184 | 0.186 | 0.188 | 0.19 | 0.192 | 0.194 | 0.196 | 0.198 | 0.2 | 0.202 | 0.204 | 0.206 | 0.208 | 0.21 | 0.212 | 0.214 | 0.216 | 0.218 | 0.22 | 0.222 | 0.224 | 0.226 | 0.228 | 0.23 | 0.232 | 0.234 | 0.236 | 0.238 | 0.24 | 0.24067 | 0.24133 | 0.242 | 0.24267 | 0.24333 | 0.244 | 0.24467 | 0.24533 | 0.246 | 0.24667 | 0.24733 | 0.248 | 0.24867 | 0.24933 | 0.25 | 0.25067 | 0.25133 | 0.252 | 0.25267 | 0.25333 | 0.254 | 0.25467 | 0.25533 | 0.256 | 0.25667 | 0.25733 | 0.258 | 0.25867 | 0.25933 | 0.26
0.55 | 0 | 0.054 | 0.063 | 0.063 | 0.045 | 0.054 | 0.054 | 0.108 | 0.162 | 0.216 | 0.234 | 0 | 0.0054 | 0.0108 | 0.0162 | 0.0216 | 0.027 | 0.0324 | 0.0378 | 0.0432 | 0.0486 | 0.054 | 0.0558 | 0.0576 | 0.0594 | 0.0612 | 0.063 | 0.063 | 0.063 | 0.063 | 0.063 | 0.063 | 0.0612 | 0.0594 | 0.0576 | 0.0558 | 0.054 | 0.0522 | 0.0504 | 0.0486 | 0.0468 | 0.045 | 0.0456 | 0.0462 | 0.0468 | 0.0474 | 0.048 | 0.0486 | 0.0492 | 0.0498 | 0.0504 | 0.051 | 0.0516 | 0.0522 | 0.0528 | 0.0534 | 0.054 | 0.054 | 0.054 | 0.054 | 0.054 | 0.054 | 0.054 | 0.054 | 0.054 | 0.054 | 0.054 | 0.054 | 0.054 | 0.054 | 0.054 | 0.054 | 0.0558 | 0.0576 | 0.0594 | 0.0612 | 0.063 | 0.0648 | 0.0666 | 0.0684 | 0.0702 | 0.072 | 0.0738 | 0.0756 | 0.0774 | 0.0792 | 0.081 | 0.0828 | 0.0846 | 0.0864 | 0.0882 | 0.09 | 0.0918 | 0.0936 | 0.0954 | 0.0972 | 0.099 | 0.1008 | 0.1026 | 0.1044 | 0.1062 | 0.108 | 0.1098 | 0.1116 | 0.1134 | 0.1152 | 0.117 | 0.1188 | 0.1206 | 0.1224 | 0.1242 | 0.126 | 0.1278 | 0.1296 | 0.1314 | 0.1332 | 0.135 | 0.1368 | 0.1386 | 0.1404 | 0.1422 | 0.144 | 0.1458 | 0.1476 | 0.1494 | 0.1512 | 0.153 | 0.1548 | 0.1566 | 0.1584 | 0.1602 | 0.162 | 0.1638 | 0.1656 | 0.1674 | 0.1692 | 0.171 | 0.1728 | 0.1746 | 0.1764 | 0.1782 | 0.18 | 0.1818 | 0.1836 | 0.1854 | 0.1872 | 0.189 | 0.1908 | 0.1926 | 0.1944 | 0.1962 | 0.198 | 0.1998 | 0.2016 | 0.2034 | 0.2052 | 0.207 | 0.2088 | 0.2106 | 0.2124 | 0.2142 | 0.216 | 0.2166 | 0.2172 | 0.2178 | 0.2184 | 0.219 | 0.2196 | 0.2202 | 0.2208 | 0.2214 | 0.222 | 0.2226 | 0.2232 | 0.2238 | 0.2244 | 0.225 | 0.2256 | 0.2262 | 0.2268 | 0.2274 | 0.228 | 0.2286 | 0.2292 | 0.2298 | 0.2304 | 0.231 | 0.2316 | 0.2322 | 0.2328 | 0.2334 | 0.234
0.6 | 0 | 0.048 | 0.056 | 0.056 | 0.04 | 0.048 | 0.048 | 0.096 | 0.144 | 0.192 | 0.208 | 3.4694e-18 | 0.0048 | 0.0096 | 0.0144 | 0.0192 | 0.024 | 0.0288 | 0.0336 | 0.0384 | 0.0432 | 0.048 | 0.0496 | 0.0512 | 0.0528 | 0.0544 | 0.056 | 0.056 | 0.056 | 0.056 | 0.056 | 0.056 | 0.0544 | 0.0528 | 0.0512 | 0.0496 | 0.048 | 0.0464 | 0.0448 | 0.0432 | 0.0416 | 0.04 | 0.040533 | 0.041067 | 0.0416 | 0.042133 | 0.042667 | 0.0432 | 0.043733 | 0.044267 | 0.0448 | 0.045333 | 0.045867 | 0.0464 | 0.046933 | 0.047467 | 0.048 | 0.048 | 0.048 | 0.048 | 0.048 | 0.048 | 0.048 | 0.048 | 0.048 | 0.048 | 0.048 | 0.048 | 0.048 | 0.048 | 0.048 | 0.048 | 0.0496 | 0.0512 | 0.0528 | 0.0544 | 0.056 | 0.0576 | 0.0592 | 0.0608 | 0.0624 | 0.064 | 0.0656 | 0.0672 | 0.0688 | 0.0704 | 0.072 | 0.0736 | 0.0752 | 0.0768 | 0.0784 | 0.08 | 0.0816 | 0.0832 | 0.0848 | 0.0864 | 0.088 | 0.0896 | 0.0912 | 0.0928 | 0.0944 | 0.096 | 0.0976 | 0.0992 | 0.1008 | 0.1024 | 0.104 | 0.1056 | 0.1072 | 0.1088 | 0.1104 | 0.112 | 0.1136 | 0.1152 | 0.1168 | 0.1184 | 0.12 | 0.1216 | 0.1232 | 0.1248 | 0.1264 | 0.128 | 0.1296 | 0.1312 | 0.1328 | 0.1344 | 0.136 | 0.1376 | 0.1392 | 0.1408 | 0.1424 | 0.144 | 0.1456 | 0.1472 | 0.1488 | 0.1504 | 0.152 | 0.1536 | 0.1552 | 0.1568 | 0.1584 | 0.16 | 0.1616 | 0.1632 | 0.1648 | 0.1664 | 0.168 | 0.1696 | 0.1712 | 0.1728 | 0.1744 | 0.176 | 0.1776 | 0.1792 | 0.1808 | 0.1824 | 0.184 | 0.1856 | 0.1872 | 0.1888 | 0.1904 | 0.192 | 0.19253 | 0.19307 | 0.1936 | 0.19413 | 0.19467 | 0.1952 | 0.19573 | 0.19627 | 0.1968 | 0.19733 | 0.19787 | 0.1984 | 0.19893 | 0.19947 | 0.2 | 0.20053 | 0.20107 | 0.2016 | 0.20213 | 0.20267 | 0.2032 | 0.20373 | 0.20427 | 0.2048 | 0.20533 | 0.20587 | 0.2064 | 0.20693 | 0.20747 | 0.208
0.65 | 0 | 0.042 | 0.049 | 0.049 | 0.035 | 0.042 | 0.042 | 0.084 | 0.126 | 0.168 | 0.182 | 3.4694e-18 | 0.0042 | 0.0084 | 0.0126 | 0.0168 | 0.021 | 0.0252 | 0.0294 | 0.0336 | 0.0378 | 0.042 | 0.0434 | 0.0448 | 0.0462 | 0.0476 | 0.049 | 0.049 | 0.049 | 0.049 | 0.049 | 0.049 | 0.0476 | 0.0462 | 0.0448 | 0.0434 | 0.042 | 0.0406 | 0.0392 | 0.0378 | 0.0364 | 0.035 | 0.035467 | 0.035933 | 0.0364 | 0.036867 | 0.037333 | 0.0378 | 0.038267 | 0.038733 | 0.0392 | 0.039667 | 0.040133 | 0.0406 | 0.041067 | 0.041533 | 0.042 | 0.042 | 0.042 | 0.042 | 0.042 | 0.042 | 0.042 | 0.042 | 0.042 | 0.042 | 0.042 | 0.042 | 0.042 | 0.042 | 0.042 | 0.042 | 0.0434 | 0.0448 | 0.0462 | 0.0476 | 0.049 | 0.0504 | 0.0518 | 0.0532 | 0.0546 | 0.056 | 0.0574 | 0.0588 | 0.0602 | 0.0616 | 0.063 | 0.0644 | 0.0658 | 0.0672 | 0.0686 | 0.07 | 0.0714 | 0.0728 | 0.0742 | 0.0756 | 0.077 | 0.0784 | 0.0798 | 0.0812 | 0.0826 | 0.084 | 0.0854 | 0.0868 | 0.0882 | 0.0896 | 0.091 | 0.0924 | 0.0938 | 0.0952 | 0.0966 | 0.098 | 0.0994 | 0.1008 | 0.1022 | 0.1036 | 0.105 | 0.1064 | 0.1078 | 0.1092 | 0.1106 | 0.112 | 0.1134 | 0.1148 | 0.1162 | 0.1176 | 0.119 | 0.1204 | 0.1218 | 0.1232 | 0.1246 | 0.126 | 0.1274 | 0.1288 | 0.1302 | 0.1316 | 0.133 | 0.1344 | 0.1358 | 0.1372 | 0.1386 | 0.14 | 0.1414 | 0.1428 | 0.1442 | 0.1456 | 0.147 | 0.1484 | 0.1498 | 0.1512 | 0.1526 | 0.154 | 0.1554 | 0.1568 | 0.1582 | 0.1596 | 0.161 | 0.1624 | 0.1638 | 0.1652 | 0.1666 | 0.168 | 0.16847 | 0.16893 | 0.1694 | 0.16987 | 0.17033 | 0.1708 | 0.17127 | 0.17173 | 0.1722 | 0.17267 | 0.17313 | 0.1736 | 0.17407 | 0.17453 | 0.175 | 0.17547 | 0.17593 | 0.1764 | 0.17687 | 0.17733 | 0.1778 | 0.17827 | 0.17873 | 0.1792 | 0.17967 | 0.18013 | 0.1806 | 0.18107 | 0.18153 | 0.182
0.7 | 0 | 0.036 | 0.042 | 0.042 | 0.03 | 0.036 | 0.036 | 0.072 | 0.108 | 0.144 | 0.156 | 0 | 0.0036 | 0.0072 | 0.0108 | 0.0144 | 0.018 | 0.0216 | 0.0252 | 0.0288 | 0.0324 | 0.036 | 0.0372 | 0.0384 | 0.0396 | 0.0408 | 0.042 | 0.042 | 0.042 | 0.042 | 0.042 | 0.042 | 0.0408 | 0.0396 | 0.0384 | 0.0372 | 0.036 | 0.0348 | 0.0336 | 0.0324 | 0.0312 | 0.03 | 0.0304 | 0.0308 | 0.0312 | 0.0316 | 0.032 | 0.0324 | 0.0328 | 0.0332 | 0.0336 | 0.034 | 0.0344 | 0.0348 | 0.0352 | 0.0356 | 0.036 | 0.036 | 0.036 | 0.036 | 0.036 | 0.036 | 0.036 | 0.036 | 0.036 | 0.036 | 0.036 | 0.036 | 0.036 | 0.036 | 0.036 | 0.036 | 0.0372 | 0.0384 | 0.0396 | 0.0408 | 0.042 | 0.0432 | 0.0444 | 0.0456 | 0.0468 | 0.048 | 0.0492 | 0.0504 | 0.0516 | 0.0528 | 0.054 | 0.0552 | 0.0564 | 0.0576 | 0.0588 | 0.06 | 0.0612 | 0.0624 | 0.0636 | 0.0648 | 0.066 | 0.0672 | 0.0684 | 0.0696 | 0.0708 | 0.072 | 0.0732 | 0.0744 | 0.0756 | 0.0768 | 0.078 | 0.0792 | 0.0804 | 0.0816 | 0.0828 | 0.084 | 0.0852 | 0.0864 | 0.0876 | 0.0888 | 0.09 | 0.0912 | 0.0924 | 0.0936 | 0.0948 | 0.096 | 0.0972 | 0.0984 | 0.0996 | 0.1008 | 0.102 | 0.1032 | 0.1044 | 0.1056 | 0.1068 | 0.108 | 0.1092 | 0.1104 | 0.1116 | 0.1128 | 0.114 | 0.1152 | 0.1164 | 0.1176 | 0.1188 | 0.12 | 0.1212 | 0.1224 | 0.1236 | 0.1248 | 0.126 | 0.1272 | 0.1284 | 0.1296 | 0.1308 | 0.132 | 0.1332 | 0.1344 | 0.1356 | 0.1368 | 0.138 | 0.1392 | 0.1404 | 0.1416 | 0.1428 | 0.144 | 0.1444 | 0.1448 | 0.1452 | 0.1456 | 0.146 | 0.1464 | 0.1468 | 0.1472 | 0.1476 | 0.148 | 0.1484 | 0.1488 | 0.1492 | 0.1496 | 0.15 | 0.1504 | 0.1508 | 0.1512 | 0.1516 | 0.152 | 0.1524 | 0.1528 | 0.1532 | 0.1536 | 0.154 | 0.1544 | 0.1548 | 0.1552 | 0.1556 | 0.156
0.75 | 0 | 0.03 | 0.035 | 0.035 | 0.025 | 0.03 | 0.03 | 0.06 | 0.09 | 0.12 | 0.13 | 0 | 0.003 | 0.006 | 0.009 | 0.012 | 0.015 | 0.018 | 0.021 | 0.024 | 0.027 | 0.03 | 0.031 | 0.032 | 0.033 | 0.034 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035 | 0.034 | 0.033 | 0.032 | 0.031 | 0.03 | 0.029 | 0.028 | 0.027 | 0.026 | 0.025 | 0.025333 | 0.025667 | 0.026 | 0.026333 | 0.026667 | 0.027 | 0.027333 | 0.027667 | 0.028 | 0.028333 | 0.028667 | 0.029 | 0.029333 | 0.029667 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.031 | 0.032 | 0.033 | 0.034 | 0.035 | 0.036 | 0.037 | 0.038 | 0.039 | 0.04 | 0.041 | 0.042 | 0.043 | 0.044 | 0.045 | 0.046 | 0.047 | 0.048 | 0.049 | 0.05 | 0.051 | 0.052 | 0.053 | 0.054 | 0.055 | 0.056 | 0.057 | 0.058 | 0.059 | 0.06 | 0.061 | 0.062 | 0.063 | 0.064 | 0.065 | 0.066 | 0.067 | 0.068 | 0.069 | 0.07 | 0.071 | 0.072 | 0.073 | 0.074 | 0.075 | 0.076 | 0.077 | 0.078 | 0.079 | 0.08 | 0.081 | 0.082 | 0.083 | 0.084 | 0.085 | 0.086 | 0.087 | 0.088 | 0.089 | 0.09 | 0.091 | 0.092 | 0.093 | 0.094 | 0.095 | 0.096 | 0.097 | 0.098 | 0.099 | 0.1 | 0.101 | 0.102 | 0.103 | 0.104 | 0.105 | 0.106 | 0.107 | 0.108 | 0.109 | 0.11 | 0.111 | 0.112 | 0.113 | 0.114 | 0.115 | 0.116 | 0.117 | 0.118 | 0.119 | 0.12 | 0.12033 | 0.12067 | 0.121 | 0.12133 | 0.12167 | 0.122 | 0.12233 | 0.12267 | 0.123 | 0.12333 | 0.12367 | 0.124 | 0.12433 | 0.12467 | 0.125 | 0.12533 | 0.12567 | 0.126 | 0.12633 | 0.12667 | 0.127 | 0.12733 | 0.12767 | 0.128 | 0.12833 | 0.12867 | 0.129 | 0.12933 | 0.12967 | 0.13
0.8 | 0 | 0.024 | 0.028 | 0.028 | 0.02 | 0.024 | 0.024 | 0.048 | 0.072 | 0.096 | 0.104 | 0 | 0.0024 | 0.0048 | 0.0072 | 0.0096 | 0.012 | 0.0144 | 0.0168 | 0.0192 | 0.0216 | 0.024 | 0.0248 | 0.0256 | 0.0264 | 0.0272 | 0.028 | 0.028 | 0.028 | 0.028 | 0.028 | 0.028 | 0.0272 | 0.0264 | 0.0256 | 0.0248 | 0.024 | 0.0232 | 0.0224 | 0.0216 | 0.0208 | 0.02 | 0.020267 | 0.020533 | 0.0208 | 0.021067 | 0.021333 | 0.0216 | 0.021867 | 0.022133 | 0.0224 | 0.022667 | 0.022933 | 0.0232 | 0.023467 | 0.023733 | 0.024 | 0.024 | 0.024 | 0.024 | 0.024 | 0.024 | 0.024 | 0.024 | 0.024 | 0.024 | 0.024 | 0.024 | 0.024 | 0.024 | 0.024 | 0.024 | 0.0248 | 0.0256 | 0.0264 | 0.0272 | 0.028 | 0.0288 | 0.0296 | 0.0304 | 0.0312 | 0.032 | 0.0328 | 0.0336 | 0.0344 | 0.0352 | 0.036 | 0.0368 | 0.0376 | 0.0384 | 0.0392 | 0.04 | 0.0408 | 0.0416 | 0.0424 | 0.0432 | 0.044 | 0.0448 | 0.0456 | 0.0464 | 0.0472 | 0.048 | 0.0488 | 0.0496 | 0.0504 | 0.0512 | 0.052 | 0.0528 | 0.0536 | 0.0544 | 0.0552 | 0.056 | 0.0568 | 0.0576 | 0.0584 | 0.0592 | 0.06 | 0.0608 | 0.0616 | 0.0624 | 0.0632 | 0.064 | 0.0648 | 0.0656 | 0.0664 | 0.0672 | 0.068 | 0.0688 | 0.0696 | 0.0704 | 0.0712 | 0.072 | 0.0728 | 0.0736 | 0.0744 | 0.0752 | 0.076 | 0.0768 | 0.0776 | 0.0784 | 0.0792 | 0.08 | 0.0808 | 0.0816 | 0.0824 | 0.0832 | 0.084 | 0.0848 | 0.0856 | 0.0864 | 0.0872 | 0.088 | 0.0888 | 0.0896 | 0.0904 | 0.0912 | 0.092 | 0.0928 | 0.0936 | 0.0944 | 0.0952 | 0.096 | 0.096267 | 0.096533 | 0.0968 | 0.097067 | 0.097333 | 0.0976 | 0.097867 | 0.098133 | 0.0984 | 0.098667 | 0.098933 | 0.0992 | 0.099467 | 0.099733 | 0.1 | 0.10027 | 0.10053 | 0.1008 | 0.10107 | 0.10133 | 0.1016 | 0.10187 | 0.10213 | 0.1024 | 0.10267 | 0.10293 | 0.1032 | 0.10347 | 0.10373 | 0.104
0.85 | 0 | 0.018 | 0.021 | 0.021 | 0.015 | 0.018 | 0.018 | 0.036 | 0.054 | 0.072 | 0.078 | 0 | 0.0018 | 0.0036 | 0.0054 | 0.0072 | 0.009 | 0.0108 | 0.0126 | 0.0144 | 0.0162 | 0.018 | 0.0186 | 0.0192 | 0.0198 | 0.0204 | 0.021 | 0.021 | 0.021 | 0.021 | 0.021 | 0.021 | 0.0204 | 0.0198 | 0.0192 | 0.0186 | 0.018 | 0.0174 | 0.0168 | 0.0162 | 0.0156 | 0.015 | 0.0152 | 0.0154 | 0.0156 | 0.0158 | 0.016 | 0.0162 | 0.0164 | 0.0166 | 0.0168 | 0.017 | 0.0172 | 0.0174 | 0.0176 | 0.0178 | 0.018 | 0.018 | 0.018 | 0.018 | 0.018 | 0.018 | 0.018 | 0.018 | 0.018 | 0.018 | 0.018 | 0.018 | 0.018 | 0.018 | 0.018 | 0.018 | 0.0186 | 0.0192 | 0.0198 | 0.0204 | 0.021 | 0.0216 | 0.0222 | 0.0228 | 0.0234 | 0.024 | 0.0246 | 0.0252 | 0.0258 | 0.0264 | 0.027 | 0.0276 | 0.0282 | 0.0288 | 0.0294 | 0.03 | 0.0306 | 0.0312 | 0.0318 | 0.0324 | 0.033 | 0.0336 | 0.0342 | 0.0348 | 0.0354 | 0.036 | 0.0366 | 0.0372 | 0.0378 | 0.0384 | 0.039 | 0.0396 | 0.0402 | 0.0408 | 0.0414 | 0.042 | 0.0426 | 0.0432 | 0.0438 | 0.0444 | 0.045 | 0.0456 | 0.0462 | 0.0468 | 0.0474 | 0.048 | 0.0486 | 0.0492 | 0.0498 | 0.0504 | 0.051 | 0.0516 | 0.0522 | 0.0528 | 0.0534 | 0.054 | 0.0546 | 0.0552 | 0.0558 | 0.0564 | 0.057 | 0.0576 | 0.0582 | 0.0588 | 0.0594 | 0.06 | 0.0606 | 0.0612 | 0.0618 | 0.0624 | 0.063 | 0.0636 | 0.0642 | 0.0648 | 0.0654 | 0.066 | 0.0666 | 0.0672 | 0.0678 | 0.0684 | 0.069 | 0.0696 | 0.0702 | 0.0708 | 0.0714 | 0.072 | 0.0722 | 0.0724 | 0.0726 | 0.0728 | 0.073 | 0.0732 | 0.0734 | 0.0736 | 0.0738 | 0.074 | 0.0742 | 0.0744 | 0.0746 | 0.0748 | 0.075 | 0.0752 | 0.0754 | 0.0756 | 0.0758 | 0.076 | 0.0762 | 0.0764 | 0.0766 | 0.0768 | 0.077 | 0.0772 | 0.0774 | 0.0776 | 0.0778 | 0.078
0.9 | 0 | 0.012 | 0.014 | 0.014 | 0.01 | 0.012 | 0.012 | 0.024 | 0.036 | 0.048 | 0.052 | 0 | 0.0012 | 0.0024 | 0.0036 | 0.0048 | 0.006 | 0.0072 | 0.0084 | 0.0096 | 0.0108 | 0.012 | 0.0124 | 0.0128 | 0.0132 | 0.0136 | 0.014 | 0.014 | 0.014 | 0.014 | 0.014 | 0.014 | 0.0136 | 0.0132 | 0.0128 | 0.0124 | 0.012 | 0.0116 | 0.0112 | 0.0108 | 0.0104 | 0.01 | 0.010133 | 0.010267 | 0.0104 | 0.010533 | 0.010667 | 0.0108 | 0.010933 | 0.011067 | 0.0112 | 0.011333 | 0.011467 | 0.0116 | 0.011733 | 0.011867 | 0.012 | 0.012 | 0.012 | 0.012 | 0.012 | 0.012 | 0.012 | 0.012 | 0.012 | 0.012 | 0.012 | 0.012 | 0.012 | 0.012 | 0.012 | 0.012 | 0.0124 | 0.0128 | 0.0132 | 0.0136 | 0.014 | 0.0144 | 0.0148 | 0.0152 | 0.0156 | 0.016 | 0.0164 | 0.0168 | 0.0172 | 0.0176 | 0.018 | 0.0184 | 0.0188 | 0.0192 | 0.0196 | 0.02 | 0.0204 | 0.0208 | 0.0212 | 0.0216 | 0.022 | 0.0224 | 0.0228 | 0.0232 | 0.0236 | 0.024 | 0.0244 | 0.0248 | 0.0252 | 0.0256 | 0.026 | 0.0264 | 0.0268 | 0.0272 | 0.0276 | 0.028 | 0.0284 | 0.0288 | 0.0292 | 0.0296 | 0.03 | 0.0304 | 0.0308 | 0.0312 | 0.0316 | 0.032 | 0.0324 | 0.0328 | 0.0332 | 0.0336 | 0.034 | 0.0344 | 0.0348 | 0.0352 | 0.0356 | 0.036 | 0.0364 | 0.0368 | 0.0372 | 0.0376 | 0.038 | 0.0384 | 0.0388 | 0.0392 | 0.0396 | 0.04 | 0.0404 | 0.0408 | 0.0412 | 0.0416 | 0.042 | 0.0424 | 0.0428 | 0.0432 | 0.0436 | 0.044 | 0.0444 | 0.0448 | 0.0452 | 0.0456 | 0.046 | 0.0464 | 0.0468 | 0.0472 | 0.0476 | 0.048 | 0.048133 | 0.048267 | 0.0484 | 0.048533 | 0.048667 | 0.0488 | 0.048933 | 0.049067 | 0.0492 | 0.049333 | 0.049467 | 0.0496 | 0.049733 | 0.049867 | 0.05 | 0.050133 | 0.050267 | 0.0504 | 0.050533 | 0.050667 | 0.0508 | 0.050933 | 0.051067 | 0.0512 | 0.051333 | 0.051467 | 0.0516 | 0.051733 | 0.051867 | 0.052
0.95 | 0 | 0.006 | 0.007 | 0.007 | 0.005 | 0.006 | 0.006 | 0.012 | 0.018 | 0.024 | 0.026 | 0 | 0.0006 | 0.0012 | 0.0018 | 0.0024 | 0.003 | 0.0036 | 0.0042 | 0.0048 | 0.0054 | 0.006 | 0.0062 | 0.0064 | 0.0066 | 0.0068 | 0.007 | 0.007 | 0.007 | 0.007 | 0.007 | 0.007 | 0.0068 | 0.0066 | 0.0064 | 0.0062 | 0.006 | 0.0058 | 0.0056 | 0.0054 | 0.0052 | 0.005 | 0.0050667 | 0.0051333 | 0.0052 | 0.0052667 | 0.0053333 | 0.0054 | 0.0054667 | 0.0055333 | 0.0056 | 0.0056667 | 0.0057333 | 0.0058 | 0.0058667 | 0.0059333 | 0.006 | 0.006 | 0.006 | 0.006 | 0.006 | 0.006 | 0.006 | 0.006 | 0.006 | 0.006 | 0.006 | 0.006 | 0.006 | 0.006 | 0.006 | 0.006 | 0.0062 | 0.0064 | 0.0066 | 0.0068 | 0.007 | 0.0072 | 0.0074 | 0.0076 | 0.0078 | 0.008 | 0.0082 | 0.0084 | 0.0086 | 0.0088 | 0.009 | 0.0092 | 0.0094 | 0.0096 | 0.0098 | 0.01 | 0.0102 | 0.0104 | 0.0106 | 0.0108 | 0.011 | 0.0112 | 0.0114 | 0.0116 | 0.0118 | 0.012 | 0.0122 | 0.0124 | 0.0126 | 0.0128 | 0.013 | 0.0132 | 0.0134 | 0.0136 | 0.0138 | 0.014 | 0.0142 | 0.0144 | 0.0146 | 0.0148 | 0.015 | 0.0152 | 0.0154 | 0.0156 | 0.0158 | 0.016 | 0.0162 | 0.0164 | 0.0166 | 0.0168 | 0.017 | 0.0172 | 0.0174 | 0.0176 | 0.0178 | 0.018 | 0.0182 | 0.0184 | 0.0186 | 0.0188 | 0.019 | 0.0192 | 0.0194 | 0.0196 | 0.0198 | 0.02 | 0.0202 | 0.0204 | 0.0206 | 0.0208 | 0.021 | 0.0212 | 0.0214 | 0.0216 | 0.0218 | 0.022 | 0.0222 | 0.0224 | 0.0226 | 0.0228 | 0.023 | 0.0232 | 0.0234 | 0.0236 | 0.0238 | 0.024 | 0.024067 | 0.024133 | 0.0242 | 0.024267 | 0.024333 | 0.0244 | 0.024467 | 0.024533 | 0.0246 | 0.024667 | 0.024733 | 0.0248 | 0.024867 | 0.024933 | 0.025 | 0.025067 | 0.025133 | 0.0252 | 0.025267 | 0.025333 | 0.0254 | 0.025467 | 0.025533 | 0.0256 | 0.025667 | 0.025733 | 0.0258 | 0.025867 | 0.025933 | 0.026
1 | 0 | 1.1102e-16 | -1.1102e-16 | 0 | 2.2204e-16 | 2.2204e-16 | 2.2204e-16 | 2.2204e-16 | 2.2204e-16 | 2.2204e-16 | 2.2204e-16 | 0 | 1.1102e-17 | 2.2204e-17 | 3.3307e-17 | 4.4409e-17 | 5.5511e-17 | 6.6613e-17 | 7.7716e-17 | 8.8818e-17 | 9.992e-17 | 1.1102e-16 | 6.6613e-17 | 2.2204e-17 | -2.2204e-17 | -6.6613e-17 | -1.1102e-16 | -8.8818e-17 | -6.6613e-17 | -4.4409e-17 | -2.2204e-17 | 0 | 2.2204e-17 | 4.4409e-17 | 6.6613e-17 | 8.8818e-17 | 1.1102e-16 | 1.3323e-16 | 1.5543e-16 | 1.7764e-16 | 1.9984e-16 | 2.2204e-16 | 2.2204e-16 | 2.2204e-16 | 2.2204e-16 | 2.2204e-16 | 2.2204e-16 | 2.2204e-16 | 2.2204e-16 | 2.2204e-16 | 2.2204e-16 | 2.2204e-16 | 2.2204e-16 | 2.2204e-16 | 2.2204e-16 | 2.2204e-16 | 2.2204e-16 | 2.2204e-16 | 2.2204e-16 | 2.2204e-16 | 2.2204e-16 | 2.2204e-16 | 2.2204e-16 | 2.2204e-16 | 2.2204e-16 | 2.2204e-16 | 2.2204e-16 | 2.2204e-16 | 2.2204e-16 | 2.2204e-16 | 2.2204e-16 | 2.2204e-16 | 2.2204e-16 | 2.2204e-16 | 2.2204e-16 | 2.2204e-16 | 2.2204e-16 | 2.2204e-16 | 2.2204e-16 | 2.2204e-16 | 2.2204e-16 | 2.2204e-16 | 2.2204e-16 | 2.2204e-16 | 2.2204e-16 | 2.2204e-16 | 2.2204e-16 | 2.2204e-16 | 2.2204e-16 | 2.2204e-16 | 2.2204e-16 | 2.2204e-16 | 2.2204e-16 | 2.2204e-16 | 2.2204e-16 | 2.2204e-16 | 2.2204e-16 | 2.2204e-16 | 2.2204e-16 | 2.2204e-16 | 2.2204e-16 | 2.2204e-16 | 2.2204e-16 | 2.2204e-16 | 2.2204e-16 | 2.2204e-16 | 2.2204e-16 | 2.2204e-16 | 2.2204e-16 | 2.2204e-16 | 2.2204e-16 | 2.2204e-16 | 2.2204e-16 | 2.2204e-16 | 2.2204e-16 | 2.2204e-16 | 2.2204e-16 | 2.2204e-16 | 2.2204e-16 | 2.2204e-16 | 2.2204e-16 | 2.2204e-16 | 2.2204e-16 | 2.2204e-16 | 2.2204e-16 | 2.2204e-16 | 2.2204e-16 | 2.2204e-16 | 2.2204e-16 | 2.2204e-16 | 2.2204e-16 | 2.2204e-16 | 2.2204e-16 | 2.2204e-16 | 2.2204e-16 | 2.2204e-16 | 2.2204e-16 | 2.2204e-16 | 2.2204e-16 | 2.2204e-16 | 2.2204e-16 | 2.2204e-16 | 2.2204e-16 | 2.2204e-16 | 2.2204e-16 | 2.2204e-16 | 2.2204e-16 | 2.2204e-16 | 2.2204e-16 | 2.2204e-16 | 2.2204e-16 | 2.2204e-16 | 2.2204e-16 | 2.2204e-16 | 2.2204e-16 | 2.2204e-16 | 2.2204e-16 | 2.2204e-16 | 2.2204e-16 | 2.2204e-16 | 2.2204e-16 | 2.2204e-16 | 2.2204e-16 | 2.2204e-16 | 2.2204e-16 | 2.2204e-16 | 2.2204e-16 | 2.2204e-16 | 2.2204e-16 | 2.2204e-16 | 2.2204e-16 | 2.2204e-16 | 2.2204e-16 | 2.2204e-16 | 2.2204e-16 | 2.2204e-16 | 2.2204e-16 | 2.2204e-16 | 2.2204e-16 | 2.2204e-16 | 2.2204e-16 | 2.2204e-16 | 2.2204e-16 | 2.2204e-16 | 2.2204e-16 | 2.2204e-16 | 2.2204e-16 | 2.2204e-16 | 2.2204e-16 | 2.2204e-16 | 2.2204e-16 | 2.2204e-16
1.05 | 0 | 0.03 | 0.042 | 0.05 | 0.06 | 0.066 | 0.066 | 0.066 | 0.064 | 0.062 | 0.06 | 0 | 0.003 | 0.006 | 0.009 | 0.012 | 0.015 | 0.018 | 0.021 | 0.024 | 0.027 | 0.03 | 0.0324 | 0.0348 | 0.0372 | 0.0396 | 0.042 | 0.0436 | 0.0452 | 0.0468 | 0.0484 | 0.05 | 0.051 | 0.052 | 0.053 | 0.054 | 0.055 | 0.056 | 0.057 | 0.058 | 0.059 | 0.06 | 0.0604 | 0.0608 | 0.0612 | 0.0616 | 0.062 | 0.0624 | 0.0628 | 0.0632 | 0.0636 | 0.064 | 0.0644 | 0.0648 | 0.0652 | 0.0656 | 0.066 | 0.066 | 0.066 | 0.066 | 0.066 | 0.066 | 0.066 | 0.066 | 0.066 | 0.066 | 0.066 | 0.066 | 0.066 | 0.066 | 0.066 | 0.066 | 0.066 | 0.066 | 0.066 | 0.066 | 0.066 | 0.066 | 0.066 | 0.066 | 0.066 | 0.066 | 0.066 | 0.066 | 0.066 | 0.066 | 0.066 | 0.066 | 0.066 | 0.066 | 0.066 | 0.066 | 0.066 | 0.066 | 0.066 | 0.066 | 0.066 | 0.066 | 0.066 | 0.066 | 0.066 | 0.066 | 0.065933 | 0.065867 | 0.0658 | 0.065733 | 0.065667 | 0.0656 | 0.065533 | 0.065467 | 0.0654 | 0.065333 | 0.065267 | 0.0652 | 0.065133 | 0.065067 | 0.065 | 0.064933 | 0.064867 | 0.0648 | 0.064733 | 0.064667 | 0.0646 | 0.064533 | 0.064467 | 0.0644 | 0.064333 | 0.064267 | 0.0642 | 0.064133 | 0.064067 | 0.064 | 0.063933 | 0.063867 | 0.0638 | 0.063733 | 0.063667 | 0.0636 | 0.063533 | 0.063467 | 0.0634 | 0.063333 | 0.063267 | 0.0632 | 0.063133 | 0.063067 | 0.063 | 0.062933 | 0.062867 | 0.0628 | 0.062733 | 0.062667 | 0.0626 | 0.062533 | 0.062467 | 0.0624 | 0.062333 | 0.062267 | 0.0622 | 0.062133 | 0.062067 | 0.062 | 0.061933 | 0.061867 | 0.0618 | 0.061733 | 0.061667 | 0.0616 | 0.061533 | 0.061467 | 0.0614 | 0.061333 | 0.061267 | 0.0612 | 0.061133 | 0.061067 | 0.061 | 0.060933 | 0.060867 | 0.0608 | 0.060733 | 0.060667 | 0.0606 | 0.060533 | 0.060467 | 0.0604 | 0.060333 | 0.060267 | 0.0602 | 0.060133 | 0.060067 | 0.06
1.1 | 0 | 0.06 | 0.084 | 0.1 | 0.12 | 0.132 | 0.132 | 0.132 | 0.128 | 0.124 | 0.12 | 0 | 0.006 | 0.012 | 0.018 | 0.024 | 0.03 | 0.036 | 0.042 | 0.048 | 0.054 | 0.06 | 0.0648 | 0.0696 | 0.0744 | 0.0792 | 0.084 | 0.0872 | 0.0904 | 0.0936 | 0.0968 | 0.1 | 0.102 | 0.104 | 0.106 | 0.108 | 0.11 | 0.112 | 0.114 | 0.116 | 0.118 | 0.12 | 0.1208 | 0.1216 | 0.1224 | 0.1232 | 0.124 | 0.1248 | 0.1256 | 0.1264 | 0.1272 | 0.128 | 0.1288 | 0.1296 | 0.1304 | 0.1312 | 0.132 | 0.132 | 0.132 | 0.132 | 0.132 | 0.132 | 0.132 | 0.132 | 0.132 | 0.132 | 0.132 | 0.132 | 0.132 | 0.132 | 0.132 | 0.132 | 0.132 | 0.132 | 0.132 | 0.132 | 0.132 | 0.132 | 0.132 | 0.132 | 0.132 | 0.132 | 0.132 | 0.132 | 0.132 | 0.132 | 0.132 | 0.132 | 0.132 | 0.132 | 0.132 | 0.132 | 0.132 | 0.132 | 0.132 | 0.132 | 0.132 | 0.132 | 0.132 | 0.132 | 0.132 | 0.132 | 0.13187 | 0.13173 | 0.1316 | 0.13147 | 0.13133 | 0.1312 | 0.13107 | 0.13093 | 0.1308 | 0.13067 | 0.13053 | 0.1304 | 0.13027 | 0.13013 | 0.13 | 0.12987 | 0.12973 | 0.1296 | 0.12947 | 0.12933 | 0.1292 | 0.12907 | 0.12893 | 0.1288 | 0.12867 | 0.12853 | 0.1284 | 0.12827 | 0.12813 | 0.128 | 0.12787 | 0.12773 | 0.1276 | 0.12747 | 0.12733 | 0.1272 | 0.12707 | 0.12693 | 0.1268 | 0.12667 | 0.12653 | 0.1264 | 0.12627 | 0.12613 | 0.126 | 0.12587 | 0.12573 | 0.1256 | 0.12547 | 0.12533 | 0.1252 | 0.12507 | 0.12493 | 0.1248 | 0.12467 | 0.12453 | 0.1244 | 0.12427 | 0.12413 | 0.124 | 0.12387 | 0.12373 | 0.1236 | 0.12347 | 0.12333 | 0.1232 | 0.12307 | 0.12293 | 0.1228 | 0.12267 | 0.12253 | 0.1224 | 0.12227 | 0.12213 | 0.122 | 0.12187 | 0.12173 | 0.1216 | 0.12147 | 0.12133 | 0.1212 | 0.12107 | 0.12093 | 0.1208 | 0.12067 | 0.12053 | 0.1204 | 0.12027 | 0.12013 | 0.12
1.15 | 0 | 0.09 | 0.126 | 0.15 | 0.18 | 0.198 | 0.198 | 0.198 | 0.192 | 0.186 | 0.18 | 0 | 0.009 | 0.018 | 0.027 | 0.036 | 0.045 | 0.054 | 0.063 | 0.072 | 0.081 | 0.09 | 0.0972 | 0.1044 | 0.1116 | 0.1188 | 0.126 | 0.1308 | 0.1356 | 0.1404 | 0.1452 | 0.15 | 0.153 | 0.156 | 0.159 | 0.162 | 0.165 | 0.168 | 0.171 | 0.174 | 0.177 | 0.18 | 0.1812 | 0.1824 | 0.1836 | 0.1848 | 0.186 | 0.1872 | 0.1884 | 0.1896 | 0.1908 | 0.192 | 0.1932 | 0.1944 | 0.1956 | 0.1968 | 0.198 | 0.198 | 0.198 | 0.198 | 0.198 | 0.198 | 0.198 | 0.198 | 0.198 | 0.198 | 0.198 | 0.198 | 0.198 | 0.198 | 0.198 | 0.198 | 0.198 | 0.198 | 0.198 | 0.198 | 0.198 | 0.198 | 0.198 | 0.198 | 0.198 | 0.198 | 0.198 | 0.198 | 0.198 | 0.198 | 0.198 | 0.198 | 0.198 | 0.198 | 0.198 | 0.198 | 0.198 | 0.198 | 0.198 | 0.198 | 0.198 | 0.198 | 0.198 | 0.198 | 0.198 | 0.198 | 0.1978 | 0.1976 | 0.1974 | 0.1972 | 0.197 | 0.1968 | 0.1966 | 0.1964 | 0.1962 | 0.196 | 0.1958 | 0.1956 | 0.1954 | 0.1952 | 0.195 | 0.1948 | 0.1946 | 0.1944 | 0.1942 | 0.194 | 0.1938 | 0.1936 | 0.1934 | 0.1932 | 0.193 | 0.1928 | 0.1926 | 0.1924 | 0.1922 | 0.192 | 0.1918 | 0.1916 | 0.1914 | 0.1912 | 0.191 | 0.1908 | 0.1906 | 0.1904 | 0.1902 | 0.19 | 0.1898 | 0.1896 | 0.1894 | 0.1892 | 0.189 | 0.1888 | 0.1886 | 0.1884 | 0.1882 | 0.188 | 0.1878 | 0.1876 | 0.1874 | 0.1872 | 0.187 | 0.1868 | 0.1866 | 0.1864 | 0.1862 | 0.186 | 0.1858 | 0.1856 | 0.1854 | 0.1852 | 0.185 | 0.1848 | 0.1846 | 0.1844 | 0.1842 | 0.184 | 0.1838 | 0.1836 | 0.1834 | 0.1832 | 0.183 | 0.1828 | 0.1826 | 0.1824 | 0.1822 | 0.182 | 0.1818 | 0.1816 | 0.1814 | 0.1812 | 0.181 | 0.1808 | 0.1806 | 0.1804 | 0.1802 | 0.18
1.2 | 0 | 0.12 | 0.168 | 0.2 | 0.24 | 0.264 | 0.264 | 0.264 | 0.256 | 0.248 | 0.24 | 0 | 0.012 | 0.024 | 0.036 | 0.048 | 0.06 | 0.072 | 0.084 | 0.096 | 0.108 | 0.12 | 0.1296 | 0.1392 | 0.1488 | 0.1584 | 0.168 | 0.1744 | 0.1808 | 0.1872 | 0.1936 | 0.2 | 0.204 | 0.208 | 0.212 | 0.216 | 0.22 | 0.224 | 0.228 | 0.232 | 0.236 | 0.24 | 0.2416 | 0.2432 | 0.2448 | 0.2464 | 0.248 | 0.2496 | 0.2512 | 0.2528 | 0.2544 | 0.256 | 0.2576 | 0.2592 | 0.2608 | 0.2624 | 0.264 | 0.264 | 0.264 | 0.264 | 0.264 | 0.264 | 0.264 | 0.264 | 0.264 | 0.264 | 0.264 | 0.264 | 0.264 | 0.264 | 0.264 | 0.264 | 0.264 | 0.264 | 0.264 | 0.264 | 0.264 | 0.264 | 0.264 | 0.264 | 0.264 | 0.264 | 0.264 | 0.264 | 0.264 | 0.264 | 0.264 | 0.264 | 0.264 | 0.264 | 0.264 | 0.264 | 0.264 | 0.264 | 0.264 | 0.264 | 0.264 | 0.264 | 0.264 | 0.264 | 0.264 | 0.264 | 0.26373 | 0.26347 | 0.2632 | 0.26293 | 0.26267 | 0.2624 | 0.26213 | 0.26187 | 0.2616 | 0.26133 | 0.26107 | 0.2608 | 0.26053 | 0.26027 | 0.26 | 0.25973 | 0.25947 | 0.2592 | 0.25893 | 0.25867 | 0.2584 | 0.25813 | 0.25787 | 0.2576 | 0.25733 | 0.25707 | 0.2568 | 0.25653 | 0.25627 | 0.256 | 0.25573 | 0.25547 | 0.2552 | 0.25493 | 0.25467 | 0.2544 | 0.25413 | 0.25387 | 0.2536 | 0.25333 | 0.25307 | 0.2528 | 0.25253 | 0.25227 | 0.252 | 0.25173 | 0.25147 | 0.2512 | 0.25093 | 0.25067 | 0.2504 | 0.25013 | 0.24987 | 0.2496 | 0.24933 | 0.24907 | 0.2488 | 0.24853 | 0.24827 | 0.248 | 0.24773 | 0.24747 | 0.2472 | 0.24693 | 0.24667 | 0.2464 | 0.24613 | 0.24587 | 0.2456 | 0.24533 | 0.24507 | 0.2448 | 0.24453 | 0.24427 | 0.244 | 0.24373 | 0.24347 | 0.2432 | 0.24293 | 0.24267 | 0.2424 | 0.24213 | 0.24187 | 0.2416 | 0.24133 | 0.24107 | 0.2408 | 0.24053 | 0.24027 | 0.24
1.25 | 0 | 0.15 | 0.21 | 0.25 | 0.3 | 0.33 | 0.33 | 0.33 | 0.32 | 0.31 | 0.3 | 0 | 0.015 | 0.03 | 0.045 | 0.06 | 0.075 | 0.09 | 0.105 | 0.12 | 0.135 | 0.15 | 0.162 | 0.174 | 0.186 | 0.198 | 0.21 | 0.218 | 0.226 | 0.234 | 0.242 | 0.25 | 0.255 | 0.26 | 0.265 | 0.27 | 0.275 | 0.28 | 0.285 | 0.29 | 0.295 | 0.3 | 0.302 | 0.304 | 0.306 | 0.308 | 0.31 | 0.312 | 0.314 | 0.316 | 0.318 | 0.32 | 0.322 | 0.324 | 0.326 | 0.328 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.32967 | 0.32933 | 0.329 | 0.32867 | 0.32833 | 0.328 | 0.32767 | 0.32733 | 0.327 | 0.32667 | 0.32633 | 0.326 | 0.32567 | 0.32533 | 0.325 | 0.32467 | 0.32433 | 0.324 | 0.32367 | 0.32333 | 0.323 | 0.32267 | 0.32233 | 0.322 | 0.32167 | 0.32133 | 0.321 | 0.32067 | 0.32033 | 0.32 | 0.31967 | 0.31933 | 0.319 | 0.31867 | 0.31833 | 0.318 | 0.31767 | 0.31733 | 0.317 | 0.31667 | 0.31633 | 0.316 | 0.31567 | 0.31533 | 0.315 | 0.31467 | 0.31433 | 0.314 | 0.31367 | 0.31333 | 0.313 | 0.31267 | 0.31233 | 0.312 | 0.31167 | 0.31133 | 0.311 | 0.31067 | 0.31033 | 0.31 | 0.30967 | 0.30933 | 0.309 | 0.30867 | 0.30833 | 0.308 | 0.30767 | 0.30733 | 0.307 | 0.30667 | 0.30633 | 0.306 | 0.30567 | 0.30533 | 0.305 | 0.30467 | 0.30433 | 0.304 | 0.30367 | 0.30333 | 0.303 | 0.30267 | 0.30233 | 0.302 | 0.30167 | 0.30133 | 0.301 | 0.30067 | 0.30033 | 0.3
1.3 | 0 | 0.18 | 0.252 | 0.3 | 0.36 | 0.396 | 0.396 | 0.396 | 0.384 | 0.372 | 0.36 | 0 | 0.018 | 0.036 | 0.054 | 0.072 | 0.09 | 0.108 | 0.126 | 0.144 | 0.162 | 0.18 | 0.1944 | 0.2088 | 0.2232 | 0.2376 | 0.252 | 0.2616 | 0.2712 | 0.2808 | 0.2904 | 0.3 | 0.306 | 0.312 | 0.318 | 0.324 | 0.33 | 0.336 | 0.342 | 0.348 | 0.354 | 0.36 | 0.3624 | 0.3648 | 0.3672 | 0.3696 | 0.372 | 0.3744 | 0.3768 | 0.3792 | 0.3816 | 0.384 | 0.3864 | 0.3888 | 0.3912 | 0.3936 | 0.396 | 0.396 | 0.396 | 0.396 | 0.396 | 0.396 | 0.396 | 0.396 | 0.396 | 0.396 | 0.396 | 0.396 | 0.396 | 0.396 | 0.396 | 0.396 | 0.396 | 0.396 | 0.396 | 0.396 | 0.396 | 0.396 | 0.396 | 0.396 | 0.396 | 0.396 | 0.396 | 0.396 | 0.396 | 0.396 | 0.396 | 0.396 | 0.396 | 0.396 | 0.396 | 0.396 | 0.396 | 0.396 | 0.396 | 0.396 | 0.396 | 0.396 | 0.396 | 0.396 | 0.396 | 0.396 | 0.3956 | 0.3952 | 0.3948 | 0.3944 | 0.394 | 0.3936 | 0.3932 | 0.3928 | 0.3924 | 0.392 | 0.3916 | 0.3912 | 0.3908 | 0.3904 | 0.39 | 0.3896 | 0.3892 | 0.3888 | 0.3884 | 0.388 | 0.3876 | 0.3872 | 0.3868 | 0.3864 | 0.386 | 0.3856 | 0.3852 | 0.3848 | 0.3844 | 0.384 | 0.3836 | 0.3832 | 0.3828 | 0.3824 | 0.382 | 0.3816 | 0.3812 | 0.3808 | 0.3804 | 0.38 | 0.3796 | 0.3792 | 0.3788 | 0.3784 | 0.378 | 0.3776 | 0.3772 | 0.3768 | 0.3764 | 0.376 | 0.3756 | 0.3752 | 0.3748 | 0.3744 | 0.374 | 0.3736 | 0.3732 | 0.3728 | 0.3724 | 0.372 | 0.3716 | 0.3712 | 0.3708 | 0.3704 | 0.37 | 0.3696 | 0.3692 | 0.3688 | 0.3684 | 0.368 | 0.3676 | 0.3672 | 0.3668 | 0.3664 | 0.366 | 0.3656 | 0.3652 | 0.3648 | 0.3644 | 0.364 | 0.3636 | 0.3632 | 0.3628 | 0.3624 | 0.362 | 0.3616 | 0.3612 | 0.3608 | 0.3604 | 0.36
1.35 | 0 | 0.21 | 0.294 | 0.35 | 0.42 | 0.462 | 0.462 | 0.462 | 0.448 | 0.434 | 0.42 | 0 | 0.021 | 0.042 | 0.063 | 0.084 | 0.105 | 0.126 | 0.147 | 0.168 | 0.189 | 0.21 | 0.2268 | 0.2436 | 0.2604 | 0.2772 | 0.294 | 0.3052 | 0.3164 | 0.3276 | 0.3388 | 0.35 | 0.357 | 0.364 | 0.371 | 0.378 | 0.385 | 0.392 | 0.399 | 0.406 | 0.413 | 0.42 | 0.4228 | 0.4256 | 0.4284 | 0.4312 | 0.434 | 0.4368 | 0.4396 | 0.4424 | 0.4452 | 0.448 | 0.4508 | 0.4536 | 0.4564 | 0.4592 | 0.462 | 0.462 | 0.462 | 0.462 | 0.462 | 0.462 | 0.462 | 0.462 | 0.462 | 0.462 | 0.462 | 0.462 | 0.462 | 0.462 | 0.462 | 0.462 | 0.462 | 0.462 | 0.462 | 0.462 | 0.462 | 0.462 | 0.462 | 0.462 | 0.462 | 0.462 | 0.462 | 0.462 | 0.462 | 0.462 | 0.462 | 0.462 | 0.462 | 0.462 | 0.462 | 0.462 | 0.462 | 0.462 | 0.462 | 0.462 | 0.462 | 0.462 | 0.462 | 0.462 | 0.462 | 0.462 | 0.46153 | 0.46107 | 0.4606 | 0.46013 | 0.45967 | 0.4592 | 0.45873 | 0.45827 | 0.4578 | 0.45733 | 0.45687 | 0.4564 | 0.45593 | 0.45547 | 0.455 | 0.45453 | 0.45407 | 0.4536 | 0.45313 | 0.45267 | 0.4522 | 0.45173 | 0.45127 | 0.4508 | 0.45033 | 0.44987 | 0.4494 | 0.44893 | 0.44847 | 0.448 | 0.44753 | 0.44707 | 0.4466 | 0.44613 | 0.44567 | 0.4452 | 0.44473 | 0.44427 | 0.4438 | 0.44333 | 0.44287 | 0.4424 | 0.44193 | 0.44147 | 0.441 | 0.44053 | 0.44007 | 0.4396 | 0.43913 | 0.43867 | 0.4382 | 0.43773 | 0.43727 | 0.4368 | 0.43633 | 0.43587 | 0.4354 | 0.43493 | 0.43447 | 0.434 | 0.43353 | 0.43307 | 0.4326 | 0.43213 | 0.43167 | 0.4312 | 0.43073 | 0.43027 | 0.4298 | 0.42933 | 0.42887 | 0.4284 | 0.42793 | 0.42747 | 0.427 | 0.42653 | 0.42607 | 0.4256 | 0.42513 | 0.42467 | 0.4242 | 0.42373 | 0.42327 | 0.4228 | 0.42233 | 0.42187 | 0.4214 | 0.42093 | 0.42047 | 0.42
1.4 | 0 | 0.24 | 0.336 | 0.4 | 0.48 | 0.528 | 0.528 | 0.528 | 0.512 | 0.496 | 0.48 | 0 | 0.024 | 0.048 | 0.072 | 0.096 | 0.12 | 0.144 | 0.168 | 0.192 | 0.216 | 0.24 | 0.2592 | 0.2784 | 0.2976 | 0.3168 | 0.336 | 0.3488 | 0.3616 | 0.3744 | 0.3872 | 0.4 | 0.408 | 0.416 | 0.424 | 0.432 | 0.44 | 0.448 | 0.456 | 0.464 | 0.472 | 0.48 | 0.4832 | 0.4864 | 0.4896 | 0.4928 | 0.496 | 0.4992 | 0.5024 | 0.5056 | 0.5088 | 0.512 | 0.5152 | 0.5184 | 0.5216 | 0.5248 | 0.528 | 0.528 | 0.528 | 0.528 | 0.528 | 0.528 | 0.528 | 0.528 | 0.528 | 0.528 | 0.528 | 0.528 | 0.528 | 0.528 | 0.528 | 0.528 | 0.528 | 0.528 | 0.528 | 0.528 | 0.528 | 0.528 | 0.528 | 0.528 | 0.528 | 0.528 | 0.528 | 0.528 | 0.528 | 0.528 | 0.528 | 0.528 | 0.528 | 0.528 | 0.528 | 0.528 | 0.528 | 0.528 | 0.528 | 0.528 | 0.528 | 0.528 | 0.528 | 0.528 | 0.528 | 0.528 | 0.52747 | 0.52693 | 0.5264 | 0.52587 | 0.52533 | 0.5248 | 0.52427 | 0.52373 | 0.5232 | 0.52267 | 0.52213 | 0.5216 | 0.52107 | 0.52053 | 0.52 | 0.51947 | 0.51893 | 0.5184 | 0.51787 | 0.51733 | 0.5168 | 0.51627 | 0.51573 | 0.5152 | 0.51467 | 0.51413 | 0.5136 | 0.51307 | 0.51253 | 0.512 | 0.51147 | 0.51093 | 0.5104 | 0.50987 | 0.50933 | 0.5088 | 0.50827 | 0.50773 | 0.5072 | 0.50667 | 0.50613 | 0.5056 | 0.50507 | 0.50453 | 0.504 | 0.50347 | 0.50293 | 0.5024 | 0.50187 | 0.50133 | 0.5008 | 0.50027 | 0.49973 | 0.4992 | 0.49867 | 0.49813 | 0.4976 | 0.49707 | 0.49653 | 0.496 | 0.49547 | 0.49493 | 0.4944 | 0.49387 | 0.49333 | 0.4928 | 0.49227 | 0.49173 | 0.4912 | 0.49067 | 0.49013 | 0.4896 | 0.48907 | 0.48853 | 0.488 | 0.48747 | 0.48693 | 0.4864 | 0.48587 | 0.48533 | 0.4848 | 0.48427 | 0.48373 | 0.4832 | 0.48267 | 0.48213 | 0.4816 | 0.48107 | 0.48053 | 0.48
1.45 | 0 | 0.27 | 0.378 | 0.45 | 0.54 | 0.594 | 0.594 | 0.594 | 0.576 | 0.558 | 0.54 | 0 | 0.027 | 0.054 | 0.081 | 0.108 | 0.135 | 0.162 | 0.189 | 0.216 | 0.243 | 0.27 | 0.2916 | 0.3132 | 0.3348 | 0.3564 | 0.378 | 0.3924 | 0.4068 | 0.4212 | 0.4356 | 0.45 | 0.459 | 0.468 | 0.477 | 0.486 | 0.495 | 0.504 | 0.513 | 0.522 | 0.531 | 0.54 | 0.5436 | 0.5472 | 0.5508 | 0.5544 | 0.558 | 0.5616 | 0.5652 | 0.5688 | 0.5724 | 0.576 | 0.5796 | 0.5832 | 0.5868 | 0.5904 | 0.594 | 0.594 | 0.594 | 0.594 | 0.594 | 0.594 | 0.594 | 0.594 | 0.594 | 0.594 | 0.594 | 0.594 | 0.594 | 0.594 | 0.594 | 0.594 | 0.594 | 0.594 | 0.594 | 0.594 | 0.594 | 0.594 | 0.594 | 0.594 | 0.594 | 0.594 | 0.594 | 0.594 | 0.594 | 0.594 | 0.594 | 0.594 | 0.594 | 0.594 | 0.594 | 0.594 | 0.594 | 0.594 | 0.594 | 0.594 | 0.594 | 0.594 | 0.594 | 0.594 | 0.594 | 0.594 | 0.5934 | 0.5928 | 0.5922 | 0.5916 | 0.591 | 0.5904 | 0.5898 | 0.5892 | 0.5886 | 0.588 | 0.5874 | 0.5868 | 0.5862 | 0.5856 | 0.585 | 0.5844 | 0.5838 | 0.5832 | 0.5826 | 0.582 | 0.5814 | 0.5808 | 0.5802 | 0.5796 | 0.579 | 0.5784 | 0.5778 | 0.5772 | 0.5766 | 0.576 | 0.5754 | 0.5748 | 0.5742 | 0.5736 | 0.573 | 0.5724 | 0.5718 | 0.5712 | 0.5706 | 0.57 | 0.5694 | 0.5688 | 0.5682 | 0.5676 | 0.567 | 0.5664 | 0.5658 | 0.5652 | 0.5646 | 0.564 | 0.5634 | 0.5628 | 0.5622 | 0.5616 | 0.561 | 0.5604 | 0.5598 | 0.5592 | 0.5586 | 0.558 | 0.5574 | 0.5568 | 0.5562 | 0.5556 | 0.555 | 0.5544 | 0.5538 | 0.5532 | 0.5526 | 0.552 | 0.5514 | 0.5508 | 0.5502 | 0.5496 | 0.549 | 0.5484 | 0.5478 | 0.5472 | 0.5466 | 0.546 | 0.5454 | 0.5448 | 0.5442 | 0.5436 | 0.543 | 0.5424 | 0.5418 | 0.5412 | 0.5406 | 0.54
1.5 | 0 | 0.3 | 0.42 | 0.5 | 0.6 | 0.66 | 0.66 | 0.66 | 0.64 | 0.62 | 0.6 | 0 | 0.03 | 0.06 | 0.09 | 0.12 | 0.15 | 0.18 | 0.21 | 0.24 | 0.27 | 0.3 | 0.324 | 0.348 | 0.372 | 0.396 | 0.42 | 0.436 | 0.452 | 0.468 | 0.484 | 0.5 | 0.51 | 0.52 | 0.53 | 0.54 | 0.55 | 0.56 | 0.57 | 0.58 | 0.59 | 0.6 | 0.604 | 0.608 | 0.612 | 0.616 | 0.62 | 0.624 | 0.628 | 0.632 | 0.636 | 0.64 | 0.644 | 0.648 | 0.652 | 0.656 | 0.66 | 0.66 | 0.66 | 0.66 | 0.66 | 0.66 | 0.66 | 0.66 | 0.66 | 0.66 | 0.66 | 0.66 | 0.66 | 0.66 | 0.66 | 0.66 | 0.66 | 0.66 | 0.66 | 0.66 | 0.66 | 0.66 | 0.66 | 0.66 | 0.66 | 0.66 | 0.66 | 0.66 | 0.66 | 0.66 | 0.66 | 0.66 | 0.66 | 0.66 | 0.66 | 0.66 | 0.66 | 0.66 | 0.66 | 0.66 | 0.66 | 0.66 | 0.66 | 0.66 | 0.66 | 0.66 | 0.65933 | 0.65867 | 0.658 | 0.65733 | 0.65667 | 0.656 | 0.65533 | 0.65467 | 0.654 | 0.65333 | 0.65267 | 0.652 | 0.65133 | 0.65067 | 0.65 | 0.64933 | 0.64867 | 0.648 | 0.64733 | 0.64667 | 0.646 | 0.64533 | 0.64467 | 0.644 | 0.64333 | 0.64267 | 0.642 | 0.64133 | 0.64067 | 0.64 | 0.63933 | 0.63867 | 0.638 | 0.63733 | 0.63667 | 0.636 | 0.63533 | 0.63467 | 0.634 | 0.63333 | 0.63267 | 0.632 | 0.63133 | 0.63067 | 0.63 | 0.62933 | 0.62867 | 0.628 | 0.62733 | 0.62667 | 0.626 | 0.62533 | 0.62467 | 0.624 | 0.62333 | 0.62267 | 0.622 | 0.62133 | 0.62067 | 0.62 | 0.61933 | 0.61867 | 0.618 | 0.61733 | 0.61667 | 0.616 | 0.61533 | 0.61467 | 0.614 | 0.61333 | 0.61267 | 0.612 | 0.61133 | 0.61067 | 0.61 | 0.60933 | 0.60867 | 0.608 | 0.60733 | 0.60667 | 0.606 | 0.60533 | 0.60467 | 0.604 | 0.60333 | 0.60267 | 0.602 | 0.60133 | 0.60067 | 0.6
1.55 | 0 | 0.33 | 0.462 | 0.55 | 0.66 | 0.726 | 0.726 | 0.726 | 0.704 | 0.682 | 0.66 | 0 | 0.033 | 0.066 | 0.099 | 0.132 | 0.165 | 0.198 | 0.231 | 0.264 | 0.297 | 0.33 | 0.3564 | 0.3828 | 0.4092 | 0.4356 | 0.462 | 0.4796 | 0.4972 | 0.5148 | 0.5324 | 0.55 | 0.561 | 0.572 | 0.583 | 0.594 | 0.605 | 0.616 | 0.627 | 0.638 | 0.649 | 0.66 | 0.6644 | 0.6688 | 0.6732 | 0.6776 | 0.682 | 0.6864 | 0.6908 | 0.6952 | 0.6996 | 0.704 | 0.7084 | 0.7128 | 0.7172 | 0.7216 | 0.726 | 0.726 | 0.726 | 0.726 | 0.726 | 0.726 | 0.726 | 0.726 | 0.726 | 0.726 | 0.726 | 0.726 | 0.726 | 0.726 | 0.726 | 0.726 | 0.726 | 0.726 | 0.726 | 0.726 | 0.726 | 0.726 | 0.726 | 0.726 | 0.726 | 0.726 | 0.726 | 0.726 | 0.726 | 0.726 | 0.726 | 0.726 | 0.726 | 0.726 | 0.726 | 0.726 | 0.726 | 0.726 | 0.726 | 0.726 | 0.726 | 0.726 | 0.726 | 0.726 | 0.726 | 0.726 | 0.72527 | 0.72453 | 0.7238 | 0.72307 | 0.72233 | 0.7216 | 0.72087 | 0.72013 | 0.7194 | 0.71867 | 0.71793 | 0.7172 | 0.71647 | 0.71573 | 0.715 | 0.71427 | 0.71353 | 0.7128 | 0.71207 | 0.71133 | 0.7106 | 0.70987 | 0.70913 | 0.7084 | 0.70767 | 0.70693 | 0.7062 | 0.70547 | 0.70473 | 0.704 | 0.70327 | 0.70253 | 0.7018 | 0.70107 | 0.70033 | 0.6996 | 0.69887 | 0.69813 | 0.6974 | 0.69667 | 0.69593 | 0.6952 | 0.69447 | 0.69373 | 0.693 | 0.69227 | 0.69153 | 0.6908 | 0.69007 | 0.68933 | 0.6886 | 0.68787 | 0.68713 | 0.6864 | 0.68567 | 0.68493 | 0.6842 | 0.68347 | 0.68273 | 0.682 | 0.68127 | 0.68053 | 0.6798 | 0.67907 | 0.67833 | 0.6776 | 0.67687 | 0.67613 | 0.6754 | 0.67467 | 0.67393 | 0.6732 | 0.67247 | 0.67173 | 0.671 | 0.67027 | 0.66953 | 0.6688 | 0.66807 | 0.66733 | 0.6666 | 0.66587 | 0.66513 | 0.6644 | 0.66367 | 0.66293 | 0.6622 | 0.66147 | 0.66073 | 0.66
1.6 | 0 | 0.36 | 0.504 | 0.6 | 0.72 | 0.792 | 0.792 | 0.792 | 0.768 | 0.744 | 0.72 | 0 | 0.036 | 0.072 | 0.108 | 0.144 | 0.18 | 0.216 | 0.252 | 0.288 | 0.324 | 0.36 | 0.3888 | 0.4176 | 0.4464 | 0.4752 | 0.504 | 0.5232 | 0.5424 | 0.5616 | 0.5808 | 0.6 | 0.612 | 0.624 | 0.636 | 0.648 | 0.66 | 0.672 | 0.684 | 0.696 | 0.708 | 0.72 | 0.7248 | 0.7296 | 0.7344 | 0.7392 | 0.744 | 0.7488 | 0.7536 | 0.7584 | 0.7632 | 0.768 | 0.7728 | 0.7776 | 0.7824 | 0.7872 | 0.792 | 0.792 | 0.792 | 0.792 | 0.792 | 0.792 | 0.792 | 0.792 | 0.792 | 0.792 | 0.792 | 0.792 | 0.792 | 0.792 | 0.792 | 0.792 | 0.792 | 0.792 | 0.792 | 0.792 | 0.792 | 0.792 | 0.792 | 0.792 | 0.792 | 0.792 | 0.792 | 0.792 | 0.792 | 0.792 | 0.792 | 0.792 | 0.792 | 0.792 | 0.792 | 0.792 | 0.792 | 0.792 | 0.792 | 0.792 | 0.792 | 0.792 | 0.792 | 0.792 | 0.792 | 0.792 | 0.7912 | 0.7904 | 0.7896 | 0.7888 | 0.788 | 0.7872 | 0.7864 | 0.7856 | 0.7848 | 0.784 | 0.7832 | 0.7824 | 0.7816 | 0.7808 | 0.78 | 0.7792 | 0.7784 | 0.7776 | 0.7768 | 0.776 | 0.7752 | 0.7744 | 0.7736 | 0.7728 | 0.772 | 0.7712 | 0.7704 | 0.7696 | 0.7688 | 0.768 | 0.7672 | 0.7664 | 0.7656 | 0.7648 | 0.764 | 0.7632 | 0.7624 | 0.7616 | 0.7608 | 0.76 | 0.7592 | 0.7584 | 0.7576 | 0.7568 | 0.756 | 0.7552 | 0.7544 | 0.7536 | 0.7528 | 0.752 | 0.7512 | 0.7504 | 0.7496 | 0.7488 | 0.748 | 0.7472 | 0.7464 | 0.7456 | 0.7448 | 0.744 | 0.7432 | 0.7424 | 0.7416 | 0.7408 | 0.74 | 0.7392 | 0.7384 | 0.7376 | 0.7368 | 0.736 | 0.7352 | 0.7344 | 0.7336 | 0.7328 | 0.732 | 0.7312 | 0.7304 | 0.7296 | 0.7288 | 0.728 | 0.7272 | 0.7264 | 0.7256 | 0.7248 | 0.724 | 0.7232 | 0.7224 | 0.7216 | 0.7208 | 0.72
1.65 | 0 | 0.39 | 0.546 | 0.65 | 0.78 | 0.858 | 0.858 | 0.858 | 0.832 | 0.806 | 0.78 | -2.7756e-17 | 0.039 | 0.078 | 0.117 | 0.156 | 0.195 | 0.234 | 0.273 | 0.312 | 0.351 | 0.39 | 0.4212 | 0.4524 | 0.4836 | 0.5148 | 0.546 | 0.5668 | 0.5876 | 0.6084 | 0.6292 | 0.65 | 0.663 | 0.676 | 0.689 | 0.702 | 0.715 | 0.728 | 0.741 | 0.754 | 0.767 | 0.78 | 0.7852 | 0.7904 | 0.7956 | 0.8008 | 0.806 | 0.8112 | 0.8164 | 0.8216 | 0.8268 | 0.832 | 0.8372 | 0.8424 | 0.8476 | 0.8528 | 0.858 | 0.858 | 0.858 | 0.858 | 0.858 | 0.858 | 0.858 | 0.858 | 0.858 | 0.858 | 0.858 | 0.858 | 0.858 | 0.858 | 0.858 | 0.858 | 0.858 | 0.858 | 0.858 | 0.858 | 0.858 | 0.858 | 0.858 | 0.858 | 0.858 | 0.858 | 0.858 | 0.858 | 0.858 | 0.858 | 0.858 | 0.858 | 0.858 | 0.858 | 0.858 | 0.858 | 0.858 | 0.858 | 0.858 | 0.858 | 0.858 | 0.858 | 0.858 | 0.858 | 0.858 | 0.858 | 0.85713 | 0.85627 | 0.8554 | 0.85453 | 0.85367 | 0.8528 | 0.85193 | 0.85107 | 0.8502 | 0.84933 | 0.84847 | 0.8476 | 0.84673 | 0.84587 | 0.845 | 0.84413 | 0.84327 | 0.8424 | 0.84153 | 0.84067 | 0.8398 | 0.83893 | 0.83807 | 0.8372 | 0.83633 | 0.83547 | 0.8346 | 0.83373 | 0.83287 | 0.832 | 0.83113 | 0.83027 | 0.8294 | 0.82853 | 0.82767 | 0.8268 | 0.82593 | 0.82507 | 0.8242 | 0.82333 | 0.82247 | 0.8216 | 0.82073 | 0.81987 | 0.819 | 0.81813 | 0.81727 | 0.8164 | 0.81553 | 0.81467 | 0.8138 | 0.81293 | 0.81207 | 0.8112 | 0.81033 | 0.80947 | 0.8086 | 0.80773 | 0.80687 | 0.806 | 0.80513 | 0.80427 | 0.8034 | 0.80253 | 0.80167 | 0.8008 | 0.79993 | 0.79907 | 0.7982 | 0.79733 | 0.79647 | 0.7956 | 0.79473 | 0.79387 | 0.793 | 0.79213 | 0.79127 | 0.7904 | 0.78953 | 0.78867 | 0.7878 | 0.78693 | 0.78607 | 0.7852 | 0.78433 | 0.78347 | 0.7826 | 0.78173 | 0.78087 | 0.78
1.7 | 0 | 0.42 | 0.588 | 0.7 | 0.84 | 0.924 | 0.924 | 0.924 | 0.896 | 0.868 | 0.84 | 2.7756e-17 | 0.042 | 0.084 | 0.126 | 0.168 | 0.21 | 0.252 | 0.294 | 0.336 | 0.378 | 0.42 | 0.4536 | 0.4872 | 0.5208 | 0.5544 | 0.588 | 0.6104 | 0.6328 | 0.6552 | 0.6776 | 0.7 | 0.714 | 0.728 | 0.742 | 0.756 | 0.77 | 0.784 | 0.798 | 0.812 | 0.826 | 0.84 | 0.8456 | 0.8512 | 0.8568 | 0.8624 | 0.868 | 0.8736 | 0.8792 | 0.8848 | 0.8904 | 0.896 | 0.9016 | 0.9072 | 0.9128 | 0.9184 | 0.924 | 0.924 | 0.924 | 0.924 | 0.924 | 0.924 | 0.924 | 0.924 | 0.924 | 0.924 | 0.924 | 0.924 | 0.924 | 0.924 | 0.924 | 0.924 | 0.924 | 0.924 | 0.924 | 0.924 | 0.924 | 0.924 | 0.924 | 0.924 | 0.924 | 0.924 | 0.924 | 0.924 | 0.924 | 0.924 | 0.924 | 0.924 | 0.924 | 0.924 | 0.924 | 0.924 | 0.924 | 0.924 | 0.924 | 0.924 | 0.924 | 0.924 | 0.924 | 0.924 | 0.924 | 0.924 | 0.92307 | 0.92213 | 0.9212 | 0.92027 | 0.91933 | 0.9184 | 0.91747 | 0.91653 | 0.9156 | 0.91467 | 0.91373 | 0.9128 | 0.91187 | 0.91093 | 0.91 | 0.90907 | 0.90813 | 0.9072 | 0.90627 | 0.90533 | 0.9044 | 0.90347 | 0.90253 | 0.9016 | 0.90067 | 0.89973 | 0.8988 | 0.89787 | 0.89693 | 0.896 | 0.89507 | 0.89413 | 0.8932 | 0.89227 | 0.89133 | 0.8904 | 0.88947 | 0.88853 | 0.8876 | 0.88667 | 0.88573 | 0.8848 | 0.88387 | 0.88293 | 0.882 | 0.88107 | 0.88013 | 0.8792 | 0.87827 | 0.87733 | 0.8764 | 0.87547 | 0.87453 | 0.8736 | 0.87267 | 0.87173 | 0.8708 | 0.86987 | 0.86893 | 0.868 | 0.86707 | 0.86613 | 0.8652 | 0.86427 | 0.86333 | 0.8624 | 0.86147 | 0.86053 | 0.8596 | 0.85867 | 0.85773 | 0.8568 | 0.85587 | 0.85493 | 0.854 | 0.85307 | 0.85213 | 0.8512 | 0.85027 | 0.84933 | 0.8484 | 0.84747 | 0.84653 | 0.8456 | 0.84467 | 0.84373 | 0.8428 | 0.84187 | 0.84093 | 0.84
1.75 | 0 | 0.45 | 0.63 | 0.75 | 0.9 | 0.99 | 0.99 | 0.99 | 0.96 | 0.93 | 0.9 | 0 | 0.045 | 0.09 | 0.135 | 0.18 | 0.225 | 0.27 | 0.315 | 0.36 | 0.405 | 0.45 | 0.486 | 0.522 | 0.558 | 0.594 | 0.63 | 0.654 | 0.678 | 0.702 | 0.726 | 0.75 | 0.765 | 0.78 | 0.795 | 0.81 | 0.825 | 0.84 | 0.855 | 0.87 | 0.885 | 0.9 | 0.906 | 0.912 | 0.918 | 0.924 | 0.93 | 0.936 | 0.942 | 0.948 | 0.954 | 0.96 | 0.966 | 0.972 | 0.978 | 0.984 | 0.99 | 0.99 | 0.99 | 0.99 | 0.99 | 0.99 | 0.99 | 0.99 | 0.99 | 0.99 | 0.99 | 0.99 | 0.99 | 0.99 | 0.99 | 0.99 | 0.99 | 0.99 | 0.99 | 0.99 | 0.99 | 0.99 | 0.99 | 0.99 | 0.99 | 0.99 | 0.99 | 0.99 | 0.99 | 0.99 | 0.99 | 0.99 | 0.99 | 0.99 | 0.99 | 0.99 | 0.99 | 0.99 | 0.99 | 0.99 | 0.99 | 0.99 | 0.99 | 0.99 | 0.99 | 0.99 | 0.989 | 0.988 | 0.987 | 0.986 | 0.985 | 0.984 | 0.983 | 0.982 | 0.981 | 0.98 | 0.979 | 0.978 | 0.977 | 0.976 | 0.975 | 0.974 | 0.973 | 0.972 | 0.971 | 0.97 | 0.969 | 0.968 | 0.967 | 0.966 | 0.965 | 0.964 | 0.963 | 0.962 | 0.961 | 0.96 | 0.959 | 0.958 | 0.957 | 0.956 | 0.955 | 0.954 | 0.953 | 0.952 | 0.951 | 0.95 | 0.949 | 0.948 | 0.947 | 0.946 | 0.945 | 0.944 | 0.943 | 0.942 | 0.941 | 0.94 | 0.939 | 0.938 | 0.937 | 0.936 | 0.935 | 0.934 | 0.933 | 0.932 | 0.931 | 0.93 | 0.929 | 0.928 | 0.927 | 0.926 | 0.925 | 0.924 | 0.923 | 0.922 | 0.921 | 0.92 | 0.919 | 0.918 | 0.917 | 0.916 | 0.915 | 0.914 | 0.913 | 0.912 | 0.911 | 0.91 | 0.909 | 0.908 | 0.907 | 0.906 | 0.905 | 0.904 | 0.903 | 0.902 | 0.901 | 0.9
1.8 | 0 | 0.48 | 0.672 | 0.8 | 0.96 | 1.056 | 1.056 | 1.056 | 1.024 | 0.992 | 0.96 | 0 | 0.048 | 0.096 | 0.144 | 0.192 | 0.24 | 0.288 | 0.336 | 0.384 | 0.432 | 0.48 | 0.5184 | 0.5568 | 0.5952 | 0.6336 | 0.672 | 0.6976 | 0.7232 | 0.7488 | 0.7744 | 0.8 | 0.816 | 0.832 | 0.848 | 0.864 | 0.88 | 0.896 | 0.912 | 0.928 | 0.944 | 0.96 | 0.9664 | 0.9728 | 0.9792 | 0.9856 | 0.992 | 0.9984 | 1.0048 | 1.0112 | 1.0176 | 1.024 | 1.0304 | 1.0368 | 1.0432 | 1.0496 | 1.056 | 1.056 | 1.056 | 1.056 | 1.056 | 1.056 | 1.056 | 1.056 | 1.056 | 1.056 | 1.056 | 1.056 | 1.056 | 1.056 | 1.056 | 1.056 | 1.056 | 1.056 | 1.056 | 1.056 | 1.056 | 1.056 | 1.056 | 1.056 | 1.056 | 1.056 | 1.056 | 1.056 | 1.056 | 1.056 | 1.056 | 1.056 | 1.056 | 1.056 | 1.056 | 1.056 | 1.056 | 1.056 | 1.056 | 1.056 | 1.056 | 1.056 | 1.056 | 1.056 | 1.056 | 1.056 | 1.0549 | 1.0539 | 1.0528 | 1.0517 | 1.0507 | 1.0496 | 1.0485 | 1.0475 | 1.0464 | 1.0453 | 1.0443 | 1.0432 | 1.0421 | 1.0411 | 1.04 | 1.0389 | 1.0379 | 1.0368 | 1.0357 | 1.0347 | 1.0336 | 1.0325 | 1.0315 | 1.0304 | 1.0293 | 1.0283 | 1.0272 | 1.0261 | 1.0251 | 1.024 | 1.0229 | 1.0219 | 1.0208 | 1.0197 | 1.0187 | 1.0176 | 1.0165 | 1.0155 | 1.0144 | 1.0133 | 1.0123 | 1.0112 | 1.0101 | 1.0091 | 1.008 | 1.0069 | 1.0059 | 1.0048 | 1.0037 | 1.0027 | 1.0016 | 1.0005 | 0.99947 | 0.9984 | 0.99733 | 0.99627 | 0.9952 | 0.99413 | 0.99307 | 0.992 | 0.99093 | 0.98987 | 0.9888 | 0.98773 | 0.98667 | 0.9856 | 0.98453 | 0.98347 | 0.9824 | 0.98133 | 0.98027 | 0.9792 | 0.97813 | 0.97707 | 0.976 | 0.97493 | 0.97387 | 0.9728 | 0.97173 | 0.97067 | 0.9696 | 0.96853 | 0.96747 | 0.9664 | 0.96533 | 0.96427 | 0.9632 | 0.96213 | 0.96107 | 0.96
1.85 | 0 | 0.51 | 0.714 | 0.85 | 1.02 | 1.122 | 1.122 | 1.122 | 1.088 | 1.054 | 1.02 | 0 | 0.051 | 0.102 | 0.153 | 0.204 | 0.255 | 0.306 | 0.357 | 0.408 | 0.459 | 0.51 | 0.5508 | 0.5916 | 0.6324 | 0.6732 | 0.714 | 0.7412 | 0.7684 | 0.7956 | 0.8228 | 0.85 | 0.867 | 0.884 | 0.901 | 0.918 | 0.935 | 0.952 | 0.969 | 0.986 | 1.003 | 1.02 | 1.0268 | 1.0336 | 1.0404 | 1.0472 | 1.054 | 1.0608 | 1.0676 | 1.0744 | 1.0812 | 1.088 | 1.0948 | 1.1016 | 1.1084 | 1.1152 | 1.122 | 1.122 | 1.122 | 1.122 | 1.122 | 1.122 | 1.122 | 1.122 | 1.122 | 1.122 | 1.122 | 1.122 | 1.122 | 1.122 | 1.122 | 1.122 | 1.122 | 1.122 | 1.122 | 1.122 | 1.122 | 1.122 | 1.122 | 1.122 | 1.122 | 1.122 | 1.122 | 1.122 | 1.122 | 1.122 | 1.122 | 1.122 | 1.122 | 1.122 | 1.122 | 1.122 | 1.122 | 1.122 | 1.122 | 1.122 | 1.122 | 1.122 | 1.122 | 1.122 | 1.122 | 1.122 | 1.1209 | 1.1197 | 1.1186 | 1.1175 | 1.1163 | 1.1152 | 1.1141 | 1.1129 | 1.1118 | 1.1107 | 1.1095 | 1.1084 | 1.1073 | 1.1061 | 1.105 | 1.1039 | 1.1027 | 1.1016 | 1.1005 | 1.0993 | 1.0982 | 1.0971 | 1.0959 | 1.0948 | 1.0937 | 1.0925 | 1.0914 | 1.0903 | 1.0891 | 1.088 | 1.0869 | 1.0857 | 1.0846 | 1.0835 | 1.0823 | 1.0812 | 1.0801 | 1.0789 | 1.0778 | 1.0767 | 1.0755 | 1.0744 | 1.0733 | 1.0721 | 1.071 | 1.0699 | 1.0687 | 1.0676 | 1.0665 | 1.0653 | 1.0642 | 1.0631 | 1.0619 | 1.0608 | 1.0597 | 1.0585 | 1.0574 | 1.0563 | 1.0551 | 1.054 | 1.0529 | 1.0517 | 1.0506 | 1.0495 | 1.0483 | 1.0472 | 1.0461 | 1.0449 | 1.0438 | 1.0427 | 1.0415 | 1.0404 | 1.0393 | 1.0381 | 1.037 | 1.0359 | 1.0347 | 1.0336 | 1.0325 | 1.0313 | 1.0302 | 1.0291 | 1.0279 | 1.0268 | 1.0257 | 1.0245 | 1.0234 | 1.0223 | 1.0211 | 1.02
1.9 | 0 | 0.54 | 0.756 | 0.9 | 1.08 | 1.188 | 1.188 | 1.188 | 1.152 | 1.116 | 1.08 | 0 | 0.054 | 0.108 | 0.162 | 0.216 | 0.27 | 0.324 | 0.378 | 0.432 | 0.486 | 0.54 | 0.5832 | 0.6264 | 0.6696 | 0.7128 | 0.756 | 0.7848 | 0.8136 | 0.8424 | 0.8712 | 0.9 | 0.918 | 0.936 | 0.954 | 0.972 | 0.99 | 1.008 | 1.026 | 1.044 | 1.062 | 1.08 | 1.0872 | 1.0944 | 1.1016 | 1.1088 | 1.116 | 1.1232 | 1.1304 | 1.1376 | 1.1448 | 1.152 | 1.1592 | 1.1664 | 1.1736 | 1.1808 | 1.188 | 1.188 | 1.188 | 1.188 | 1.188 | 1.188 | 1.188 | 1.188 | 1.188 | 1.188 | 1.188 | 1.188 | 1.188 | 1.188 | 1.188 | 1.188 | 1.188 | 1.188 | 1.188 | 1.188 | 1.188 | 1.188 | 1.188 | 1.188 | 1.188 | 1.188 | 1.188 | 1.188 | 1.188 | 1.188 | 1.188 | 1.188 | 1.188 | 1.188 | 1.188 | 1.188 | 1.188 | 1.188 | 1.188 | 1.188 | 1.188 | 1.188 | 1.188 | 1.188 | 1.188 | 1.188 | 1.1868 | 1.1856 | 1.1844 | 1.1832 | 1.182 | 1.1808 | 1.1796 | 1.1784 | 1.1772 | 1.176 | 1.1748 | 1.1736 | 1.1724 | 1.1712 | 1.17 | 1.1688 | 1.1676 | 1.1664 | 1.1652 | 1.164 | 1.1628 | 1.1616 | 1.1604 | 1.1592 | 1.158 | 1.1568 | 1.1556 | 1.1544 | 1.1532 | 1.152 | 1.1508 | 1.1496 | 1.1484 | 1.1472 | 1.146 | 1.1448 | 1.1436 | 1.1424 | 1.1412 | 1.14 | 1.1388 | 1.1376 | 1.1364 | 1.1352 | 1.134 | 1.1328 | 1.1316 | 1.1304 | 1.1292 | 1.128 | 1.1268 | 1.1256 | 1.1244 | 1.1232 | 1.122 | 1.1208 | 1.1196 | 1.1184 | 1.1172 | 1.116 | 1.1148 | 1.1136 | 1.1124 | 1.1112 | 1.11 | 1.1088 | 1.1076 | 1.1064 | 1.1052 | 1.104 | 1.1028 | 1.1016 | 1.1004 | 1.0992 | 1.098 | 1.0968 | 1.0956 | 1.0944 | 1.0932 | 1.092 | 1.0908 | 1.0896 | 1.0884 | 1.0872 | 1.086 | 1.0848 | 1.0836 | 1.0824 | 1.0812 | 1.08
1.95 | 0 | 0.57 | 0.798 | 0.95 | 1.14 | 1.254 | 1.254 | 1.254 | 1.216 | 1.178 | 1.14 | 0 | 0.057 | 0.114 | 0.171 | 0.228 | 0.285 | 0.342 | 0.399 | 0.456 | 0.513 | 0.57 | 0.6156 | 0.6612 | 0.7068 | 0.7524 | 0.798 | 0.8284 | 0.8588 | 0.8892 | 0.9196 | 0.95 | 0.969 | 0.988 | 1.007 | 1.026 | 1.045 | 1.064 | 1.083 | 1.102 | 1.121 | 1.14 | 1.1476 | 1.1552 | 1.1628 | 1.1704 | 1.178 | 1.1856 | 1.1932 | 1.2008 | 1.2084 | 1.216 | 1.2236 | 1.2312 | 1.2388 | 1.2464 | 1.254 | 1.254 | 1.254 | 1.254 | 1.254 | 1.254 | 1.254 | 1.254 | 1.254 | 1.254 | 1.254 | 1.254 | 1.254 | 1.254 | 1.254 | 1.254 | 1.254 | 1.254 | 1.254 | 1.254 | 1.254 | 1.254 | 1.254 | 1.254 | 1.254 | 1.254 | 1.254 | 1.254 | 1.254 | 1.254 | 1.254 | 1.254 | 1.254 | 1.254 | 1.254 | 1.254 | 1.254 | 1.254 | 1.254 | 1.254 | 1.254 | 1.254 | 1.254 | 1.254 | 1.254 | 1.254 | 1.2527 | 1.2515 | 1.2502 | 1.2489 | 1.2477 | 1.2464 | 1.2451 | 1.2439 | 1.2426 | 1.2413 | 1.2401 | 1.2388 | 1.2375 | 1.2363 | 1.235 | 1.2337 | 1.2325 | 1.2312 | 1.2299 | 1.2287 | 1.2274 | 1.2261 | 1.2249 | 1.2236 | 1.2223 | 1.2211 | 1.2198 | 1.2185 | 1.2173 | 1.216 | 1.2147 | 1.2135 | 1.2122 | 1.2109 | 1.2097 | 1.2084 | 1.2071 | 1.2059 | 1.2046 | 1.2033 | 1.2021 | 1.2008 | 1.1995 | 1.1983 | 1.197 | 1.1957 | 1.1945 | 1.1932 | 1.1919 | 1.1907 | 1.1894 | 1.1881 | 1.1869 | 1.1856 | 1.1843 | 1.1831 | 1.1818 | 1.1805 | 1.1793 | 1.178 | 1.1767 | 1.1755 | 1.1742 | 1.1729 | 1.1717 | 1.1704 | 1.1691 | 1.1679 | 1.1666 | 1.1653 | 1.1641 | 1.1628 | 1.1615 | 1.1603 | 1.159 | 1.1577 | 1.1565 | 1.1552 | 1.1539 | 1.1527 | 1.1514 | 1.1501 | 1.1489 | 1.1476 | 1.1463 | 1.1451 | 1.1438 | 1.1425 | 1.1413 | 1.14
2 | 0 | 0.6 | 0.84 | 1 | 1.2 | 1.32 | 1.32 | 1.32 | 1.28 | 1.24 | 1.2 | 0 | 0.06 | 0.12 | 0.18 | 0.24 | 0.3 | 0.36 | 0.42 | 0.48 | 0.54 | 0.6 | 0.648 | 0.696 | 0.744 | 0.792 | 0.84 | 0.872 | 0.904 | 0.936 | 0.968 | 1 | 1.02 | 1.04 | 1.06 | 1.08 | 1.1 | 1.12 | 1.14 | 1.16 | 1.18 | 1.2 | 1.208 | 1.216 | 1.224 | 1.232 | 1.24 | 1.248 | 1.256 | 1.264 | 1.272 | 1.28 | 1.288 | 1.296 | 1.304 | 1.312 | 1.32 | 1.32 | 1.32 | 1.32 | 1.32 | 1.32 | 1.32 | 1.32 | 1.32 | 1.32 | 1.32 | 1.32 | 1.32 | 1.32 | 1.32 | 1.32 | 1.32 | 1.32 | 1.32 | 1.32 | 1.32 | 1.32 | 1.32 | 1.32 | 1.32 | 1.32 | 1.32 | 1.32 | 1.32 | 1.32 | 1.32 | 1.32 | 1.32 | 1.32 | 1.32 | 1.32 | 1.32 | 1.32 | 1.32 | 1.32 | 1.32 | 1.32 | 1.32 | 1.32 | 1.32 | 1.32 | 1.3187 | 1.3173 | 1.316 | 1.3147 | 1.3133 | 1.312 | 1.3107 | 1.3093 | 1.308 | 1.3067 | 1.3053 | 1.304 | 1.3027 | 1.3013 | 1.3 | 1.2987 | 1.2973 | 1.296 | 1.2947 | 1.2933 | 1.292 | 1.2907 | 1.2893 | 1.288 | 1.2867 | 1.2853 | 1.284 | 1.2827 | 1.2813 | 1.28 | 1.2787 | 1.2773 | 1.276 | 1.2747 | 1.2733 | 1.272 | 1.2707 | 1.2693 | 1.268 | 1.2667 | 1.2653 | 1.264 | 1.2627 | 1.2613 | 1.26 | 1.2587 | 1.2573 | 1.256 | 1.2547 | 1.2533 | 1.252 | 1.2507 | 1.2493 | 1.248 | 1.2467 | 1.2453 | 1.244 | 1.2427 | 1.2413 | 1.24 | 1.2387 | 1.2373 | 1.236 | 1.2347 | 1.2333 | 1.232 | 1.2307 | 1.2293 | 1.228 | 1.2267 | 1.2253 | 1.224 | 1.2227 | 1.2213 | 1.22 | 1.2187 | 1.2173 | 1.216 | 1.2147 | 1.2133 | 1.212 | 1.2107 | 1.2093 | 1.208 | 1.2067 | 1.2053 | 1.204 | 1.2027 | 1.2013 | 1.2
2.05 | 0 | 0.685 | 0.963 | 1.155 | 1.378 | 1.519 | 1.535 | 1.543 | 1.504 | 1.465 | 1.426 | 0 | 0.0685 | 0.137 | 0.2055 | 0.274 | 0.3425 | 0.411 | 0.4795 | 0.548 | 0.6165 | 0.685 | 0.7406 | 0.7962 | 0.8518 | 0.9074 | 0.963 | 1.0014 | 1.0398 | 1.0782 | 1.1166 | 1.155 | 1.1773 | 1.1996 | 1.2219 | 1.2442 | 1.2665 | 1.2888 | 1.3111 | 1.3334 | 1.3557 | 1.378 | 1.3874 | 1.3968 | 1.4062 | 1.4156 | 1.425 | 1.4344 | 1.4438 | 1.4532 | 1.4626 | 1.472 | 1.4814 | 1.4908 | 1.5002 | 1.5096 | 1.519 | 1.5201 | 1.5211 | 1.5222 | 1.5233 | 1.5243 | 1.5254 | 1.5265 | 1.5275 | 1.5286 | 1.5297 | 1.5307 | 1.5318 | 1.5329 | 1.5339 | 1.535 | 1.5353 | 1.5355 | 1.5358 | 1.5361 | 1.5363 | 1.5366 | 1.5369 | 1.5371 | 1.5374 | 1.5377 | 1.5379 | 1.5382 | 1.5385 | 1.5387 | 1.539 | 1.5393 | 1.5395 | 1.5398 | 1.5401 | 1.5403 | 1.5406 | 1.5409 | 1.5411 | 1.5414 | 1.5417 | 1.5419 | 1.5422 | 1.5425 | 1.5427 | 1.543 | 1.5417 | 1.5404 | 1.5391 | 1.5378 | 1.5365 | 1.5352 | 1.5339 | 1.5326 | 1.5313 | 1.53 | 1.5287 | 1.5274 | 1.5261 | 1.5248 | 1.5235 | 1.5222 | 1.5209 | 1.5196 | 1.5183 | 1.517 | 1.5157 | 1.5144 | 1.5131 | 1.5118 | 1.5105 | 1.5092 | 1.5079 | 1.5066 | 1.5053 | 1.504 | 1.5027 | 1.5014 | 1.5001 | 1.4988 | 1.4975 | 1.4962 | 1.4949 | 1.4936 | 1.4923 | 1.491 | 1.4897 | 1.4884 | 1.4871 | 1.4858 | 1.4845 | 1.4832 | 1.4819 | 1.4806 | 1.4793 | 1.478 | 1.4767 | 1.4754 | 1.4741 | 1.4728 | 1.4715 | 1.4702 | 1.4689 | 1.4676 | 1.4663 | 1.465 | 1.4637 | 1.4624 | 1.4611 | 1.4598 | 1.4585 | 1.4572 | 1.4559 | 1.4546 | 1.4533 | 1.452 | 1.4507 | 1.4494 | 1.4481 | 1.4468 | 1.4455 | 1.4442 | 1.4429 | 1.4416 | 1.4403 | 1.439 | 1.4377 | 1.4364 | 1.4351 | 1.4338 | 1.4325 | 1.4312 | 1.4299 | 1.4286 | 1.4273 | 1.426
2.1 | 0 | 0.77 | 1.086 | 1.31 | 1.556 | 1.718 | 1.75 | 1.766 | 1.728 | 1.69 | 1.652 | 0 | 0.077 | 0.154 | 0.231 | 0.308 | 0.385 | 0.462 | 0.539 | 0.616 | 0.693 | 0.77 | 0.8332 | 0.8964 | 0.9596 | 1.0228 | 1.086 | 1.1308 | 1.1756 | 1.2204 | 1.2652 | 1.31 | 1.3346 | 1.3592 | 1.3838 | 1.4084 | 1.433 | 1.4576 | 1.4822 | 1.5068 | 1.5314 | 1.556 | 1.5668 | 1.5776 | 1.5884 | 1.5992 | 1.61 | 1.6208 | 1.6316 | 1.6424 | 1.6532 | 1.664 | 1.6748 | 1.6856 | 1.6964 | 1.7072 | 1.718 | 1.7201 | 1.7223 | 1.7244 | 1.7265 | 1.7287 | 1.7308 | 1.7329 | 1.7351 | 1.7372 | 1.7393 | 1.7415 | 1.7436 | 1.7457 | 1.7479 | 1.75 | 1.7505 | 1.7511 | 1.7516 | 1.7521 | 1.7527 | 1.7532 | 1.7537 | 1.7543 | 1.7548 | 1.7553 | 1.7559 | 1.7564 | 1.7569 | 1.7575 | 1.758 | 1.7585 | 1.7591 | 1.7596 | 1.7601 | 1.7607 | 1.7612 | 1.7617 | 1.7623 | 1.7628 | 1.7633 | 1.7639 | 1.7644 | 1.7649 | 1.7655 | 1.766 | 1.7647 | 1.7635 | 1.7622 | 1.7609 | 1.7597 | 1.7584 | 1.7571 | 1.7559 | 1.7546 | 1.7533 | 1.7521 | 1.7508 | 1.7495 | 1.7483 | 1.747 | 1.7457 | 1.7445 | 1.7432 | 1.7419 | 1.7407 | 1.7394 | 1.7381 | 1.7369 | 1.7356 | 1.7343 | 1.7331 | 1.7318 | 1.7305 | 1.7293 | 1.728 | 1.7267 | 1.7255 | 1.7242 | 1.7229 | 1.7217 | 1.7204 | 1.7191 | 1.7179 | 1.7166 | 1.7153 | 1.7141 | 1.7128 | 1.7115 | 1.7103 | 1.709 | 1.7077 | 1.7065 | 1.7052 | 1.7039 | 1.7027 | 1.7014 | 1.7001 | 1.6989 | 1.6976 | 1.6963 | 1.6951 | 1.6938 | 1.6925 | 1.6913 | 1.69 | 1.6887 | 1.6875 | 1.6862 | 1.6849 | 1.6837 | 1.6824 | 1.6811 | 1.6799 | 1.6786 | 1.6773 | 1.6761 | 1.6748 | 1.6735 | 1.6723 | 1.671 | 1.6697 | 1.6685 | 1.6672 | 1.6659 | 1.6647 | 1.6634 | 1.6621 | 1.6609 | 1.6596 | 1.6583 | 1.6571 | 1.6558 | 1.6545 | 1.6533 | 1.652
2.15 | 0 | 0.855 | 1.209 | 1.465 | 1.734 | 1.917 | 1.965 | 1.989 | 1.952 | 1.915 | 1.878 | -5.5511e-17 | 0.0855 | 0.171 | 0.2565 | 0.342 | 0.4275 | 0.513 | 0.5985 | 0.684 | 0.7695 | 0.855 | 0.9258 | 0.9966 | 1.0674 | 1.1382 | 1.209 | 1.2602 | 1.3114 | 1.3626 | 1.4138 | 1.465 | 1.4919 | 1.5188 | 1.5457 | 1.5726 | 1.5995 | 1.6264 | 1.6533 | 1.6802 | 1.7071 | 1.734 | 1.7462 | 1.7584 | 1.7706 | 1.7828 | 1.795 | 1.8072 | 1.8194 | 1.8316 | 1.8438 | 1.856 | 1.8682 | 1.8804 | 1.8926 | 1.9048 | 1.917 | 1.9202 | 1.9234 | 1.9266 | 1.9298 | 1.933 | 1.9362 | 1.9394 | 1.9426 | 1.9458 | 1.949 | 1.9522 | 1.9554 | 1.9586 | 1.9618 | 1.965 | 1.9658 | 1.9666 | 1.9674 | 1.9682 | 1.969 | 1.9698 | 1.9706 | 1.9714 | 1.9722 | 1.973 | 1.9738 | 1.9746 | 1.9754 | 1.9762 | 1.977 | 1.9778 | 1.9786 | 1.9794 | 1.9802 | 1.981 | 1.9818 | 1.9826 | 1.9834 | 1.9842 | 1.985 | 1.9858 | 1.9866 | 1.9874 | 1.9882 | 1.989 | 1.9878 | 1.9865 | 1.9853 | 1.9841 | 1.9828 | 1.9816 | 1.9804 | 1.9791 | 1.9779 | 1.9767 | 1.9754 | 1.9742 | 1.973 | 1.9717 | 1.9705 | 1.9693 | 1.968 | 1.9668 | 1.9656 | 1.9643 | 1.9631 | 1.9619 | 1.9606 | 1.9594 | 1.9582 | 1.9569 | 1.9557 | 1.9545 | 1.9532 | 1.952 | 1.9508 | 1.9495 | 1.9483 | 1.9471 | 1.9458 | 1.9446 | 1.9434 | 1.9421 | 1.9409 | 1.9397 | 1.9384 | 1.9372 | 1.936 | 1.9347 | 1.9335 | 1.9323 | 1.931 | 1.9298 | 1.9286 | 1.9273 | 1.9261 | 1.9249 | 1.9236 | 1.9224 | 1.9212 | 1.9199 | 1.9187 | 1.9175 | 1.9162 | 1.915 | 1.9138 | 1.9125 | 1.9113 | 1.9101 | 1.9088 | 1.9076 | 1.9064 | 1.9051 | 1.9039 | 1.9027 | 1.9014 | 1.9002 | 1.899 | 1.8977 | 1.8965 | 1.8953 | 1.894 | 1.8928 | 1.8916 | 1.8903 | 1.8891 | 1.8879 | 1.8866 | 1.8854 | 1.8842 | 1.8829 | 1.8817 | 1.8805 | 1.8792 | 1.878
2.2 | 0 | 0.94 | 1.332 | 1.62 | 1.912 | 2.116 | 2.18 | 2.212 | 2.176 | 2.14 | 2.104 | 0 | 0.094 | 0.188 | 0.282 | 0.376 | 0.47 | 0.564 | 0.658 | 0.752 | 0.846 | 0.94 | 1.0184 | 1.0968 | 1.1752 | 1.2536 | 1.332 | 1.3896 | 1.4472 | 1.5048 | 1.5624 | 1.62 | 1.6492 | 1.6784 | 1.7076 | 1.7368 | 1.766 | 1.7952 | 1.8244 | 1.8536 | 1.8828 | 1.912 | 1.9256 | 1.9392 | 1.9528 | 1.9664 | 1.98 | 1.9936 | 2.0072 | 2.0208 | 2.0344 | 2.048 | 2.0616 | 2.0752 | 2.0888 | 2.1024 | 2.116 | 2.1203 | 2.1245 | 2.1288 | 2.1331 | 2.1373 | 2.1416 | 2.1459 | 2.1501 | 2.1544 | 2.1587 | 2.1629 | 2.1672 | 2.1715 | 2.1757 | 2.18 | 2.1811 | 2.1821 | 2.1832 | 2.1843 | 2.1853 | 2.1864 | 2.1875 | 2.1885 | 2.1896 | 2.1907 | 2.1917 | 2.1928 | 2.1939 | 2.1949 | 2.196 | 2.1971 | 2.1981 | 2.1992 | 2.2003 | 2.2013 | 2.2024 | 2.2035 | 2.2045 | 2.2056 | 2.2067 | 2.2077 | 2.2088 | 2.2099 | 2.2109 | 2.212 | 2.2108 | 2.2096 | 2.2084 | 2.2072 | 2.206 | 2.2048 | 2.2036 | 2.2024 | 2.2012 | 2.2 | 2.1988 | 2.1976 | 2.1964 | 2.1952 | 2.194 | 2.1928 | 2.1916 | 2.1904 | 2.1892 | 2.188 | 2.1868 | 2.1856 | 2.1844 | 2.1832 | 2.182 | 2.1808 | 2.1796 | 2.1784 | 2.1772 | 2.176 | 2.1748 | 2.1736 | 2.1724 | 2.1712 | 2.17 | 2.1688 | 2.1676 | 2.1664 | 2.1652 | 2.164 | 2.1628 | 2.1616 | 2.1604 | 2.1592 | 2.158 | 2.1568 | 2.1556 | 2.1544 | 2.1532 | 2.152 | 2.1508 | 2.1496 | 2.1484 | 2.1472 | 2.146 | 2.1448 | 2.1436 | 2.1424 | 2.1412 | 2.14 | 2.1388 | 2.1376 | 2.1364 | 2.1352 | 2.134 | 2.1328 | 2.1316 | 2.1304 | 2.1292 | 2.128 | 2.1268 | 2.1256 | 2.1244 | 2.1232 | 2.122 | 2.1208 | 2.1196 | 2.1184 | 2.1172 | 2.116 | 2.1148 | 2.1136 | 2.1124 | 2.1112 | 2.11 | 2.1088 | 2.1076 | 2.1064 | 2.1052 | 2.104
2.25 | 0 | 1.025 | 1.455 | 1.775 | 2.09 | 2.315 | 2.395 | 2.435 | 2.4 | 2.365 | 2.33 | 0 | 0.1025 | 0.205 | 0.3075 | 0.41 | 0.5125 | 0.615 | 0.7175 | 0.82 | 0.9225 | 1.025 | 1.111 | 1.197 | 1.283 | 1.369 | 1.455 | 1.519 | 1.583 | 1.647 | 1.711 | 1.775 | 1.8065 | 1.838 | 1.8695 | 1.901 | 1.9325 | 1.964 | 1.9955 | 2.027 | 2.0585 | 2.09 | 2.105 | 2.12 | 2.135 | 2.15 | 2.165 | 2.18 | 2.195 | 2.21 | 2.225 | 2.24 | 2.255 | 2.27 | 2.285 | 2.3 | 2.315 | 2.3203 | 2.3257 | 2.331 | 2.3363 | 2.3417 | 2.347 | 2.3523 | 2.3577 | 2.363 | 2.3683 | 2.3737 | 2.379 | 2.3843 | 2.3897 | 2.395 | 2.3963 | 2.3977 | 2.399 | 2.4003 | 2.4017 | 2.403 | 2.4043 | 2.4057 | 2.407 | 2.4083 | 2.4097 | 2.411 | 2.4123 | 2.4137 | 2.415 | 2.4163 | 2.4177 | 2.419 | 2.4203 | 2.4217 | 2.423 | 2.4243 | 2.4257 | 2.427 | 2.4283 | 2.4297 | 2.431 | 2.4323 | 2.4337 | 2.435 | 2.4338 | 2.4327 | 2.4315 | 2.4303 | 2.4292 | 2.428 | 2.4268 | 2.4257 | 2.4245 | 2.4233 | 2.4222 | 2.421 | 2.4198 | 2.4187 | 2.4175 | 2.4163 | 2.4152 | 2.414 | 2.4128 | 2.4117 | 2.4105 | 2.4093 | 2.4082 | 2.407 | 2.4058 | 2.4047 | 2.4035 | 2.4023 | 2.4012 | 2.4 | 2.3988 | 2.3977 | 2.3965 | 2.3953 | 2.3942 | 2.393 | 2.3918 | 2.3907 | 2.3895 | 2.3883 | 2.3872 | 2.386 | 2.3848 | 2.3837 | 2.3825 | 2.3813 | 2.3802 | 2.379 | 2.3778 | 2.3767 | 2.3755 | 2.3743 | 2.3732 | 2.372 | 2.3708 | 2.3697 | 2.3685 | 2.3673 | 2.3662 | 2.365 | 2.3638 | 2.3627 | 2.3615 | 2.3603 | 2.3592 | 2.358 | 2.3568 | 2.3557 | 2.3545 | 2.3533 | 2.3522 | 2.351 | 2.3498 | 2.3487 | 2.3475 | 2.3463 | 2.3452 | 2.344 | 2.3428 | 2.3417 | 2.3405 | 2.3393 | 2.3382 | 2.337 | 2.3358 | 2.3347 | 2.3335 | 2.3323 | 2.3312 | 2.33
2.3 | 0 | 1.11 | 1.578 | 1.93 | 2.268 | 2.514 | 2.61 | 2.658 | 2.624 | 2.59 | 2.556 | 1.1102e-16 | 0.111 | 0.222 | 0.333 | 0.444 | 0.555 | 0.666 | 0.777 | 0.888 | 0.999 | 1.11 | 1.2036 | 1.2972 | 1.3908 | 1.4844 | 1.578 | 1.6484 | 1.7188 | 1.7892 | 1.8596 | 1.93 | 1.9638 | 1.9976 | 2.0314 | 2.0652 | 2.099 | 2.1328 | 2.1666 | 2.2004 | 2.2342 | 2.268 | 2.2844 | 2.3008 | 2.3172 | 2.3336 | 2.35 | 2.3664 | 2.3828 | 2.3992 | 2.4156 | 2.432 | 2.4484 | 2.4648 | 2.4812 | 2.4976 | 2.514 | 2.5204 | 2.5268 | 2.5332 | 2.5396 | 2.546 | 2.5524 | 2.5588 | 2.5652 | 2.5716 | 2.578 | 2.5844 | 2.5908 | 2.5972 | 2.6036 | 2.61 | 2.6116 | 2.6132 | 2.6148 | 2.6164 | 2.618 | 2.6196 | 2.6212 | 2.6228 | 2.6244 | 2.626 | 2.6276 | 2.6292 | 2.6308 | 2.6324 | 2.634 | 2.6356 | 2.6372 | 2.6388 | 2.6404 | 2.642 | 2.6436 | 2.6452 | 2.6468 | 2.6484 | 2.65 | 2.6516 | 2.6532 | 2.6548 | 2.6564 | 2.658 | 2.6569 | 2.6557 | 2.6546 | 2.6535 | 2.6523 | 2.6512 | 2.6501 | 2.6489 | 2.6478 | 2.6467 | 2.6455 | 2.6444 | 2.6433 | 2.6421 | 2.641 | 2.6399 | 2.6387 | 2.6376 | 2.6365 | 2.6353 | 2.6342 | 2.6331 | 2.6319 | 2.6308 | 2.6297 | 2.6285 | 2.6274 | 2.6263 | 2.6251 | 2.624 | 2.6229 | 2.6217 | 2.6206 | 2.6195 | 2.6183 | 2.6172 | 2.6161 | 2.6149 | 2.6138 | 2.6127 | 2.6115 | 2.6104 | 2.6093 | 2.6081 | 2.607 | 2.6059 | 2.6047 | 2.6036 | 2.6025 | 2.6013 | 2.6002 | 2.5991 | 2.5979 | 2.5968 | 2.5957 | 2.5945 | 2.5934 | 2.5923 | 2.5911 | 2.59 | 2.5889 | 2.5877 | 2.5866 | 2.5855 | 2.5843 | 2.5832 | 2.5821 | 2.5809 | 2.5798 | 2.5787 | 2.5775 | 2.5764 | 2.5753 | 2.5741 | 2.573 | 2.5719 | 2.5707 | 2.5696 | 2.5685 | 2.5673 | 2.5662 | 2.5651 | 2.5639 | 2.5628 | 2.5617 | 2.5605 | 2.5594 | 2.5583 | 2.5571 | 2.556
2.35 | 0 | 1.195 | 1.701 | 2.085 | 2.446 | 2.713 | 2.825 | 2.881 | 2.848 | 2.815 | 2.782 | 0 | 0.1195 | 0.239 | 0.3585 | 0.478 | 0.5975 | 0.717 | 0.8365 | 0.956 | 1.0755 | 1.195 | 1.2962 | 1.3974 | 1.4986 | 1.5998 | 1.701 | 1.7778 | 1.8546 | 1.9314 | 2.0082 | 2.085 | 2.1211 | 2.1572 | 2.1933 | 2.2294 | 2.2655 | 2.3016 | 2.3377 | 2.3738 | 2.4099 | 2.446 | 2.4638 | 2.4816 | 2.4994 | 2.5172 | 2.535 | 2.5528 | 2.5706 | 2.5884 | 2.6062 | 2.624 | 2.6418 | 2.6596 | 2.6774 | 2.6952 | 2.713 | 2.7205 | 2.7279 | 2.7354 | 2.7429 | 2.7503 | 2.7578 | 2.7653 | 2.7727 | 2.7802 | 2.7877 | 2.7951 | 2.8026 | 2.8101 | 2.8175 | 2.825 | 2.8269 | 2.8287 | 2.8306 | 2.8325 | 2.8343 | 2.8362 | 2.8381 | 2.8399 | 2.8418 | 2.8437 | 2.8455 | 2.8474 | 2.8493 | 2.8511 | 2.853 | 2.8549 | 2.8567 | 2.8586 | 2.8605 | 2.8623 | 2.8642 | 2.8661 | 2.8679 | 2.8698 | 2.8717 | 2.8735 | 2.8754 | 2.8773 | 2.8791 | 2.881 | 2.8799 | 2.8788 | 2.8777 | 2.8766 | 2.8755 | 2.8744 | 2.8733 | 2.8722 | 2.8711 | 2.87 | 2.8689 | 2.8678 | 2.8667 | 2.8656 | 2.8645 | 2.8634 | 2.8623 | 2.8612 | 2.8601 | 2.859 | 2.8579 | 2.8568 | 2.8557 | 2.8546 | 2.8535 | 2.8524 | 2.8513 | 2.8502 | 2.8491 | 2.848 | 2.8469 | 2.8458 | 2.8447 | 2.8436 | 2.8425 | 2.8414 | 2.8403 | 2.8392 | 2.8381 | 2.837 | 2.8359 | 2.8348 | 2.8337 | 2.8326 | 2.8315 | 2.8304 | 2.8293 | 2.8282 | 2.8271 | 2.826 | 2.8249 | 2.8238 | 2.8227 | 2.8216 | 2.8205 | 2.8194 | 2.8183 | 2.8172 | 2.8161 | 2.815 | 2.8139 | 2.8128 | 2.8117 | 2.8106 | 2.8095 | 2.8084 | 2.8073 | 2.8062 | 2.8051 | 2.804 | 2.8029 | 2.8018 | 2.8007 | 2.7996 | 2.7985 | 2.7974 | 2.7963 | 2.7952 | 2.7941 | 2.793 | 2.7919 | 2.7908 | 2.7897 | 2.7886 | 2.7875 | 2.7864 | 2.7853 | 2.7842 | 2.7831 | 2.782
2.4 | 0 | 1.28 | 1.824 | 2.24 | 2.624 | 2.912 | 3.04 | 3.104 | 3.072 | 3.04 | 3.008 | 0 | 0.128 | 0.256 | 0.384 | 0.512 | 0.64 | 0.768 | 0.896 | 1.024 | 1.152 | 1.28 | 1.3888 | 1.4976 | 1.6064 | 1.7152 | 1.824 | 1.9072 | 1.9904 | 2.0736 | 2.1568 | 2.24 | 2.2784 | 2.3168 | 2.3552 | 2.3936 | 2.432 | 2.4704 | 2.5088 | 2.5472 | 2.5856 | 2.624 | 2.6432 | 2.6624 | 2.6816 | 2.7008 | 2.72 | 2.7392 | 2.7584 | 2.7776 | 2.7968 | 2.816 | 2.8352 | 2.8544 | 2.8736 | 2.8928 | 2.912 | 2.9205 | 2.9291 | 2.9376 | 2.9461 | 2.9547 | 2.9632 | 2.9717 | 2.9803 | 2.9888 | 2.9973 | 3.0059 | 3.0144 | 3.0229 | 3.0315 | 3.04 | 3.0421 | 3.0443 | 3.0464 | 3.0485 | 3.0507 | 3.0528 | 3.0549 | 3.0571 | 3.0592 | 3.0613 | 3.0635 | 3.0656 | 3.0677 | 3.0699 | 3.072 | 3.0741 | 3.0763 | 3.0784 | 3.0805 | 3.0827 | 3.0848 | 3.0869 | 3.0891 | 3.0912 | 3.0933 | 3.0955 | 3.0976 | 3.0997 | 3.1019 | 3.104 | 3.1029 | 3.1019 | 3.1008 | 3.0997 | 3.0987 | 3.0976 | 3.0965 | 3.0955 | 3.0944 | 3.0933 | 3.0923 | 3.0912 | 3.0901 | 3.0891 | 3.088 | 3.0869 | 3.0859 | 3.0848 | 3.0837 | 3.0827 | 3.0816 | 3.0805 | 3.0795 | 3.0784 | 3.0773 | 3.0763 | 3.0752 | 3.0741 | 3.0731 | 3.072 | 3.0709 | 3.0699 | 3.0688 | 3.0677 | 3.0667 | 3.0656 | 3.0645 | 3.0635 | 3.0624 | 3.0613 | 3.0603 | 3.0592 | 3.0581 | 3.0571 | 3.056 | 3.0549 | 3.0539 | 3.0528 | 3.0517 | 3.0507 | 3.0496 | 3.0485 | 3.0475 | 3.0464 | 3.0453 | 3.0443 | 3.0432 | 3.0421 | 3.0411 | 3.04 | 3.0389 | 3.0379 | 3.0368 | 3.0357 | 3.0347 | 3.0336 | 3.0325 | 3.0315 | 3.0304 | 3.0293 | 3.0283 | 3.0272 | 3.0261 | 3.0251 | 3.024 | 3.0229 | 3.0219 | 3.0208 | 3.0197 | 3.0187 | 3.0176 | 3.0165 | 3.0155 | 3.0144 | 3.0133 | 3.0123 | 3.0112 | 3.0101 | 3.0091 | 3.008
2.45 | 0 | 1.365 | 1.947 | 2.395 | 2.802 | 3.111 | 3.255 | 3.327 | 3.296 | 3.265 | 3.234 | 0 | 0.1365 | 0.273 | 0.4095 | 0.546 | 0.6825 | 0.819 | 0.9555 | 1.092 | 1.2285 | 1.365 | 1.4814 | 1.5978 | 1.7142 | 1.8306 | 1.947 | 2.0366 | 2.1262 | 2.2158 | 2.3054 | 2.395 | 2.4357 | 2.4764 | 2.5171 | 2.5578 | 2.5985 | 2.6392 | 2.6799 | 2.7206 | 2.7613 | 2.802 | 2.8226 | 2.8432 | 2.8638 | 2.8844 | 2.905 | 2.9256 | 2.9462 | 2.9668 | 2.9874 | 3.008 | 3.0286 | 3.0492 | 3.0698 | 3.0904 | 3.111 | 3.1206 | 3.1302 | 3.1398 | 3.1494 | 3.159 | 3.1686 | 3.1782 | 3.1878 | 3.1974 | 3.207 | 3.2166 | 3.2262 | 3.2358 | 3.2454 | 3.255 | 3.2574 | 3.2598 | 3.2622 | 3.2646 | 3.267 | 3.2694 | 3.2718 | 3.2742 | 3.2766 | 3.279 | 3.2814 | 3.2838 | 3.2862 | 3.2886 | 3.291 | 3.2934 | 3.2958 | 3.2982 | 3.3006 | 3.303 | 3.3054 | 3.3078 | 3.3102 | 3.3126 | 3.315 | 3.3174 | 3.3198 | 3.3222 | 3.3246 | 3.327 | 3.326 | 3.3249 | 3.3239 | 3.3229 | 3.3218 | 3.3208 | 3.3198 | 3.3187 | 3.3177 | 3.3167 | 3.3156 | 3.3146 | 3.3136 | 3.3125 | 3.3115 | 3.3105 | 3.3094 | 3.3084 | 3.3074 | 3.3063 | 3.3053 | 3.3043 | 3.3032 | 3.3022 | 3.3012 | 3.3001 | 3.2991 | 3.2981 | 3.297 | 3.296 | 3.295 | 3.2939 | 3.2929 | 3.2919 | 3.2908 | 3.2898 | 3.2888 | 3.2877 | 3.2867 | 3.2857 | 3.2846 | 3.2836 | 3.2826 | 3.2815 | 3.2805 | 3.2795 | 3.2784 | 3.2774 | 3.2764 | 3.2753 | 3.2743 | 3.2733 | 3.2722 | 3.2712 | 3.2702 | 3.2691 | 3.2681 | 3.2671 | 3.266 | 3.265 | 3.264 | 3.2629 | 3.2619 | 3.2609 | 3.2598 | 3.2588 | 3.2578 | 3.2567 | 3.2557 | 3.2547 | 3.2536 | 3.2526 | 3.2516 | 3.2505 | 3.2495 | 3.2485 | 3.2474 | 3.2464 | 3.2454 | 3.2443 | 3.2433 | 3.2423 | 3.2412 | 3.2402 | 3.2392 | 3.2381 | 3.2371 | 3.2361 | 3.235 | 3.234
2.5 | 0 | 1.45 | 2.07 | 2.55 | 2.98 | 3.31 | 3.47 | 3.55 | 3.52 | 3.49 | 3.46 | 0 | 0.145 | 0.29 | 0.435 | 0.58 | 0.725 | 0.87 | 1.015 | 1.16 | 1.305 | 1.45 | 1.574 | 1.698 | 1.822 | 1.946 | 2.07 | 2.166 | 2.262 | 2.358 | 2.454 | 2.55 | 2.593 | 2.636 | 2.679 | 2.722 | 2.765 | 2.808 | 2.851 | 2.894 | 2.937 | 2.98 | 3.002 | 3.024 | 3.046 | 3.068 | 3.09 | 3.112 | 3.134 | 3.156 | 3.178 | 3.2 | 3.222 | 3.244 | 3.266 | 3.288 | 3.31 | 3.3207 | 3.3313 | 3.342 | 3.3527 | 3.3633 | 3.374 | 3.3847 | 3.3953 | 3.406 | 3.4167 | 3.4273 | 3.438 | 3.4487 | 3.4593 | 3.47 | 3.4727 | 3.4753 | 3.478 | 3.4807 | 3.4833 | 3.486 | 3.4887 | 3.4913 | 3.494 | 3.4967 | 3.4993 | 3.502 | 3.5047 | 3.5073 | 3.51 | 3.5127 | 3.5153 | 3.518 | 3.5207 | 3.5233 | 3.526 | 3.5287 | 3.5313 | 3.534 | 3.5367 | 3.5393 | 3.542 | 3.5447 | 3.5473 | 3.55 | 3.549 | 3.548 | 3.547 | 3.546 | 3.545 | 3.544 | 3.543 | 3.542 | 3.541 | 3.54 | 3.539 | 3.538 | 3.537 | 3.536 | 3.535 | 3.534 | 3.533 | 3.532 | 3.531 | 3.53 | 3.529 | 3.528 | 3.527 | 3.526 | 3.525 | 3.524 | 3.523 | 3.522 | 3.521 | 3.52 | 3.519 | 3.518 | 3.517 | 3.516 | 3.515 | 3.514 | 3.513 | 3.512 | 3.511 | 3.51 | 3.509 | 3.508 | 3.507 | 3.506 | 3.505 | 3.504 | 3.503 | 3.502 | 3.501 | 3.5 | 3.499 | 3.498 | 3.497 | 3.496 | 3.495 | 3.494 | 3.493 | 3.492 | 3.491 | 3.49 | 3.489 | 3.488 | 3.487 | 3.486 | 3.485 | 3.484 | 3.483 | 3.482 | 3.481 | 3.48 | 3.479 | 3.478 | 3.477 | 3.476 | 3.475 | 3.474 | 3.473 | 3.472 | 3.471 | 3.47 | 3.469 | 3.468 | 3.467 | 3.466 | 3.465 | 3.464 | 3.463 | 3.462 | 3.461 | 3.46
2.55 | 0 | 1.535 | 2.193 | 2.705 | 3.158 | 3.509 | 3.685 | 3.773 | 3.744 | 3.715 | 3.686 | 0 | 0.1535 | 0.307 | 0.4605 | 0.614 | 0.7675 | 0.921 | 1.0745 | 1.228 | 1.3815 | 1.535 | 1.6666 | 1.7982 | 1.9298 | 2.0614 | 2.193 | 2.2954 | 2.3978 | 2.5002 | 2.6026 | 2.705 | 2.7503 | 2.7956 | 2.8409 | 2.8862 | 2.9315 | 2.9768 | 3.0221 | 3.0674 | 3.1127 | 3.158 | 3.1814 | 3.2048 | 3.2282 | 3.2516 | 3.275 | 3.2984 | 3.3218 | 3.3452 | 3.3686 | 3.392 | 3.4154 | 3.4388 | 3.4622 | 3.4856 | 3.509 | 3.5207 | 3.5325 | 3.5442 | 3.5559 | 3.5677 | 3.5794 | 3.5911 | 3.6029 | 3.6146 | 3.6263 | 3.6381 | 3.6498 | 3.6615 | 3.6733 | 3.685 | 3.6879 | 3.6909 | 3.6938 | 3.6967 | 3.6997 | 3.7026 | 3.7055 | 3.7085 | 3.7114 | 3.7143 | 3.7173 | 3.7202 | 3.7231 | 3.7261 | 3.729 | 3.7319 | 3.7349 | 3.7378 | 3.7407 | 3.7437 | 3.7466 | 3.7495 | 3.7525 | 3.7554 | 3.7583 | 3.7613 | 3.7642 | 3.7671 | 3.7701 | 3.773 | 3.772 | 3.7711 | 3.7701 | 3.7691 | 3.7682 | 3.7672 | 3.7662 | 3.7653 | 3.7643 | 3.7633 | 3.7624 | 3.7614 | 3.7604 | 3.7595 | 3.7585 | 3.7575 | 3.7566 | 3.7556 | 3.7546 | 3.7537 | 3.7527 | 3.7517 | 3.7508 | 3.7498 | 3.7488 | 3.7479 | 3.7469 | 3.7459 | 3.745 | 3.744 | 3.743 | 3.7421 | 3.7411 | 3.7401 | 3.7392 | 3.7382 | 3.7372 | 3.7363 | 3.7353 | 3.7343 | 3.7334 | 3.7324 | 3.7314 | 3.7305 | 3.7295 | 3.7285 | 3.7276 | 3.7266 | 3.7256 | 3.7247 | 3.7237 | 3.7227 | 3.7218 | 3.7208 | 3.7198 | 3.7189 | 3.7179 | 3.7169 | 3.716 | 3.715 | 3.714 | 3.7131 | 3.7121 | 3.7111 | 3.7102 | 3.7092 | 3.7082 | 3.7073 | 3.7063 | 3.7053 | 3.7044 | 3.7034 | 3.7024 | 3.7015 | 3.7005 | 3.6995 | 3.6986 | 3.6976 | 3.6966 | 3.6957 | 3.6947 | 3.6937 | 3.6928 | 3.6918 | 3.6908 | 3.6899 | 3.6889 | 3.6879 | 3.687 | 3.686
2.6 | 0 | 1.62 | 2.316 | 2.86 | 3.336 | 3.708 | 3.9 | 3.996 | 3.968 | 3.94 | 3.912 | -1.1102e-16 | 0.162 | 0.324 | 0.486 | 0.648 | 0.81 | 0.972 | 1.134 | 1.296 | 1.458 | 1.62 | 1.7592 | 1.8984 | 2.0376 | 2.1768 | 2.316 | 2.4248 | 2.5336 | 2.6424 | 2.7512 | 2.86 | 2.9076 | 2.9552 | 3.0028 | 3.0504 | 3.098 | 3.1456 | 3.1932 | 3.2408 | 3.2884 | 3.336 | 3.3608 | 3.3856 | 3.4104 | 3.4352 | 3.46 | 3.4848 | 3.5096 | 3.5344 | 3.5592 | 3.584 | 3.6088 | 3.6336 | 3.6584 | 3.6832 | 3.708 | 3.7208 | 3.7336 | 3.7464 | 3.7592 | 3.772 | 3.7848 | 3.7976 | 3.8104 | 3.8232 | 3.836 | 3.8488 | 3.8616 | 3.8744 | 3.8872 | 3.9 | 3.9032 | 3.9064 | 3.9096 | 3.9128 | 3.916 | 3.9192 | 3.9224 | 3.9256 | 3.9288 | 3.932 | 3.9352 | 3.9384 | 3.9416 | 3.9448 | 3.948 | 3.9512 | 3.9544 | 3.9576 | 3.9608 | 3.964 | 3.9672 | 3.9704 | 3.9736 | 3.9768 | 3.98 | 3.9832 | 3.9864 | 3.9896 | 3.9928 | 3.996 | 3.9951 | 3.9941 | 3.9932 | 3.9923 | 3.9913 | 3.9904 | 3.9895 | 3.9885 | 3.9876 | 3.9867 | 3.9857 | 3.9848 | 3.9839 | 3.9829 | 3.982 | 3.9811 | 3.9801 | 3.9792 | 3.9783 | 3.9773 | 3.9764 | 3.9755 | 3.9745 | 3.9736 | 3.9727 | 3.9717 | 3.9708 | 3.9699 | 3.9689 | 3.968 | 3.9671 | 3.9661 | 3.9652 | 3.9643 | 3.9633 | 3.9624 | 3.9615 | 3.9605 | 3.9596 | 3.9587 | 3.9577 | 3.9568 | 3.9559 | 3.9549 | 3.954 | 3.9531 | 3.9521 | 3.9512 | 3.9503 | 3.9493 | 3.9484 | 3.9475 | 3.9465 | 3.9456 | 3.9447 | 3.9437 | 3.9428 | 3.9419 | 3.9409 | 3.94 | 3.9391 | 3.9381 | 3.9372 | 3.9363 | 3.9353 | 3.9344 | 3.9335 | 3.9325 | 3.9316 | 3.9307 | 3.9297 | 3.9288 | 3.9279 | 3.9269 | 3.926 | 3.9251 | 3.9241 | 3.9232 | 3.9223 | 3.9213 | 3.9204 | 3.9195 | 3.9185 | 3.9176 | 3.9167 | 3.9157 | 3.9148 | 3.9139 | 3.9129 | 3.912
2.65 | 0 | 1.705 | 2.439 | 3.015 | 3.514 | 3.907 | 4.115 | 4.219 | 4.192 | 4.165 | 4.138 | 0 | 0.1705 | 0.341 | 0.5115 | 0.682 | 0.8525 | 1.023 | 1.1935 | 1.364 | 1.5345 | 1.705 | 1.8518 | 1.9986 | 2.1454 | 2.2922 | 2.439 | 2.5542 | 2.6694 | 2.7846 | 2.8998 | 3.015 | 3.0649 | 3.1148 | 3.1647 | 3.2146 | 3.2645 | 3.3144 | 3.3643 | 3.4142 | 3.4641 | 3.514 | 3.5402 | 3.5664 | 3.5926 | 3.6188 | 3.645 | 3.6712 | 3.6974 | 3.7236 | 3.7498 | 3.776 | 3.8022 | 3.8284 | 3.8546 | 3.8808 | 3.907 | 3.9209 | 3.9347 | 3.9486 | 3.9625 | 3.9763 | 3.9902 | 4.0041 | 4.0179 | 4.0318 | 4.0457 | 4.0595 | 4.0734 | 4.0873 | 4.1011 | 4.115 | 4.1185 | 4.1219 | 4.1254 | 4.1289 | 4.1323 | 4.1358 | 4.1393 | 4.1427 | 4.1462 | 4.1497 | 4.1531 | 4.1566 | 4.1601 | 4.1635 | 4.167 | 4.1705 | 4.1739 | 4.1774 | 4.1809 | 4.1843 | 4.1878 | 4.1913 | 4.1947 | 4.1982 | 4.2017 | 4.2051 | 4.2086 | 4.2121 | 4.2155 | 4.219 | 4.2181 | 4.2172 | 4.2163 | 4.2154 | 4.2145 | 4.2136 | 4.2127 | 4.2118 | 4.2109 | 4.21 | 4.2091 | 4.2082 | 4.2073 | 4.2064 | 4.2055 | 4.2046 | 4.2037 | 4.2028 | 4.2019 | 4.201 | 4.2001 | 4.1992 | 4.1983 | 4.1974 | 4.1965 | 4.1956 | 4.1947 | 4.1938 | 4.1929 | 4.192 | 4.1911 | 4.1902 | 4.1893 | 4.1884 | 4.1875 | 4.1866 | 4.1857 | 4.1848 | 4.1839 | 4.183 | 4.1821 | 4.1812 | 4.1803 | 4.1794 | 4.1785 | 4.1776 | 4.1767 | 4.1758 | 4.1749 | 4.174 | 4.1731 | 4.1722 | 4.1713 | 4.1704 | 4.1695 | 4.1686 | 4.1677 | 4.1668 | 4.1659 | 4.165 | 4.1641 | 4.1632 | 4.1623 | 4.1614 | 4.1605 | 4.1596 | 4.1587 | 4.1578 | 4.1569 | 4.156 | 4.1551 | 4.1542 | 4.1533 | 4.1524 | 4.1515 | 4.1506 | 4.1497 | 4.1488 | 4.1479 | 4.147 | 4.1461 | 4.1452 | 4.1443 | 4.1434 | 4.1425 | 4.1416 | 4.1407 | 4.1398 | 4.1389 | 4.138
2.7 | 0 | 1.79 | 2.562 | 3.17 | 3.692 | 4.106 | 4.33 | 4.442 | 4.416 | 4.39 | 4.364 | 0 | 0.179 | 0.358 | 0.537 | 0.716 | 0.895 | 1.074 | 1.253 | 1.432 | 1.611 | 1.79 | 1.9444 | 2.0988 | 2.2532 | 2.4076 | 2.562 | 2.6836 | 2.8052 | 2.9268 | 3.0484 | 3.17 | 3.2222 | 3.2744 | 3.3266 | 3.3788 | 3.431 | 3.4832 | 3.5354 | 3.5876 | 3.6398 | 3.692 | 3.7196 | 3.7472 | 3.7748 | 3.8024 | 3.83 | 3.8576 | 3.8852 | 3.9128 | 3.9404 | 3.968 | 3.9956 | 4.0232 | 4.0508 | 4.0784 | 4.106 | 4.1209 | 4.1359 | 4.1508 | 4.1657 | 4.1807 | 4.1956 | 4.2105 | 4.2255 | 4.2404 | 4.2553 | 4.2703 | 4.2852 | 4.3001 | 4.3151 | 4.33 | 4.3337 | 4.3375 | 4.3412 | 4.3449 | 4.3487 | 4.3524 | 4.3561 | 4.3599 | 4.3636 | 4.3673 | 4.3711 | 4.3748 | 4.3785 | 4.3823 | 4.386 | 4.3897 | 4.3935 | 4.3972 | 4.4009 | 4.4047 | 4.4084 | 4.4121 | 4.4159 | 4.4196 | 4.4233 | 4.4271 | 4.4308 | 4.4345 | 4.4383 | 4.442 | 4.4411 | 4.4403 | 4.4394 | 4.4385 | 4.4377 | 4.4368 | 4.4359 | 4.4351 | 4.4342 | 4.4333 | 4.4325 | 4.4316 | 4.4307 | 4.4299 | 4.429 | 4.4281 | 4.4273 | 4.4264 | 4.4255 | 4.4247 | 4.4238 | 4.4229 | 4.4221 | 4.4212 | 4.4203 | 4.4195 | 4.4186 | 4.4177 | 4.4169 | 4.416 | 4.4151 | 4.4143 | 4.4134 | 4.4125 | 4.4117 | 4.4108 | 4.4099 | 4.4091 | 4.4082 | 4.4073 | 4.4065 | 4.4056 | 4.4047 | 4.4039 | 4.403 | 4.4021 | 4.4013 | 4.4004 | 4.3995 | 4.3987 | 4.3978 | 4.3969 | 4.3961 | 4.3952 | 4.3943 | 4.3935 | 4.3926 | 4.3917 | 4.3909 | 4.39 | 4.3891 | 4.3883 | 4.3874 | 4.3865 | 4.3857 | 4.3848 | 4.3839 | 4.3831 | 4.3822 | 4.3813 | 4.3805 | 4.3796 | 4.3787 | 4.3779 | 4.377 | 4.3761 | 4.3753 | 4.3744 | 4.3735 | 4.3727 | 4.3718 | 4.3709 | 4.3701 | 4.3692 | 4.3683 | 4.3675 | 4.3666 | 4.3657 | 4.3649 | 4.364
2.75 | 0 | 1.875 | 2.685 | 3.325 | 3.87 | 4.305 | 4.545 | 4.665 | 4.64 | 4.615 | 4.59 | 0 | 0.1875 | 0.375 | 0.5625 | 0.75 | 0.9375 | 1.125 | 1.3125 | 1.5 | 1.6875 | 1.875 | 2.037 | 2.199 | 2.361 | 2.523 | 2.685 | 2.813 | 2.941 | 3.069 | 3.197 | 3.325 | 3.3795 | 3.434 | 3.4885 | 3.543 | 3.5975 | 3.652 | 3.7065 | 3.761 | 3.8155 | 3.87 | 3.899 | 3.928 | 3.957 | 3.986 | 4.015 | 4.044 | 4.073 | 4.102 | 4.131 | 4.16 | 4.189 | 4.218 | 4.247 | 4.276 | 4.305 | 4.321 | 4.337 | 4.353 | 4.369 | 4.385 | 4.401 | 4.417 | 4.433 | 4.449 | 4.465 | 4.481 | 4.497 | 4.513 | 4.529 | 4.545 | 4.549 | 4.553 | 4.557 | 4.561 | 4.565 | 4.569 | 4.573 | 4.577 | 4.581 | 4.585 | 4.589 | 4.593 | 4.597 | 4.601 | 4.605 | 4.609 | 4.613 | 4.617 | 4.621 | 4.625 | 4.629 | 4.633 | 4.637 | 4.641 | 4.645 | 4.649 | 4.653 | 4.657 | 4.661 | 4.665 | 4.6642 | 4.6633 | 4.6625 | 4.6617 | 4.6608 | 4.66 | 4.6592 | 4.6583 | 4.6575 | 4.6567 | 4.6558 | 4.655 | 4.6542 | 4.6533 | 4.6525 | 4.6517 | 4.6508 | 4.65 | 4.6492 | 4.6483 | 4.6475 | 4.6467 | 4.6458 | 4.645 | 4.6442 | 4.6433 | 4.6425 | 4.6417 | 4.6408 | 4.64 | 4.6392 | 4.6383 | 4.6375 | 4.6367 | 4.6358 | 4.635 | 4.6342 | 4.6333 | 4.6325 | 4.6317 | 4.6308 | 4.63 | 4.6292 | 4.6283 | 4.6275 | 4.6267 | 4.6258 | 4.625 | 4.6242 | 4.6233 | 4.6225 | 4.6217 | 4.6208 | 4.62 | 4.6192 | 4.6183 | 4.6175 | 4.6167 | 4.6158 | 4.615 | 4.6142 | 4.6133 | 4.6125 | 4.6117 | 4.6108 | 4.61 | 4.6092 | 4.6083 | 4.6075 | 4.6067 | 4.6058 | 4.605 | 4.6042 | 4.6033 | 4.6025 | 4.6017 | 4.6008 | 4.6 | 4.5992 | 4.5983 | 4.5975 | 4.5967 | 4.5958 | 4.595 | 4.5942 | 4.5933 | 4.5925 | 4.5917 | 4.5908 | 4.59
2.8 | 0 | 1.96 | 2.808 | 3.48 | 4.048 | 4.504 | 4.76 | 4.888 | 4.864 | 4.84 | 4.816 | 0 | 0.196 | 0.392 | 0.588 | 0.784 | 0.98 | 1.176 | 1.372 | 1.568 | 1.764 | 1.96 | 2.1296 | 2.2992 | 2.4688 | 2.6384 | 2.808 | 2.9424 | 3.0768 | 3.2112 | 3.3456 | 3.48 | 3.5368 | 3.5936 | 3.6504 | 3.7072 | 3.764 | 3.8208 | 3.8776 | 3.9344 | 3.9912 | 4.048 | 4.0784 | 4.1088 | 4.1392 | 4.1696 | 4.2 | 4.2304 | 4.2608 | 4.2912 | 4.3216 | 4.352 | 4.3824 | 4.4128 | 4.4432 | 4.4736 | 4.504 | 4.5211 | 4.5381 | 4.5552 | 4.5723 | 4.5893 | 4.6064 | 4.6235 | 4.6405 | 4.6576 | 4.6747 | 4.6917 | 4.7088 | 4.7259 | 4.7429 | 4.76 | 4.7643 | 4.7685 | 4.7728 | 4.7771 | 4.7813 | 4.7856 | 4.7899 | 4.7941 | 4.7984 | 4.8027 | 4.8069 | 4.8112 | 4.8155 | 4.8197 | 4.824 | 4.8283 | 4.8325 | 4.8368 | 4.8411 | 4.8453 | 4.8496 | 4.8539 | 4.8581 | 4.8624 | 4.8667 | 4.8709 | 4.8752 | 4.8795 | 4.8837 | 4.888 | 4.8872 | 4.8864 | 4.8856 | 4.8848 | 4.884 | 4.8832 | 4.8824 | 4.8816 | 4.8808 | 4.88 | 4.8792 | 4.8784 | 4.8776 | 4.8768 | 4.876 | 4.8752 | 4.8744 | 4.8736 | 4.8728 | 4.872 | 4.8712 | 4.8704 | 4.8696 | 4.8688 | 4.868 | 4.8672 | 4.8664 | 4.8656 | 4.8648 | 4.864 | 4.8632 | 4.8624 | 4.8616 | 4.8608 | 4.86 | 4.8592 | 4.8584 | 4.8576 | 4.8568 | 4.856 | 4.8552 | 4.8544 | 4.8536 | 4.8528 | 4.852 | 4.8512 | 4.8504 | 4.8496 | 4.8488 | 4.848 | 4.8472 | 4.8464 | 4.8456 | 4.8448 | 4.844 | 4.8432 | 4.8424 | 4.8416 | 4.8408 | 4.84 | 4.8392 | 4.8384 | 4.8376 | 4.8368 | 4.836 | 4.8352 | 4.8344 | 4.8336 | 4.8328 | 4.832 | 4.8312 | 4.8304 | 4.8296 | 4.8288 | 4.828 | 4.8272 | 4.8264 | 4.8256 | 4.8248 | 4.824 | 4.8232 | 4.8224 | 4.8216 | 4.8208 | 4.82 | 4.8192 | 4.8184 | 4.8176 | 4.8168 | 4.816
2.85 | 0 | 2.045 | 2.931 | 3.635 | 4.226 | 4.703 | 4.975 | 5.111 | 5.088 | 5.065 | 5.042 | 0 | 0.2045 | 0.409 | 0.6135 | 0.818 | 1.0225 | 1.227 | 1.4315 | 1.636 | 1.8405 | 2.045 | 2.2222 | 2.3994 | 2.5766 | 2.7538 | 2.931 | 3.0718 | 3.2126 | 3.3534 | 3.4942 | 3.635 | 3.6941 | 3.7532 | 3.8123 | 3.8714 | 3.9305 | 3.9896 | 4.0487 | 4.1078 | 4.1669 | 4.226 | 4.2578 | 4.2896 | 4.3214 | 4.3532 | 4.385 | 4.4168 | 4.4486 | 4.4804 | 4.5122 | 4.544 | 4.5758 | 4.6076 | 4.6394 | 4.6712 | 4.703 | 4.7211 | 4.7393 | 4.7574 | 4.7755 | 4.7937 | 4.8118 | 4.8299 | 4.8481 | 4.8662 | 4.8843 | 4.9025 | 4.9206 | 4.9387 | 4.9569 | 4.975 | 4.9795 | 4.9841 | 4.9886 | 4.9931 | 4.9977 | 5.0022 | 5.0067 | 5.0113 | 5.0158 | 5.0203 | 5.0249 | 5.0294 | 5.0339 | 5.0385 | 5.043 | 5.0475 | 5.0521 | 5.0566 | 5.0611 | 5.0657 | 5.0702 | 5.0747 | 5.0793 | 5.0838 | 5.0883 | 5.0929 | 5.0974 | 5.1019 | 5.1065 | 5.111 | 5.1102 | 5.1095 | 5.1087 | 5.1079 | 5.1072 | 5.1064 | 5.1056 | 5.1049 | 5.1041 | 5.1033 | 5.1026 | 5.1018 | 5.101 | 5.1003 | 5.0995 | 5.0987 | 5.098 | 5.0972 | 5.0964 | 5.0957 | 5.0949 | 5.0941 | 5.0934 | 5.0926 | 5.0918 | 5.0911 | 5.0903 | 5.0895 | 5.0888 | 5.088 | 5.0872 | 5.0865 | 5.0857 | 5.0849 | 5.0842 | 5.0834 | 5.0826 | 5.0819 | 5.0811 | 5.0803 | 5.0796 | 5.0788 | 5.078 | 5.0773 | 5.0765 | 5.0757 | 5.075 | 5.0742 | 5.0734 | 5.0727 | 5.0719 | 5.0711 | 5.0704 | 5.0696 | 5.0688 | 5.0681 | 5.0673 | 5.0665 | 5.0658 | 5.065 | 5.0642 | 5.0635 | 5.0627 | 5.0619 | 5.0612 | 5.0604 | 5.0596 | 5.0589 | 5.0581 | 5.0573 | 5.0566 | 5.0558 | 5.055 | 5.0543 | 5.0535 | 5.0527 | 5.052 | 5.0512 | 5.0504 | 5.0497 | 5.0489 | 5.0481 | 5.0474 | 5.0466 | 5.0458 | 5.0451 | 5.0443 | 5.0435 | 5.0428 | 5.042
2.9 | 0 | 2.13 | 3.054 | 3.79 | 4.404 | 4.902 | 5.19 | 5.334 | 5.312 | 5.29 | 5.268 | 0 | 0.213 | 0.426 | 0.639 | 0.852 | 1.065 | 1.278 | 1.491 | 1.704 | 1.917 | 2.13 | 2.3148 | 2.4996 | 2.6844 | 2.8692 | 3.054 | 3.2012 | 3.3484 | 3.4956 | 3.6428 | 3.79 | 3.8514 | 3.9128 | 3.9742 | 4.0356 | 4.097 | 4.1584 | 4.2198 | 4.2812 | 4.3426 | 4.404 | 4.4372 | 4.4704 | 4.5036 | 4.5368 | 4.57 | 4.6032 | 4.6364 | 4.6696 | 4.7028 | 4.736 | 4.7692 | 4.8024 | 4.8356 | 4.8688 | 4.902 | 4.9212 | 4.9404 | 4.9596 | 4.9788 | 4.998 | 5.0172 | 5.0364 | 5.0556 | 5.0748 | 5.094 | 5.1132 | 5.1324 | 5.1516 | 5.1708 | 5.19 | 5.1948 | 5.1996 | 5.2044 | 5.2092 | 5.214 | 5.2188 | 5.2236 | 5.2284 | 5.2332 | 5.238 | 5.2428 | 5.2476 | 5.2524 | 5.2572 | 5.262 | 5.2668 | 5.2716 | 5.2764 | 5.2812 | 5.286 | 5.2908 | 5.2956 | 5.3004 | 5.3052 | 5.31 | 5.3148 | 5.3196 | 5.3244 | 5.3292 | 5.334 | 5.3333 | 5.3325 | 5.3318 | 5.3311 | 5.3303 | 5.3296 | 5.3289 | 5.3281 | 5.3274 | 5.3267 | 5.3259 | 5.3252 | 5.3245 | 5.3237 | 5.323 | 5.3223 | 5.3215 | 5.3208 | 5.3201 | 5.3193 | 5.3186 | 5.3179 | 5.3171 | 5.3164 | 5.3157 | 5.3149 | 5.3142 | 5.3135 | 5.3127 | 5.312 | 5.3113 | 5.3105 | 5.3098 | 5.3091 | 5.3083 | 5.3076 | 5.3069 | 5.3061 | 5.3054 | 5.3047 | 5.3039 | 5.3032 | 5.3025 | 5.3017 | 5.301 | 5.3003 | 5.2995 | 5.2988 | 5.2981 | 5.2973 | 5.2966 | 5.2959 | 5.2951 | 5.2944 | 5.2937 | 5.2929 | 5.2922 | 5.2915 | 5.2907 | 5.29 | 5.2893 | 5.2885 | 5.2878 | 5.2871 | 5.2863 | 5.2856 | 5.2849 | 5.2841 | 5.2834 | 5.2827 | 5.2819 | 5.2812 | 5.2805 | 5.2797 | 5.279 | 5.2783 | 5.2775 | 5.2768 | 5.2761 | 5.2753 | 5.2746 | 5.2739 | 5.2731 | 5.2724 | 5.2717 | 5.2709 | 5.2702 | 5.2695 | 5.2687 | 5.268
2.95 | 0 | 2.215 | 3.177 | 3.945 | 4.582 | 5.101 | 5.405 | 5.557 | 5.536 | 5.515 | 5.494 | 0 | 0.2215 | 0.443 | 0.6645 | 0.886 | 1.1075 | 1.329 | 1.5505 | 1.772 | 1.9935 | 2.215 | 2.4074 | 2.5998 | 2.7922 | 2.9846 | 3.177 | 3.3306 | 3.4842 | 3.6378 | 3.7914 | 3.945 | 4.0087 | 4.0724 | 4.1361 | 4.1998 | 4.2635 | 4.3272 | 4.3909 | 4.4546 | 4.5183 | 4.582 | 4.6166 | 4.6512 | 4.6858 | 4.7204 | 4.755 | 4.7896 | 4.8242 | 4.8588 | 4.8934 | 4.928 | 4.9626 | 4.9972 | 5.0318 | 5.0664 | 5.101 | 5.1213 | 5.1415 | 5.1618 | 5.1821 | 5.2023 | 5.2226 | 5.2429 | 5.2631 | 5.2834 | 5.3037 | 5.3239 | 5.3442 | 5.3645 | 5.3847 | 5.405 | 5.4101 | 5.4151 | 5.4202 | 5.4253 | 5.4303 | 5.4354 | 5.4405 | 5.4455 | 5.4506 | 5.4557 | 5.4607 | 5.4658 | 5.4709 | 5.4759 | 5.481 | 5.4861 | 5.4911 | 5.4962 | 5.5013 | 5.5063 | 5.5114 | 5.5165 | 5.5215 | 5.5266 | 5.5317 | 5.5367 | 5.5418 | 5.5469 | 5.5519 | 5.557 | 5.5563 | 5.5556 | 5.5549 | 5.5542 | 5.5535 | 5.5528 | 5.5521 | 5.5514 | 5.5507 | 5.55 | 5.5493 | 5.5486 | 5.5479 | 5.5472 | 5.5465 | 5.5458 | 5.5451 | 5.5444 | 5.5437 | 5.543 | 5.5423 | 5.5416 | 5.5409 | 5.5402 | 5.5395 | 5.5388 | 5.5381 | 5.5374 | 5.5367 | 5.536 | 5.5353 | 5.5346 | 5.5339 | 5.5332 | 5.5325 | 5.5318 | 5.5311 | 5.5304 | 5.5297 | 5.529 | 5.5283 | 5.5276 | 5.5269 | 5.5262 | 5.5255 | 5.5248 | 5.5241 | 5.5234 | 5.5227 | 5.522 | 5.5213 | 5.5206 | 5.5199 | 5.5192 | 5.5185 | 5.5178 | 5.5171 | 5.5164 | 5.5157 | 5.515 | 5.5143 | 5.5136 | 5.5129 | 5.5122 | 5.5115 | 5.5108 | 5.5101 | 5.5094 | 5.5087 | 5.508 | 5.5073 | 5.5066 | 5.5059 | 5.5052 | 5.5045 | 5.5038 | 5.5031 | 5.5024 | 5.5017 | 5.501 | 5.5003 | 5.4996 | 5.4989 | 5.4982 | 5.4975 | 5.4968 | 5.4961 | 5.4954 | 5.4947 | 5.494
3 | 0 | 2.3 | 3.3 | 4.1 | 4.76 | 5.3 | 5.62 | 5.78 | 5.76 | 5.74 | 5.72 | -2.2204e-16 | 0.23 | 0.46 | 0.69 | 0.92 | 1.15 | 1.38 | 1.61 | 1.84 | 2.07 | 2.3 | 2.5 | 2.7 | 2.9 | 3.1 | 3.3 | 3.46 | 3.62 | 3.78 | 3.94 | 4.1 | 4.166 | 4.232 | 4.298 | 4.364 | 4.43 | 4.496 | 4.562 | 4.628 | 4.694 | 4.76 | 4.796 | 4.832 | 4.868 | 4.904 | 4.94 | 4.976 | 5.012 | 5.048 | 5.084 | 5.12 | 5.156 | 5.192 | 5.228 | 5.264 | 5.3 | 5.3213 | 5.3427 | 5.364 | 5.3853 | 5.4067 | 5.428 | 5.4493 | 5.4707 | 5.492 | 5.5133 | 5.5347 | 5.556 | 5.5773 | 5.5987 | 5.62 | 5.6253 | 5.6307 | 5.636 | 5.6413 | 5.6467 | 5.652 | 5.6573 | 5.6627 | 5.668 | 5.6733 | 5.6787 | 5.684 | 5.6893 | 5.6947 | 5.7 | 5.7053 | 5.7107 | 5.716 | 5.7213 | 5.7267 | 5.732 | 5.7373 | 5.7427 | 5.748 | 5.7533 | 5.7587 | 5.764 | 5.7693 | 5.7747 | 5.78 | 5.7793 | 5.7787 | 5.778 | 5.7773 | 5.7767 | 5.776 | 5.7753 | 5.7747 | 5.774 | 5.7733 | 5.7727 | 5.772 | 5.7713 | 5.7707 | 5.77 | 5.7693 | 5.7687 | 5.768 | 5.7673 | 5.7667 | 5.766 | 5.7653 | 5.7647 | 5.764 | 5.7633 | 5.7627 | 5.762 | 5.7613 | 5.7607 | 5.76 | 5.7593 | 5.7587 | 5.758 | 5.7573 | 5.7567 | 5.756 | 5.7553 | 5.7547 | 5.754 | 5.7533 | 5.7527 | 5.752 | 5.7513 | 5.7507 | 5.75 | 5.7493 | 5.7487 | 5.748 | 5.7473 | 5.7467 | 5.746 | 5.7453 | 5.7447 | 5.744 | 5.7433 | 5.7427 | 5.742 | 5.7413 | 5.7407 | 5.74 | 5.7393 | 5.7387 | 5.738 | 5.7373 | 5.7367 | 5.736 | 5.7353 | 5.7347 | 5.734 | 5.7333 | 5.7327 | 5.732 | 5.7313 | 5.7307 | 5.73 | 5.7293 | 5.7287 | 5.728 | 5.7273 | 5.7267 | 5.726 | 5.7253 | 5.7247 | 5.724 | 5.7233 | 5.7227 | 5.722 | 5.7213 | 5.7207 | 5.72
3.05 | 0 | 2.385 | 3.423 | 4.255 | 4.938 | 5.499 | 5.835 | 6.003 | 5.984 | 5.965 | 5.946 | 0 | 0.2385 | 0.477 | 0.7155 | 0.954 | 1.1925 | 1.431 | 1.6695 | 1.908 | 2.1465 | 2.385 | 2.5926 | 2.8002 | 3.0078 | 3.2154 | 3.423 | 3.5894 | 3.7558 | 3.9222 | 4.0886 | 4.255 | 4.3233 | 4.3916 | 4.4599 | 4.5282 | 4.5965 | 4.6648 | 4.7331 | 4.8014 | 4.8697 | 4.938 | 4.9754 | 5.0128 | 5.0502 | 5.0876 | 5.125 | 5.1624 | 5.1998 | 5.2372 | 5.2746 | 5.312 | 5.3494 | 5.3868 | 5.4242 | 5.4616 | 5.499 | 5.5214 | 5.5438 | 5.5662 | 5.5886 | 5.611 | 5.6334 | 5.6558 | 5.6782 | 5.7006 | 5.723 | 5.7454 | 5.7678 | 5.7902 | 5.8126 | 5.835 | 5.8406 | 5.8462 | 5.8518 | 5.8574 | 5.863 | 5.8686 | 5.8742 | 5.8798 | 5.8854 | 5.891 | 5.8966 | 5.9022 | 5.9078 | 5.9134 | 5.919 | 5.9246 | 5.9302 | 5.9358 | 5.9414 | 5.947 | 5.9526 | 5.9582 | 5.9638 | 5.9694 | 5.975 | 5.9806 | 5.9862 | 5.9918 | 5.9974 | 6.003 | 6.0024 | 6.0017 | 6.0011 | 6.0005 | 5.9998 | 5.9992 | 5.9986 | 5.9979 | 5.9973 | 5.9967 | 5.996 | 5.9954 | 5.9948 | 5.9941 | 5.9935 | 5.9929 | 5.9922 | 5.9916 | 5.991 | 5.9903 | 5.9897 | 5.9891 | 5.9884 | 5.9878 | 5.9872 | 5.9865 | 5.9859 | 5.9853 | 5.9846 | 5.984 | 5.9834 | 5.9827 | 5.9821 | 5.9815 | 5.9808 | 5.9802 | 5.9796 | 5.9789 | 5.9783 | 5.9777 | 5.977 | 5.9764 | 5.9758 | 5.9751 | 5.9745 | 5.9739 | 5.9732 | 5.9726 | 5.972 | 5.9713 | 5.9707 | 5.9701 | 5.9694 | 5.9688 | 5.9682 | 5.9675 | 5.9669 | 5.9663 | 5.9656 | 5.965 | 5.9644 | 5.9637 | 5.9631 | 5.9625 | 5.9618 | 5.9612 | 5.9606 | 5.9599 | 5.9593 | 5.9587 | 5.958 | 5.9574 | 5.9568 | 5.9561 | 5.9555 | 5.9549 | 5.9542 | 5.9536 | 5.953 | 5.9523 | 5.9517 | 5.9511 | 5.9504 | 5.9498 | 5.9492 | 5.9485 | 5.9479 | 5.9473 | 5.9466 | 5.946
3.1 | 0 | 2.47 | 3.546 | 4.41 | 5.116 | 5.698 | 6.05 | 6.226 | 6.208 | 6.19 | 6.172 | 0 | 0.247 | 0.494 | 0.741 | 0.988 | 1.235 | 1.482 | 1.729 | 1.976 | 2.223 | 2.47 | 2.6852 | 2.9004 | 3.1156 | 3.3308 | 3.546 | 3.7188 | 3.8916 | 4.0644 | 4.2372 | 4.41 | 4.4806 | 4.5512 | 4.6218 | 4.6924 | 4.763 | 4.8336 | 4.9042 | 4.9748 | 5.0454 | 5.116 | 5.1548 | 5.1936 | 5.2324 | 5.2712 | 5.31 | 5.3488 | 5.3876 | 5.4264 | 5.4652 | 5.504 | 5.5428 | 5.5816 | 5.6204 | 5.6592 | 5.698 | 5.7215 | 5.7449 | 5.7684 | 5.7919 | 5.8153 | 5.8388 | 5.8623 | 5.8857 | 5.9092 | 5.9327 | 5.9561 | 5.9796 | 6.0031 | 6.0265 | 6.05 | 6.0559 | 6.0617 | 6.0676 | 6.0735 | 6.0793 | 6.0852 | 6.0911 | 6.0969 | 6.1028 | 6.1087 | 6.1145 | 6.1204 | 6.1263 | 6.1321 | 6.138 | 6.1439 | 6.1497 | 6.1556 | 6.1615 | 6.1673 | 6.1732 | 6.1791 | 6.1849 | 6.1908 | 6.1967 | 6.2025 | 6.2084 | 6.2143 | 6.2201 | 6.226 | 6.2254 | 6.2248 | 6.2242 | 6.2236 | 6.223 | 6.2224 | 6.2218 | 6.2212 | 6.2206 | 6.22 | 6.2194 | 6.2188 | 6.2182 | 6.2176 | 6.217 | 6.2164 | 6.2158 | 6.2152 | 6.2146 | 6.214 | 6.2134 | 6.2128 | 6.2122 | 6.2116 | 6.211 | 6.2104 | 6.2098 | 6.2092 | 6.2086 | 6.208 | 6.2074 | 6.2068 | 6.2062 | 6.2056 | 6.205 | 6.2044 | 6.2038 | 6.2032 | 6.2026 | 6.202 | 6.2014 | 6.2008 | 6.2002 | 6.1996 | 6.199 | 6.1984 | 6.1978 | 6.1972 | 6.1966 | 6.196 | 6.1954 | 6.1948 | 6.1942 | 6.1936 | 6.193 | 6.1924 | 6.1918 | 6.1912 | 6.1906 | 6.19 | 6.1894 | 6.1888 | 6.1882 | 6.1876 | 6.187 | 6.1864 | 6.1858 | 6.1852 | 6.1846 | 6.184 | 6.1834 | 6.1828 | 6.1822 | 6.1816 | 6.181 | 6.1804 | 6.1798 | 6.1792 | 6.1786 | 6.178 | 6.1774 | 6.1768 | 6.1762 | 6.1756 | 6.175 | 6.1744 | 6.1738 | 6.1732 | 6.1726 | 6.172
3.15 | 0 | 2.555 | 3.669 | 4.565 | 5.294 | 5.897 | 6.265 | 6.449 | 6.432 | 6.415 | 6.398 | 0 | 0.2555 | 0.511 | 0.7665 | 1.022 | 1.2775 | 1.533 | 1.7885 | 2.044 | 2.2995 | 2.555 | 2.7778 | 3.0006 | 3.2234 | 3.4462 | 3.669 | 3.8482 | 4.0274 | 4.2066 | 4.3858 | 4.565 | 4.6379 | 4.7108 | 4.7837 | 4.8566 | 4.9295 | 5.0024 | 5.0753 | 5.1482 | 5.2211 | 5.294 | 5.3342 | 5.3744 | 5.4146 | 5.4548 | 5.495 | 5.5352 | 5.5754 | 5.6156 | 5.6558 | 5.696 | 5.7362 | 5.7764 | 5.8166 | 5.8568 | 5.897 | 5.9215 | 5.9461 | 5.9706 | 5.9951 | 6.0197 | 6.0442 | 6.0687 | 6.0933 | 6.1178 | 6.1423 | 6.1669 | 6.1914 | 6.2159 | 6.2405 | 6.265 | 6.2711 | 6.2773 | 6.2834 | 6.2895 | 6.2957 | 6.3018 | 6.3079 | 6.3141 | 6.3202 | 6.3263 | 6.3325 | 6.3386 | 6.3447 | 6.3509 | 6.357 | 6.3631 | 6.3693 | 6.3754 | 6.3815 | 6.3877 | 6.3938 | 6.3999 | 6.4061 | 6.4122 | 6.4183 | 6.4245 | 6.4306 | 6.4367 | 6.4429 | 6.449 | 6.4484 | 6.4479 | 6.4473 | 6.4467 | 6.4462 | 6.4456 | 6.445 | 6.4445 | 6.4439 | 6.4433 | 6.4428 | 6.4422 | 6.4416 | 6.4411 | 6.4405 | 6.4399 | 6.4394 | 6.4388 | 6.4382 | 6.4377 | 6.4371 | 6.4365 | 6.436 | 6.4354 | 6.4348 | 6.4343 | 6.4337 | 6.4331 | 6.4326 | 6.432 | 6.4314 | 6.4309 | 6.4303 | 6.4297 | 6.4292 | 6.4286 | 6.428 | 6.4275 | 6.4269 | 6.4263 | 6.4258 | 6.4252 | 6.4246 | 6.4241 | 6.4235 | 6.4229 | 6.4224 | 6.4218 | 6.4212 | 6.4207 | 6.4201 | 6.4195 | 6.419 | 6.4184 | 6.4178 | 6.4173 | 6.4167 | 6.4161 | 6.4156 | 6.415 | 6.4144 | 6.4139 | 6.4133 | 6.4127 | 6.4122 | 6.4116 | 6.411 | 6.4105 | 6.4099 | 6.4093 | 6.4088 | 6.4082 | 6.4076 | 6.4071 | 6.4065 | 6.4059 | 6.4054 | 6.4048 | 6.4042 | 6.4037 | 6.4031 | 6.4025 | 6.402 | 6.4014 | 6.4008 | 6.4003 | 6.3997 | 6.3991 | 6.3986 | 6.398
3.2 | 0 | 2.64 | 3.792 | 4.72 | 5.472 | 6.096 | 6.48 | 6.672 | 6.656 | 6.64 | 6.624 | 0 | 0.264 | 0.528 | 0.792 | 1.056 | 1.32 | 1.584 | 1.848 | 2.112 | 2.376 | 2.64 | 2.8704 | 3.1008 | 3.3312 | 3.5616 | 3.792 | 3.9776 | 4.1632 | 4.3488 | 4.5344 | 4.72 | 4.7952 | 4.8704 | 4.9456 | 5.0208 | 5.096 | 5.1712 | 5.2464 | 5.3216 | 5.3968 | 5.472 | 5.5136 | 5.5552 | 5.5968 | 5.6384 | 5.68 | 5.7216 | 5.7632 | 5.8048 | 5.8464 | 5.888 | 5.9296 | 5.9712 | 6.0128 | 6.0544 | 6.096 | 6.1216 | 6.1472 | 6.1728 | 6.1984 | 6.224 | 6.2496 | 6.2752 | 6.3008 | 6.3264 | 6.352 | 6.3776 | 6.4032 | 6.4288 | 6.4544 | 6.48 | 6.4864 | 6.4928 | 6.4992 | 6.5056 | 6.512 | 6.5184 | 6.5248 | 6.5312 | 6.5376 | 6.544 | 6.5504 | 6.5568 | 6.5632 | 6.5696 | 6.576 | 6.5824 | 6.5888 | 6.5952 | 6.6016 | 6.608 | 6.6144 | 6.6208 | 6.6272 | 6.6336 | 6.64 | 6.6464 | 6.6528 | 6.6592 | 6.6656 | 6.672 | 6.6715 | 6.6709 | 6.6704 | 6.6699 | 6.6693 | 6.6688 | 6.6683 | 6.6677 | 6.6672 | 6.6667 | 6.6661 | 6.6656 | 6.6651 | 6.6645 | 6.664 | 6.6635 | 6.6629 | 6.6624 | 6.6619 | 6.6613 | 6.6608 | 6.6603 | 6.6597 | 6.6592 | 6.6587 | 6.6581 | 6.6576 | 6.6571 | 6.6565 | 6.656 | 6.6555 | 6.6549 | 6.6544 | 6.6539 | 6.6533 | 6.6528 | 6.6523 | 6.6517 | 6.6512 | 6.6507 | 6.6501 | 6.6496 | 6.6491 | 6.6485 | 6.648 | 6.6475 | 6.6469 | 6.6464 | 6.6459 | 6.6453 | 6.6448 | 6.6443 | 6.6437 | 6.6432 | 6.6427 | 6.6421 | 6.6416 | 6.6411 | 6.6405 | 6.64 | 6.6395 | 6.6389 | 6.6384 | 6.6379 | 6.6373 | 6.6368 | 6.6363 | 6.6357 | 6.6352 | 6.6347 | 6.6341 | 6.6336 | 6.6331 | 6.6325 | 6.632 | 6.6315 | 6.6309 | 6.6304 | 6.6299 | 6.6293 | 6.6288 | 6.6283 | 6.6277 | 6.6272 | 6.6267 | 6.6261 | 6.6256 | 6.6251 | 6.6245 | 6.624
3.25 | 0 | 2.725 | 3.915 | 4.875 | 5.65 | 6.295 | 6.695 | 6.895 | 6.88 | 6.865 | 6.85 | 0 | 0.2725 | 0.545 | 0.8175 | 1.09 | 1.3625 | 1.635 | 1.9075 | 2.18 | 2.4525 | 2.725 | 2.963 | 3.201 | 3.439 | 3.677 | 3.915 | 4.107 | 4.299 | 4.491 | 4.683 | 4.875 | 4.9525 | 5.03 | 5.1075 | 5.185 | 5.2625 | 5.34 | 5.4175 | 5.495 | 5.5725 | 5.65 | 5.693 | 5.736 | 5.779 | 5.822 | 5.865 | 5.908 | 5.951 | 5.994 | 6.037 | 6.08 | 6.123 | 6.166 | 6.209 | 6.252 | 6.295 | 6.3217 | 6.3483 | 6.375 | 6.4017 | 6.4283 | 6.455 | 6.4817 | 6.5083 | 6.535 | 6.5617 | 6.5883 | 6.615 | 6.6417 | 6.6683 | 6.695 | 6.7017 | 6.7083 | 6.715 | 6.7217 | 6.7283 | 6.735 | 6.7417 | 6.7483 | 6.755 | 6.7617 | 6.7683 | 6.775 | 6.7817 | 6.7883 | 6.795 | 6.8017 | 6.8083 | 6.815 | 6.8217 | 6.8283 | 6.835 | 6.8417 | 6.8483 | 6.855 | 6.8617 | 6.8683 | 6.875 | 6.8817 | 6.8883 | 6.895 | 6.8945 | 6.894 | 6.8935 | 6.893 | 6.8925 | 6.892 | 6.8915 | 6.891 | 6.8905 | 6.89 | 6.8895 | 6.889 | 6.8885 | 6.888 | 6.8875 | 6.887 | 6.8865 | 6.886 | 6.8855 | 6.885 | 6.8845 | 6.884 | 6.8835 | 6.883 | 6.8825 | 6.882 | 6.8815 | 6.881 | 6.8805 | 6.88 | 6.8795 | 6.879 | 6.8785 | 6.878 | 6.8775 | 6.877 | 6.8765 | 6.876 | 6.8755 | 6.875 | 6.8745 | 6.874 | 6.8735 | 6.873 | 6.8725 | 6.872 | 6.8715 | 6.871 | 6.8705 | 6.87 | 6.8695 | 6.869 | 6.8685 | 6.868 | 6.8675 | 6.867 | 6.8665 | 6.866 | 6.8655 | 6.865 | 6.8645 | 6.864 | 6.8635 | 6.863 | 6.8625 | 6.862 | 6.8615 | 6.861 | 6.8605 | 6.86 | 6.8595 | 6.859 | 6.8585 | 6.858 | 6.8575 | 6.857 | 6.8565 | 6.856 | 6.8555 | 6.855 | 6.8545 | 6.854 | 6.8535 | 6.853 | 6.8525 | 6.852 | 6.8515 | 6.851 | 6.8505 | 6.85
3.3 | 0 | 2.81 | 4.038 | 5.03 | 5.828 | 6.494 | 6.91 | 7.118 | 7.104 | 7.09 | 7.076 | 2.2204e-16 | 0.281 | 0.562 | 0.843 | 1.124 | 1.405 | 1.686 | 1.967 | 2.248 | 2.529 | 2.81 | 3.0556 | 3.3012 | 3.5468 | 3.7924 | 4.038 | 4.2364 | 4.4348 | 4.6332 | 4.8316 | 5.03 | 5.1098 | 5.1896 | 5.2694 | 5.3492 | 5.429 | 5.5088 | 5.5886 | 5.6684 | 5.7482 | 5.828 | 5.8724 | 5.9168 | 5.9612 | 6.0056 | 6.05 | 6.0944 | 6.1388 | 6.1832 | 6.2276 | 6.272 | 6.3164 | 6.3608 | 6.4052 | 6.4496 | 6.494 | 6.5217 | 6.5495 | 6.5772 | 6.6049 | 6.6327 | 6.6604 | 6.6881 | 6.7159 | 6.7436 | 6.7713 | 6.7991 | 6.8268 | 6.8545 | 6.8823 | 6.91 | 6.9169 | 6.9239 | 6.9308 | 6.9377 | 6.9447 | 6.9516 | 6.9585 | 6.9655 | 6.9724 | 6.9793 | 6.9863 | 6.9932 | 7.0001 | 7.0071 | 7.014 | 7.0209 | 7.0279 | 7.0348 | 7.0417 | 7.0487 | 7.0556 | 7.0625 | 7.0695 | 7.0764 | 7.0833 | 7.0903 | 7.0972 | 7.1041 | 7.1111 | 7.118 | 7.1175 | 7.1171 | 7.1166 | 7.1161 | 7.1157 | 7.1152 | 7.1147 | 7.1143 | 7.1138 | 7.1133 | 7.1129 | 7.1124 | 7.1119 | 7.1115 | 7.111 | 7.1105 | 7.1101 | 7.1096 | 7.1091 | 7.1087 | 7.1082 | 7.1077 | 7.1073 | 7.1068 | 7.1063 | 7.1059 | 7.1054 | 7.1049 | 7.1045 | 7.104 | 7.1035 | 7.1031 | 7.1026 | 7.1021 | 7.1017 | 7.1012 | 7.1007 | 7.1003 | 7.0998 | 7.0993 | 7.0989 | 7.0984 | 7.0979 | 7.0975 | 7.097 | 7.0965 | 7.0961 | 7.0956 | 7.0951 | 7.0947 | 7.0942 | 7.0937 | 7.0933 | 7.0928 | 7.0923 | 7.0919 | 7.0914 | 7.0909 | 7.0905 | 7.09 | 7.0895 | 7.0891 | 7.0886 | 7.0881 | 7.0877 | 7.0872 | 7.0867 | 7.0863 | 7.0858 | 7.0853 | 7.0849 | 7.0844 | 7.0839 | 7.0835 | 7.083 | 7.0825 | 7.0821 | 7.0816 | 7.0811 | 7.0807 | 7.0802 | 7.0797 | 7.0793 | 7.0788 | 7.0783 | 7.0779 | 7.0774 | 7.0769 | 7.0765 | 7.076
3.35 | 0 | 2.895 | 4.161 | 5.185 | 6.006 | 6.693 | 7.125 | 7.341 | 7.328 | 7.315 | 7.302 | 0 | 0.2895 | 0.579 | 0.8685 | 1.158 | 1.4475 | 1.737 | 2.0265 | 2.316 | 2.6055 | 2.895 | 3.1482 | 3.4014 | 3.6546 | 3.9078 | 4.161 | 4.3658 | 4.5706 | 4.7754 | 4.9802 | 5.185 | 5.2671 | 5.3492 | 5.4313 | 5.5134 | 5.5955 | 5.6776 | 5.7597 | 5.8418 | 5.9239 | 6.006 | 6.0518 | 6.0976 | 6.1434 | 6.1892 | 6.235 | 6.2808 | 6.3266 | 6.3724 | 6.4182 | 6.464 | 6.5098 | 6.5556 | 6.6014 | 6.6472 | 6.693 | 6.7218 | 6.7506 | 6.7794 | 6.8082 | 6.837 | 6.8658 | 6.8946 | 6.9234 | 6.9522 | 6.981 | 7.0098 | 7.0386 | 7.0674 | 7.0962 | 7.125 | 7.1322 | 7.1394 | 7.1466 | 7.1538 | 7.161 | 7.1682 | 7.1754 | 7.1826 | 7.1898 | 7.197 | 7.2042 | 7.2114 | 7.2186 | 7.2258 | 7.233 | 7.2402 | 7.2474 | 7.2546 | 7.2618 | 7.269 | 7.2762 | 7.2834 | 7.2906 | 7.2978 | 7.305 | 7.3122 | 7.3194 | 7.3266 | 7.3338 | 7.341 | 7.3406 | 7.3401 | 7.3397 | 7.3393 | 7.3388 | 7.3384 | 7.338 | 7.3375 | 7.3371 | 7.3367 | 7.3362 | 7.3358 | 7.3354 | 7.3349 | 7.3345 | 7.3341 | 7.3336 | 7.3332 | 7.3328 | 7.3323 | 7.3319 | 7.3315 | 7.331 | 7.3306 | 7.3302 | 7.3297 | 7.3293 | 7.3289 | 7.3284 | 7.328 | 7.3276 | 7.3271 | 7.3267 | 7.3263 | 7.3258 | 7.3254 | 7.325 | 7.3245 | 7.3241 | 7.3237 | 7.3232 | 7.3228 | 7.3224 | 7.3219 | 7.3215 | 7.3211 | 7.3206 | 7.3202 | 7.3198 | 7.3193 | 7.3189 | 7.3185 | 7.318 | 7.3176 | 7.3172 | 7.3167 | 7.3163 | 7.3159 | 7.3154 | 7.315 | 7.3146 | 7.3141 | 7.3137 | 7.3133 | 7.3128 | 7.3124 | 7.312 | 7.3115 | 7.3111 | 7.3107 | 7.3102 | 7.3098 | 7.3094 | 7.3089 | 7.3085 | 7.3081 | 7.3076 | 7.3072 | 7.3068 | 7.3063 | 7.3059 | 7.3055 | 7.305 | 7.3046 | 7.3042 | 7.3037 | 7.3033 | 7.3029 | 7.3024 | 7.302
3.4 | 0 | 2.98 | 4.284 | 5.34 | 6.184 | 6.892 | 7.34 | 7.564 | 7.552 | 7.54 | 7.528 | -2.2204e-16 | 0.298 | 0.596 | 0.894 | 1.192 | 1.49 | 1.788 | 2.086 | 2.384 | 2.682 | 2.98 | 3.2408 | 3.5016 | 3.7624 | 4.0232 | 4.284 | 4.4952 | 4.7064 | 4.9176 | 5.1288 | 5.34 | 5.4244 | 5.5088 | 5.5932 | 5.6776 | 5.762 | 5.8464 | 5.9308 | 6.0152 | 6.0996 | 6.184 | 6.2312 | 6.2784 | 6.3256 | 6.3728 | 6.42 | 6.4672 | 6.5144 | 6.5616 | 6.6088 | 6.656 | 6.7032 | 6.7504 | 6.7976 | 6.8448 | 6.892 | 6.9219 | 6.9517 | 6.9816 | 7.0115 | 7.0413 | 7.0712 | 7.1011 | 7.1309 | 7.1608 | 7.1907 | 7.2205 | 7.2504 | 7.2803 | 7.3101 | 7.34 | 7.3475 | 7.3549 | 7.3624 | 7.3699 | 7.3773 | 7.3848 | 7.3923 | 7.3997 | 7.4072 | 7.4147 | 7.4221 | 7.4296 | 7.4371 | 7.4445 | 7.452 | 7.4595 | 7.4669 | 7.4744 | 7.4819 | 7.4893 | 7.4968 | 7.5043 | 7.5117 | 7.5192 | 7.5267 | 7.5341 | 7.5416 | 7.5491 | 7.5565 | 7.564 | 7.5636 | 7.5632 | 7.5628 | 7.5624 | 7.562 | 7.5616 | 7.5612 | 7.5608 | 7.5604 | 7.56 | 7.5596 | 7.5592 | 7.5588 | 7.5584 | 7.558 | 7.5576 | 7.5572 | 7.5568 | 7.5564 | 7.556 | 7.5556 | 7.5552 | 7.5548 | 7.5544 | 7.554 | 7.5536 | 7.5532 | 7.5528 | 7.5524 | 7.552 | 7.5516 | 7.5512 | 7.5508 | 7.5504 | 7.55 | 7.5496 | 7.5492 | 7.5488 | 7.5484 | 7.548 | 7.5476 | 7.5472 | 7.5468 | 7.5464 | 7.546 | 7.5456 | 7.5452 | 7.5448 | 7.5444 | 7.544 | 7.5436 | 7.5432 | 7.5428 | 7.5424 | 7.542 | 7.5416 | 7.5412 | 7.5408 | 7.5404 | 7.54 | 7.5396 | 7.5392 | 7.5388 | 7.5384 | 7.538 | 7.5376 | 7.5372 | 7.5368 | 7.5364 | 7.536 | 7.5356 | 7.5352 | 7.5348 | 7.5344 | 7.534 | 7.5336 | 7.5332 | 7.5328 | 7.5324 | 7.532 | 7.5316 | 7.5312 | 7.5308 | 7.5304 | 7.53 | 7.5296 | 7.5292 | 7.5288 | 7.5284 | 7.528
3.45 | 0 | 3.065 | 4.407 | 5.495 | 6.362 | 7.091 | 7.555 | 7.787 | 7.776 | 7.765 | 7.754 | 0 | 0.3065 | 0.613 | 0.9195 | 1.226 | 1.5325 | 1.839 | 2.1455 | 2.452 | 2.7585 | 3.065 | 3.3334 | 3.6018 | 3.8702 | 4.1386 | 4.407 | 4.6246 | 4.8422 | 5.0598 | 5.2774 | 5.495 | 5.5817 | 5.6684 | 5.7551 | 5.8418 | 5.9285 | 6.0152 | 6.1019 | 6.1886 | 6.2753 | 6.362 | 6.4106 | 6.4592 | 6.5078 | 6.5564 | 6.605 | 6.6536 | 6.7022 | 6.7508 | 6.7994 | 6.848 | 6.8966 | 6.9452 | 6.9938 | 7.0424 | 7.091 | 7.1219 | 7.1529 | 7.1838 | 7.2147 | 7.2457 | 7.2766 | 7.3075 | 7.3385 | 7.3694 | 7.4003 | 7.4313 | 7.4622 | 7.4931 | 7.5241 | 7.555 | 7.5627 | 7.5705 | 7.5782 | 7.5859 | 7.5937 | 7.6014 | 7.6091 | 7.6169 | 7.6246 | 7.6323 | 7.6401 | 7.6478 | 7.6555 | 7.6633 | 7.671 | 7.6787 | 7.6865 | 7.6942 | 7.7019 | 7.7097 | 7.7174 | 7.7251 | 7.7329 | 7.7406 | 7.7483 | 7.7561 | 7.7638 | 7.7715 | 7.7793 | 7.787 | 7.7866 | 7.7863 | 7.7859 | 7.7855 | 7.7852 | 7.7848 | 7.7844 | 7.7841 | 7.7837 | 7.7833 | 7.783 | 7.7826 | 7.7822 | 7.7819 | 7.7815 | 7.7811 | 7.7808 | 7.7804 | 7.78 | 7.7797 | 7.7793 | 7.7789 | 7.7786 | 7.7782 | 7.7778 | 7.7775 | 7.7771 | 7.7767 | 7.7764 | 7.776 | 7.7756 | 7.7753 | 7.7749 | 7.7745 | 7.7742 | 7.7738 | 7.7734 | 7.7731 | 7.7727 | 7.7723 | 7.772 | 7.7716 | 7.7712 | 7.7709 | 7.7705 | 7.7701 | 7.7698 | 7.7694 | 7.769 | 7.7687 | 7.7683 | 7.7679 | 7.7676 | 7.7672 | 7.7668 | 7.7665 | 7.7661 | 7.7657 | 7.7654 | 7.765 | 7.7646 | 7.7643 | 7.7639 | 7.7635 | 7.7632 | 7.7628 | 7.7624 | 7.7621 | 7.7617 | 7.7613 | 7.761 | 7.7606 | 7.7602 | 7.7599 | 7.7595 | 7.7591 | 7.7588 | 7.7584 | 7.758 | 7.7577 | 7.7573 | 7.7569 | 7.7566 | 7.7562 | 7.7558 | 7.7555 | 7.7551 | 7.7547 | 7.7544 | 7.754
3.5 | 0 | 3.15 | 4.53 | 5.65 | 6.54 | 7.29 | 7.77 | 8.01 | 8 | 7.99 | 7.98 | 0 | 0.315 | 0.63 | 0.945 | 1.26 | 1.575 | 1.89 | 2.205 | 2.52 | 2.835 | 3.15 | 3.426 | 3.702 | 3.978 | 4.254 | 4.53 | 4.754 | 4.978 | 5.202 | 5.426 | 5.65 | 5.739 | 5.828 | 5.917 | 6.006 | 6.095 | 6.184 | 6.273 | 6.362 | 6.451 | 6.54 | 6.59 | 6.64 | 6.69 | 6.74 | 6.79 | 6.84 | 6.89 | 6.94 | 6.99 | 7.04 | 7.09 | 7.14 | 7.19 | 7.24 | 7.29 | 7.322 | 7.354 | 7.386 | 7.418 | 7.45 | 7.482 | 7.514 | 7.546 | 7.578 | 7.61 | 7.642 | 7.674 | 7.706 | 7.738 | 7.77 | 7.778 | 7.786 | 7.794 | 7.802 | 7.81 | 7.818 | 7.826 | 7.834 | 7.842 | 7.85 | 7.858 | 7.866 | 7.874 | 7.882 | 7.89 | 7.898 | 7.906 | 7.914 | 7.922 | 7.93 | 7.938 | 7.946 | 7.954 | 7.962 | 7.97 | 7.978 | 7.986 | 7.994 | 8.002 | 8.01 | 8.0097 | 8.0093 | 8.009 | 8.0087 | 8.0083 | 8.008 | 8.0077 | 8.0073 | 8.007 | 8.0067 | 8.0063 | 8.006 | 8.0057 | 8.0053 | 8.005 | 8.0047 | 8.0043 | 8.004 | 8.0037 | 8.0033 | 8.003 | 8.0027 | 8.0023 | 8.002 | 8.0017 | 8.0013 | 8.001 | 8.0007 | 8.0003 | 8 | 7.9997 | 7.9993 | 7.999 | 7.9987 | 7.9983 | 7.998 | 7.9977 | 7.9973 | 7.997 | 7.9967 | 7.9963 | 7.996 | 7.9957 | 7.9953 | 7.995 | 7.9947 | 7.9943 | 7.994 | 7.9937 | 7.9933 | 7.993 | 7.9927 | 7.9923 | 7.992 | 7.9917 | 7.9913 | 7.991 | 7.9907 | 7.9903 | 7.99 | 7.9897 | 7.9893 | 7.989 | 7.9887 | 7.9883 | 7.988 | 7.9877 | 7.9873 | 7.987 | 7.9867 | 7.9863 | 7.986 | 7.9857 | 7.9853 | 7.985 | 7.9847 | 7.9843 | 7.984 | 7.9837 | 7.9833 | 7.983 | 7.9827 | 7.9823 | 7.982 | 7.9817 | 7.9813 | 7.981 | 7.9807 | 7.9803 | 7.98
3.55 | 0 | 3.235 | 4.653 | 5.805 | 6.718 | 7.489 | 7.985 | 8.233 | 8.224 | 8.215 | 8.206 | 0 | 0.3235 | 0.647 | 0.9705 | 1.294 | 1.6175 | 1.941 | 2.2645 | 2.588 | 2.9115 | 3.235 | 3.5186 | 3.8022 | 4.0858 | 4.3694 | 4.653 | 4.8834 | 5.1138 | 5.3442 | 5.5746 | 5.805 | 5.8963 | 5.9876 | 6.0789 | 6.1702 | 6.2615 | 6.3528 | 6.4441 | 6.5354 | 6.6267 | 6.718 | 6.7694 | 6.8208 | 6.8722 | 6.9236 | 6.975 | 7.0264 | 7.0778 | 7.1292 | 7.1806 | 7.232 | 7.2834 | 7.3348 | 7.3862 | 7.4376 | 7.489 | 7.5221 | 7.5551 | 7.5882 | 7.6213 | 7.6543 | 7.6874 | 7.7205 | 7.7535 | 7.7866 | 7.8197 | 7.8527 | 7.8858 | 7.9189 | 7.9519 | 7.985 | 7.9933 | 8.0015 | 8.0098 | 8.0181 | 8.0263 | 8.0346 | 8.0429 | 8.0511 | 8.0594 | 8.0677 | 8.0759 | 8.0842 | 8.0925 | 8.1007 | 8.109 | 8.1173 | 8.1255 | 8.1338 | 8.1421 | 8.1503 | 8.1586 | 8.1669 | 8.1751 | 8.1834 | 8.1917 | 8.1999 | 8.2082 | 8.2165 | 8.2247 | 8.233 | 8.2327 | 8.2324 | 8.2321 | 8.2318 | 8.2315 | 8.2312 | 8.2309 | 8.2306 | 8.2303 | 8.23 | 8.2297 | 8.2294 | 8.2291 | 8.2288 | 8.2285 | 8.2282 | 8.2279 | 8.2276 | 8.2273 | 8.227 | 8.2267 | 8.2264 | 8.2261 | 8.2258 | 8.2255 | 8.2252 | 8.2249 | 8.2246 | 8.2243 | 8.224 | 8.2237 | 8.2234 | 8.2231 | 8.2228 | 8.2225 | 8.2222 | 8.2219 | 8.2216 | 8.2213 | 8.221 | 8.2207 | 8.2204 | 8.2201 | 8.2198 | 8.2195 | 8.2192 | 8.2189 | 8.2186 | 8.2183 | 8.218 | 8.2177 | 8.2174 | 8.2171 | 8.2168 | 8.2165 | 8.2162 | 8.2159 | 8.2156 | 8.2153 | 8.215 | 8.2147 | 8.2144 | 8.2141 | 8.2138 | 8.2135 | 8.2132 | 8.2129 | 8.2126 | 8.2123 | 8.212 | 8.2117 | 8.2114 | 8.2111 | 8.2108 | 8.2105 | 8.2102 | 8.2099 | 8.2096 | 8.2093 | 8.209 | 8.2087 | 8.2084 | 8.2081 | 8.2078 | 8.2075 | 8.2072 | 8.2069 | 8.2066 | 8.2063 | 8.206
3.6 | 0 | 3.32 | 4.776 | 5.96 | 6.896 | 7.688 | 8.2 | 8.456 | 8.448 | 8.44 | 8.432 | 0 | 0.332 | 0.664 | 0.996 | 1.328 | 1.66 | 1.992 | 2.324 | 2.656 | 2.988 | 3.32 | 3.6112 | 3.9024 | 4.1936 | 4.4848 | 4.776 | 5.0128 | 5.2496 | 5.4864 | 5.7232 | 5.96 | 6.0536 | 6.1472 | 6.2408 | 6.3344 | 6.428 | 6.5216 | 6.6152 | 6.7088 | 6.8024 | 6.896 | 6.9488 | 7.0016 | 7.0544 | 7.1072 | 7.16 | 7.2128 | 7.2656 | 7.3184 | 7.3712 | 7.424 | 7.4768 | 7.5296 | 7.5824 | 7.6352 | 7.688 | 7.7221 | 7.7563 | 7.7904 | 7.8245 | 7.8587 | 7.8928 | 7.9269 | 7.9611 | 7.9952 | 8.0293 | 8.0635 | 8.0976 | 8.1317 | 8.1659 | 8.2 | 8.2085 | 8.2171 | 8.2256 | 8.2341 | 8.2427 | 8.2512 | 8.2597 | 8.2683 | 8.2768 | 8.2853 | 8.2939 | 8.3024 | 8.3109 | 8.3195 | 8.328 | 8.3365 | 8.3451 | 8.3536 | 8.3621 | 8.3707 | 8.3792 | 8.3877 | 8.3963 | 8.4048 | 8.4133 | 8.4219 | 8.4304 | 8.4389 | 8.4475 | 8.456 | 8.4557 | 8.4555 | 8.4552 | 8.4549 | 8.4547 | 8.4544 | 8.4541 | 8.4539 | 8.4536 | 8.4533 | 8.4531 | 8.4528 | 8.4525 | 8.4523 | 8.452 | 8.4517 | 8.4515 | 8.4512 | 8.4509 | 8.4507 | 8.4504 | 8.4501 | 8.4499 | 8.4496 | 8.4493 | 8.4491 | 8.4488 | 8.4485 | 8.4483 | 8.448 | 8.4477 | 8.4475 | 8.4472 | 8.4469 | 8.4467 | 8.4464 | 8.4461 | 8.4459 | 8.4456 | 8.4453 | 8.4451 | 8.4448 | 8.4445 | 8.4443 | 8.444 | 8.4437 | 8.4435 | 8.4432 | 8.4429 | 8.4427 | 8.4424 | 8.4421 | 8.4419 | 8.4416 | 8.4413 | 8.4411 | 8.4408 | 8.4405 | 8.4403 | 8.44 | 8.4397 | 8.4395 | 8.4392 | 8.4389 | 8.4387 | 8.4384 | 8.4381 | 8.4379 | 8.4376 | 8.4373 | 8.4371 | 8.4368 | 8.4365 | 8.4363 | 8.436 | 8.4357 | 8.4355 | 8.4352 | 8.4349 | 8.4347 | 8.4344 | 8.4341 | 8.4339 | 8.4336 | 8.4333 | 8.4331 | 8.4328 | 8.4325 | 8.4323 | 8.432
3.65 | 0 | 3.405 | 4.899 | 6.115 | 7.074 | 7.887 | 8.415 | 8.679 | 8.672 | 8.665 | 8.658 | 0 | 0.3405 | 0.681 | 1.0215 | 1.362 | 1.7025 | 2.043 | 2.3835 | 2.724 | 3.0645 | 3.405 | 3.7038 | 4.0026 | 4.3014 | 4.6002 | 4.899 | 5.1422 | 5.3854 | 5.6286 | 5.8718 | 6.115 | 6.2109 | 6.3068 | 6.4027 | 6.4986 | 6.5945 | 6.6904 | 6.7863 | 6.8822 | 6.9781 | 7.074 | 7.1282 | 7.1824 | 7.2366 | 7.2908 | 7.345 | 7.3992 | 7.4534 | 7.5076 | 7.5618 | 7.616 | 7.6702 | 7.7244 | 7.7786 | 7.8328 | 7.887 | 7.9222 | 7.9574 | 7.9926 | 8.0278 | 8.063 | 8.0982 | 8.1334 | 8.1686 | 8.2038 | 8.239 | 8.2742 | 8.3094 | 8.3446 | 8.3798 | 8.415 | 8.4238 | 8.4326 | 8.4414 | 8.4502 | 8.459 | 8.4678 | 8.4766 | 8.4854 | 8.4942 | 8.503 | 8.5118 | 8.5206 | 8.5294 | 8.5382 | 8.547 | 8.5558 | 8.5646 | 8.5734 | 8.5822 | 8.591 | 8.5998 | 8.6086 | 8.6174 | 8.6262 | 8.635 | 8.6438 | 8.6526 | 8.6614 | 8.6702 | 8.679 | 8.6788 | 8.6785 | 8.6783 | 8.6781 | 8.6778 | 8.6776 | 8.6774 | 8.6771 | 8.6769 | 8.6767 | 8.6764 | 8.6762 | 8.676 | 8.6757 | 8.6755 | 8.6753 | 8.675 | 8.6748 | 8.6746 | 8.6743 | 8.6741 | 8.6739 | 8.6736 | 8.6734 | 8.6732 | 8.6729 | 8.6727 | 8.6725 | 8.6722 | 8.672 | 8.6718 | 8.6715 | 8.6713 | 8.6711 | 8.6708 | 8.6706 | 8.6704 | 8.6701 | 8.6699 | 8.6697 | 8.6694 | 8.6692 | 8.669 | 8.6687 | 8.6685 | 8.6683 | 8.668 | 8.6678 | 8.6676 | 8.6673 | 8.6671 | 8.6669 | 8.6666 | 8.6664 | 8.6662 | 8.6659 | 8.6657 | 8.6655 | 8.6652 | 8.665 | 8.6648 | 8.6645 | 8.6643 | 8.6641 | 8.6638 | 8.6636 | 8.6634 | 8.6631 | 8.6629 | 8.6627 | 8.6624 | 8.6622 | 8.662 | 8.6617 | 8.6615 | 8.6613 | 8.661 | 8.6608 | 8.6606 | 8.6603 | 8.6601 | 8.6599 | 8.6596 | 8.6594 | 8.6592 | 8.6589 | 8.6587 | 8.6585 | 8.6582 | 8.658
3.7 | 0 | 3.49 | 5.022 | 6.27 | 7.252 | 8.086 | 8.63 | 8.902 | 8.896 | 8.89 | 8.884 | 0 | 0.349 | 0.698 | 1.047 | 1.396 | 1.745 | 2.094 | 2.443 | 2.792 | 3.141 | 3.49 | 3.7964 | 4.1028 | 4.4092 | 4.7156 | 5.022 | 5.2716 | 5.5212 | 5.7708 | 6.0204 | 6.27 | 6.3682 | 6.4664 | 6.5646 | 6.6628 | 6.761 | 6.8592 | 6.9574 | 7.0556 | 7.1538 | 7.252 | 7.3076 | 7.3632 | 7.4188 | 7.4744 | 7.53 | 7.5856 | 7.6412 | 7.6968 | 7.7524 | 7.808 | 7.8636 | 7.9192 | 7.9748 | 8.0304 | 8.086 | 8.1223 | 8.1585 | 8.1948 | 8.2311 | 8.2673 | 8.3036 | 8.3399 | 8.3761 | 8.4124 | 8.4487 | 8.4849 | 8.5212 | 8.5575 | 8.5937 | 8.63 | 8.6391 | 8.6481 | 8.6572 | 8.6663 | 8.6753 | 8.6844 | 8.6935 | 8.7025 | 8.7116 | 8.7207 | 8.7297 | 8.7388 | 8.7479 | 8.7569 | 8.766 | 8.7751 | 8.7841 | 8.7932 | 8.8023 | 8.8113 | 8.8204 | 8.8295 | 8.8385 | 8.8476 | 8.8567 | 8.8657 | 8.8748 | 8.8839 | 8.8929 | 8.902 | 8.9018 | 8.9016 | 8.9014 | 8.9012 | 8.901 | 8.9008 | 8.9006 | 8.9004 | 8.9002 | 8.9 | 8.8998 | 8.8996 | 8.8994 | 8.8992 | 8.899 | 8.8988 | 8.8986 | 8.8984 | 8.8982 | 8.898 | 8.8978 | 8.8976 | 8.8974 | 8.8972 | 8.897 | 8.8968 | 8.8966 | 8.8964 | 8.8962 | 8.896 | 8.8958 | 8.8956 | 8.8954 | 8.8952 | 8.895 | 8.8948 | 8.8946 | 8.8944 | 8.8942 | 8.894 | 8.8938 | 8.8936 | 8.8934 | 8.8932 | 8.893 | 8.8928 | 8.8926 | 8.8924 | 8.8922 | 8.892 | 8.8918 | 8.8916 | 8.8914 | 8.8912 | 8.891 | 8.8908 | 8.8906 | 8.8904 | 8.8902 | 8.89 | 8.8898 | 8.8896 | 8.8894 | 8.8892 | 8.889 | 8.8888 | 8.8886 | 8.8884 | 8.8882 | 8.888 | 8.8878 | 8.8876 | 8.8874 | 8.8872 | 8.887 | 8.8868 | 8.8866 | 8.8864 | 8.8862 | 8.886 | 8.8858 | 8.8856 | 8.8854 | 8.8852 | 8.885 | 8.8848 | 8.8846 | 8.8844 | 8.8842 | 8.884
3.75 | 0 | 3.575 | 5.145 | 6.425 | 7.43 | 8.285 | 8.845 | 9.125 | 9.12 | 9.115 | 9.11 | 2.2204e-16 | 0.3575 | 0.715 | 1.0725 | 1.43 | 1.7875 | 2.145 | 2.5025 | 2.86 | 3.2175 | 3.575 | 3.889 | 4.203 | 4.517 | 4.831 | 5.145 | 5.401 | 5.657 | 5.913 | 6.169 | 6.425 | 6.5255 | 6.626 | 6.7265 | 6.827 | 6.9275 | 7.028 | 7.1285 | 7.229 | 7.3295 | 7.43 | 7.487 | 7.544 | 7.601 | 7.658 | 7.715 | 7.772 | 7.829 | 7.886 | 7.943 | 8 | 8.057 | 8.114 | 8.171 | 8.228 | 8.285 | 8.3223 | 8.3597 | 8.397 | 8.4343 | 8.4717 | 8.509 | 8.5463 | 8.5837 | 8.621 | 8.6583 | 8.6957 | 8.733 | 8.7703 | 8.8077 | 8.845 | 8.8543 | 8.8637 | 8.873 | 8.8823 | 8.8917 | 8.901 | 8.9103 | 8.9197 | 8.929 | 8.9383 | 8.9477 | 8.957 | 8.9663 | 8.9757 | 8.985 | 8.9943 | 9.0037 | 9.013 | 9.0223 | 9.0317 | 9.041 | 9.0503 | 9.0597 | 9.069 | 9.0783 | 9.0877 | 9.097 | 9.1063 | 9.1157 | 9.125 | 9.1248 | 9.1247 | 9.1245 | 9.1243 | 9.1242 | 9.124 | 9.1238 | 9.1237 | 9.1235 | 9.1233 | 9.1232 | 9.123 | 9.1228 | 9.1227 | 9.1225 | 9.1223 | 9.1222 | 9.122 | 9.1218 | 9.1217 | 9.1215 | 9.1213 | 9.1212 | 9.121 | 9.1208 | 9.1207 | 9.1205 | 9.1203 | 9.1202 | 9.12 | 9.1198 | 9.1197 | 9.1195 | 9.1193 | 9.1192 | 9.119 | 9.1188 | 9.1187 | 9.1185 | 9.1183 | 9.1182 | 9.118 | 9.1178 | 9.1177 | 9.1175 | 9.1173 | 9.1172 | 9.117 | 9.1168 | 9.1167 | 9.1165 | 9.1163 | 9.1162 | 9.116 | 9.1158 | 9.1157 | 9.1155 | 9.1153 | 9.1152 | 9.115 | 9.1148 | 9.1147 | 9.1145 | 9.1143 | 9.1142 | 9.114 | 9.1138 | 9.1137 | 9.1135 | 9.1133 | 9.1132 | 9.113 | 9.1128 | 9.1127 | 9.1125 | 9.1123 | 9.1122 | 9.112 | 9.1118 | 9.1117 | 9.1115 | 9.1113 | 9.1112 | 9.111 | 9.1108 | 9.1107 | 9.1105 | 9.1103 | 9.1102 | 9.11
3.8 | 0 | 3.66 | 5.268 | 6.58 | 7.608 | 8.484 | 9.06 | 9.348 | 9.344 | 9.34 | 9.336 | 0 | 0.366 | 0.732 | 1.098 | 1.464 | 1.83 | 2.196 | 2.562 | 2.928 | 3.294 | 3.66 | 3.9816 | 4.3032 | 4.6248 | 4.9464 | 5.268 | 5.5304 | 5.7928 | 6.0552 | 6.3176 | 6.58 | 6.6828 | 6.7856 | 6.8884 | 6.9912 | 7.094 | 7.1968 | 7.2996 | 7.4024 | 7.5052 | 7.608 | 7.6664 | 7.7248 | 7.7832 | 7.8416 | 7.9 | 7.9584 | 8.0168 | 8.0752 | 8.1336 | 8.192 | 8.2504 | 8.3088 | 8.3672 | 8.4256 | 8.484 | 8.5224 | 8.5608 | 8.5992 | 8.6376 | 8.676 | 8.7144 | 8.7528 | 8.7912 | 8.8296 | 8.868 | 8.9064 | 8.9448 | 8.9832 | 9.0216 | 9.06 | 9.0696 | 9.0792 | 9.0888 | 9.0984 | 9.108 | 9.1176 | 9.1272 | 9.1368 | 9.1464 | 9.156 | 9.1656 | 9.1752 | 9.1848 | 9.1944 | 9.204 | 9.2136 | 9.2232 | 9.2328 | 9.2424 | 9.252 | 9.2616 | 9.2712 | 9.2808 | 9.2904 | 9.3 | 9.3096 | 9.3192 | 9.3288 | 9.3384 | 9.348 | 9.3479 | 9.3477 | 9.3476 | 9.3475 | 9.3473 | 9.3472 | 9.3471 | 9.3469 | 9.3468 | 9.3467 | 9.3465 | 9.3464 | 9.3463 | 9.3461 | 9.346 | 9.3459 | 9.3457 | 9.3456 | 9.3455 | 9.3453 | 9.3452 | 9.3451 | 9.3449 | 9.3448 | 9.3447 | 9.3445 | 9.3444 | 9.3443 | 9.3441 | 9.344 | 9.3439 | 9.3437 | 9.3436 | 9.3435 | 9.3433 | 9.3432 | 9.3431 | 9.3429 | 9.3428 | 9.3427 | 9.3425 | 9.3424 | 9.3423 | 9.3421 | 9.342 | 9.3419 | 9.3417 | 9.3416 | 9.3415 | 9.3413 | 9.3412 | 9.3411 | 9.3409 | 9.3408 | 9.3407 | 9.3405 | 9.3404 | 9.3403 | 9.3401 | 9.34 | 9.3399 | 9.3397 | 9.3396 | 9.3395 | 9.3393 | 9.3392 | 9.3391 | 9.3389 | 9.3388 | 9.3387 | 9.3385 | 9.3384 | 9.3383 | 9.3381 | 9.338 | 9.3379 | 9.3377 | 9.3376 | 9.3375 | 9.3373 | 9.3372 | 9.3371 | 9.3369 | 9.3368 | 9.3367 | 9.3365 | 9.3364 | 9.3363 | 9.3361 | 9.336
3.85 | 0 | 3.745 | 5.391 | 6.735 | 7.786 | 8.683 | 9.275 | 9.571 | 9.568 | 9.565 | 9.562 | -2.2204e-16 | 0.3745 | 0.749 | 1.1235 | 1.498 | 1.8725 | 2.247 | 2.6215 | 2.996 | 3.3705 | 3.745 | 4.0742 | 4.4034 | 4.7326 | 5.0618 | 5.391 | 5.6598 | 5.9286 | 6.1974 | 6.4662 | 6.735 | 6.8401 | 6.9452 | 7.0503 | 7.1554 | 7.2605 | 7.3656 | 7.4707 | 7.5758 | 7.6809 | 7.786 | 7.8458 | 7.9056 | 7.9654 | 8.0252 | 8.085 | 8.1448 | 8.2046 | 8.2644 | 8.3242 | 8.384 | 8.4438 | 8.5036 | 8.5634 | 8.6232 | 8.683 | 8.7225 | 8.7619 | 8.8014 | 8.8409 | 8.8803 | 8.9198 | 8.9593 | 8.9987 | 9.0382 | 9.0777 | 9.1171 | 9.1566 | 9.1961 | 9.2355 | 9.275 | 9.2849 | 9.2947 | 9.3046 | 9.3145 | 9.3243 | 9.3342 | 9.3441 | 9.3539 | 9.3638 | 9.3737 | 9.3835 | 9.3934 | 9.4033 | 9.4131 | 9.423 | 9.4329 | 9.4427 | 9.4526 | 9.4625 | 9.4723 | 9.4822 | 9.4921 | 9.5019 | 9.5118 | 9.5217 | 9.5315 | 9.5414 | 9.5513 | 9.5611 | 9.571 | 9.5709 | 9.5708 | 9.5707 | 9.5706 | 9.5705 | 9.5704 | 9.5703 | 9.5702 | 9.5701 | 9.57 | 9.5699 | 9.5698 | 9.5697 | 9.5696 | 9.5695 | 9.5694 | 9.5693 | 9.5692 | 9.5691 | 9.569 | 9.5689 | 9.5688 | 9.5687 | 9.5686 | 9.5685 | 9.5684 | 9.5683 | 9.5682 | 9.5681 | 9.568 | 9.5679 | 9.5678 | 9.5677 | 9.5676 | 9.5675 | 9.5674 | 9.5673 | 9.5672 | 9.5671 | 9.567 | 9.5669 | 9.5668 | 9.5667 | 9.5666 | 9.5665 | 9.5664 | 9.5663 | 9.5662 | 9.5661 | 9.566 | 9.5659 | 9.5658 | 9.5657 | 9.5656 | 9.5655 | 9.5654 | 9.5653 | 9.5652 | 9.5651 | 9.565 | 9.5649 | 9.5648 | 9.5647 | 9.5646 | 9.5645 | 9.5644 | 9.5643 | 9.5642 | 9.5641 | 9.564 | 9.5639 | 9.5638 | 9.5637 | 9.5636 | 9.5635 | 9.5634 | 9.5633 | 9.5632 | 9.5631 | 9.563 | 9.5629 | 9.5628 | 9.5627 | 9.5626 | 9.5625 | 9.5624 | 9.5623 | 9.5622 | 9.5621 | 9.562
3.9 | 0 | 3.83 | 5.514 | 6.89 | 7.964 | 8.882 | 9.49 | 9.794 | 9.792 | 9.79 | 9.788 | 2.2204e-16 | 0.383 | 0.766 | 1.149 | 1.532 | 1.915 | 2.298 | 2.681 | 3.064 | 3.447 | 3.83 | 4.1668 | 4.5036 | 4.8404 | 5.1772 | 5.514 | 5.7892 | 6.0644 | 6.3396 | 6.6148 | 6.89 | 6.9974 | 7.1048 | 7.2122 | 7.3196 | 7.427 | 7.5344 | 7.6418 | 7.7492 | 7.8566 | 7.964 | 8.0252 | 8.0864 | 8.1476 | 8.2088 | 8.27 | 8.3312 | 8.3924 | 8.4536 | 8.5148 | 8.576 | 8.6372 | 8.6984 | 8.7596 | 8.8208 | 8.882 | 8.9225 | 8.9631 | 9.0036 | 9.0441 | 9.0847 | 9.1252 | 9.1657 | 9.2063 | 9.2468 | 9.2873 | 9.3279 | 9.3684 | 9.4089 | 9.4495 | 9.49 | 9.5001 | 9.5103 | 9.5204 | 9.5305 | 9.5407 | 9.5508 | 9.5609 | 9.5711 | 9.5812 | 9.5913 | 9.6015 | 9.6116 | 9.6217 | 9.6319 | 9.642 | 9.6521 | 9.6623 | 9.6724 | 9.6825 | 9.6927 | 9.7028 | 9.7129 | 9.7231 | 9.7332 | 9.7433 | 9.7535 | 9.7636 | 9.7737 | 9.7839 | 9.794 | 9.7939 | 9.7939 | 9.7938 | 9.7937 | 9.7937 | 9.7936 | 9.7935 | 9.7935 | 9.7934 | 9.7933 | 9.7933 | 9.7932 | 9.7931 | 9.7931 | 9.793 | 9.7929 | 9.7929 | 9.7928 | 9.7927 | 9.7927 | 9.7926 | 9.7925 | 9.7925 | 9.7924 | 9.7923 | 9.7923 | 9.7922 | 9.7921 | 9.7921 | 9.792 | 9.7919 | 9.7919 | 9.7918 | 9.7917 | 9.7917 | 9.7916 | 9.7915 | 9.7915 | 9.7914 | 9.7913 | 9.7913 | 9.7912 | 9.7911 | 9.7911 | 9.791 | 9.7909 | 9.7909 | 9.7908 | 9.7907 | 9.7907 | 9.7906 | 9.7905 | 9.7905 | 9.7904 | 9.7903 | 9.7903 | 9.7902 | 9.7901 | 9.7901 | 9.79 | 9.7899 | 9.7899 | 9.7898 | 9.7897 | 9.7897 | 9.7896 | 9.7895 | 9.7895 | 9.7894 | 9.7893 | 9.7893 | 9.7892 | 9.7891 | 9.7891 | 9.789 | 9.7889 | 9.7889 | 9.7888 | 9.7887 | 9.7887 | 9.7886 | 9.7885 | 9.7885 | 9.7884 | 9.7883 | 9.7883 | 9.7882 | 9.7881 | 9.7881 | 9.788
3.95 | 0 | 3.915 | 5.637 | 7.045 | 8.142 | 9.081 | 9.705 | 10.017 | 10.016 | 10.015 | 10.014 | 2.2204e-16 | 0.3915 | 0.783 | 1.1745 | 1.566 | 1.9575 | 2.349 | 2.7405 | 3.132 | 3.5235 | 3.915 | 4.2594 | 4.6038 | 4.9482 | 5.2926 | 5.637 | 5.9186 | 6.2002 | 6.4818 | 6.7634 | 7.045 | 7.1547 | 7.2644 | 7.3741 | 7.4838 | 7.5935 | 7.7032 | 7.8129 | 7.9226 | 8.0323 | 8.142 | 8.2046 | 8.2672 | 8.3298 | 8.3924 | 8.455 | 8.5176 | 8.5802 | 8.6428 | 8.7054 | 8.768 | 8.8306 | 8.8932 | 8.9558 | 9.0184 | 9.081 | 9.1226 | 9.1642 | 9.2058 | 9.2474 | 9.289 | 9.3306 | 9.3722 | 9.4138 | 9.4554 | 9.497 | 9.5386 | 9.5802 | 9.6218 | 9.6634 | 9.705 | 9.7154 | 9.7258 | 9.7362 | 9.7466 | 9.757 | 9.7674 | 9.7778 | 9.7882 | 9.7986 | 9.809 | 9.8194 | 9.8298 | 9.8402 | 9.8506 | 9.861 | 9.8714 | 9.8818 | 9.8922 | 9.9026 | 9.913 | 9.9234 | 9.9338 | 9.9442 | 9.9546 | 9.965 | 9.9754 | 9.9858 | 9.9962 | 10.0066 | 10.017 | 10.017 | 10.0169 | 10.0169 | 10.0169 | 10.0168 | 10.0168 | 10.0168 | 10.0167 | 10.0167 | 10.0167 | 10.0166 | 10.0166 | 10.0166 | 10.0165 | 10.0165 | 10.0165 | 10.0164 | 10.0164 | 10.0164 | 10.0163 | 10.0163 | 10.0163 | 10.0162 | 10.0162 | 10.0162 | 10.0161 | 10.0161 | 10.0161 | 10.016 | 10.016 | 10.016 | 10.0159 | 10.0159 | 10.0159 | 10.0158 | 10.0158 | 10.0158 | 10.0157 | 10.0157 | 10.0157 | 10.0156 | 10.0156 | 10.0156 | 10.0155 | 10.0155 | 10.0155 | 10.0154 | 10.0154 | 10.0154 | 10.0153 | 10.0153 | 10.0153 | 10.0152 | 10.0152 | 10.0152 | 10.0151 | 10.0151 | 10.0151 | 10.015 | 10.015 | 10.015 | 10.0149 | 10.0149 | 10.0149 | 10.0148 | 10.0148 | 10.0148 | 10.0147 | 10.0147 | 10.0147 | 10.0146 | 10.0146 | 10.0146 | 10.0145 | 10.0145 | 10.0145 | 10.0144 | 10.0144 | 10.0144 | 10.0143 | 10.0143 | 10.0143 | 10.0142 | 10.0142 | 10.0142 | 10.0141 | 10.0141 | 10.0141 | 10.014 | 10.014
4 | 0 | 4 | 5.76 | 7.2 | 8.32 | 9.28 | 9.92 | 10.24 | 10.24 | 10.24 | 10.24 | 0 | 0.4 | 0.8 | 1.2 | 1.6 | 2 | 2.4 | 2.8 | 3.2 | 3.6 | 4 | 4.352 | 4.704 | 5.056 | 5.408 | 5.76 | 6.048 | 6.336 | 6.624 | 6.912 | 7.2 | 7.312 | 7.424 | 7.536 | 7.648 | 7.76 | 7.872 | 7.984 | 8.096 | 8.208 | 8.32 | 8.384 | 8.448 | 8.512 | 8.576 | 8.64 | 8.704 | 8.768 | 8.832 | 8.896 | 8.96 | 9.024 | 9.088 | 9.152 | 9.216 | 9.28 | 9.3227 | 9.3653 | 9.408 | 9.4507 | 9.4933 | 9.536 | 9.5787 | 9.6213 | 9.664 | 9.7067 | 9.7493 | 9.792 | 9.8347 | 9.8773 | 9.92 | 9.9307 | 9.9413 | 9.952 | 9.9627 | 9.9733 | 9.984 | 9.9947 | 10.0053 | 10.016 | 10.0267 | 10.0373 | 10.048 | 10.0587 | 10.0693 | 10.08 | 10.0907 | 10.1013 | 10.112 | 10.1227 | 10.1333 | 10.144 | 10.1547 | 10.1653 | 10.176 | 10.1867 | 10.1973 | 10.208 | 10.2187 | 10.2293 | 10.24 | 10.24 | 10.24 | 10.24 | 10.24 | 10.24 | 10.24 | 10.24 | 10.24 | 10.24 | 10.24 | 10.24 | 10.24 | 10.24 | 10.24 | 10.24 | 10.24 | 10.24 | 10.24 | 10.24 | 10.24 | 10.24 | 10.24 | 10.24 | 10.24 | 10.24 | 10.24 | 10.24 | 10.24 | 10.24 | 10.24 | 10.24 | 10.24 | 10.24 | 10.24 | 10.24 | 10.24 | 10.24 | 10.24 | 10.24 | 10.24 | 10.24 | 10.24 | 10.24 | 10.24 | 10.24 | 10.24 | 10.24 | 10.24 | 10.24 | 10.24 | 10.24 | 10.24 | 10.24 | 10.24 | 10.24 | 10.24 | 10.24 | 10.24 | 10.24 | 10.24 | 10.24 | 10.24 | 10.24 | 10.24 | 10.24 | 10.24 | 10.24 | 10.24 | 10.24 | 10.24 | 10.24 | 10.24 | 10.24 | 10.24 | 10.24 | 10.24 | 10.24 | 10.24 | 10.24 | 10.24 | 10.24 | 10.24 | 10.24 | 10.24 | 10.24 | 10.24 | 10.24 | 10.24 | 10.24 | 10.24
4.05 | 0 | 4.2167 | 6.1287 | 7.5817 | 8.784 | 9.8277 | 10.5373 | 10.8963 | 10.913 | 10.913 | 10.888 | 0 | 0.42167 | 0.84333 | 1.265 | 1.6867 | 2.1083 | 2.53 | 2.9517 | 3.3733 | 3.795 | 4.2167 | 4.5991 | 4.9815 | 5.3639 | 5.7463 | 6.1287 | 6.4193 | 6.7099 | 7.0005 | 7.2911 | 7.5817 | 7.7019 | 7.8221 | 7.9424 | 8.0626 | 8.1828 | 8.3031 | 8.4233 | 8.5435 | 8.6638 | 8.784 | 8.8536 | 8.9232 | 8.9927 | 9.0623 | 9.1319 | 9.2015 | 9.271 | 9.3406 | 9.4102 | 9.4798 | 9.5494 | 9.6189 | 9.6885 | 9.7581 | 9.8277 | 9.875 | 9.9223 | 9.9696 | 10.0169 | 10.0642 | 10.1115 | 10.1588 | 10.2062 | 10.2535 | 10.3008 | 10.3481 | 10.3954 | 10.4427 | 10.49 | 10.5373 | 10.5493 | 10.5613 | 10.5732 | 10.5852 | 10.5972 | 10.6091 | 10.6211 | 10.6331 | 10.645 | 10.657 | 10.669 | 10.6809 | 10.6929 | 10.7049 | 10.7168 | 10.7288 | 10.7408 | 10.7527 | 10.7647 | 10.7767 | 10.7886 | 10.8006 | 10.8126 | 10.8245 | 10.8365 | 10.8485 | 10.8604 | 10.8724 | 10.8844 | 10.8963 | 10.8969 | 10.8974 | 10.898 | 10.8986 | 10.8991 | 10.8997 | 10.9002 | 10.9008 | 10.9013 | 10.9019 | 10.9024 | 10.903 | 10.9036 | 10.9041 | 10.9047 | 10.9052 | 10.9058 | 10.9063 | 10.9069 | 10.9074 | 10.908 | 10.9086 | 10.9091 | 10.9097 | 10.9102 | 10.9108 | 10.9113 | 10.9119 | 10.9124 | 10.913 | 10.913 | 10.913 | 10.913 | 10.913 | 10.913 | 10.913 | 10.913 | 10.913 | 10.913 | 10.913 | 10.913 | 10.913 | 10.913 | 10.913 | 10.913 | 10.913 | 10.913 | 10.913 | 10.913 | 10.913 | 10.913 | 10.913 | 10.913 | 10.913 | 10.913 | 10.913 | 10.913 | 10.913 | 10.913 | 10.913 | 10.9122 | 10.9113 | 10.9105 | 10.9097 | 10.9088 | 10.908 | 10.9072 | 10.9063 | 10.9055 | 10.9047 | 10.9038 | 10.903 | 10.9022 | 10.9013 | 10.9005 | 10.8997 | 10.8988 | 10.898 | 10.8972 | 10.8963 | 10.8955 | 10.8947 | 10.8938 | 10.893 | 10.8922 | 10.8913 | 10.8905 | 10.8897 | 10.8888 | 10.888
4.1 | 0 | 4.4333 | 6.4973 | 7.9633 | 9.248 | 10.3753 | 11.1547 | 11.5527 | 11.586 | 11.586 | 11.536 | 0 | 0.44333 | 0.88667 | 1.33 | 1.7733 | 2.2167 | 2.66 | 3.1033 | 3.5467 | 3.99 | 4.4333 | 4.8461 | 5.2589 | 5.6717 | 6.0845 | 6.4973 | 6.7905 | 7.0837 | 7.3769 | 7.6701 | 7.9633 | 8.0918 | 8.2203 | 8.3487 | 8.4772 | 8.6057 | 8.7341 | 8.8626 | 8.9911 | 9.1195 | 9.248 | 9.3232 | 9.3983 | 9.4735 | 9.5486 | 9.6238 | 9.6989 | 9.7741 | 9.8492 | 9.9244 | 9.9996 | 10.0747 | 10.1499 | 10.225 | 10.3002 | 10.3753 | 10.4273 | 10.4792 | 10.5312 | 10.5832 | 10.6351 | 10.6871 | 10.739 | 10.791 | 10.8429 | 10.8949 | 10.9468 | 10.9988 | 11.0508 | 11.1027 | 11.1547 | 11.1679 | 11.1812 | 11.1945 | 11.2077 | 11.221 | 11.2343 | 11.2475 | 11.2608 | 11.2741 | 11.2873 | 11.3006 | 11.3139 | 11.3271 | 11.3404 | 11.3537 | 11.3669 | 11.3802 | 11.3935 | 11.4067 | 11.42 | 11.4333 | 11.4465 | 11.4598 | 11.4731 | 11.4863 | 11.4996 | 11.5129 | 11.5261 | 11.5394 | 11.5527 | 11.5538 | 11.5549 | 11.556 | 11.5571 | 11.5582 | 11.5593 | 11.5604 | 11.5616 | 11.5627 | 11.5638 | 11.5649 | 11.566 | 11.5671 | 11.5682 | 11.5693 | 11.5704 | 11.5716 | 11.5727 | 11.5738 | 11.5749 | 11.576 | 11.5771 | 11.5782 | 11.5793 | 11.5804 | 11.5816 | 11.5827 | 11.5838 | 11.5849 | 11.586 | 11.586 | 11.586 | 11.586 | 11.586 | 11.586 | 11.586 | 11.586 | 11.586 | 11.586 | 11.586 | 11.586 | 11.586 | 11.586 | 11.586 | 11.586 | 11.586 | 11.586 | 11.586 | 11.586 | 11.586 | 11.586 | 11.586 | 11.586 | 11.586 | 11.586 | 11.586 | 11.586 | 11.586 | 11.586 | 11.586 | 11.5843 | 11.5827 | 11.581 | 11.5793 | 11.5777 | 11.576 | 11.5743 | 11.5727 | 11.571 | 11.5693 | 11.5677 | 11.566 | 11.5643 | 11.5627 | 11.561 | 11.5593 | 11.5577 | 11.556 | 11.5543 | 11.5527 | 11.551 | 11.5493 | 11.5477 | 11.546 | 11.5443 | 11.5427 | 11.541 | 11.5393 | 11.5377 | 11.536
4.15 | 0 | 4.65 | 6.866 | 8.345 | 9.712 | 10.923 | 11.772 | 12.209 | 12.259 | 12.259 | 12.184 | 0 | 0.465 | 0.93 | 1.395 | 1.86 | 2.325 | 2.79 | 3.255 | 3.72 | 4.185 | 4.65 | 5.0932 | 5.5364 | 5.9796 | 6.4228 | 6.866 | 7.1618 | 7.4576 | 7.7534 | 8.0492 | 8.345 | 8.4817 | 8.6184 | 8.7551 | 8.8918 | 9.0285 | 9.1652 | 9.3019 | 9.4386 | 9.5753 | 9.712 | 9.7927 | 9.8735 | 9.9542 | 10.0349 | 10.1157 | 10.1964 | 10.2771 | 10.3579 | 10.4386 | 10.5193 | 10.6001 | 10.6808 | 10.7615 | 10.8423 | 10.923 | 10.9796 | 11.0362 | 11.0928 | 11.1494 | 11.206 | 11.2626 | 11.3192 | 11.3758 | 11.4324 | 11.489 | 11.5456 | 11.6022 | 11.6588 | 11.7154 | 11.772 | 11.7866 | 11.8011 | 11.8157 | 11.8303 | 11.8448 | 11.8594 | 11.874 | 11.8885 | 11.9031 | 11.9177 | 11.9322 | 11.9468 | 11.9614 | 11.9759 | 11.9905 | 12.0051 | 12.0196 | 12.0342 | 12.0488 | 12.0633 | 12.0779 | 12.0925 | 12.107 | 12.1216 | 12.1362 | 12.1507 | 12.1653 | 12.1799 | 12.1944 | 12.209 | 12.2107 | 12.2123 | 12.214 | 12.2157 | 12.2173 | 12.219 | 12.2207 | 12.2223 | 12.224 | 12.2257 | 12.2273 | 12.229 | 12.2307 | 12.2323 | 12.234 | 12.2357 | 12.2373 | 12.239 | 12.2407 | 12.2423 | 12.244 | 12.2457 | 12.2473 | 12.249 | 12.2507 | 12.2523 | 12.254 | 12.2557 | 12.2573 | 12.259 | 12.259 | 12.259 | 12.259 | 12.259 | 12.259 | 12.259 | 12.259 | 12.259 | 12.259 | 12.259 | 12.259 | 12.259 | 12.259 | 12.259 | 12.259 | 12.259 | 12.259 | 12.259 | 12.259 | 12.259 | 12.259 | 12.259 | 12.259 | 12.259 | 12.259 | 12.259 | 12.259 | 12.259 | 12.259 | 12.259 | 12.2565 | 12.254 | 12.2515 | 12.249 | 12.2465 | 12.244 | 12.2415 | 12.239 | 12.2365 | 12.234 | 12.2315 | 12.229 | 12.2265 | 12.224 | 12.2215 | 12.219 | 12.2165 | 12.214 | 12.2115 | 12.209 | 12.2065 | 12.204 | 12.2015 | 12.199 | 12.1965 | 12.194 | 12.1915 | 12.189 | 12.1865 | 12.184
4.2 | 0 | 4.8667 | 7.2347 | 8.7267 | 10.176 | 11.4707 | 12.3893 | 12.8653 | 12.932 | 12.932 | 12.832 | 0 | 0.48667 | 0.97333 | 1.46 | 1.9467 | 2.4333 | 2.92 | 3.4067 | 3.8933 | 4.38 | 4.8667 | 5.3403 | 5.8139 | 6.2875 | 6.7611 | 7.2347 | 7.5331 | 7.8315 | 8.1299 | 8.4283 | 8.7267 | 8.8716 | 9.0165 | 9.1615 | 9.3064 | 9.4513 | 9.5963 | 9.7412 | 9.8861 | 10.0311 | 10.176 | 10.2623 | 10.3486 | 10.4349 | 10.5212 | 10.6076 | 10.6939 | 10.7802 | 10.8665 | 10.9528 | 11.0391 | 11.1254 | 11.2117 | 11.298 | 11.3844 | 11.4707 | 11.5319 | 11.5932 | 11.6544 | 11.7156 | 11.7769 | 11.8381 | 11.8994 | 11.9606 | 12.0219 | 12.0831 | 12.1444 | 12.2056 | 12.2668 | 12.3281 | 12.3893 | 12.4052 | 12.4211 | 12.4369 | 12.4528 | 12.4687 | 12.4845 | 12.5004 | 12.5163 | 12.5321 | 12.548 | 12.5639 | 12.5797 | 12.5956 | 12.6115 | 12.6273 | 12.6432 | 12.6591 | 12.6749 | 12.6908 | 12.7067 | 12.7225 | 12.7384 | 12.7543 | 12.7701 | 12.786 | 12.8019 | 12.8177 | 12.8336 | 12.8495 | 12.8653 | 12.8676 | 12.8698 | 12.872 | 12.8742 | 12.8764 | 12.8787 | 12.8809 | 12.8831 | 12.8853 | 12.8876 | 12.8898 | 12.892 | 12.8942 | 12.8964 | 12.8987 | 12.9009 | 12.9031 | 12.9053 | 12.9076 | 12.9098 | 12.912 | 12.9142 | 12.9164 | 12.9187 | 12.9209 | 12.9231 | 12.9253 | 12.9276 | 12.9298 | 12.932 | 12.932 | 12.932 | 12.932 | 12.932 | 12.932 | 12.932 | 12.932 | 12.932 | 12.932 | 12.932 | 12.932 | 12.932 | 12.932 | 12.932 | 12.932 | 12.932 | 12.932 | 12.932 | 12.932 | 12.932 | 12.932 | 12.932 | 12.932 | 12.932 | 12.932 | 12.932 | 12.932 | 12.932 | 12.932 | 12.932 | 12.9287 | 12.9253 | 12.922 | 12.9187 | 12.9153 | 12.912 | 12.9087 | 12.9053 | 12.902 | 12.8987 | 12.8953 | 12.892 | 12.8887 | 12.8853 | 12.882 | 12.8787 | 12.8753 | 12.872 | 12.8687 | 12.8653 | 12.862 | 12.8587 | 12.8553 | 12.852 | 12.8487 | 12.8453 | 12.842 | 12.8387 | 12.8353 | 12.832
4.25 | 0 | 5.0833 | 7.6033 | 9.1083 | 10.64 | 12.0183 | 13.0067 | 13.5217 | 13.605 | 13.605 | 13.48 | 0 | 0.50833 | 1.0167 | 1.525 | 2.0333 | 2.5417 | 3.05 | 3.5583 | 4.0667 | 4.575 | 5.0833 | 5.5873 | 6.0913 | 6.5953 | 7.0993 | 7.6033 | 7.9043 | 8.2053 | 8.5063 | 8.8073 | 9.1083 | 9.2615 | 9.4147 | 9.5678 | 9.721 | 9.8742 | 10.0273 | 10.1805 | 10.3337 | 10.4868 | 10.64 | 10.7319 | 10.8238 | 10.9157 | 11.0076 | 11.0994 | 11.1913 | 11.2832 | 11.3751 | 11.467 | 11.5589 | 11.6508 | 11.7427 | 11.8346 | 11.9264 | 12.0183 | 12.0842 | 12.1501 | 12.216 | 12.2819 | 12.3478 | 12.4137 | 12.4796 | 12.5454 | 12.6113 | 12.6772 | 12.7431 | 12.809 | 12.8749 | 12.9408 | 13.0067 | 13.0238 | 13.041 | 13.0582 | 13.0753 | 13.0925 | 13.1097 | 13.1268 | 13.144 | 13.1612 | 13.1783 | 13.1955 | 13.2127 | 13.2298 | 13.247 | 13.2642 | 13.2813 | 13.2985 | 13.3157 | 13.3328 | 13.35 | 13.3672 | 13.3843 | 13.4015 | 13.4187 | 13.4358 | 13.453 | 13.4702 | 13.4873 | 13.5045 | 13.5217 | 13.5244 | 13.5272 | 13.53 | 13.5328 | 13.5356 | 13.5383 | 13.5411 | 13.5439 | 13.5467 | 13.5494 | 13.5522 | 13.555 | 13.5578 | 13.5606 | 13.5633 | 13.5661 | 13.5689 | 13.5717 | 13.5744 | 13.5772 | 13.58 | 13.5828 | 13.5856 | 13.5883 | 13.5911 | 13.5939 | 13.5967 | 13.5994 | 13.6022 | 13.605 | 13.605 | 13.605 | 13.605 | 13.605 | 13.605 | 13.605 | 13.605 | 13.605 | 13.605 | 13.605 | 13.605 | 13.605 | 13.605 | 13.605 | 13.605 | 13.605 | 13.605 | 13.605 | 13.605 | 13.605 | 13.605 | 13.605 | 13.605 | 13.605 | 13.605 | 13.605 | 13.605 | 13.605 | 13.605 | 13.605 | 13.6008 | 13.5967 | 13.5925 | 13.5883 | 13.5842 | 13.58 | 13.5758 | 13.5717 | 13.5675 | 13.5633 | 13.5592 | 13.555 | 13.5508 | 13.5467 | 13.5425 | 13.5383 | 13.5342 | 13.53 | 13.5258 | 13.5217 | 13.5175 | 13.5133 | 13.5092 | 13.505 | 13.5008 | 13.4967 | 13.4925 | 13.4883 | 13.4842 | 13.48
4.3 | 0 | 5.3 | 7.972 | 9.49 | 11.104 | 12.566 | 13.624 | 14.178 | 14.278 | 14.278 | 14.128 | 0 | 0.53 | 1.06 | 1.59 | 2.12 | 2.65 | 3.18 | 3.71 | 4.24 | 4.77 | 5.3 | 5.8344 | 6.3688 | 6.9032 | 7.4376 | 7.972 | 8.2756 | 8.5792 | 8.8828 | 9.1864 | 9.49 | 9.6514 | 9.8128 | 9.9742 | 10.1356 | 10.297 | 10.4584 | 10.6198 | 10.7812 | 10.9426 | 11.104 | 11.2015 | 11.2989 | 11.3964 | 11.4939 | 11.5913 | 11.6888 | 11.7863 | 11.8837 | 11.9812 | 12.0787 | 12.1761 | 12.2736 | 12.3711 | 12.4685 | 12.566 | 12.6365 | 12.7071 | 12.7776 | 12.8481 | 12.9187 | 12.9892 | 13.0597 | 13.1303 | 13.2008 | 13.2713 | 13.3419 | 13.4124 | 13.4829 | 13.5535 | 13.624 | 13.6425 | 13.6609 | 13.6794 | 13.6979 | 13.7163 | 13.7348 | 13.7533 | 13.7717 | 13.7902 | 13.8087 | 13.8271 | 13.8456 | 13.8641 | 13.8825 | 13.901 | 13.9195 | 13.9379 | 13.9564 | 13.9749 | 13.9933 | 14.0118 | 14.0303 | 14.0487 | 14.0672 | 14.0857 | 14.1041 | 14.1226 | 14.1411 | 14.1595 | 14.178 | 14.1813 | 14.1847 | 14.188 | 14.1913 | 14.1947 | 14.198 | 14.2013 | 14.2047 | 14.208 | 14.2113 | 14.2147 | 14.218 | 14.2213 | 14.2247 | 14.228 | 14.2313 | 14.2347 | 14.238 | 14.2413 | 14.2447 | 14.248 | 14.2513 | 14.2547 | 14.258 | 14.2613 | 14.2647 | 14.268 | 14.2713 | 14.2747 | 14.278 | 14.278 | 14.278 | 14.278 | 14.278 | 14.278 | 14.278 | 14.278 | 14.278 | 14.278 | 14.278 | 14.278 | 14.278 | 14.278 | 14.278 | 14.278 | 14.278 | 14.278 | 14.278 | 14.278 | 14.278 | 14.278 | 14.278 | 14.278 | 14.278 | 14.278 | 14.278 | 14.278 | 14.278 | 14.278 | 14.278 | 14.273 | 14.268 | 14.263 | 14.258 | 14.253 | 14.248 | 14.243 | 14.238 | 14.233 | 14.228 | 14.223 | 14.218 | 14.213 | 14.208 | 14.203 | 14.198 | 14.193 | 14.188 | 14.183 | 14.178 | 14.173 | 14.168 | 14.163 | 14.158 | 14.153 | 14.148 | 14.143 | 14.138 | 14.133 | 14.128
4.35 | 0 | 5.5167 | 8.3407 | 9.8717 | 11.568 | 13.1137 | 14.2413 | 14.8343 | 14.951 | 14.951 | 14.776 | 0 | 0.55167 | 1.1033 | 1.655 | 2.2067 | 2.7583 | 3.31 | 3.8617 | 4.4133 | 4.965 | 5.5167 | 6.0815 | 6.6463 | 7.2111 | 7.7759 | 8.3407 | 8.6469 | 8.9531 | 9.2593 | 9.5655 | 9.8717 | 10.0413 | 10.2109 | 10.3806 | 10.5502 | 10.7198 | 10.8895 | 11.0591 | 11.2287 | 11.3984 | 11.568 | 11.671 | 11.7741 | 11.8771 | 11.9802 | 12.0832 | 12.1863 | 12.2893 | 12.3924 | 12.4954 | 12.5984 | 12.7015 | 12.8045 | 12.9076 | 13.0106 | 13.1137 | 13.1888 | 13.264 | 13.3392 | 13.4144 | 13.4896 | 13.5647 | 13.6399 | 13.7151 | 13.7903 | 13.8654 | 13.9406 | 14.0158 | 14.091 | 14.1662 | 14.2413 | 14.2611 | 14.2809 | 14.3006 | 14.3204 | 14.3402 | 14.3599 | 14.3797 | 14.3995 | 14.4192 | 14.439 | 14.4588 | 14.4785 | 14.4983 | 14.5181 | 14.5378 | 14.5576 | 14.5774 | 14.5971 | 14.6169 | 14.6367 | 14.6564 | 14.6762 | 14.696 | 14.7157 | 14.7355 | 14.7553 | 14.775 | 14.7948 | 14.8146 | 14.8343 | 14.8382 | 14.8421 | 14.846 | 14.8499 | 14.8538 | 14.8577 | 14.8616 | 14.8654 | 14.8693 | 14.8732 | 14.8771 | 14.881 | 14.8849 | 14.8888 | 14.8927 | 14.8966 | 14.9004 | 14.9043 | 14.9082 | 14.9121 | 14.916 | 14.9199 | 14.9238 | 14.9277 | 14.9316 | 14.9354 | 14.9393 | 14.9432 | 14.9471 | 14.951 | 14.951 | 14.951 | 14.951 | 14.951 | 14.951 | 14.951 | 14.951 | 14.951 | 14.951 | 14.951 | 14.951 | 14.951 | 14.951 | 14.951 | 14.951 | 14.951 | 14.951 | 14.951 | 14.951 | 14.951 | 14.951 | 14.951 | 14.951 | 14.951 | 14.951 | 14.951 | 14.951 | 14.951 | 14.951 | 14.951 | 14.9452 | 14.9393 | 14.9335 | 14.9277 | 14.9218 | 14.916 | 14.9102 | 14.9043 | 14.8985 | 14.8927 | 14.8868 | 14.881 | 14.8752 | 14.8693 | 14.8635 | 14.8577 | 14.8518 | 14.846 | 14.8402 | 14.8343 | 14.8285 | 14.8227 | 14.8168 | 14.811 | 14.8052 | 14.7993 | 14.7935 | 14.7877 | 14.7818 | 14.776
4.4 | 0 | 5.7333 | 8.7093 | 10.2533 | 12.032 | 13.6613 | 14.8587 | 15.4907 | 15.624 | 15.624 | 15.424 | 0 | 0.57333 | 1.1467 | 1.72 | 2.2933 | 2.8667 | 3.44 | 4.0133 | 4.5867 | 5.16 | 5.7333 | 6.3285 | 6.9237 | 7.5189 | 8.1141 | 8.7093 | 9.0181 | 9.3269 | 9.6357 | 9.9445 | 10.2533 | 10.4312 | 10.6091 | 10.7869 | 10.9648 | 11.1427 | 11.3205 | 11.4984 | 11.6763 | 11.8541 | 12.032 | 12.1406 | 12.2492 | 12.3579 | 12.4665 | 12.5751 | 12.6837 | 12.7924 | 12.901 | 13.0096 | 13.1182 | 13.2268 | 13.3355 | 13.4441 | 13.5527 | 13.6613 | 13.7412 | 13.821 | 13.9008 | 13.9806 | 14.0604 | 14.1403 | 14.2201 | 14.2999 | 14.3797 | 14.4596 | 14.5394 | 14.6192 | 14.699 | 14.7788 | 14.8587 | 14.8797 | 14.9008 | 14.9219 | 14.9429 | 14.964 | 14.9851 | 15.0061 | 15.0272 | 15.0483 | 15.0693 | 15.0904 | 15.1115 | 15.1325 | 15.1536 | 15.1747 | 15.1957 | 15.2168 | 15.2379 | 15.2589 | 15.28 | 15.3011 | 15.3221 | 15.3432 | 15.3643 | 15.3853 | 15.4064 | 15.4275 | 15.4485 | 15.4696 | 15.4907 | 15.4951 | 15.4996 | 15.504 | 15.5084 | 15.5129 | 15.5173 | 15.5218 | 15.5262 | 15.5307 | 15.5351 | 15.5396 | 15.544 | 15.5484 | 15.5529 | 15.5573 | 15.5618 | 15.5662 | 15.5707 | 15.5751 | 15.5796 | 15.584 | 15.5884 | 15.5929 | 15.5973 | 15.6018 | 15.6062 | 15.6107 | 15.6151 | 15.6196 | 15.624 | 15.624 | 15.624 | 15.624 | 15.624 | 15.624 | 15.624 | 15.624 | 15.624 | 15.624 | 15.624 | 15.624 | 15.624 | 15.624 | 15.624 | 15.624 | 15.624 | 15.624 | 15.624 | 15.624 | 15.624 | 15.624 | 15.624 | 15.624 | 15.624 | 15.624 | 15.624 | 15.624 | 15.624 | 15.624 | 15.624 | 15.6173 | 15.6107 | 15.604 | 15.5973 | 15.5907 | 15.584 | 15.5773 | 15.5707 | 15.564 | 15.5573 | 15.5507 | 15.544 | 15.5373 | 15.5307 | 15.524 | 15.5173 | 15.5107 | 15.504 | 15.4973 | 15.4907 | 15.484 | 15.4773 | 15.4707 | 15.464 | 15.4573 | 15.4507 | 15.444 | 15.4373 | 15.4307 | 15.424
4.45 | 0 | 5.95 | 9.078 | 10.635 | 12.496 | 14.209 | 15.476 | 16.147 | 16.297 | 16.297 | 16.072 | 0 | 0.595 | 1.19 | 1.785 | 2.38 | 2.975 | 3.57 | 4.165 | 4.76 | 5.355 | 5.95 | 6.5756 | 7.2012 | 7.8268 | 8.4524 | 9.078 | 9.3894 | 9.7008 | 10.0122 | 10.3236 | 10.635 | 10.8211 | 11.0072 | 11.1933 | 11.3794 | 11.5655 | 11.7516 | 11.9377 | 12.1238 | 12.3099 | 12.496 | 12.6102 | 12.7244 | 12.8386 | 12.9528 | 13.067 | 13.1812 | 13.2954 | 13.4096 | 13.5238 | 13.638 | 13.7522 | 13.8664 | 13.9806 | 14.0948 | 14.209 | 14.2935 | 14.3779 | 14.4624 | 14.5469 | 14.6313 | 14.7158 | 14.8003 | 14.8847 | 14.9692 | 15.0537 | 15.1381 | 15.2226 | 15.3071 | 15.3915 | 15.476 | 15.4984 | 15.5207 | 15.5431 | 15.5655 | 15.5878 | 15.6102 | 15.6326 | 15.6549 | 15.6773 | 15.6997 | 15.722 | 15.7444 | 15.7668 | 15.7891 | 15.8115 | 15.8339 | 15.8562 | 15.8786 | 15.901 | 15.9233 | 15.9457 | 15.9681 | 15.9904 | 16.0128 | 16.0352 | 16.0575 | 16.0799 | 16.1023 | 16.1246 | 16.147 | 16.152 | 16.157 | 16.162 | 16.167 | 16.172 | 16.177 | 16.182 | 16.187 | 16.192 | 16.197 | 16.202 | 16.207 | 16.212 | 16.217 | 16.222 | 16.227 | 16.232 | 16.237 | 16.242 | 16.247 | 16.252 | 16.257 | 16.262 | 16.267 | 16.272 | 16.277 | 16.282 | 16.287 | 16.292 | 16.297 | 16.297 | 16.297 | 16.297 | 16.297 | 16.297 | 16.297 | 16.297 | 16.297 | 16.297 | 16.297 | 16.297 | 16.297 | 16.297 | 16.297 | 16.297 | 16.297 | 16.297 | 16.297 | 16.297 | 16.297 | 16.297 | 16.297 | 16.297 | 16.297 | 16.297 | 16.297 | 16.297 | 16.297 | 16.297 | 16.297 | 16.2895 | 16.282 | 16.2745 | 16.267 | 16.2595 | 16.252 | 16.2445 | 16.237 | 16.2295 | 16.222 | 16.2145 | 16.207 | 16.1995 | 16.192 | 16.1845 | 16.177 | 16.1695 | 16.162 | 16.1545 | 16.147 | 16.1395 | 16.132 | 16.1245 | 16.117 | 16.1095 | 16.102 | 16.0945 | 16.087 | 16.0795 | 16.072
4.5 | 0 | 6.1667 | 9.4467 | 11.0167 | 12.96 | 14.7567 | 16.0933 | 16.8033 | 16.97 | 16.97 | 16.72 | 0 | 0.61667 | 1.2333 | 1.85 | 2.4667 | 3.0833 | 3.7 | 4.3167 | 4.9333 | 5.55 | 6.1667 | 6.8227 | 7.4787 | 8.1347 | 8.7907 | 9.4467 | 9.7607 | 10.0747 | 10.3887 | 10.7027 | 11.0167 | 11.211 | 11.4053 | 11.5997 | 11.794 | 11.9883 | 12.1827 | 12.377 | 12.5713 | 12.7657 | 12.96 | 13.0798 | 13.1996 | 13.3193 | 13.4391 | 13.5589 | 13.6787 | 13.7984 | 13.9182 | 14.038 | 14.1578 | 14.2776 | 14.3973 | 14.5171 | 14.6369 | 14.7567 | 14.8458 | 14.9349 | 15.024 | 15.1131 | 15.2022 | 15.2913 | 15.3804 | 15.4696 | 15.5587 | 15.6478 | 15.7369 | 15.826 | 15.9151 | 16.0042 | 16.0933 | 16.117 | 16.1407 | 16.1643 | 16.188 | 16.2117 | 16.2353 | 16.259 | 16.2827 | 16.3063 | 16.33 | 16.3537 | 16.3773 | 16.401 | 16.4247 | 16.4483 | 16.472 | 16.4957 | 16.5193 | 16.543 | 16.5667 | 16.5903 | 16.614 | 16.6377 | 16.6613 | 16.685 | 16.7087 | 16.7323 | 16.756 | 16.7797 | 16.8033 | 16.8089 | 16.8144 | 16.82 | 16.8256 | 16.8311 | 16.8367 | 16.8422 | 16.8478 | 16.8533 | 16.8589 | 16.8644 | 16.87 | 16.8756 | 16.8811 | 16.8867 | 16.8922 | 16.8978 | 16.9033 | 16.9089 | 16.9144 | 16.92 | 16.9256 | 16.9311 | 16.9367 | 16.9422 | 16.9478 | 16.9533 | 16.9589 | 16.9644 | 16.97 | 16.97 | 16.97 | 16.97 | 16.97 | 16.97 | 16.97 | 16.97 | 16.97 | 16.97 | 16.97 | 16.97 | 16.97 | 16.97 | 16.97 | 16.97 | 16.97 | 16.97 | 16.97 | 16.97 | 16.97 | 16.97 | 16.97 | 16.97 | 16.97 | 16.97 | 16.97 | 16.97 | 16.97 | 16.97 | 16.97 | 16.9617 | 16.9533 | 16.945 | 16.9367 | 16.9283 | 16.92 | 16.9117 | 16.9033 | 16.895 | 16.8867 | 16.8783 | 16.87 | 16.8617 | 16.8533 | 16.845 | 16.8367 | 16.8283 | 16.82 | 16.8117 | 16.8033 | 16.795 | 16.7867 | 16.7783 | 16.77 | 16.7617 | 16.7533 | 16.745 | 16.7367 | 16.7283 | 16.72
4.55 | 0 | 6.3833 | 9.8153 | 11.3983 | 13.424 | 15.3043 | 16.7107 | 17.4597 | 17.643 | 17.643 | 17.368 | 0 | 0.63833 | 1.2767 | 1.915 | 2.5533 | 3.1917 | 3.83 | 4.4683 | 5.1067 | 5.745 | 6.3833 | 7.0697 | 7.7561 | 8.4425 | 9.1289 | 9.8153 | 10.1319 | 10.4485 | 10.7651 | 11.0817 | 11.3983 | 11.6009 | 11.8035 | 12.006 | 12.2086 | 12.4112 | 12.6137 | 12.8163 | 13.0189 | 13.2214 | 13.424 | 13.5494 | 13.6747 | 13.8001 | 13.9254 | 14.0508 | 14.1761 | 14.3015 | 14.4268 | 14.5522 | 14.6776 | 14.8029 | 14.9283 | 15.0536 | 15.179 | 15.3043 | 15.3981 | 15.4918 | 15.5856 | 15.6794 | 15.7731 | 15.8669 | 15.9606 | 16.0544 | 16.1481 | 16.2419 | 16.3356 | 16.4294 | 16.5232 | 16.6169 | 16.7107 | 16.7356 | 16.7606 | 16.7856 | 16.8105 | 16.8355 | 16.8605 | 16.8854 | 16.9104 | 16.9354 | 16.9603 | 16.9853 | 17.0103 | 17.0352 | 17.0602 | 17.0852 | 17.1101 | 17.1351 | 17.1601 | 17.185 | 17.21 | 17.235 | 17.2599 | 17.2849 | 17.3099 | 17.3348 | 17.3598 | 17.3848 | 17.4097 | 17.4347 | 17.4597 | 17.4658 | 17.4719 | 17.478 | 17.4841 | 17.4902 | 17.4963 | 17.5024 | 17.5086 | 17.5147 | 17.5208 | 17.5269 | 17.533 | 17.5391 | 17.5452 | 17.5513 | 17.5574 | 17.5636 | 17.5697 | 17.5758 | 17.5819 | 17.588 | 17.5941 | 17.6002 | 17.6063 | 17.6124 | 17.6186 | 17.6247 | 17.6308 | 17.6369 | 17.643 | 17.643 | 17.643 | 17.643 | 17.643 | 17.643 | 17.643 | 17.643 | 17.643 | 17.643 | 17.643 | 17.643 | 17.643 | 17.643 | 17.643 | 17.643 | 17.643 | 17.643 | 17.643 | 17.643 | 17.643 | 17.643 | 17.643 | 17.643 | 17.643 | 17.643 | 17.643 | 17.643 | 17.643 | 17.643 | 17.643 | 17.6338 | 17.6247 | 17.6155 | 17.6063 | 17.5972 | 17.588 | 17.5788 | 17.5697 | 17.5605 | 17.5513 | 17.5422 | 17.533 | 17.5238 | 17.5147 | 17.5055 | 17.4963 | 17.4872 | 17.478 | 17.4688 | 17.4597 | 17.4505 | 17.4413 | 17.4322 | 17.423 | 17.4138 | 17.4047 | 17.3955 | 17.3863 | 17.3772 | 17.368
4.6 | 0 | 6.6 | 10.184 | 11.78 | 13.888 | 15.852 | 17.328 | 18.116 | 18.316 | 18.316 | 18.016 | 4.4409e-16 | 0.66 | 1.32 | 1.98 | 2.64 | 3.3 | 3.96 | 4.62 | 5.28 | 5.94 | 6.6 | 7.3168 | 8.0336 | 8.7504 | 9.4672 | 10.184 | 10.5032 | 10.8224 | 11.1416 | 11.4608 | 11.78 | 11.9908 | 12.2016 | 12.4124 | 12.6232 | 12.834 | 13.0448 | 13.2556 | 13.4664 | 13.6772 | 13.888 | 14.0189 | 14.1499 | 14.2808 | 14.4117 | 14.5427 | 14.6736 | 14.8045 | 14.9355 | 15.0664 | 15.1973 | 15.3283 | 15.4592 | 15.5901 | 15.7211 | 15.852 | 15.9504 | 16.0488 | 16.1472 | 16.2456 | 16.344 | 16.4424 | 16.5408 | 16.6392 | 16.7376 | 16.836 | 16.9344 | 17.0328 | 17.1312 | 17.2296 | 17.328 | 17.3543 | 17.3805 | 17.4068 | 17.4331 | 17.4593 | 17.4856 | 17.5119 | 17.5381 | 17.5644 | 17.5907 | 17.6169 | 17.6432 | 17.6695 | 17.6957 | 17.722 | 17.7483 | 17.7745 | 17.8008 | 17.8271 | 17.8533 | 17.8796 | 17.9059 | 17.9321 | 17.9584 | 17.9847 | 18.0109 | 18.0372 | 18.0635 | 18.0897 | 18.116 | 18.1227 | 18.1293 | 18.136 | 18.1427 | 18.1493 | 18.156 | 18.1627 | 18.1693 | 18.176 | 18.1827 | 18.1893 | 18.196 | 18.2027 | 18.2093 | 18.216 | 18.2227 | 18.2293 | 18.236 | 18.2427 | 18.2493 | 18.256 | 18.2627 | 18.2693 | 18.276 | 18.2827 | 18.2893 | 18.296 | 18.3027 | 18.3093 | 18.316 | 18.316 | 18.316 | 18.316 | 18.316 | 18.316 | 18.316 | 18.316 | 18.316 | 18.316 | 18.316 | 18.316 | 18.316 | 18.316 | 18.316 | 18.316 | 18.316 | 18.316 | 18.316 | 18.316 | 18.316 | 18.316 | 18.316 | 18.316 | 18.316 | 18.316 | 18.316 | 18.316 | 18.316 | 18.316 | 18.316 | 18.306 | 18.296 | 18.286 | 18.276 | 18.266 | 18.256 | 18.246 | 18.236 | 18.226 | 18.216 | 18.206 | 18.196 | 18.186 | 18.176 | 18.166 | 18.156 | 18.146 | 18.136 | 18.126 | 18.116 | 18.106 | 18.096 | 18.086 | 18.076 | 18.066 | 18.056 | 18.046 | 18.036 | 18.026 | 18.016
4.65 | 0 | 6.8167 | 10.5527 | 12.1617 | 14.352 | 16.3997 | 17.9453 | 18.7723 | 18.989 | 18.989 | 18.664 | 4.4409e-16 | 0.68167 | 1.3633 | 2.045 | 2.7267 | 3.4083 | 4.09 | 4.7717 | 5.4533 | 6.135 | 6.8167 | 7.5639 | 8.3111 | 9.0583 | 9.8055 | 10.5527 | 10.8745 | 11.1963 | 11.5181 | 11.8399 | 12.1617 | 12.3807 | 12.5997 | 12.8188 | 13.0378 | 13.2568 | 13.4759 | 13.6949 | 13.9139 | 14.133 | 14.352 | 14.4885 | 14.625 | 14.7615 | 14.898 | 15.0346 | 15.1711 | 15.3076 | 15.4441 | 15.5806 | 15.7171 | 15.8536 | 15.9901 | 16.1266 | 16.2632 | 16.3997 | 16.5027 | 16.6058 | 16.7088 | 16.8118 | 16.9149 | 17.0179 | 17.121 | 17.224 | 17.3271 | 17.4301 | 17.5332 | 17.6362 | 17.7392 | 17.8423 | 17.9453 | 17.9729 | 18.0005 | 18.028 | 18.0556 | 18.0832 | 18.1107 | 18.1383 | 18.1659 | 18.1934 | 18.221 | 18.2486 | 18.2761 | 18.3037 | 18.3313 | 18.3588 | 18.3864 | 18.414 | 18.4415 | 18.4691 | 18.4967 | 18.5242 | 18.5518 | 18.5794 | 18.6069 | 18.6345 | 18.6621 | 18.6896 | 18.7172 | 18.7448 | 18.7723 | 18.7796 | 18.7868 | 18.794 | 18.8012 | 18.8084 | 18.8157 | 18.8229 | 18.8301 | 18.8373 | 18.8446 | 18.8518 | 18.859 | 18.8662 | 18.8734 | 18.8807 | 18.8879 | 18.8951 | 18.9023 | 18.9096 | 18.9168 | 18.924 | 18.9312 | 18.9384 | 18.9457 | 18.9529 | 18.9601 | 18.9673 | 18.9746 | 18.9818 | 18.989 | 18.989 | 18.989 | 18.989 | 18.989 | 18.989 | 18.989 | 18.989 | 18.989 | 18.989 | 18.989 | 18.989 | 18.989 | 18.989 | 18.989 | 18.989 | 18.989 | 18.989 | 18.989 | 18.989 | 18.989 | 18.989 | 18.989 | 18.989 | 18.989 | 18.989 | 18.989 | 18.989 | 18.989 | 18.989 | 18.989 | 18.9782 | 18.9673 | 18.9565 | 18.9457 | 18.9348 | 18.924 | 18.9132 | 18.9023 | 18.8915 | 18.8807 | 18.8698 | 18.859 | 18.8482 | 18.8373 | 18.8265 | 18.8157 | 18.8048 | 18.794 | 18.7832 | 18.7723 | 18.7615 | 18.7507 | 18.7398 | 18.729 | 18.7182 | 18.7073 | 18.6965 | 18.6857 | 18.6748 | 18.664
4.7 | 0 | 7.0333 | 10.9213 | 12.5433 | 14.816 | 16.9473 | 18.5627 | 19.4287 | 19.662 | 19.662 | 19.312 | 0 | 0.70333 | 1.4067 | 2.11 | 2.8133 | 3.5167 | 4.22 | 4.9233 | 5.6267 | 6.33 | 7.0333 | 7.8109 | 8.5885 | 9.3661 | 10.1437 | 10.9213 | 11.2457 | 11.5701 | 11.8945 | 12.2189 | 12.5433 | 12.7706 | 12.9979 | 13.2251 | 13.4524 | 13.6797 | 13.9069 | 14.1342 | 14.3615 | 14.5887 | 14.816 | 14.9581 | 15.1002 | 15.2423 | 15.3844 | 15.5264 | 15.6685 | 15.8106 | 15.9527 | 16.0948 | 16.2369 | 16.379 | 16.5211 | 16.6632 | 16.8052 | 16.9473 | 17.055 | 17.1627 | 17.2704 | 17.3781 | 17.4858 | 17.5935 | 17.7012 | 17.8088 | 17.9165 | 18.0242 | 18.1319 | 18.2396 | 18.3473 | 18.455 | 18.5627 | 18.5915 | 18.6204 | 18.6493 | 18.6781 | 18.707 | 18.7359 | 18.7647 | 18.7936 | 18.8225 | 18.8513 | 18.8802 | 18.9091 | 18.9379 | 18.9668 | 18.9957 | 19.0245 | 19.0534 | 19.0823 | 19.1111 | 19.14 | 19.1689 | 19.1977 | 19.2266 | 19.2555 | 19.2843 | 19.3132 | 19.3421 | 19.3709 | 19.3998 | 19.4287 | 19.4364 | 19.4442 | 19.452 | 19.4598 | 19.4676 | 19.4753 | 19.4831 | 19.4909 | 19.4987 | 19.5064 | 19.5142 | 19.522 | 19.5298 | 19.5376 | 19.5453 | 19.5531 | 19.5609 | 19.5687 | 19.5764 | 19.5842 | 19.592 | 19.5998 | 19.6076 | 19.6153 | 19.6231 | 19.6309 | 19.6387 | 19.6464 | 19.6542 | 19.662 | 19.662 | 19.662 | 19.662 | 19.662 | 19.662 | 19.662 | 19.662 | 19.662 | 19.662 | 19.662 | 19.662 | 19.662 | 19.662 | 19.662 | 19.662 | 19.662 | 19.662 | 19.662 | 19.662 | 19.662 | 19.662 | 19.662 | 19.662 | 19.662 | 19.662 | 19.662 | 19.662 | 19.662 | 19.662 | 19.662 | 19.6503 | 19.6387 | 19.627 | 19.6153 | 19.6037 | 19.592 | 19.5803 | 19.5687 | 19.557 | 19.5453 | 19.5337 | 19.522 | 19.5103 | 19.4987 | 19.487 | 19.4753 | 19.4637 | 19.452 | 19.4403 | 19.4287 | 19.417 | 19.4053 | 19.3937 | 19.382 | 19.3703 | 19.3587 | 19.347 | 19.3353 | 19.3237 | 19.312
4.75 | 0 | 7.25 | 11.29 | 12.925 | 15.28 | 17.495 | 19.18 | 20.085 | 20.335 | 20.335 | 19.96 | 0 | 0.725 | 1.45 | 2.175 | 2.9 | 3.625 | 4.35 | 5.075 | 5.8 | 6.525 | 7.25 | 8.058 | 8.866 | 9.674 | 10.482 | 11.29 | 11.617 | 11.944 | 12.271 | 12.598 | 12.925 | 13.1605 | 13.396 | 13.6315 | 13.867 | 14.1025 | 14.338 | 14.5735 | 14.809 | 15.0445 | 15.28 | 15.4277 | 15.5753 | 15.723 | 15.8707 | 16.0183 | 16.166 | 16.3137 | 16.4613 | 16.609 | 16.7567 | 16.9043 | 17.052 | 17.1997 | 17.3473 | 17.495 | 17.6073 | 17.7197 | 17.832 | 17.9443 | 18.0567 | 18.169 | 18.2813 | 18.3937 | 18.506 | 18.6183 | 18.7307 | 18.843 | 18.9553 | 19.0677 | 19.18 | 19.2102 | 19.2403 | 19.2705 | 19.3007 | 19.3308 | 19.361 | 19.3912 | 19.4213 | 19.4515 | 19.4817 | 19.5118 | 19.542 | 19.5722 | 19.6023 | 19.6325 | 19.6627 | 19.6928 | 19.723 | 19.7532 | 19.7833 | 19.8135 | 19.8437 | 19.8738 | 19.904 | 19.9342 | 19.9643 | 19.9945 | 20.0247 | 20.0548 | 20.085 | 20.0933 | 20.1017 | 20.11 | 20.1183 | 20.1267 | 20.135 | 20.1433 | 20.1517 | 20.16 | 20.1683 | 20.1767 | 20.185 | 20.1933 | 20.2017 | 20.21 | 20.2183 | 20.2267 | 20.235 | 20.2433 | 20.2517 | 20.26 | 20.2683 | 20.2767 | 20.285 | 20.2933 | 20.3017 | 20.31 | 20.3183 | 20.3267 | 20.335 | 20.335 | 20.335 | 20.335 | 20.335 | 20.335 | 20.335 | 20.335 | 20.335 | 20.335 | 20.335 | 20.335 | 20.335 | 20.335 | 20.335 | 20.335 | 20.335 | 20.335 | 20.335 | 20.335 | 20.335 | 20.335 | 20.335 | 20.335 | 20.335 | 20.335 | 20.335 | 20.335 | 20.335 | 20.335 | 20.335 | 20.3225 | 20.31 | 20.2975 | 20.285 | 20.2725 | 20.26 | 20.2475 | 20.235 | 20.2225 | 20.21 | 20.1975 | 20.185 | 20.1725 | 20.16 | 20.1475 | 20.135 | 20.1225 | 20.11 | 20.0975 | 20.085 | 20.0725 | 20.06 | 20.0475 | 20.035 | 20.0225 | 20.01 | 19.9975 | 19.985 | 19.9725 | 19.96
4.8 | 0 | 7.4667 | 11.6587 | 13.3067 | 15.744 | 18.0427 | 19.7973 | 20.7413 | 21.008 | 21.008 | 20.608 | -4.4409e-16 | 0.74667 | 1.4933 | 2.24 | 2.9867 | 3.7333 | 4.48 | 5.2267 | 5.9733 | 6.72 | 7.4667 | 8.3051 | 9.1435 | 9.9819 | 10.8203 | 11.6587 | 11.9883 | 12.3179 | 12.6475 | 12.9771 | 13.3067 | 13.5504 | 13.7941 | 14.0379 | 14.2816 | 14.5253 | 14.7691 | 15.0128 | 15.2565 | 15.5003 | 15.744 | 15.8972 | 16.0505 | 16.2037 | 16.357 | 16.5102 | 16.6635 | 16.8167 | 16.97 | 17.1232 | 17.2764 | 17.4297 | 17.5829 | 17.7362 | 17.8894 | 18.0427 | 18.1596 | 18.2766 | 18.3936 | 18.5106 | 18.6276 | 18.7445 | 18.8615 | 18.9785 | 19.0955 | 19.2124 | 19.3294 | 19.4464 | 19.5634 | 19.6804 | 19.7973 | 19.8288 | 19.8603 | 19.8917 | 19.9232 | 19.9547 | 19.9861 | 20.0176 | 20.0491 | 20.0805 | 20.112 | 20.1435 | 20.1749 | 20.2064 | 20.2379 | 20.2693 | 20.3008 | 20.3323 | 20.3637 | 20.3952 | 20.4267 | 20.4581 | 20.4896 | 20.5211 | 20.5525 | 20.584 | 20.6155 | 20.6469 | 20.6784 | 20.7099 | 20.7413 | 20.7502 | 20.7591 | 20.768 | 20.7769 | 20.7858 | 20.7947 | 20.8036 | 20.8124 | 20.8213 | 20.8302 | 20.8391 | 20.848 | 20.8569 | 20.8658 | 20.8747 | 20.8836 | 20.8924 | 20.9013 | 20.9102 | 20.9191 | 20.928 | 20.9369 | 20.9458 | 20.9547 | 20.9636 | 20.9724 | 20.9813 | 20.9902 | 20.9991 | 21.008 | 21.008 | 21.008 | 21.008 | 21.008 | 21.008 | 21.008 | 21.008 | 21.008 | 21.008 | 21.008 | 21.008 | 21.008 | 21.008 | 21.008 | 21.008 | 21.008 | 21.008 | 21.008 | 21.008 | 21.008 | 21.008 | 21.008 | 21.008 | 21.008 | 21.008 | 21.008 | 21.008 | 21.008 | 21.008 | 21.008 | 20.9947 | 20.9813 | 20.968 | 20.9547 | 20.9413 | 20.928 | 20.9147 | 20.9013 | 20.888 | 20.8747 | 20.8613 | 20.848 | 20.8347 | 20.8213 | 20.808 | 20.7947 | 20.7813 | 20.768 | 20.7547 | 20.7413 | 20.728 | 20.7147 | 20.7013 | 20.688 | 20.6747 | 20.6613 | 20.648 | 20.6347 | 20.6213 | 20.608
4.85 | 0 | 7.6833 | 12.0273 | 13.6883 | 16.208 | 18.5903 | 20.4147 | 21.3977 | 21.681 | 21.681 | 21.256 | 0 | 0.76833 | 1.5367 | 2.305 | 3.0733 | 3.8417 | 4.61 | 5.3783 | 6.1467 | 6.915 | 7.6833 | 8.5521 | 9.4209 | 10.2897 | 11.1585 | 12.0273 | 12.3595 | 12.6917 | 13.0239 | 13.3561 | 13.6883 | 13.9403 | 14.1923 | 14.4442 | 14.6962 | 14.9482 | 15.2001 | 15.4521 | 15.7041 | 15.956 | 16.208 | 16.3668 | 16.5256 | 16.6845 | 16.8433 | 17.0021 | 17.1609 | 17.3198 | 17.4786 | 17.6374 | 17.7962 | 17.955 | 18.1139 | 18.2727 | 18.4315 | 18.5903 | 18.712 | 18.8336 | 18.9552 | 19.0768 | 19.1984 | 19.3201 | 19.4417 | 19.5633 | 19.6849 | 19.8066 | 19.9282 | 20.0498 | 20.1714 | 20.293 | 20.4147 | 20.4474 | 20.4802 | 20.513 | 20.5457 | 20.5785 | 20.6113 | 20.644 | 20.6768 | 20.7096 | 20.7423 | 20.7751 | 20.8079 | 20.8406 | 20.8734 | 20.9062 | 20.9389 | 20.9717 | 21.0045 | 21.0372 | 21.07 | 21.1028 | 21.1355 | 21.1683 | 21.2011 | 21.2338 | 21.2666 | 21.2994 | 21.3321 | 21.3649 | 21.3977 | 21.4071 | 21.4166 | 21.426 | 21.4354 | 21.4449 | 21.4543 | 21.4638 | 21.4732 | 21.4827 | 21.4921 | 21.5016 | 21.511 | 21.5204 | 21.5299 | 21.5393 | 21.5488 | 21.5582 | 21.5677 | 21.5771 | 21.5866 | 21.596 | 21.6054 | 21.6149 | 21.6243 | 21.6338 | 21.6432 | 21.6527 | 21.6621 | 21.6716 | 21.681 | 21.681 | 21.681 | 21.681 | 21.681 | 21.681 | 21.681 | 21.681 | 21.681 | 21.681 | 21.681 | 21.681 | 21.681 | 21.681 | 21.681 | 21.681 | 21.681 | 21.681 | 21.681 | 21.681 | 21.681 | 21.681 | 21.681 | 21.681 | 21.681 | 21.681 | 21.681 | 21.681 | 21.681 | 21.681 | 21.681 | 21.6668 | 21.6527 | 21.6385 | 21.6243 | 21.6102 | 21.596 | 21.5818 | 21.5677 | 21.5535 | 21.5393 | 21.5252 | 21.511 | 21.4968 | 21.4827 | 21.4685 | 21.4543 | 21.4402 | 21.426 | 21.4118 | 21.3977 | 21.3835 | 21.3693 | 21.3552 | 21.341 | 21.3268 | 21.3127 | 21.2985 | 21.2843 | 21.2702 | 21.256
4.9 | 0 | 7.9 | 12.396 | 14.07 | 16.672 | 19.138 | 21.032 | 22.054 | 22.354 | 22.354 | 21.904 | 0 | 0.79 | 1.58 | 2.37 | 3.16 | 3.95 | 4.74 | 5.53 | 6.32 | 7.11 | 7.9 | 8.7992 | 9.6984 | 10.5976 | 11.4968 | 12.396 | 12.7308 | 13.0656 | 13.4004 | 13.7352 | 14.07 | 14.3302 | 14.5904 | 14.8506 | 15.1108 | 15.371 | 15.6312 | 15.8914 | 16.1516 | 16.4118 | 16.672 | 16.8364 | 17.0008 | 17.1652 | 17.3296 | 17.494 | 17.6584 | 17.8228 | 17.9872 | 18.1516 | 18.316 | 18.4804 | 18.6448 | 18.8092 | 18.9736 | 19.138 | 19.2643 | 19.3905 | 19.5168 | 19.6431 | 19.7693 | 19.8956 | 20.0219 | 20.1481 | 20.2744 | 20.4007 | 20.5269 | 20.6532 | 20.7795 | 20.9057 | 21.032 | 21.0661 | 21.1001 | 21.1342 | 21.1683 | 21.2023 | 21.2364 | 21.2705 | 21.3045 | 21.3386 | 21.3727 | 21.4067 | 21.4408 | 21.4749 | 21.5089 | 21.543 | 21.5771 | 21.6111 | 21.6452 | 21.6793 | 21.7133 | 21.7474 | 21.7815 | 21.8155 | 21.8496 | 21.8837 | 21.9177 | 21.9518 | 21.9859 | 22.0199 | 22.054 | 22.064 | 22.074 | 22.084 | 22.094 | 22.104 | 22.114 | 22.124 | 22.134 | 22.144 | 22.154 | 22.164 | 22.174 | 22.184 | 22.194 | 22.204 | 22.214 | 22.224 | 22.234 | 22.244 | 22.254 | 22.264 | 22.274 | 22.284 | 22.294 | 22.304 | 22.314 | 22.324 | 22.334 | 22.344 | 22.354 | 22.354 | 22.354 | 22.354 | 22.354 | 22.354 | 22.354 | 22.354 | 22.354 | 22.354 | 22.354 | 22.354 | 22.354 | 22.354 | 22.354 | 22.354 | 22.354 | 22.354 | 22.354 | 22.354 | 22.354 | 22.354 | 22.354 | 22.354 | 22.354 | 22.354 | 22.354 | 22.354 | 22.354 | 22.354 | 22.354 | 22.339 | 22.324 | 22.309 | 22.294 | 22.279 | 22.264 | 22.249 | 22.234 | 22.219 | 22.204 | 22.189 | 22.174 | 22.159 | 22.144 | 22.129 | 22.114 | 22.099 | 22.084 | 22.069 | 22.054 | 22.039 | 22.024 | 22.009 | 21.994 | 21.979 | 21.964 | 21.949 | 21.934 | 21.919 | 21.904
4.95 | 0 | 8.1167 | 12.7647 | 14.4517 | 17.136 | 19.6857 | 21.6493 | 22.7103 | 23.027 | 23.027 | 22.552 | 0 | 0.81167 | 1.6233 | 2.435 | 3.2467 | 4.0583 | 4.87 | 5.6817 | 6.4933 | 7.305 | 8.1167 | 9.0463 | 9.9759 | 10.9055 | 11.8351 | 12.7647 | 13.1021 | 13.4395 | 13.7769 | 14.1143 | 14.4517 | 14.7201 | 14.9885 | 15.257 | 15.5254 | 15.7938 | 16.0623 | 16.3307 | 16.5991 | 16.8676 | 17.136 | 17.306 | 17.476 | 17.6459 | 17.8159 | 17.9859 | 18.1559 | 18.3258 | 18.4958 | 18.6658 | 18.8358 | 19.0058 | 19.1757 | 19.3457 | 19.5157 | 19.6857 | 19.8166 | 19.9475 | 20.0784 | 20.2093 | 20.3402 | 20.4711 | 20.602 | 20.733 | 20.8639 | 20.9948 | 21.1257 | 21.2566 | 21.3875 | 21.5184 | 21.6493 | 21.6847 | 21.7201 | 21.7554 | 21.7908 | 21.8262 | 21.8615 | 21.8969 | 21.9323 | 21.9676 | 22.003 | 22.0384 | 22.0737 | 22.1091 | 22.1445 | 22.1798 | 22.2152 | 22.2506 | 22.2859 | 22.3213 | 22.3567 | 22.392 | 22.4274 | 22.4628 | 22.4981 | 22.5335 | 22.5689 | 22.6042 | 22.6396 | 22.675 | 22.7103 | 22.7209 | 22.7314 | 22.742 | 22.7526 | 22.7631 | 22.7737 | 22.7842 | 22.7948 | 22.8053 | 22.8159 | 22.8264 | 22.837 | 22.8476 | 22.8581 | 22.8687 | 22.8792 | 22.8898 | 22.9003 | 22.9109 | 22.9214 | 22.932 | 22.9426 | 22.9531 | 22.9637 | 22.9742 | 22.9848 | 22.9953 | 23.0059 | 23.0164 | 23.027 | 23.027 | 23.027 | 23.027 | 23.027 | 23.027 | 23.027 | 23.027 | 23.027 | 23.027 | 23.027 | 23.027 | 23.027 | 23.027 | 23.027 | 23.027 | 23.027 | 23.027 | 23.027 | 23.027 | 23.027 | 23.027 | 23.027 | 23.027 | 23.027 | 23.027 | 23.027 | 23.027 | 23.027 | 23.027 | 23.027 | 23.0112 | 22.9953 | 22.9795 | 22.9637 | 22.9478 | 22.932 | 22.9162 | 22.9003 | 22.8845 | 22.8687 | 22.8528 | 22.837 | 22.8212 | 22.8053 | 22.7895 | 22.7737 | 22.7578 | 22.742 | 22.7262 | 22.7103 | 22.6945 | 22.6787 | 22.6628 | 22.647 | 22.6312 | 22.6153 | 22.5995 | 22.5837 | 22.5678 | 22.552
5 | 0 | 8.3333 | 13.1333 | 14.8333 | 17.6 | 20.2333 | 22.2667 | 23.3667 | 23.7 | 23.7 | 23.2 | 0 | 0.83333 | 1.6667 | 2.5 | 3.3333 | 4.1667 | 5 | 5.8333 | 6.6667 | 7.5 | 8.3333 | 9.2933 | 10.2533 | 11.2133 | 12.1733 | 13.1333 | 13.4733 | 13.8133 | 14.1533 | 14.4933 | 14.8333 | 15.11 | 15.3867 | 15.6633 | 15.94 | 16.2167 | 16.4933 | 16.77 | 17.0467 | 17.3233 | 17.6 | 17.7756 | 17.9511 | 18.1267 | 18.3022 | 18.4778 | 18.6533 | 18.8289 | 19.0044 | 19.18 | 19.3556 | 19.5311 | 19.7067 | 19.8822 | 20.0578 | 20.2333 | 20.3689 | 20.5044 | 20.64 | 20.7756 | 20.9111 | 21.0467 | 21.1822 | 21.3178 | 21.4533 | 21.5889 | 21.7244 | 21.86 | 21.9956 | 22.1311 | 22.2667 | 22.3033 | 22.34 | 22.3767 | 22.4133 | 22.45 | 22.4867 | 22.5233 | 22.56 | 22.5967 | 22.6333 | 22.67 | 22.7067 | 22.7433 | 22.78 | 22.8167 | 22.8533 | 22.89 | 22.9267 | 22.9633 | 23 | 23.0367 | 23.0733 | 23.11 | 23.1467 | 23.1833 | 23.22 | 23.2567 | 23.2933 | 23.33 | 23.3667 | 23.3778 | 23.3889 | 23.4 | 23.4111 | 23.4222 | 23.4333 | 23.4444 | 23.4556 | 23.4667 | 23.4778 | 23.4889 | 23.5 | 23.5111 | 23.5222 | 23.5333 | 23.5444 | 23.5556 | 23.5667 | 23.5778 | 23.5889 | 23.6 | 23.6111 | 23.6222 | 23.6333 | 23.6444 | 23.6556 | 23.6667 | 23.6778 | 23.6889 | 23.7 | 23.7 | 23.7 | 23.7 | 23.7 | 23.7 | 23.7 | 23.7 | 23.7 | 23.7 | 23.7 | 23.7 | 23.7 | 23.7 | 23.7 | 23.7 | 23.7 | 23.7 | 23.7 | 23.7 | 23.7 | 23.7 | 23.7 | 23.7 | 23.7 | 23.7 | 23.7 | 23.7 | 23.7 | 23.7 | 23.7 | 23.6833 | 23.6667 | 23.65 | 23.6333 | 23.6167 | 23.6 | 23.5833 | 23.5667 | 23.55 | 23.5333 | 23.5167 | 23.5 | 23.4833 | 23.4667 | 23.45 | 23.4333 | 23.4167 | 23.4 | 23.3833 | 23.3667 | 23.35 | 23.3333 | 23.3167 | 23.3 | 23.2833 | 23.2667 | 23.25 | 23.2333 | 23.2167 | 23.2
5.05 | 0 | 8.55 | 13.502 | 15.215 | 18.064 | 20.781 | 22.884 | 24.023 | 24.373 | 24.373 | 23.848 | 0 | 0.855 | 1.71 | 2.565 | 3.42 | 4.275 | 5.13 | 5.985 | 6.84 | 7.695 | 8.55 | 9.5404 | 10.5308 | 11.5212 | 12.5116 | 13.502 | 13.8446 | 14.1872 | 14.5298 | 14.8724 | 15.215 | 15.4999 | 15.7848 | 16.0697 | 16.3546 | 16.6395 | 16.9244 | 17.2093 | 17.4942 | 17.7791 | 18.064 | 18.2451 | 18.4263 | 18.6074 | 18.7885 | 18.9697 | 19.1508 | 19.3319 | 19.5131 | 19.6942 | 19.8753 | 20.0565 | 20.2376 | 20.4187 | 20.5999 | 20.781 | 20.9212 | 21.0614 | 21.2016 | 21.3418 | 21.482 | 21.6222 | 21.7624 | 21.9026 | 22.0428 | 22.183 | 22.3232 | 22.4634 | 22.6036 | 22.7438 | 22.884 | 22.922 | 22.9599 | 22.9979 | 23.0359 | 23.0738 | 23.1118 | 23.1498 | 23.1877 | 23.2257 | 23.2637 | 23.3016 | 23.3396 | 23.3776 | 23.4155 | 23.4535 | 23.4915 | 23.5294 | 23.5674 | 23.6054 | 23.6433 | 23.6813 | 23.7193 | 23.7572 | 23.7952 | 23.8332 | 23.8711 | 23.9091 | 23.9471 | 23.985 | 24.023 | 24.0347 | 24.0463 | 24.058 | 24.0697 | 24.0813 | 24.093 | 24.1047 | 24.1163 | 24.128 | 24.1397 | 24.1513 | 24.163 | 24.1747 | 24.1863 | 24.198 | 24.2097 | 24.2213 | 24.233 | 24.2447 | 24.2563 | 24.268 | 24.2797 | 24.2913 | 24.303 | 24.3147 | 24.3263 | 24.338 | 24.3497 | 24.3613 | 24.373 | 24.373 | 24.373 | 24.373 | 24.373 | 24.373 | 24.373 | 24.373 | 24.373 | 24.373 | 24.373 | 24.373 | 24.373 | 24.373 | 24.373 | 24.373 | 24.373 | 24.373 | 24.373 | 24.373 | 24.373 | 24.373 | 24.373 | 24.373 | 24.373 | 24.373 | 24.373 | 24.373 | 24.373 | 24.373 | 24.373 | 24.3555 | 24.338 | 24.3205 | 24.303 | 24.2855 | 24.268 | 24.2505 | 24.233 | 24.2155 | 24.198 | 24.1805 | 24.163 | 24.1455 | 24.128 | 24.1105 | 24.093 | 24.0755 | 24.058 | 24.0405 | 24.023 | 24.0055 | 23.988 | 23.9705 | 23.953 | 23.9355 | 23.918 | 23.9005 | 23.883 | 23.8655 | 23.848
5.1 | 0 | 8.7667 | 13.8707 | 15.5967 | 18.528 | 21.3287 | 23.5013 | 24.6793 | 25.046 | 25.046 | 24.496 | 0 | 0.87667 | 1.7533 | 2.63 | 3.5067 | 4.3833 | 5.26 | 6.1367 | 7.0133 | 7.89 | 8.7667 | 9.7875 | 10.8083 | 11.8291 | 12.8499 | 13.8707 | 14.2159 | 14.5611 | 14.9063 | 15.2515 | 15.5967 | 15.8898 | 16.1829 | 16.4761 | 16.7692 | 17.0623 | 17.3555 | 17.6486 | 17.9417 | 18.2349 | 18.528 | 18.7147 | 18.9014 | 19.0881 | 19.2748 | 19.4616 | 19.6483 | 19.835 | 20.0217 | 20.2084 | 20.3951 | 20.5818 | 20.7685 | 20.9552 | 21.142 | 21.3287 | 21.4735 | 21.6184 | 21.7632 | 21.908 | 22.0529 | 22.1977 | 22.3426 | 22.4874 | 22.6323 | 22.7771 | 22.922 | 23.0668 | 23.2116 | 23.3565 | 23.5013 | 23.5406 | 23.5799 | 23.6191 | 23.6584 | 23.6977 | 23.7369 | 23.7762 | 23.8155 | 23.8547 | 23.894 | 23.9333 | 23.9725 | 24.0118 | 24.0511 | 24.0903 | 24.1296 | 24.1689 | 24.2081 | 24.2474 | 24.2867 | 24.3259 | 24.3652 | 24.4045 | 24.4437 | 24.483 | 24.5223 | 24.5615 | 24.6008 | 24.6401 | 24.6793 | 24.6916 | 24.7038 | 24.716 | 24.7282 | 24.7404 | 24.7527 | 24.7649 | 24.7771 | 24.7893 | 24.8016 | 24.8138 | 24.826 | 24.8382 | 24.8504 | 24.8627 | 24.8749 | 24.8871 | 24.8993 | 24.9116 | 24.9238 | 24.936 | 24.9482 | 24.9604 | 24.9727 | 24.9849 | 24.9971 | 25.0093 | 25.0216 | 25.0338 | 25.046 | 25.046 | 25.046 | 25.046 | 25.046 | 25.046 | 25.046 | 25.046 | 25.046 | 25.046 | 25.046 | 25.046 | 25.046 | 25.046 | 25.046 | 25.046 | 25.046 | 25.046 | 25.046 | 25.046 | 25.046 | 25.046 | 25.046 | 25.046 | 25.046 | 25.046 | 25.046 | 25.046 | 25.046 | 25.046 | 25.046 | 25.0277 | 25.0093 | 24.991 | 24.9727 | 24.9543 | 24.936 | 24.9177 | 24.8993 | 24.881 | 24.8627 | 24.8443 | 24.826 | 24.8077 | 24.7893 | 24.771 | 24.7527 | 24.7343 | 24.716 | 24.6977 | 24.6793 | 24.661 | 24.6427 | 24.6243 | 24.606 | 24.5877 | 24.5693 | 24.551 | 24.5327 | 24.5143 | 24.496
5.15 | 0 | 8.9833 | 14.2393 | 15.9783 | 18.992 | 21.8763 | 24.1187 | 25.3357 | 25.719 | 25.719 | 25.144 | 0 | 0.89833 | 1.7967 | 2.695 | 3.5933 | 4.4917 | 5.39 | 6.2883 | 7.1867 | 8.085 | 8.9833 | 10.0345 | 11.0857 | 12.1369 | 13.1881 | 14.2393 | 14.5871 | 14.9349 | 15.2827 | 15.6305 | 15.9783 | 16.2797 | 16.5811 | 16.8824 | 17.1838 | 17.4852 | 17.7865 | 18.0879 | 18.3893 | 18.6906 | 18.992 | 19.1843 | 19.3766 | 19.5689 | 19.7612 | 19.9534 | 20.1457 | 20.338 | 20.5303 | 20.7226 | 20.9149 | 21.1072 | 21.2995 | 21.4918 | 21.684 | 21.8763 | 22.0258 | 22.1753 | 22.3248 | 22.4743 | 22.6238 | 22.7733 | 22.9228 | 23.0722 | 23.2217 | 23.3712 | 23.5207 | 23.6702 | 23.8197 | 23.9692 | 24.1187 | 24.1592 | 24.1998 | 24.2404 | 24.2809 | 24.3215 | 24.3621 | 24.4026 | 24.4432 | 24.4838 | 24.5243 | 24.5649 | 24.6055 | 24.646 | 24.6866 | 24.7272 | 24.7677 | 24.8083 | 24.8489 | 24.8894 | 24.93 | 24.9706 | 25.0111 | 25.0517 | 25.0923 | 25.1328 | 25.1734 | 25.214 | 25.2545 | 25.2951 | 25.3357 | 25.3484 | 25.3612 | 25.374 | 25.3868 | 25.3996 | 25.4123 | 25.4251 | 25.4379 | 25.4507 | 25.4634 | 25.4762 | 25.489 | 25.5018 | 25.5146 | 25.5273 | 25.5401 | 25.5529 | 25.5657 | 25.5784 | 25.5912 | 25.604 | 25.6168 | 25.6296 | 25.6423 | 25.6551 | 25.6679 | 25.6807 | 25.6934 | 25.7062 | 25.719 | 25.719 | 25.719 | 25.719 | 25.719 | 25.719 | 25.719 | 25.719 | 25.719 | 25.719 | 25.719 | 25.719 | 25.719 | 25.719 | 25.719 | 25.719 | 25.719 | 25.719 | 25.719 | 25.719 | 25.719 | 25.719 | 25.719 | 25.719 | 25.719 | 25.719 | 25.719 | 25.719 | 25.719 | 25.719 | 25.719 | 25.6998 | 25.6807 | 25.6615 | 25.6423 | 25.6232 | 25.604 | 25.5848 | 25.5657 | 25.5465 | 25.5273 | 25.5082 | 25.489 | 25.4698 | 25.4507 | 25.4315 | 25.4123 | 25.3932 | 25.374 | 25.3548 | 25.3357 | 25.3165 | 25.2973 | 25.2782 | 25.259 | 25.2398 | 25.2207 | 25.2015 | 25.1823 | 25.1632 | 25.144
5.2 | 0 | 9.2 | 14.608 | 16.36 | 19.456 | 22.424 | 24.736 | 25.992 | 26.392 | 26.392 | 25.792 | -8.8818e-16 | 0.92 | 1.84 | 2.76 | 3.68 | 4.6 | 5.52 | 6.44 | 7.36 | 8.28 | 9.2 | 10.2816 | 11.3632 | 12.4448 | 13.5264 | 14.608 | 14.9584 | 15.3088 | 15.6592 | 16.0096 | 16.36 | 16.6696 | 16.9792 | 17.2888 | 17.5984 | 17.908 | 18.2176 | 18.5272 | 18.8368 | 19.1464 | 19.456 | 19.6539 | 19.8517 | 20.0496 | 20.2475 | 20.4453 | 20.6432 | 20.8411 | 21.0389 | 21.2368 | 21.4347 | 21.6325 | 21.8304 | 22.0283 | 22.2261 | 22.424 | 22.5781 | 22.7323 | 22.8864 | 23.0405 | 23.1947 | 23.3488 | 23.5029 | 23.6571 | 23.8112 | 23.9653 | 24.1195 | 24.2736 | 24.4277 | 24.5819 | 24.736 | 24.7779 | 24.8197 | 24.8616 | 24.9035 | 24.9453 | 24.9872 | 25.0291 | 25.0709 | 25.1128 | 25.1547 | 25.1965 | 25.2384 | 25.2803 | 25.3221 | 25.364 | 25.4059 | 25.4477 | 25.4896 | 25.5315 | 25.5733 | 25.6152 | 25.6571 | 25.6989 | 25.7408 | 25.7827 | 25.8245 | 25.8664 | 25.9083 | 25.9501 | 25.992 | 26.0053 | 26.0187 | 26.032 | 26.0453 | 26.0587 | 26.072 | 26.0853 | 26.0987 | 26.112 | 26.1253 | 26.1387 | 26.152 | 26.1653 | 26.1787 | 26.192 | 26.2053 | 26.2187 | 26.232 | 26.2453 | 26.2587 | 26.272 | 26.2853 | 26.2987 | 26.312 | 26.3253 | 26.3387 | 26.352 | 26.3653 | 26.3787 | 26.392 | 26.392 | 26.392 | 26.392 | 26.392 | 26.392 | 26.392 | 26.392 | 26.392 | 26.392 | 26.392 | 26.392 | 26.392 | 26.392 | 26.392 | 26.392 | 26.392 | 26.392 | 26.392 | 26.392 | 26.392 | 26.392 | 26.392 | 26.392 | 26.392 | 26.392 | 26.392 | 26.392 | 26.392 | 26.392 | 26.392 | 26.372 | 26.352 | 26.332 | 26.312 | 26.292 | 26.272 | 26.252 | 26.232 | 26.212 | 26.192 | 26.172 | 26.152 | 26.132 | 26.112 | 26.092 | 26.072 | 26.052 | 26.032 | 26.012 | 25.992 | 25.972 | 25.952 | 25.932 | 25.912 | 25.892 | 25.872 | 25.852 | 25.832 | 25.812 | 25.792
5.25 | 0 | 9.4167 | 14.9767 | 16.7417 | 19.92 | 22.9717 | 25.3533 | 26.6483 | 27.065 | 27.065 | 26.44 | 0 | 0.94167 | 1.8833 | 2.825 | 3.7667 | 4.7083 | 5.65 | 6.5917 | 7.5333 | 8.475 | 9.4167 | 10.5287 | 11.6407 | 12.7527 | 13.8647 | 14.9767 | 15.3297 | 15.6827 | 16.0357 | 16.3887 | 16.7417 | 17.0595 | 17.3773 | 17.6952 | 18.013 | 18.3308 | 18.6487 | 18.9665 | 19.2843 | 19.6022 | 19.92 | 20.1234 | 20.3269 | 20.5303 | 20.7338 | 20.9372 | 21.1407 | 21.3441 | 21.5476 | 21.751 | 21.9544 | 22.1579 | 22.3613 | 22.5648 | 22.7682 | 22.9717 | 23.1304 | 23.2892 | 23.448 | 23.6068 | 23.7656 | 23.9243 | 24.0831 | 24.2419 | 24.4007 | 24.5594 | 24.7182 | 24.877 | 25.0358 | 25.1946 | 25.3533 | 25.3965 | 25.4397 | 25.4828 | 25.526 | 25.5692 | 25.6123 | 25.6555 | 25.6987 | 25.7418 | 25.785 | 25.8282 | 25.8713 | 25.9145 | 25.9577 | 26.0008 | 26.044 | 26.0872 | 26.1303 | 26.1735 | 26.2167 | 26.2598 | 26.303 | 26.3462 | 26.3893 | 26.4325 | 26.4757 | 26.5188 | 26.562 | 26.6052 | 26.6483 | 26.6622 | 26.6761 | 26.69 | 26.7039 | 26.7178 | 26.7317 | 26.7456 | 26.7594 | 26.7733 | 26.7872 | 26.8011 | 26.815 | 26.8289 | 26.8428 | 26.8567 | 26.8706 | 26.8844 | 26.8983 | 26.9122 | 26.9261 | 26.94 | 26.9539 | 26.9678 | 26.9817 | 26.9956 | 27.0094 | 27.0233 | 27.0372 | 27.0511 | 27.065 | 27.065 | 27.065 | 27.065 | 27.065 | 27.065 | 27.065 | 27.065 | 27.065 | 27.065 | 27.065 | 27.065 | 27.065 | 27.065 | 27.065 | 27.065 | 27.065 | 27.065 | 27.065 | 27.065 | 27.065 | 27.065 | 27.065 | 27.065 | 27.065 | 27.065 | 27.065 | 27.065 | 27.065 | 27.065 | 27.065 | 27.0442 | 27.0233 | 27.0025 | 26.9817 | 26.9608 | 26.94 | 26.9192 | 26.8983 | 26.8775 | 26.8567 | 26.8358 | 26.815 | 26.7942 | 26.7733 | 26.7525 | 26.7317 | 26.7108 | 26.69 | 26.6692 | 26.6483 | 26.6275 | 26.6067 | 26.5858 | 26.565 | 26.5442 | 26.5233 | 26.5025 | 26.4817 | 26.4608 | 26.44
5.3 | 0 | 9.6333 | 15.3453 | 17.1233 | 20.384 | 23.5193 | 25.9707 | 27.3047 | 27.738 | 27.738 | 27.088 | 0 | 0.96333 | 1.9267 | 2.89 | 3.8533 | 4.8167 | 5.78 | 6.7433 | 7.7067 | 8.67 | 9.6333 | 10.7757 | 11.9181 | 13.0605 | 14.2029 | 15.3453 | 15.7009 | 16.0565 | 16.4121 | 16.7677 | 17.1233 | 17.4494 | 17.7755 | 18.1015 | 18.4276 | 18.7537 | 19.0797 | 19.4058 | 19.7319 | 20.0579 | 20.384 | 20.593 | 20.802 | 21.0111 | 21.2201 | 21.4291 | 21.6381 | 21.8472 | 22.0562 | 22.2652 | 22.4742 | 22.6832 | 22.8923 | 23.1013 | 23.3103 | 23.5193 | 23.6828 | 23.8462 | 24.0096 | 24.173 | 24.3364 | 24.4999 | 24.6633 | 24.8267 | 24.9901 | 25.1536 | 25.317 | 25.4804 | 25.6438 | 25.8072 | 25.9707 | 26.0151 | 26.0596 | 26.1041 | 26.1485 | 26.193 | 26.2375 | 26.2819 | 26.3264 | 26.3709 | 26.4153 | 26.4598 | 26.5043 | 26.5487 | 26.5932 | 26.6377 | 26.6821 | 26.7266 | 26.7711 | 26.8155 | 26.86 | 26.9045 | 26.9489 | 26.9934 | 27.0379 | 27.0823 | 27.1268 | 27.1713 | 27.2157 | 27.2602 | 27.3047 | 27.3191 | 27.3336 | 27.348 | 27.3624 | 27.3769 | 27.3913 | 27.4058 | 27.4202 | 27.4347 | 27.4491 | 27.4636 | 27.478 | 27.4924 | 27.5069 | 27.5213 | 27.5358 | 27.5502 | 27.5647 | 27.5791 | 27.5936 | 27.608 | 27.6224 | 27.6369 | 27.6513 | 27.6658 | 27.6802 | 27.6947 | 27.7091 | 27.7236 | 27.738 | 27.738 | 27.738 | 27.738 | 27.738 | 27.738 | 27.738 | 27.738 | 27.738 | 27.738 | 27.738 | 27.738 | 27.738 | 27.738 | 27.738 | 27.738 | 27.738 | 27.738 | 27.738 | 27.738 | 27.738 | 27.738 | 27.738 | 27.738 | 27.738 | 27.738 | 27.738 | 27.738 | 27.738 | 27.738 | 27.738 | 27.7163 | 27.6947 | 27.673 | 27.6513 | 27.6297 | 27.608 | 27.5863 | 27.5647 | 27.543 | 27.5213 | 27.4997 | 27.478 | 27.4563 | 27.4347 | 27.413 | 27.3913 | 27.3697 | 27.348 | 27.3263 | 27.3047 | 27.283 | 27.2613 | 27.2397 | 27.218 | 27.1963 | 27.1747 | 27.153 | 27.1313 | 27.1097 | 27.088
5.35 | 0 | 9.85 | 15.714 | 17.505 | 20.848 | 24.067 | 26.588 | 27.961 | 28.411 | 28.411 | 27.736 | 0 | 0.985 | 1.97 | 2.955 | 3.94 | 4.925 | 5.91 | 6.895 | 7.88 | 8.865 | 9.85 | 11.0228 | 12.1956 | 13.3684 | 14.5412 | 15.714 | 16.0722 | 16.4304 | 16.7886 | 17.1468 | 17.505 | 17.8393 | 18.1736 | 18.5079 | 18.8422 | 19.1765 | 19.5108 | 19.8451 | 20.1794 | 20.5137 | 20.848 | 21.0626 | 21.2772 | 21.4918 | 21.7064 | 21.921 | 22.1356 | 22.3502 | 22.5648 | 22.7794 | 22.994 | 23.2086 | 23.4232 | 23.6378 | 23.8524 | 24.067 | 24.2351 | 24.4031 | 24.5712 | 24.7393 | 24.9073 | 25.0754 | 25.2435 | 25.4115 | 25.5796 | 25.7477 | 25.9157 | 26.0838 | 26.2519 | 26.4199 | 26.588 | 26.6338 | 26.6795 | 26.7253 | 26.7711 | 26.8168 | 26.8626 | 26.9084 | 26.9541 | 26.9999 | 27.0457 | 27.0914 | 27.1372 | 27.183 | 27.2287 | 27.2745 | 27.3203 | 27.366 | 27.4118 | 27.4576 | 27.5033 | 27.5491 | 27.5949 | 27.6406 | 27.6864 | 27.7322 | 27.7779 | 27.8237 | 27.8695 | 27.9152 | 27.961 | 27.976 | 27.991 | 28.006 | 28.021 | 28.036 | 28.051 | 28.066 | 28.081 | 28.096 | 28.111 | 28.126 | 28.141 | 28.156 | 28.171 | 28.186 | 28.201 | 28.216 | 28.231 | 28.246 | 28.261 | 28.276 | 28.291 | 28.306 | 28.321 | 28.336 | 28.351 | 28.366 | 28.381 | 28.396 | 28.411 | 28.411 | 28.411 | 28.411 | 28.411 | 28.411 | 28.411 | 28.411 | 28.411 | 28.411 | 28.411 | 28.411 | 28.411 | 28.411 | 28.411 | 28.411 | 28.411 | 28.411 | 28.411 | 28.411 | 28.411 | 28.411 | 28.411 | 28.411 | 28.411 | 28.411 | 28.411 | 28.411 | 28.411 | 28.411 | 28.411 | 28.3885 | 28.366 | 28.3435 | 28.321 | 28.2985 | 28.276 | 28.2535 | 28.231 | 28.2085 | 28.186 | 28.1635 | 28.141 | 28.1185 | 28.096 | 28.0735 | 28.051 | 28.0285 | 28.006 | 27.9835 | 27.961 | 27.9385 | 27.916 | 27.8935 | 27.871 | 27.8485 | 27.826 | 27.8035 | 27.781 | 27.7585 | 27.736
5.4 | 0 | 10.0667 | 16.0827 | 17.8867 | 21.312 | 24.6147 | 27.2053 | 28.6173 | 29.084 | 29.084 | 28.384 | 0 | 1.0067 | 2.0133 | 3.02 | 4.0267 | 5.0333 | 6.04 | 7.0467 | 8.0533 | 9.06 | 10.0667 | 11.2699 | 12.4731 | 13.6763 | 14.8795 | 16.0827 | 16.4435 | 16.8043 | 17.1651 | 17.5259 | 17.8867 | 18.2292 | 18.5717 | 18.9143 | 19.2568 | 19.5993 | 19.9419 | 20.2844 | 20.6269 | 20.9695 | 21.312 | 21.5322 | 21.7524 | 21.9725 | 22.1927 | 22.4129 | 22.6331 | 22.8532 | 23.0734 | 23.2936 | 23.5138 | 23.734 | 23.9541 | 24.1743 | 24.3945 | 24.6147 | 24.7874 | 24.9601 | 25.1328 | 25.3055 | 25.4782 | 25.6509 | 25.8236 | 25.9964 | 26.1691 | 26.3418 | 26.5145 | 26.6872 | 26.8599 | 27.0326 | 27.2053 | 27.2524 | 27.2995 | 27.3465 | 27.3936 | 27.4407 | 27.4877 | 27.5348 | 27.5819 | 27.6289 | 27.676 | 27.7231 | 27.7701 | 27.8172 | 27.8643 | 27.9113 | 27.9584 | 28.0055 | 28.0525 | 28.0996 | 28.1467 | 28.1937 | 28.2408 | 28.2879 | 28.3349 | 28.382 | 28.4291 | 28.4761 | 28.5232 | 28.5703 | 28.6173 | 28.6329 | 28.6484 | 28.664 | 28.6796 | 28.6951 | 28.7107 | 28.7262 | 28.7418 | 28.7573 | 28.7729 | 28.7884 | 28.804 | 28.8196 | 28.8351 | 28.8507 | 28.8662 | 28.8818 | 28.8973 | 28.9129 | 28.9284 | 28.944 | 28.9596 | 28.9751 | 28.9907 | 29.0062 | 29.0218 | 29.0373 | 29.0529 | 29.0684 | 29.084 | 29.084 | 29.084 | 29.084 | 29.084 | 29.084 | 29.084 | 29.084 | 29.084 | 29.084 | 29.084 | 29.084 | 29.084 | 29.084 | 29.084 | 29.084 | 29.084 | 29.084 | 29.084 | 29.084 | 29.084 | 29.084 | 29.084 | 29.084 | 29.084 | 29.084 | 29.084 | 29.084 | 29.084 | 29.084 | 29.084 | 29.0607 | 29.0373 | 29.014 | 28.9907 | 28.9673 | 28.944 | 28.9207 | 28.8973 | 28.874 | 28.8507 | 28.8273 | 28.804 | 28.7807 | 28.7573 | 28.734 | 28.7107 | 28.6873 | 28.664 | 28.6407 | 28.6173 | 28.594 | 28.5707 | 28.5473 | 28.524 | 28.5007 | 28.4773 | 28.454 | 28.4307 | 28.4073 | 28.384
5.45 | 0 | 10.2833 | 16.4513 | 18.2683 | 21.776 | 25.1623 | 27.8227 | 29.2737 | 29.757 | 29.757 | 29.032 | 8.8818e-16 | 1.0283 | 2.0567 | 3.085 | 4.1133 | 5.1417 | 6.17 | 7.1983 | 8.2267 | 9.255 | 10.2833 | 11.5169 | 12.7505 | 13.9841 | 15.2177 | 16.4513 | 16.8147 | 17.1781 | 17.5415 | 17.9049 | 18.2683 | 18.6191 | 18.9699 | 19.3206 | 19.6714 | 20.0222 | 20.3729 | 20.7237 | 21.0745 | 21.4252 | 21.776 | 22.0018 | 22.2275 | 22.4533 | 22.679 | 22.9048 | 23.1305 | 23.3563 | 23.582 | 23.8078 | 24.0336 | 24.2593 | 24.4851 | 24.7108 | 24.9366 | 25.1623 | 25.3397 | 25.517 | 25.6944 | 25.8718 | 26.0491 | 26.2265 | 26.4038 | 26.5812 | 26.7585 | 26.9359 | 27.1132 | 27.2906 | 27.468 | 27.6453 | 27.8227 | 27.871 | 27.9194 | 27.9678 | 28.0161 | 28.0645 | 28.1129 | 28.1612 | 28.2096 | 28.258 | 28.3063 | 28.3547 | 28.4031 | 28.4514 | 28.4998 | 28.5482 | 28.5965 | 28.6449 | 28.6933 | 28.7416 | 28.79 | 28.8384 | 28.8867 | 28.9351 | 28.9835 | 29.0318 | 29.0802 | 29.1286 | 29.1769 | 29.2253 | 29.2737 | 29.2898 | 29.3059 | 29.322 | 29.3381 | 29.3542 | 29.3703 | 29.3864 | 29.4026 | 29.4187 | 29.4348 | 29.4509 | 29.467 | 29.4831 | 29.4992 | 29.5153 | 29.5314 | 29.5476 | 29.5637 | 29.5798 | 29.5959 | 29.612 | 29.6281 | 29.6442 | 29.6603 | 29.6764 | 29.6926 | 29.7087 | 29.7248 | 29.7409 | 29.757 | 29.757 | 29.757 | 29.757 | 29.757 | 29.757 | 29.757 | 29.757 | 29.757 | 29.757 | 29.757 | 29.757 | 29.757 | 29.757 | 29.757 | 29.757 | 29.757 | 29.757 | 29.757 | 29.757 | 29.757 | 29.757 | 29.757 | 29.757 | 29.757 | 29.757 | 29.757 | 29.757 | 29.757 | 29.757 | 29.757 | 29.7328 | 29.7087 | 29.6845 | 29.6603 | 29.6362 | 29.612 | 29.5878 | 29.5637 | 29.5395 | 29.5153 | 29.4912 | 29.467 | 29.4428 | 29.4187 | 29.3945 | 29.3703 | 29.3462 | 29.322 | 29.2978 | 29.2737 | 29.2495 | 29.2253 | 29.2012 | 29.177 | 29.1528 | 29.1287 | 29.1045 | 29.0803 | 29.0562 | 29.032
5.5 | 0 | 10.5 | 16.82 | 18.65 | 22.24 | 25.71 | 28.44 | 29.93 | 30.43 | 30.43 | 29.68 | 0 | 1.05 | 2.1 | 3.15 | 4.2 | 5.25 | 6.3 | 7.35 | 8.4 | 9.45 | 10.5 | 11.764 | 13.028 | 14.292 | 15.556 | 16.82 | 17.186 | 17.552 | 17.918 | 18.284 | 18.65 | 19.009 | 19.368 | 19.727 | 20.086 | 20.445 | 20.804 | 21.163 | 21.522 | 21.881 | 22.24 | 22.4713 | 22.7027 | 22.934 | 23.1653 | 23.3967 | 23.628 | 23.8593 | 24.0907 | 24.322 | 24.5533 | 24.7847 | 25.016 | 25.2473 | 25.4787 | 25.71 | 25.892 | 26.074 | 26.256 | 26.438 | 26.62 | 26.802 | 26.984 | 27.166 | 27.348 | 27.53 | 27.712 | 27.894 | 28.076 | 28.258 | 28.44 | 28.4897 | 28.5393 | 28.589 | 28.6387 | 28.6883 | 28.738 | 28.7877 | 28.8373 | 28.887 | 28.9367 | 28.9863 | 29.036 | 29.0857 | 29.1353 | 29.185 | 29.2347 | 29.2843 | 29.334 | 29.3837 | 29.4333 | 29.483 | 29.5327 | 29.5823 | 29.632 | 29.6817 | 29.7313 | 29.781 | 29.8307 | 29.8803 | 29.93 | 29.9467 | 29.9633 | 29.98 | 29.9967 | 30.0133 | 30.03 | 30.0467 | 30.0633 | 30.08 | 30.0967 | 30.1133 | 30.13 | 30.1467 | 30.1633 | 30.18 | 30.1967 | 30.2133 | 30.23 | 30.2467 | 30.2633 | 30.28 | 30.2967 | 30.3133 | 30.33 | 30.3467 | 30.3633 | 30.38 | 30.3967 | 30.4133 | 30.43 | 30.43 | 30.43 | 30.43 | 30.43 | 30.43 | 30.43 | 30.43 | 30.43 | 30.43 | 30.43 | 30.43 | 30.43 | 30.43 | 30.43 | 30.43 | 30.43 | 30.43 | 30.43 | 30.43 | 30.43 | 30.43 | 30.43 | 30.43 | 30.43 | 30.43 | 30.43 | 30.43 | 30.43 | 30.43 | 30.43 | 30.405 | 30.38 | 30.355 | 30.33 | 30.305 | 30.28 | 30.255 | 30.23 | 30.205 | 30.18 | 30.155 | 30.13 | 30.105 | 30.08 | 30.055 | 30.03 | 30.005 | 29.98 | 29.955 | 29.93 | 29.905 | 29.88 | 29.855 | 29.83 | 29.805 | 29.78 | 29.755 | 29.73 | 29.705 | 29.68
5.55 | 0 | 10.7167 | 17.1887 | 19.0317 | 22.704 | 26.2577 | 29.0573 | 30.5863 | 31.103 | 31.103 | 30.328 | 0 | 1.0717 | 2.1433 | 3.215 | 4.2867 | 5.3583 | 6.43 | 7.5017 | 8.5733 | 9.645 | 10.7167 | 12.0111 | 13.3055 | 14.5999 | 15.8943 | 17.1887 | 17.5573 | 17.9259 | 18.2945 | 18.6631 | 19.0317 | 19.3989 | 19.7661 | 20.1334 | 20.5006 | 20.8678 | 21.2351 | 21.6023 | 21.9695 | 22.3368 | 22.704 | 22.9409 | 23.1778 | 23.4147 | 23.6516 | 23.8886 | 24.1255 | 24.3624 | 24.5993 | 24.8362 | 25.0731 | 25.31 | 25.5469 | 25.7838 | 26.0208 | 26.2577 | 26.4443 | 26.631 | 26.8176 | 27.0042 | 27.1909 | 27.3775 | 27.5642 | 27.7508 | 27.9375 | 28.1241 | 28.3108 | 28.4974 | 28.684 | 28.8707 | 29.0573 | 29.1083 | 29.1593 | 29.2102 | 29.2612 | 29.3122 | 29.3631 | 29.4141 | 29.4651 | 29.516 | 29.567 | 29.618 | 29.6689 | 29.7199 | 29.7709 | 29.8218 | 29.8728 | 29.9238 | 29.9747 | 30.0257 | 30.0767 | 30.1276 | 30.1786 | 30.2296 | 30.2805 | 30.3315 | 30.3825 | 30.4334 | 30.4844 | 30.5354 | 30.5863 | 30.6036 | 30.6208 | 30.638 | 30.6552 | 30.6724 | 30.6897 | 30.7069 | 30.7241 | 30.7413 | 30.7586 | 30.7758 | 30.793 | 30.8102 | 30.8274 | 30.8447 | 30.8619 | 30.8791 | 30.8963 | 30.9136 | 30.9308 | 30.948 | 30.9652 | 30.9824 | 30.9997 | 31.0169 | 31.0341 | 31.0513 | 31.0686 | 31.0858 | 31.103 | 31.103 | 31.103 | 31.103 | 31.103 | 31.103 | 31.103 | 31.103 | 31.103 | 31.103 | 31.103 | 31.103 | 31.103 | 31.103 | 31.103 | 31.103 | 31.103 | 31.103 | 31.103 | 31.103 | 31.103 | 31.103 | 31.103 | 31.103 | 31.103 | 31.103 | 31.103 | 31.103 | 31.103 | 31.103 | 31.103 | 31.0772 | 31.0513 | 31.0255 | 30.9997 | 30.9738 | 30.948 | 30.9222 | 30.8963 | 30.8705 | 30.8447 | 30.8188 | 30.793 | 30.7672 | 30.7413 | 30.7155 | 30.6897 | 30.6638 | 30.638 | 30.6122 | 30.5863 | 30.5605 | 30.5347 | 30.5088 | 30.483 | 30.4572 | 30.4313 | 30.4055 | 30.3797 | 30.3538 | 30.328
5.6 | 0 | 10.9333 | 17.5573 | 19.4133 | 23.168 | 26.8053 | 29.6747 | 31.2427 | 31.776 | 31.776 | 30.976 | 0 | 1.0933 | 2.1867 | 3.28 | 4.3733 | 5.4667 | 6.56 | 7.6533 | 8.7467 | 9.84 | 10.9333 | 12.2581 | 13.5829 | 14.9077 | 16.2325 | 17.5573 | 17.9285 | 18.2997 | 18.6709 | 19.0421 | 19.4133 | 19.7888 | 20.1643 | 20.5397 | 20.9152 | 21.2907 | 21.6661 | 22.0416 | 22.4171 | 22.7925 | 23.168 | 23.4105 | 23.653 | 23.8955 | 24.138 | 24.3804 | 24.6229 | 24.8654 | 25.1079 | 25.3504 | 25.5929 | 25.8354 | 26.0779 | 26.3204 | 26.5628 | 26.8053 | 26.9966 | 27.1879 | 27.3792 | 27.5705 | 27.7618 | 27.9531 | 28.1444 | 28.3356 | 28.5269 | 28.7182 | 28.9095 | 29.1008 | 29.2921 | 29.4834 | 29.6747 | 29.7269 | 29.7792 | 29.8315 | 29.8837 | 29.936 | 29.9883 | 30.0405 | 30.0928 | 30.1451 | 30.1973 | 30.2496 | 30.3019 | 30.3541 | 30.4064 | 30.4587 | 30.5109 | 30.5632 | 30.6155 | 30.6677 | 30.72 | 30.7723 | 30.8245 | 30.8768 | 30.9291 | 30.9813 | 31.0336 | 31.0859 | 31.1381 | 31.1904 | 31.2427 | 31.2604 | 31.2782 | 31.296 | 31.3138 | 31.3316 | 31.3493 | 31.3671 | 31.3849 | 31.4027 | 31.4204 | 31.4382 | 31.456 | 31.4738 | 31.4916 | 31.5093 | 31.5271 | 31.5449 | 31.5627 | 31.5804 | 31.5982 | 31.616 | 31.6338 | 31.6516 | 31.6693 | 31.6871 | 31.7049 | 31.7227 | 31.7404 | 31.7582 | 31.776 | 31.776 | 31.776 | 31.776 | 31.776 | 31.776 | 31.776 | 31.776 | 31.776 | 31.776 | 31.776 | 31.776 | 31.776 | 31.776 | 31.776 | 31.776 | 31.776 | 31.776 | 31.776 | 31.776 | 31.776 | 31.776 | 31.776 | 31.776 | 31.776 | 31.776 | 31.776 | 31.776 | 31.776 | 31.776 | 31.776 | 31.7493 | 31.7227 | 31.696 | 31.6693 | 31.6427 | 31.616 | 31.5893 | 31.5627 | 31.536 | 31.5093 | 31.4827 | 31.456 | 31.4293 | 31.4027 | 31.376 | 31.3493 | 31.3227 | 31.296 | 31.2693 | 31.2427 | 31.216 | 31.1893 | 31.1627 | 31.136 | 31.1093 | 31.0827 | 31.056 | 31.0293 | 31.0027 | 30.976
5.65 | 0 | 11.15 | 17.926 | 19.795 | 23.632 | 27.353 | 30.292 | 31.899 | 32.449 | 32.449 | 31.624 | 0 | 1.115 | 2.23 | 3.345 | 4.46 | 5.575 | 6.69 | 7.805 | 8.92 | 10.035 | 11.15 | 12.5052 | 13.8604 | 15.2156 | 16.5708 | 17.926 | 18.2998 | 18.6736 | 19.0474 | 19.4212 | 19.795 | 20.1787 | 20.5624 | 20.9461 | 21.3298 | 21.7135 | 22.0972 | 22.4809 | 22.8646 | 23.2483 | 23.632 | 23.8801 | 24.1281 | 24.3762 | 24.6243 | 24.8723 | 25.1204 | 25.3685 | 25.6165 | 25.8646 | 26.1127 | 26.3607 | 26.6088 | 26.8569 | 27.1049 | 27.353 | 27.5489 | 27.7449 | 27.9408 | 28.1367 | 28.3327 | 28.5286 | 28.7245 | 28.9205 | 29.1164 | 29.3123 | 29.5083 | 29.7042 | 29.9001 | 30.0961 | 30.292 | 30.3456 | 30.3991 | 30.4527 | 30.5063 | 30.5598 | 30.6134 | 30.667 | 30.7205 | 30.7741 | 30.8277 | 30.8812 | 30.9348 | 30.9884 | 31.0419 | 31.0955 | 31.1491 | 31.2026 | 31.2562 | 31.3098 | 31.3633 | 31.4169 | 31.4705 | 31.524 | 31.5776 | 31.6312 | 31.6847 | 31.7383 | 31.7919 | 31.8454 | 31.899 | 31.9173 | 31.9357 | 31.954 | 31.9723 | 31.9907 | 32.009 | 32.0273 | 32.0457 | 32.064 | 32.0823 | 32.1007 | 32.119 | 32.1373 | 32.1557 | 32.174 | 32.1923 | 32.2107 | 32.229 | 32.2473 | 32.2657 | 32.284 | 32.3023 | 32.3207 | 32.339 | 32.3573 | 32.3757 | 32.394 | 32.4123 | 32.4307 | 32.449 | 32.449 | 32.449 | 32.449 | 32.449 | 32.449 | 32.449 | 32.449 | 32.449 | 32.449 | 32.449 | 32.449 | 32.449 | 32.449 | 32.449 | 32.449 | 32.449 | 32.449 | 32.449 | 32.449 | 32.449 | 32.449 | 32.449 | 32.449 | 32.449 | 32.449 | 32.449 | 32.449 | 32.449 | 32.449 | 32.449 | 32.4215 | 32.394 | 32.3665 | 32.339 | 32.3115 | 32.284 | 32.2565 | 32.229 | 32.2015 | 32.174 | 32.1465 | 32.119 | 32.0915 | 32.064 | 32.0365 | 32.009 | 31.9815 | 31.954 | 31.9265 | 31.899 | 31.8715 | 31.844 | 31.8165 | 31.789 | 31.7615 | 31.734 | 31.7065 | 31.679 | 31.6515 | 31.624
5.7 | 0 | 11.3667 | 18.2947 | 20.1767 | 24.096 | 27.9007 | 30.9093 | 32.5553 | 33.122 | 33.122 | 32.272 | 0 | 1.1367 | 2.2733 | 3.41 | 4.5467 | 5.6833 | 6.82 | 7.9567 | 9.0933 | 10.23 | 11.3667 | 12.7523 | 14.1379 | 15.5235 | 16.9091 | 18.2947 | 18.6711 | 19.0475 | 19.4239 | 19.8003 | 20.1767 | 20.5686 | 20.9605 | 21.3525 | 21.7444 | 22.1363 | 22.5283 | 22.9202 | 23.3121 | 23.7041 | 24.096 | 24.3496 | 24.6033 | 24.8569 | 25.1106 | 25.3642 | 25.6179 | 25.8715 | 26.1252 | 26.3788 | 26.6324 | 26.8861 | 27.1397 | 27.3934 | 27.647 | 27.9007 | 28.1012 | 28.3018 | 28.5024 | 28.703 | 28.9036 | 29.1041 | 29.3047 | 29.5053 | 29.7059 | 29.9064 | 30.107 | 30.3076 | 30.5082 | 30.7088 | 30.9093 | 30.9642 | 31.0191 | 31.0739 | 31.1288 | 31.1837 | 31.2385 | 31.2934 | 31.3483 | 31.4031 | 31.458 | 31.5129 | 31.5677 | 31.6226 | 31.6775 | 31.7323 | 31.7872 | 31.8421 | 31.8969 | 31.9518 | 32.0067 | 32.0615 | 32.1164 | 32.1713 | 32.2261 | 32.281 | 32.3359 | 32.3907 | 32.4456 | 32.5005 | 32.5553 | 32.5742 | 32.5931 | 32.612 | 32.6309 | 32.6498 | 32.6687 | 32.6876 | 32.7064 | 32.7253 | 32.7442 | 32.7631 | 32.782 | 32.8009 | 32.8198 | 32.8387 | 32.8576 | 32.8764 | 32.8953 | 32.9142 | 32.9331 | 32.952 | 32.9709 | 32.9898 | 33.0087 | 33.0276 | 33.0464 | 33.0653 | 33.0842 | 33.1031 | 33.122 | 33.122 | 33.122 | 33.122 | 33.122 | 33.122 | 33.122 | 33.122 | 33.122 | 33.122 | 33.122 | 33.122 | 33.122 | 33.122 | 33.122 | 33.122 | 33.122 | 33.122 | 33.122 | 33.122 | 33.122 | 33.122 | 33.122 | 33.122 | 33.122 | 33.122 | 33.122 | 33.122 | 33.122 | 33.122 | 33.122 | 33.0937 | 33.0653 | 33.037 | 33.0087 | 32.9803 | 32.952 | 32.9237 | 32.8953 | 32.867 | 32.8387 | 32.8103 | 32.782 | 32.7537 | 32.7253 | 32.697 | 32.6687 | 32.6403 | 32.612 | 32.5837 | 32.5553 | 32.527 | 32.4987 | 32.4703 | 32.442 | 32.4137 | 32.3853 | 32.357 | 32.3287 | 32.3003 | 32.272
5.75 | 0 | 11.5833 | 18.6633 | 20.5583 | 24.56 | 28.4483 | 31.5267 | 33.2117 | 33.795 | 33.795 | 32.92 | 0 | 1.1583 | 2.3167 | 3.475 | 4.6333 | 5.7917 | 6.95 | 8.1083 | 9.2667 | 10.425 | 11.5833 | 12.9993 | 14.4153 | 15.8313 | 17.2473 | 18.6633 | 19.0423 | 19.4213 | 19.8003 | 20.1793 | 20.5583 | 20.9585 | 21.3587 | 21.7588 | 22.159 | 22.5592 | 22.9593 | 23.3595 | 23.7597 | 24.1598 | 24.56 | 24.8192 | 25.0784 | 25.3377 | 25.5969 | 25.8561 | 26.1153 | 26.3746 | 26.6338 | 26.893 | 27.1522 | 27.4114 | 27.6707 | 27.9299 | 28.1891 | 28.4483 | 28.6536 | 28.8588 | 29.064 | 29.2692 | 29.4744 | 29.6797 | 29.8849 | 30.0901 | 30.2953 | 30.5006 | 30.7058 | 30.911 | 31.1162 | 31.3214 | 31.5267 | 31.5828 | 31.639 | 31.6952 | 31.7513 | 31.8075 | 31.8637 | 31.9198 | 31.976 | 32.0322 | 32.0883 | 32.1445 | 32.2007 | 32.2568 | 32.313 | 32.3692 | 32.4253 | 32.4815 | 32.5377 | 32.5938 | 32.65 | 32.7062 | 32.7623 | 32.8185 | 32.8747 | 32.9308 | 32.987 | 33.0432 | 33.0993 | 33.1555 | 33.2117 | 33.2311 | 33.2506 | 33.27 | 33.2894 | 33.3089 | 33.3283 | 33.3478 | 33.3672 | 33.3867 | 33.4061 | 33.4256 | 33.445 | 33.4644 | 33.4839 | 33.5033 | 33.5228 | 33.5422 | 33.5617 | 33.5811 | 33.6006 | 33.62 | 33.6394 | 33.6589 | 33.6783 | 33.6978 | 33.7172 | 33.7367 | 33.7561 | 33.7756 | 33.795 | 33.795 | 33.795 | 33.795 | 33.795 | 33.795 | 33.795 | 33.795 | 33.795 | 33.795 | 33.795 | 33.795 | 33.795 | 33.795 | 33.795 | 33.795 | 33.795 | 33.795 | 33.795 | 33.795 | 33.795 | 33.795 | 33.795 | 33.795 | 33.795 | 33.795 | 33.795 | 33.795 | 33.795 | 33.795 | 33.795 | 33.7658 | 33.7367 | 33.7075 | 33.6783 | 33.6492 | 33.62 | 33.5908 | 33.5617 | 33.5325 | 33.5033 | 33.4742 | 33.445 | 33.4158 | 33.3867 | 33.3575 | 33.3283 | 33.2992 | 33.27 | 33.2408 | 33.2117 | 33.1825 | 33.1533 | 33.1242 | 33.095 | 33.0658 | 33.0367 | 33.0075 | 32.9783 | 32.9492 | 32.92
5.8 | 0 | 11.8 | 19.032 | 20.94 | 25.024 | 28.996 | 32.144 | 33.868 | 34.468 | 34.468 | 33.568 | 0 | 1.18 | 2.36 | 3.54 | 4.72 | 5.9 | 7.08 | 8.26 | 9.44 | 10.62 | 11.8 | 13.2464 | 14.6928 | 16.1392 | 17.5856 | 19.032 | 19.4136 | 19.7952 | 20.1768 | 20.5584 | 20.94 | 21.3484 | 21.7568 | 22.1652 | 22.5736 | 22.982 | 23.3904 | 23.7988 | 24.2072 | 24.6156 | 25.024 | 25.2888 | 25.5536 | 25.8184 | 26.0832 | 26.348 | 26.6128 | 26.8776 | 27.1424 | 27.4072 | 27.672 | 27.9368 | 28.2016 | 28.4664 | 28.7312 | 28.996 | 29.2059 | 29.4157 | 29.6256 | 29.8355 | 30.0453 | 30.2552 | 30.4651 | 30.6749 | 30.8848 | 31.0947 | 31.3045 | 31.5144 | 31.7243 | 31.9341 | 32.144 | 32.2015 | 32.2589 | 32.3164 | 32.3739 | 32.4313 | 32.4888 | 32.5463 | 32.6037 | 32.6612 | 32.7187 | 32.7761 | 32.8336 | 32.8911 | 32.9485 | 33.006 | 33.0635 | 33.1209 | 33.1784 | 33.2359 | 33.2933 | 33.3508 | 33.4083 | 33.4657 | 33.5232 | 33.5807 | 33.6381 | 33.6956 | 33.7531 | 33.8105 | 33.868 | 33.888 | 33.908 | 33.928 | 33.948 | 33.968 | 33.988 | 34.008 | 34.028 | 34.048 | 34.068 | 34.088 | 34.108 | 34.128 | 34.148 | 34.168 | 34.188 | 34.208 | 34.228 | 34.248 | 34.268 | 34.288 | 34.308 | 34.328 | 34.348 | 34.368 | 34.388 | 34.408 | 34.428 | 34.448 | 34.468 | 34.468 | 34.468 | 34.468 | 34.468 | 34.468 | 34.468 | 34.468 | 34.468 | 34.468 | 34.468 | 34.468 | 34.468 | 34.468 | 34.468 | 34.468 | 34.468 | 34.468 | 34.468 | 34.468 | 34.468 | 34.468 | 34.468 | 34.468 | 34.468 | 34.468 | 34.468 | 34.468 | 34.468 | 34.468 | 34.468 | 34.438 | 34.408 | 34.378 | 34.348 | 34.318 | 34.288 | 34.258 | 34.228 | 34.198 | 34.168 | 34.138 | 34.108 | 34.078 | 34.048 | 34.018 | 33.988 | 33.958 | 33.928 | 33.898 | 33.868 | 33.838 | 33.808 | 33.778 | 33.748 | 33.718 | 33.688 | 33.658 | 33.628 | 33.598 | 33.568
5.85 | 0 | 12.0167 | 19.4007 | 21.3217 | 25.488 | 29.5437 | 32.7613 | 34.5243 | 35.141 | 35.141 | 34.216 | 0 | 1.2017 | 2.4033 | 3.605 | 4.8067 | 6.0083 | 7.21 | 8.4117 | 9.6133 | 10.815 | 12.0167 | 13.4935 | 14.9703 | 16.4471 | 17.9239 | 19.4007 | 19.7849 | 20.1691 | 20.5533 | 20.9375 | 21.3217 | 21.7383 | 22.1549 | 22.5716 | 22.9882 | 23.4048 | 23.8215 | 24.2381 | 24.6547 | 25.0714 | 25.488 | 25.7584 | 26.0288 | 26.2991 | 26.5695 | 26.8399 | 27.1103 | 27.3806 | 27.651 | 27.9214 | 28.1918 | 28.4622 | 28.7325 | 29.0029 | 29.2733 | 29.5437 | 29.7582 | 29.9727 | 30.1872 | 30.4017 | 30.6162 | 30.8307 | 31.0452 | 31.2598 | 31.4743 | 31.6888 | 31.9033 | 32.1178 | 32.3323 | 32.5468 | 32.7613 | 32.8201 | 32.8789 | 32.9376 | 32.9964 | 33.0552 | 33.1139 | 33.1727 | 33.2315 | 33.2902 | 33.349 | 33.4078 | 33.4665 | 33.5253 | 33.5841 | 33.6428 | 33.7016 | 33.7604 | 33.8191 | 33.8779 | 33.9367 | 33.9954 | 34.0542 | 34.113 | 34.1717 | 34.2305 | 34.2893 | 34.348 | 34.4068 | 34.4656 | 34.5243 | 34.5449 | 34.5654 | 34.586 | 34.6066 | 34.6271 | 34.6477 | 34.6682 | 34.6888 | 34.7093 | 34.7299 | 34.7504 | 34.771 | 34.7916 | 34.8121 | 34.8327 | 34.8532 | 34.8738 | 34.8943 | 34.9149 | 34.9354 | 34.956 | 34.9766 | 34.9971 | 35.0177 | 35.0382 | 35.0588 | 35.0793 | 35.0999 | 35.1204 | 35.141 | 35.141 | 35.141 | 35.141 | 35.141 | 35.141 | 35.141 | 35.141 | 35.141 | 35.141 | 35.141 | 35.141 | 35.141 | 35.141 | 35.141 | 35.141 | 35.141 | 35.141 | 35.141 | 35.141 | 35.141 | 35.141 | 35.141 | 35.141 | 35.141 | 35.141 | 35.141 | 35.141 | 35.141 | 35.141 | 35.141 | 35.1102 | 35.0793 | 35.0485 | 35.0177 | 34.9868 | 34.956 | 34.9252 | 34.8943 | 34.8635 | 34.8327 | 34.8018 | 34.771 | 34.7402 | 34.7093 | 34.6785 | 34.6477 | 34.6168 | 34.586 | 34.5552 | 34.5243 | 34.4935 | 34.4627 | 34.4318 | 34.401 | 34.3702 | 34.3393 | 34.3085 | 34.2777 | 34.2468 | 34.216
5.9 | 0 | 12.2333 | 19.7693 | 21.7033 | 25.952 | 30.0913 | 33.3787 | 35.1807 | 35.814 | 35.814 | 34.864 | 0 | 1.2233 | 2.4467 | 3.67 | 4.8933 | 6.1167 | 7.34 | 8.5633 | 9.7867 | 11.01 | 12.2333 | 13.7405 | 15.2477 | 16.7549 | 18.2621 | 19.7693 | 20.1561 | 20.5429 | 20.9297 | 21.3165 | 21.7033 | 22.1282 | 22.5531 | 22.9779 | 23.4028 | 23.8277 | 24.2525 | 24.6774 | 25.1023 | 25.5271 | 25.952 | 26.228 | 26.5039 | 26.7799 | 27.0558 | 27.3318 | 27.6077 | 27.8837 | 28.1596 | 28.4356 | 28.7116 | 28.9875 | 29.2635 | 29.5394 | 29.8154 | 30.0913 | 30.3105 | 30.5296 | 30.7488 | 30.968 | 31.1871 | 31.4063 | 31.6254 | 31.8446 | 32.0637 | 32.2829 | 32.502 | 32.7212 | 32.9404 | 33.1595 | 33.3787 | 33.4387 | 33.4988 | 33.5589 | 33.6189 | 33.679 | 33.7391 | 33.7991 | 33.8592 | 33.9193 | 33.9793 | 34.0394 | 34.0995 | 34.1595 | 34.2196 | 34.2797 | 34.3397 | 34.3998 | 34.4599 | 34.5199 | 34.58 | 34.6401 | 34.7001 | 34.7602 | 34.8203 | 34.8803 | 34.9404 | 35.0005 | 35.0605 | 35.1206 | 35.1807 | 35.2018 | 35.2229 | 35.244 | 35.2651 | 35.2862 | 35.3073 | 35.3284 | 35.3496 | 35.3707 | 35.3918 | 35.4129 | 35.434 | 35.4551 | 35.4762 | 35.4973 | 35.5184 | 35.5396 | 35.5607 | 35.5818 | 35.6029 | 35.624 | 35.6451 | 35.6662 | 35.6873 | 35.7084 | 35.7296 | 35.7507 | 35.7718 | 35.7929 | 35.814 | 35.814 | 35.814 | 35.814 | 35.814 | 35.814 | 35.814 | 35.814 | 35.814 | 35.814 | 35.814 | 35.814 | 35.814 | 35.814 | 35.814 | 35.814 | 35.814 | 35.814 | 35.814 | 35.814 | 35.814 | 35.814 | 35.814 | 35.814 | 35.814 | 35.814 | 35.814 | 35.814 | 35.814 | 35.814 | 35.814 | 35.7823 | 35.7507 | 35.719 | 35.6873 | 35.6557 | 35.624 | 35.5923 | 35.5607 | 35.529 | 35.4973 | 35.4657 | 35.434 | 35.4023 | 35.3707 | 35.339 | 35.3073 | 35.2757 | 35.244 | 35.2123 | 35.1807 | 35.149 | 35.1173 | 35.0857 | 35.054 | 35.0223 | 34.9907 | 34.959 | 34.9273 | 34.8957 | 34.864
5.95 | 0 | 12.45 | 20.138 | 22.085 | 26.416 | 30.639 | 33.996 | 35.837 | 36.487 | 36.487 | 35.512 | -8.8818e-16 | 1.245 | 2.49 | 3.735 | 4.98 | 6.225 | 7.47 | 8.715 | 9.96 | 11.205 | 12.45 | 13.9876 | 15.5252 | 17.0628 | 18.6004 | 20.138 | 20.5274 | 20.9168 | 21.3062 | 21.6956 | 22.085 | 22.5181 | 22.9512 | 23.3843 | 23.8174 | 24.2505 | 24.6836 | 25.1167 | 25.5498 | 25.9829 | 26.416 | 26.6975 | 26.9791 | 27.2606 | 27.5421 | 27.8237 | 28.1052 | 28.3867 | 28.6683 | 28.9498 | 29.2313 | 29.5129 | 29.7944 | 30.0759 | 30.3575 | 30.639 | 30.8628 | 31.0866 | 31.3104 | 31.5342 | 31.758 | 31.9818 | 32.2056 | 32.4294 | 32.6532 | 32.877 | 33.1008 | 33.3246 | 33.5484 | 33.7722 | 33.996 | 34.0574 | 34.1187 | 34.1801 | 34.2415 | 34.3028 | 34.3642 | 34.4256 | 34.4869 | 34.5483 | 34.6097 | 34.671 | 34.7324 | 34.7938 | 34.8551 | 34.9165 | 34.9779 | 35.0392 | 35.1006 | 35.162 | 35.2233 | 35.2847 | 35.3461 | 35.4074 | 35.4688 | 35.5302 | 35.5915 | 35.6529 | 35.7143 | 35.7756 | 35.837 | 35.8587 | 35.8803 | 35.902 | 35.9237 | 35.9453 | 35.967 | 35.9887 | 36.0103 | 36.032 | 36.0537 | 36.0753 | 36.097 | 36.1187 | 36.1403 | 36.162 | 36.1837 | 36.2053 | 36.227 | 36.2487 | 36.2703 | 36.292 | 36.3137 | 36.3353 | 36.357 | 36.3787 | 36.4003 | 36.422 | 36.4437 | 36.4653 | 36.487 | 36.487 | 36.487 | 36.487 | 36.487 | 36.487 | 36.487 | 36.487 | 36.487 | 36.487 | 36.487 | 36.487 | 36.487 | 36.487 | 36.487 | 36.487 | 36.487 | 36.487 | 36.487 | 36.487 | 36.487 | 36.487 | 36.487 | 36.487 | 36.487 | 36.487 | 36.487 | 36.487 | 36.487 | 36.487 | 36.487 | 36.4545 | 36.422 | 36.3895 | 36.357 | 36.3245 | 36.292 | 36.2595 | 36.227 | 36.1945 | 36.162 | 36.1295 | 36.097 | 36.0645 | 36.032 | 35.9995 | 35.967 | 35.9345 | 35.902 | 35.8695 | 35.837 | 35.8045 | 35.772 | 35.7395 | 35.707 | 35.6745 | 35.642 | 35.6095 | 35.577 | 35.5445 | 35.512
6 | 0 | 12.6667 | 20.5067 | 22.4667 | 26.88 | 31.1867 | 34.6133 | 36.4933 | 37.16 | 37.16 | 36.16 | 0 | 1.2667 | 2.5333 | 3.8 | 5.0667 | 6.3333 | 7.6 | 8.8667 | 10.1333 | 11.4 | 12.6667 | 14.2347 | 15.8027 | 17.3707 | 18.9387 | 20.5067 | 20.8987 | 21.2907 | 21.6827 | 22.0747 | 22.4667 | 22.908 | 23.3493 | 23.7907 | 24.232 | 24.6733 | 25.1147 | 25.556 | 25.9973 | 26.4387 | 26.88 | 27.1671 | 27.4542 | 27.7413 | 28.0284 | 28.3156 | 28.6027 | 28.8898 | 29.1769 | 29.464 | 29.7511 | 30.0382 | 30.3253 | 30.6124 | 30.8996 | 31.1867 | 31.4151 | 31.6436 | 31.872 | 32.1004 | 32.3289 | 32.5573 | 32.7858 | 33.0142 | 33.2427 | 33.4711 | 33.6996 | 33.928 | 34.1564 | 34.3849 | 34.6133 | 34.676 | 34.7387 | 34.8013 | 34.864 | 34.9267 | 34.9893 | 35.052 | 35.1147 | 35.1773 | 35.24 | 35.3027 | 35.3653 | 35.428 | 35.4907 | 35.5533 | 35.616 | 35.6787 | 35.7413 | 35.804 | 35.8667 | 35.9293 | 35.992 | 36.0547 | 36.1173 | 36.18 | 36.2427 | 36.3053 | 36.368 | 36.4307 | 36.4933 | 36.5156 | 36.5378 | 36.56 | 36.5822 | 36.6044 | 36.6267 | 36.6489 | 36.6711 | 36.6933 | 36.7156 | 36.7378 | 36.76 | 36.7822 | 36.8044 | 36.8267 | 36.8489 | 36.8711 | 36.8933 | 36.9156 | 36.9378 | 36.96 | 36.9822 | 37.0044 | 37.0267 | 37.0489 | 37.0711 | 37.0933 | 37.1156 | 37.1378 | 37.16 | 37.16 | 37.16 | 37.16 | 37.16 | 37.16 | 37.16 | 37.16 | 37.16 | 37.16 | 37.16 | 37.16 | 37.16 | 37.16 | 37.16 | 37.16 | 37.16 | 37.16 | 37.16 | 37.16 | 37.16 | 37.16 | 37.16 | 37.16 | 37.16 | 37.16 | 37.16 | 37.16 | 37.16 | 37.16 | 37.16 | 37.1267 | 37.0933 | 37.06 | 37.0267 | 36.9933 | 36.96 | 36.9267 | 36.8933 | 36.86 | 36.8267 | 36.7933 | 36.76 | 36.7267 | 36.6933 | 36.66 | 36.6267 | 36.5933 | 36.56 | 36.5267 | 36.4933 | 36.46 | 36.4267 | 36.3933 | 36.36 | 36.3267 | 36.2933 | 36.26 | 36.2267 | 36.1933 | 36.16
6.05 | 0 | 12.8833 | 20.8753 | 22.8483 | 27.344 | 31.7343 | 35.2307 | 37.1497 | 37.833 | 37.833 | 36.808 | 8.8818e-16 | 1.2883 | 2.5767 | 3.865 | 5.1533 | 6.4417 | 7.73 | 9.0183 | 10.3067 | 11.595 | 12.8833 | 14.4817 | 16.0801 | 17.6785 | 19.2769 | 20.8753 | 21.2699 | 21.6645 | 22.0591 | 22.4537 | 22.8483 | 23.2979 | 23.7475 | 24.197 | 24.6466 | 25.0962 | 25.5457 | 25.9953 | 26.4449 | 26.8944 | 27.344 | 27.6367 | 27.9294 | 28.2221 | 28.5148 | 28.8074 | 29.1001 | 29.3928 | 29.6855 | 29.9782 | 30.2709 | 30.5636 | 30.8563 | 31.149 | 31.4416 | 31.7343 | 31.9674 | 32.2005 | 32.4336 | 32.6667 | 32.8998 | 33.1329 | 33.366 | 33.599 | 33.8321 | 34.0652 | 34.2983 | 34.5314 | 34.7645 | 34.9976 | 35.2307 | 35.2946 | 35.3586 | 35.4226 | 35.4865 | 35.5505 | 35.6145 | 35.6784 | 35.7424 | 35.8064 | 35.8703 | 35.9343 | 35.9983 | 36.0622 | 36.1262 | 36.1902 | 36.2541 | 36.3181 | 36.3821 | 36.446 | 36.51 | 36.574 | 36.6379 | 36.7019 | 36.7659 | 36.8298 | 36.8938 | 36.9578 | 37.0217 | 37.0857 | 37.1497 | 37.1724 | 37.1952 | 37.218 | 37.2408 | 37.2636 | 37.2863 | 37.3091 | 37.3319 | 37.3547 | 37.3774 | 37.4002 | 37.423 | 37.4458 | 37.4686 | 37.4913 | 37.5141 | 37.5369 | 37.5597 | 37.5824 | 37.6052 | 37.628 | 37.6508 | 37.6736 | 37.6963 | 37.7191 | 37.7419 | 37.7647 | 37.7874 | 37.8102 | 37.833 | 37.833 | 37.833 | 37.833 | 37.833 | 37.833 | 37.833 | 37.833 | 37.833 | 37.833 | 37.833 | 37.833 | 37.833 | 37.833 | 37.833 | 37.833 | 37.833 | 37.833 | 37.833 | 37.833 | 37.833 | 37.833 | 37.833 | 37.833 | 37.833 | 37.833 | 37.833 | 37.833 | 37.833 | 37.833 | 37.833 | 37.7988 | 37.7647 | 37.7305 | 37.6963 | 37.6622 | 37.628 | 37.5938 | 37.5597 | 37.5255 | 37.4913 | 37.4572 | 37.423 | 37.3888 | 37.3547 | 37.3205 | 37.2863 | 37.2522 | 37.218 | 37.1838 | 37.1497 | 37.1155 | 37.0813 | 37.0472 | 37.013 | 36.9788 | 36.9447 | 36.9105 | 36.8763 | 36.8422 | 36.808
6.1 | 0 | 13.1 | 21.244 | 23.23 | 27.808 | 32.282 | 35.848 | 37.806 | 38.506 | 38.506 | 37.456 | 8.8818e-16 | 1.31 | 2.62 | 3.93 | 5.24 | 6.55 | 7.86 | 9.17 | 10.48 | 11.79 | 13.1 | 14.7288 | 16.3576 | 17.9864 | 19.6152 | 21.244 | 21.6412 | 22.0384 | 22.4356 | 22.8328 | 23.23 | 23.6878 | 24.1456 | 24.6034 | 25.0612 | 25.519 | 25.9768 | 26.4346 | 26.8924 | 27.3502 | 27.808 | 28.1063 | 28.4045 | 28.7028 | 29.0011 | 29.2993 | 29.5976 | 29.8959 | 30.1941 | 30.4924 | 30.7907 | 31.0889 | 31.3872 | 31.6855 | 31.9837 | 32.282 | 32.5197 | 32.7575 | 32.9952 | 33.2329 | 33.4707 | 33.7084 | 33.9461 | 34.1839 | 34.4216 | 34.6593 | 34.8971 | 35.1348 | 35.3725 | 35.6103 | 35.848 | 35.9133 | 35.9785 | 36.0438 | 36.1091 | 36.1743 | 36.2396 | 36.3049 | 36.3701 | 36.4354 | 36.5007 | 36.5659 | 36.6312 | 36.6965 | 36.7617 | 36.827 | 36.8923 | 36.9575 | 37.0228 | 37.0881 | 37.1533 | 37.2186 | 37.2839 | 37.3491 | 37.4144 | 37.4797 | 37.5449 | 37.6102 | 37.6755 | 37.7407 | 37.806 | 37.8293 | 37.8527 | 37.876 | 37.8993 | 37.9227 | 37.946 | 37.9693 | 37.9927 | 38.016 | 38.0393 | 38.0627 | 38.086 | 38.1093 | 38.1327 | 38.156 | 38.1793 | 38.2027 | 38.226 | 38.2493 | 38.2727 | 38.296 | 38.3193 | 38.3427 | 38.366 | 38.3893 | 38.4127 | 38.436 | 38.4593 | 38.4827 | 38.506 | 38.506 | 38.506 | 38.506 | 38.506 | 38.506 | 38.506 | 38.506 | 38.506 | 38.506 | 38.506 | 38.506 | 38.506 | 38.506 | 38.506 | 38.506 | 38.506 | 38.506 | 38.506 | 38.506 | 38.506 | 38.506 | 38.506 | 38.506 | 38.506 | 38.506 | 38.506 | 38.506 | 38.506 | 38.506 | 38.506 | 38.471 | 38.436 | 38.401 | 38.366 | 38.331 | 38.296 | 38.261 | 38.226 | 38.191 | 38.156 | 38.121 | 38.086 | 38.051 | 38.016 | 37.981 | 37.946 | 37.911 | 37.876 | 37.841 | 37.806 | 37.771 | 37.736 | 37.701 | 37.666 | 37.631 | 37.596 | 37.561 | 37.526 | 37.491 | 37.456
6.15 | 0 | 13.3167 | 21.6127 | 23.6117 | 28.272 | 32.8297 | 36.4653 | 38.4623 | 39.179 | 39.179 | 38.104 | 0 | 1.3317 | 2.6633 | 3.995 | 5.3267 | 6.6583 | 7.99 | 9.3217 | 10.6533 | 11.985 | 13.3167 | 14.9759 | 16.6351 | 18.2943 | 19.9535 | 21.6127 | 22.0125 | 22.4123 | 22.8121 | 23.2119 | 23.6117 | 24.0777 | 24.5437 | 25.0098 | 25.4758 | 25.9418 | 26.4079 | 26.8739 | 27.3399 | 27.806 | 28.272 | 28.5758 | 28.8797 | 29.1835 | 29.4874 | 29.7912 | 30.0951 | 30.3989 | 30.7028 | 31.0066 | 31.3104 | 31.6143 | 31.9181 | 32.222 | 32.5258 | 32.8297 | 33.072 | 33.3144 | 33.5568 | 33.7992 | 34.0416 | 34.2839 | 34.5263 | 34.7687 | 35.0111 | 35.2534 | 35.4958 | 35.7382 | 35.9806 | 36.223 | 36.4653 | 36.5319 | 36.5985 | 36.665 | 36.7316 | 36.7982 | 36.8647 | 36.9313 | 36.9979 | 37.0644 | 37.131 | 37.1976 | 37.2641 | 37.3307 | 37.3973 | 37.4638 | 37.5304 | 37.597 | 37.6635 | 37.7301 | 37.7967 | 37.8632 | 37.9298 | 37.9964 | 38.0629 | 38.1295 | 38.1961 | 38.2626 | 38.3292 | 38.3958 | 38.4623 | 38.4862 | 38.5101 | 38.534 | 38.5579 | 38.5818 | 38.6057 | 38.6296 | 38.6534 | 38.6773 | 38.7012 | 38.7251 | 38.749 | 38.7729 | 38.7968 | 38.8207 | 38.8446 | 38.8684 | 38.8923 | 38.9162 | 38.9401 | 38.964 | 38.9879 | 39.0118 | 39.0357 | 39.0596 | 39.0834 | 39.1073 | 39.1312 | 39.1551 | 39.179 | 39.179 | 39.179 | 39.179 | 39.179 | 39.179 | 39.179 | 39.179 | 39.179 | 39.179 | 39.179 | 39.179 | 39.179 | 39.179 | 39.179 | 39.179 | 39.179 | 39.179 | 39.179 | 39.179 | 39.179 | 39.179 | 39.179 | 39.179 | 39.179 | 39.179 | 39.179 | 39.179 | 39.179 | 39.179 | 39.179 | 39.1432 | 39.1073 | 39.0715 | 39.0357 | 38.9998 | 38.964 | 38.9282 | 38.8923 | 38.8565 | 38.8207 | 38.7848 | 38.749 | 38.7132 | 38.6773 | 38.6415 | 38.6057 | 38.5698 | 38.534 | 38.4982 | 38.4623 | 38.4265 | 38.3907 | 38.3548 | 38.319 | 38.2832 | 38.2473 | 38.2115 | 38.1757 | 38.1398 | 38.104
6.2 | 0 | 13.5333 | 21.9813 | 23.9933 | 28.736 | 33.3773 | 37.0827 | 39.1187 | 39.852 | 39.852 | 38.752 | 0 | 1.3533 | 2.7067 | 4.06 | 5.4133 | 6.7667 | 8.12 | 9.4733 | 10.8267 | 12.18 | 13.5333 | 15.2229 | 16.9125 | 18.6021 | 20.2917 | 21.9813 | 22.3837 | 22.7861 | 23.1885 | 23.5909 | 23.9933 | 24.4676 | 24.9419 | 25.4161 | 25.8904 | 26.3647 | 26.8389 | 27.3132 | 27.7875 | 28.2617 | 28.736 | 29.0454 | 29.3548 | 29.6643 | 29.9737 | 30.2831 | 30.5925 | 30.902 | 31.2114 | 31.5208 | 31.8302 | 32.1396 | 32.4491 | 32.7585 | 33.0679 | 33.3773 | 33.6244 | 33.8714 | 34.1184 | 34.3654 | 34.6124 | 34.8595 | 35.1065 | 35.3535 | 35.6005 | 35.8476 | 36.0946 | 36.3416 | 36.5886 | 36.8356 | 37.0827 | 37.1505 | 37.2184 | 37.2863 | 37.3541 | 37.422 | 37.4899 | 37.5577 | 37.6256 | 37.6935 | 37.7613 | 37.8292 | 37.8971 | 37.9649 | 38.0328 | 38.1007 | 38.1685 | 38.2364 | 38.3043 | 38.3721 | 38.44 | 38.5079 | 38.5757 | 38.6436 | 38.7115 | 38.7793 | 38.8472 | 38.9151 | 38.9829 | 39.0508 | 39.1187 | 39.1431 | 39.1676 | 39.192 | 39.2164 | 39.2409 | 39.2653 | 39.2898 | 39.3142 | 39.3387 | 39.3631 | 39.3876 | 39.412 | 39.4364 | 39.4609 | 39.4853 | 39.5098 | 39.5342 | 39.5587 | 39.5831 | 39.6076 | 39.632 | 39.6564 | 39.6809 | 39.7053 | 39.7298 | 39.7542 | 39.7787 | 39.8031 | 39.8276 | 39.852 | 39.852 | 39.852 | 39.852 | 39.852 | 39.852 | 39.852 | 39.852 | 39.852 | 39.852 | 39.852 | 39.852 | 39.852 | 39.852 | 39.852 | 39.852 | 39.852 | 39.852 | 39.852 | 39.852 | 39.852 | 39.852 | 39.852 | 39.852 | 39.852 | 39.852 | 39.852 | 39.852 | 39.852 | 39.852 | 39.852 | 39.8153 | 39.7787 | 39.742 | 39.7053 | 39.6687 | 39.632 | 39.5953 | 39.5587 | 39.522 | 39.4853 | 39.4487 | 39.412 | 39.3753 | 39.3387 | 39.302 | 39.2653 | 39.2287 | 39.192 | 39.1553 | 39.1187 | 39.082 | 39.0453 | 39.0087 | 38.972 | 38.9353 | 38.8987 | 38.862 | 38.8253 | 38.7887 | 38.752
6.25 | 0 | 13.75 | 22.35 | 24.375 | 29.2 | 33.925 | 37.7 | 39.775 | 40.525 | 40.525 | 39.4 | 0 | 1.375 | 2.75 | 4.125 | 5.5 | 6.875 | 8.25 | 9.625 | 11 | 12.375 | 13.75 | 15.47 | 17.19 | 18.91 | 20.63 | 22.35 | 22.755 | 23.16 | 23.565 | 23.97 | 24.375 | 24.8575 | 25.34 | 25.8225 | 26.305 | 26.7875 | 27.27 | 27.7525 | 28.235 | 28.7175 | 29.2 | 29.515 | 29.83 | 30.145 | 30.46 | 30.775 | 31.09 | 31.405 | 31.72 | 32.035 | 32.35 | 32.665 | 32.98 | 33.295 | 33.61 | 33.925 | 34.1767 | 34.4283 | 34.68 | 34.9317 | 35.1833 | 35.435 | 35.6867 | 35.9383 | 36.19 | 36.4417 | 36.6933 | 36.945 | 37.1967 | 37.4483 | 37.7 | 37.7692 | 37.8383 | 37.9075 | 37.9767 | 38.0458 | 38.115 | 38.1842 | 38.2533 | 38.3225 | 38.3917 | 38.4608 | 38.53 | 38.5992 | 38.6683 | 38.7375 | 38.8067 | 38.8758 | 38.945 | 39.0142 | 39.0833 | 39.1525 | 39.2217 | 39.2908 | 39.36 | 39.4292 | 39.4983 | 39.5675 | 39.6367 | 39.7058 | 39.775 | 39.8 | 39.825 | 39.85 | 39.875 | 39.9 | 39.925 | 39.95 | 39.975 | 40 | 40.025 | 40.05 | 40.075 | 40.1 | 40.125 | 40.15 | 40.175 | 40.2 | 40.225 | 40.25 | 40.275 | 40.3 | 40.325 | 40.35 | 40.375 | 40.4 | 40.425 | 40.45 | 40.475 | 40.5 | 40.525 | 40.525 | 40.525 | 40.525 | 40.525 | 40.525 | 40.525 | 40.525 | 40.525 | 40.525 | 40.525 | 40.525 | 40.525 | 40.525 | 40.525 | 40.525 | 40.525 | 40.525 | 40.525 | 40.525 | 40.525 | 40.525 | 40.525 | 40.525 | 40.525 | 40.525 | 40.525 | 40.525 | 40.525 | 40.525 | 40.525 | 40.4875 | 40.45 | 40.4125 | 40.375 | 40.3375 | 40.3 | 40.2625 | 40.225 | 40.1875 | 40.15 | 40.1125 | 40.075 | 40.0375 | 40 | 39.9625 | 39.925 | 39.8875 | 39.85 | 39.8125 | 39.775 | 39.7375 | 39.7 | 39.6625 | 39.625 | 39.5875 | 39.55 | 39.5125 | 39.475 | 39.4375 | 39.4
6.3 | 0 | 13.9667 | 22.7187 | 24.7567 | 29.664 | 34.4727 | 38.3173 | 40.4313 | 41.198 | 41.198 | 40.048 | 0 | 1.3967 | 2.7933 | 4.19 | 5.5867 | 6.9833 | 8.38 | 9.7767 | 11.1733 | 12.57 | 13.9667 | 15.7171 | 17.4675 | 19.2179 | 20.9683 | 22.7187 | 23.1263 | 23.5339 | 23.9415 | 24.3491 | 24.7567 | 25.2474 | 25.7381 | 26.2289 | 26.7196 | 27.2103 | 27.7011 | 28.1918 | 28.6825 | 29.1733 | 29.664 | 29.9846 | 30.3052 | 30.6257 | 30.9463 | 31.2669 | 31.5875 | 31.908 | 32.2286 | 32.5492 | 32.8698 | 33.1904 | 33.5109 | 33.8315 | 34.1521 | 34.4727 | 34.729 | 34.9853 | 35.2416 | 35.4979 | 35.7542 | 36.0105 | 36.2668 | 36.5232 | 36.7795 | 37.0358 | 37.2921 | 37.5484 | 37.8047 | 38.061 | 38.3173 | 38.3878 | 38.4583 | 38.5287 | 38.5992 | 38.6697 | 38.7401 | 38.8106 | 38.8811 | 38.9515 | 39.022 | 39.0925 | 39.1629 | 39.2334 | 39.3039 | 39.3743 | 39.4448 | 39.5153 | 39.5857 | 39.6562 | 39.7267 | 39.7971 | 39.8676 | 39.9381 | 40.0085 | 40.079 | 40.1495 | 40.2199 | 40.2904 | 40.3609 | 40.4313 | 40.4569 | 40.4824 | 40.508 | 40.5336 | 40.5591 | 40.5847 | 40.6102 | 40.6358 | 40.6613 | 40.6869 | 40.7124 | 40.738 | 40.7636 | 40.7891 | 40.8147 | 40.8402 | 40.8658 | 40.8913 | 40.9169 | 40.9424 | 40.968 | 40.9936 | 41.0191 | 41.0447 | 41.0702 | 41.0958 | 41.1213 | 41.1469 | 41.1724 | 41.198 | 41.198 | 41.198 | 41.198 | 41.198 | 41.198 | 41.198 | 41.198 | 41.198 | 41.198 | 41.198 | 41.198 | 41.198 | 41.198 | 41.198 | 41.198 | 41.198 | 41.198 | 41.198 | 41.198 | 41.198 | 41.198 | 41.198 | 41.198 | 41.198 | 41.198 | 41.198 | 41.198 | 41.198 | 41.198 | 41.198 | 41.1597 | 41.1213 | 41.083 | 41.0447 | 41.0063 | 40.968 | 40.9297 | 40.8913 | 40.853 | 40.8147 | 40.7763 | 40.738 | 40.6997 | 40.6613 | 40.623 | 40.5847 | 40.5463 | 40.508 | 40.4697 | 40.4313 | 40.393 | 40.3547 | 40.3163 | 40.278 | 40.2397 | 40.2013 | 40.163 | 40.1247 | 40.0863 | 40.048
6.35 | 0 | 14.1833 | 23.0873 | 25.1383 | 30.128 | 35.0203 | 38.9347 | 41.0877 | 41.871 | 41.871 | 40.696 | -8.8818e-16 | 1.4183 | 2.8367 | 4.255 | 5.6733 | 7.0917 | 8.51 | 9.9283 | 11.3467 | 12.765 | 14.1833 | 15.9641 | 17.7449 | 19.5257 | 21.3065 | 23.0873 | 23.4975 | 23.9077 | 24.3179 | 24.7281 | 25.1383 | 25.6373 | 26.1363 | 26.6352 | 27.1342 | 27.6332 | 28.1321 | 28.6311 | 29.1301 | 29.629 | 30.128 | 30.4542 | 30.7803 | 31.1065 | 31.4326 | 31.7588 | 32.0849 | 32.4111 | 32.7372 | 33.0634 | 33.3896 | 33.7157 | 34.0419 | 34.368 | 34.6942 | 35.0203 | 35.2813 | 35.5422 | 35.8032 | 36.0642 | 36.3251 | 36.5861 | 36.847 | 37.108 | 37.3689 | 37.6299 | 37.8908 | 38.1518 | 38.4128 | 38.6737 | 38.9347 | 39.0064 | 39.0782 | 39.15 | 39.2217 | 39.2935 | 39.3653 | 39.437 | 39.5088 | 39.5806 | 39.6523 | 39.7241 | 39.7959 | 39.8676 | 39.9394 | 40.0112 | 40.0829 | 40.1547 | 40.2265 | 40.2982 | 40.37 | 40.4418 | 40.5135 | 40.5853 | 40.6571 | 40.7288 | 40.8006 | 40.8724 | 40.9441 | 41.0159 | 41.0877 | 41.1138 | 41.1399 | 41.166 | 41.1921 | 41.2182 | 41.2443 | 41.2704 | 41.2966 | 41.3227 | 41.3488 | 41.3749 | 41.401 | 41.4271 | 41.4532 | 41.4793 | 41.5054 | 41.5316 | 41.5577 | 41.5838 | 41.6099 | 41.636 | 41.6621 | 41.6882 | 41.7143 | 41.7404 | 41.7666 | 41.7927 | 41.8188 | 41.8449 | 41.871 | 41.871 | 41.871 | 41.871 | 41.871 | 41.871 | 41.871 | 41.871 | 41.871 | 41.871 | 41.871 | 41.871 | 41.871 | 41.871 | 41.871 | 41.871 | 41.871 | 41.871 | 41.871 | 41.871 | 41.871 | 41.871 | 41.871 | 41.871 | 41.871 | 41.871 | 41.871 | 41.871 | 41.871 | 41.871 | 41.871 | 41.8318 | 41.7927 | 41.7535 | 41.7143 | 41.6752 | 41.636 | 41.5968 | 41.5577 | 41.5185 | 41.4793 | 41.4402 | 41.401 | 41.3618 | 41.3227 | 41.2835 | 41.2443 | 41.2052 | 41.166 | 41.1268 | 41.0877 | 41.0485 | 41.0093 | 40.9702 | 40.931 | 40.8918 | 40.8527 | 40.8135 | 40.7743 | 40.7352 | 40.696
6.4 | 0 | 14.4 | 23.456 | 25.52 | 30.592 | 35.568 | 39.552 | 41.744 | 42.544 | 42.544 | 41.344 | -8.8818e-16 | 1.44 | 2.88 | 4.32 | 5.76 | 7.2 | 8.64 | 10.08 | 11.52 | 12.96 | 14.4 | 16.2112 | 18.0224 | 19.8336 | 21.6448 | 23.456 | 23.8688 | 24.2816 | 24.6944 | 25.1072 | 25.52 | 26.0272 | 26.5344 | 27.0416 | 27.5488 | 28.056 | 28.5632 | 29.0704 | 29.5776 | 30.0848 | 30.592 | 30.9237 | 31.2555 | 31.5872 | 31.9189 | 32.2507 | 32.5824 | 32.9141 | 33.2459 | 33.5776 | 33.9093 | 34.2411 | 34.5728 | 34.9045 | 35.2363 | 35.568 | 35.8336 | 36.0992 | 36.3648 | 36.6304 | 36.896 | 37.1616 | 37.4272 | 37.6928 | 37.9584 | 38.224 | 38.4896 | 38.7552 | 39.0208 | 39.2864 | 39.552 | 39.6251 | 39.6981 | 39.7712 | 39.8443 | 39.9173 | 39.9904 | 40.0635 | 40.1365 | 40.2096 | 40.2827 | 40.3557 | 40.4288 | 40.5019 | 40.5749 | 40.648 | 40.7211 | 40.7941 | 40.8672 | 40.9403 | 41.0133 | 41.0864 | 41.1595 | 41.2325 | 41.3056 | 41.3787 | 41.4517 | 41.5248 | 41.5979 | 41.6709 | 41.744 | 41.7707 | 41.7973 | 41.824 | 41.8507 | 41.8773 | 41.904 | 41.9307 | 41.9573 | 41.984 | 42.0107 | 42.0373 | 42.064 | 42.0907 | 42.1173 | 42.144 | 42.1707 | 42.1973 | 42.224 | 42.2507 | 42.2773 | 42.304 | 42.3307 | 42.3573 | 42.384 | 42.4107 | 42.4373 | 42.464 | 42.4907 | 42.5173 | 42.544 | 42.544 | 42.544 | 42.544 | 42.544 | 42.544 | 42.544 | 42.544 | 42.544 | 42.544 | 42.544 | 42.544 | 42.544 | 42.544 | 42.544 | 42.544 | 42.544 | 42.544 | 42.544 | 42.544 | 42.544 | 42.544 | 42.544 | 42.544 | 42.544 | 42.544 | 42.544 | 42.544 | 42.544 | 42.544 | 42.544 | 42.504 | 42.464 | 42.424 | 42.384 | 42.344 | 42.304 | 42.264 | 42.224 | 42.184 | 42.144 | 42.104 | 42.064 | 42.024 | 41.984 | 41.944 | 41.904 | 41.864 | 41.824 | 41.784 | 41.744 | 41.704 | 41.664 | 41.624 | 41.584 | 41.544 | 41.504 | 41.464 | 41.424 | 41.384 | 41.344
6.45 | 0 | 14.6167 | 23.8247 | 25.9017 | 31.056 | 36.1157 | 40.1693 | 42.4003 | 43.217 | 43.217 | 41.992 | -8.8818e-16 | 1.4617 | 2.9233 | 4.385 | 5.8467 | 7.3083 | 8.77 | 10.2317 | 11.6933 | 13.155 | 14.6167 | 16.4583 | 18.2999 | 20.1415 | 21.9831 | 23.8247 | 24.2401 | 24.6555 | 25.0709 | 25.4863 | 25.9017 | 26.4171 | 26.9325 | 27.448 | 27.9634 | 28.4788 | 28.9943 | 29.5097 | 30.0251 | 30.5406 | 31.056 | 31.3933 | 31.7306 | 32.0679 | 32.4052 | 32.7426 | 33.0799 | 33.4172 | 33.7545 | 34.0918 | 34.4291 | 34.7664 | 35.1037 | 35.441 | 35.7784 | 36.1157 | 36.3859 | 36.6562 | 36.9264 | 37.1966 | 37.4669 | 37.7371 | 38.0074 | 38.2776 | 38.5479 | 38.8181 | 39.0884 | 39.3586 | 39.6288 | 39.8991 | 40.1693 | 40.2437 | 40.3181 | 40.3924 | 40.4668 | 40.5412 | 40.6155 | 40.6899 | 40.7643 | 40.8386 | 40.913 | 40.9874 | 41.0617 | 41.1361 | 41.2105 | 41.2848 | 41.3592 | 41.4336 | 41.5079 | 41.5823 | 41.6567 | 41.731 | 41.8054 | 41.8798 | 41.9541 | 42.0285 | 42.1029 | 42.1772 | 42.2516 | 42.326 | 42.4003 | 42.4276 | 42.4548 | 42.482 | 42.5092 | 42.5364 | 42.5637 | 42.5909 | 42.6181 | 42.6453 | 42.6726 | 42.6998 | 42.727 | 42.7542 | 42.7814 | 42.8087 | 42.8359 | 42.8631 | 42.8903 | 42.9176 | 42.9448 | 42.972 | 42.9992 | 43.0264 | 43.0537 | 43.0809 | 43.1081 | 43.1353 | 43.1626 | 43.1898 | 43.217 | 43.217 | 43.217 | 43.217 | 43.217 | 43.217 | 43.217 | 43.217 | 43.217 | 43.217 | 43.217 | 43.217 | 43.217 | 43.217 | 43.217 | 43.217 | 43.217 | 43.217 | 43.217 | 43.217 | 43.217 | 43.217 | 43.217 | 43.217 | 43.217 | 43.217 | 43.217 | 43.217 | 43.217 | 43.217 | 43.217 | 43.1762 | 43.1353 | 43.0945 | 43.0537 | 43.0128 | 42.972 | 42.9312 | 42.8903 | 42.8495 | 42.8087 | 42.7678 | 42.727 | 42.6862 | 42.6453 | 42.6045 | 42.5637 | 42.5228 | 42.482 | 42.4412 | 42.4003 | 42.3595 | 42.3187 | 42.2778 | 42.237 | 42.1962 | 42.1553 | 42.1145 | 42.0737 | 42.0328 | 41.992
6.5 | 0 | 14.8333 | 24.1933 | 26.2833 | 31.52 | 36.6633 | 40.7867 | 43.0567 | 43.89 | 43.89 | 42.64 | 0 | 1.4833 | 2.9667 | 4.45 | 5.9333 | 7.4167 | 8.9 | 10.3833 | 11.8667 | 13.35 | 14.8333 | 16.7053 | 18.5773 | 20.4493 | 22.3213 | 24.1933 | 24.6113 | 25.0293 | 25.4473 | 25.8653 | 26.2833 | 26.807 | 27.3307 | 27.8543 | 28.378 | 28.9017 | 29.4253 | 29.949 | 30.4727 | 30.9963 | 31.52 | 31.8629 | 32.2058 | 32.5487 | 32.8916 | 33.2344 | 33.5773 | 33.9202 | 34.2631 | 34.606 | 34.9489 | 35.2918 | 35.6347 | 35.9776 | 36.3204 | 36.6633 | 36.9382 | 37.2131 | 37.488 | 37.7629 | 38.0378 | 38.3127 | 38.5876 | 38.8624 | 39.1373 | 39.4122 | 39.6871 | 39.962 | 40.2369 | 40.5118 | 40.7867 | 40.8623 | 40.938 | 41.0137 | 41.0893 | 41.165 | 41.2407 | 41.3163 | 41.392 | 41.4677 | 41.5433 | 41.619 | 41.6947 | 41.7703 | 41.846 | 41.9217 | 41.9973 | 42.073 | 42.1487 | 42.2243 | 42.3 | 42.3757 | 42.4513 | 42.527 | 42.6027 | 42.6783 | 42.754 | 42.8297 | 42.9053 | 42.981 | 43.0567 | 43.0844 | 43.1122 | 43.14 | 43.1678 | 43.1956 | 43.2233 | 43.2511 | 43.2789 | 43.3067 | 43.3344 | 43.3622 | 43.39 | 43.4178 | 43.4456 | 43.4733 | 43.5011 | 43.5289 | 43.5567 | 43.5844 | 43.6122 | 43.64 | 43.6678 | 43.6956 | 43.7233 | 43.7511 | 43.7789 | 43.8067 | 43.8344 | 43.8622 | 43.89 | 43.89 | 43.89 | 43.89 | 43.89 | 43.89 | 43.89 | 43.89 | 43.89 | 43.89 | 43.89 | 43.89 | 43.89 | 43.89 | 43.89 | 43.89 | 43.89 | 43.89 | 43.89 | 43.89 | 43.89 | 43.89 | 43.89 | 43.89 | 43.89 | 43.89 | 43.89 | 43.89 | 43.89 | 43.89 | 43.89 | 43.8483 | 43.8067 | 43.765 | 43.7233 | 43.6817 | 43.64 | 43.5983 | 43.5567 | 43.515 | 43.4733 | 43.4317 | 43.39 | 43.3483 | 43.3067 | 43.265 | 43.2233 | 43.1817 | 43.14 | 43.0983 | 43.0567 | 43.015 | 42.9733 | 42.9317 | 42.89 | 42.8483 | 42.8067 | 42.765 | 42.7233 | 42.6817 | 42.64
6.55 | 0 | 15.05 | 24.562 | 26.665 | 31.984 | 37.211 | 41.404 | 43.713 | 44.563 | 44.563 | 43.288 | 0 | 1.505 | 3.01 | 4.515 | 6.02 | 7.525 | 9.03 | 10.535 | 12.04 | 13.545 | 15.05 | 16.9524 | 18.8548 | 20.7572 | 22.6596 | 24.562 | 24.9826 | 25.4032 | 25.8238 | 26.2444 | 26.665 | 27.1969 | 27.7288 | 28.2607 | 28.7926 | 29.3245 | 29.8564 | 30.3883 | 30.9202 | 31.4521 | 31.984 | 32.3325 | 32.6809 | 33.0294 | 33.3779 | 33.7263 | 34.0748 | 34.4233 | 34.7717 | 35.1202 | 35.4687 | 35.8171 | 36.1656 | 36.5141 | 36.8625 | 37.211 | 37.4905 | 37.7701 | 38.0496 | 38.3291 | 38.6087 | 38.8882 | 39.1677 | 39.4473 | 39.7268 | 40.0063 | 40.2859 | 40.5654 | 40.8449 | 41.1245 | 41.404 | 41.481 | 41.5579 | 41.6349 | 41.7119 | 41.7888 | 41.8658 | 41.9428 | 42.0197 | 42.0967 | 42.1737 | 42.2506 | 42.3276 | 42.4046 | 42.4815 | 42.5585 | 42.6355 | 42.7124 | 42.7894 | 42.8664 | 42.9433 | 43.0203 | 43.0973 | 43.1742 | 43.2512 | 43.3282 | 43.4051 | 43.4821 | 43.5591 | 43.636 | 43.713 | 43.7413 | 43.7697 | 43.798 | 43.8263 | 43.8547 | 43.883 | 43.9113 | 43.9397 | 43.968 | 43.9963 | 44.0247 | 44.053 | 44.0813 | 44.1097 | 44.138 | 44.1663 | 44.1947 | 44.223 | 44.2513 | 44.2797 | 44.308 | 44.3363 | 44.3647 | 44.393 | 44.4213 | 44.4497 | 44.478 | 44.5063 | 44.5347 | 44.563 | 44.563 | 44.563 | 44.563 | 44.563 | 44.563 | 44.563 | 44.563 | 44.563 | 44.563 | 44.563 | 44.563 | 44.563 | 44.563 | 44.563 | 44.563 | 44.563 | 44.563 | 44.563 | 44.563 | 44.563 | 44.563 | 44.563 | 44.563 | 44.563 | 44.563 | 44.563 | 44.563 | 44.563 | 44.563 | 44.563 | 44.5205 | 44.478 | 44.4355 | 44.393 | 44.3505 | 44.308 | 44.2655 | 44.223 | 44.1805 | 44.138 | 44.0955 | 44.053 | 44.0105 | 43.968 | 43.9255 | 43.883 | 43.8405 | 43.798 | 43.7555 | 43.713 | 43.6705 | 43.628 | 43.5855 | 43.543 | 43.5005 | 43.458 | 43.4155 | 43.373 | 43.3305 | 43.288
6.6 | 0 | 15.2667 | 24.9307 | 27.0467 | 32.448 | 37.7587 | 42.0213 | 44.3693 | 45.236 | 45.236 | 43.936 | 0 | 1.5267 | 3.0533 | 4.58 | 6.1067 | 7.6333 | 9.16 | 10.6867 | 12.2133 | 13.74 | 15.2667 | 17.1995 | 19.1323 | 21.0651 | 22.9979 | 24.9307 | 25.3539 | 25.7771 | 26.2003 | 26.6235 | 27.0467 | 27.5868 | 28.1269 | 28.6671 | 29.2072 | 29.7473 | 30.2875 | 30.8276 | 31.3677 | 31.9079 | 32.448 | 32.802 | 33.1561 | 33.5101 | 33.8642 | 34.2182 | 34.5723 | 34.9263 | 35.2804 | 35.6344 | 35.9884 | 36.3425 | 36.6965 | 37.0506 | 37.4046 | 37.7587 | 38.0428 | 38.327 | 38.6112 | 38.8954 | 39.1796 | 39.4637 | 39.7479 | 40.0321 | 40.3163 | 40.6004 | 40.8846 | 41.1688 | 41.453 | 41.7372 | 42.0213 | 42.0996 | 42.1779 | 42.2561 | 42.3344 | 42.4127 | 42.4909 | 42.5692 | 42.6475 | 42.7257 | 42.804 | 42.8823 | 42.9605 | 43.0388 | 43.1171 | 43.1953 | 43.2736 | 43.3519 | 43.4301 | 43.5084 | 43.5867 | 43.6649 | 43.7432 | 43.8215 | 43.8997 | 43.978 | 44.0563 | 44.1345 | 44.2128 | 44.2911 | 44.3693 | 44.3982 | 44.4271 | 44.456 | 44.4849 | 44.5138 | 44.5427 | 44.5716 | 44.6004 | 44.6293 | 44.6582 | 44.6871 | 44.716 | 44.7449 | 44.7738 | 44.8027 | 44.8316 | 44.8604 | 44.8893 | 44.9182 | 44.9471 | 44.976 | 45.0049 | 45.0338 | 45.0627 | 45.0916 | 45.1204 | 45.1493 | 45.1782 | 45.2071 | 45.236 | 45.236 | 45.236 | 45.236 | 45.236 | 45.236 | 45.236 | 45.236 | 45.236 | 45.236 | 45.236 | 45.236 | 45.236 | 45.236 | 45.236 | 45.236 | 45.236 | 45.236 | 45.236 | 45.236 | 45.236 | 45.236 | 45.236 | 45.236 | 45.236 | 45.236 | 45.236 | 45.236 | 45.236 | 45.236 | 45.236 | 45.1927 | 45.1493 | 45.106 | 45.0627 | 45.0193 | 44.976 | 44.9327 | 44.8893 | 44.846 | 44.8027 | 44.7593 | 44.716 | 44.6727 | 44.6293 | 44.586 | 44.5427 | 44.4993 | 44.456 | 44.4127 | 44.3693 | 44.326 | 44.2827 | 44.2393 | 44.196 | 44.1527 | 44.1093 | 44.066 | 44.0227 | 43.9793 | 43.936
6.65 | 0 | 15.4833 | 25.2993 | 27.4283 | 32.912 | 38.3063 | 42.6387 | 45.0257 | 45.909 | 45.909 | 44.584 | 0 | 1.5483 | 3.0967 | 4.645 | 6.1933 | 7.7417 | 9.29 | 10.8383 | 12.3867 | 13.935 | 15.4833 | 17.4465 | 19.4097 | 21.3729 | 23.3361 | 25.2993 | 25.7251 | 26.1509 | 26.5767 | 27.0025 | 27.4283 | 27.9767 | 28.5251 | 29.0734 | 29.6218 | 30.1702 | 30.7185 | 31.2669 | 31.8153 | 32.3636 | 32.912 | 33.2716 | 33.6312 | 33.9909 | 34.3505 | 34.7101 | 35.0697 | 35.4294 | 35.789 | 36.1486 | 36.5082 | 36.8678 | 37.2275 | 37.5871 | 37.9467 | 38.3063 | 38.5952 | 38.884 | 39.1728 | 39.4616 | 39.7504 | 40.0393 | 40.3281 | 40.6169 | 40.9057 | 41.1946 | 41.4834 | 41.7722 | 42.061 | 42.3498 | 42.6387 | 42.7182 | 42.7978 | 42.8774 | 42.9569 | 43.0365 | 43.1161 | 43.1956 | 43.2752 | 43.3548 | 43.4343 | 43.5139 | 43.5935 | 43.673 | 43.7526 | 43.8322 | 43.9117 | 43.9913 | 44.0709 | 44.1504 | 44.23 | 44.3096 | 44.3891 | 44.4687 | 44.5483 | 44.6278 | 44.7074 | 44.787 | 44.8665 | 44.9461 | 45.0257 | 45.0551 | 45.0846 | 45.114 | 45.1434 | 45.1729 | 45.2023 | 45.2318 | 45.2612 | 45.2907 | 45.3201 | 45.3496 | 45.379 | 45.4084 | 45.4379 | 45.4673 | 45.4968 | 45.5262 | 45.5557 | 45.5851 | 45.6146 | 45.644 | 45.6734 | 45.7029 | 45.7323 | 45.7618 | 45.7912 | 45.8207 | 45.8501 | 45.8796 | 45.909 | 45.909 | 45.909 | 45.909 | 45.909 | 45.909 | 45.909 | 45.909 | 45.909 | 45.909 | 45.909 | 45.909 | 45.909 | 45.909 | 45.909 | 45.909 | 45.909 | 45.909 | 45.909 | 45.909 | 45.909 | 45.909 | 45.909 | 45.909 | 45.909 | 45.909 | 45.909 | 45.909 | 45.909 | 45.909 | 45.909 | 45.8648 | 45.8207 | 45.7765 | 45.7323 | 45.6882 | 45.644 | 45.5998 | 45.5557 | 45.5115 | 45.4673 | 45.4232 | 45.379 | 45.3348 | 45.2907 | 45.2465 | 45.2023 | 45.1582 | 45.114 | 45.0698 | 45.0257 | 44.9815 | 44.9373 | 44.8932 | 44.849 | 44.8048 | 44.7607 | 44.7165 | 44.6723 | 44.6282 | 44.584
6.7 | 0 | 15.7 | 25.668 | 27.81 | 33.376 | 38.854 | 43.256 | 45.682 | 46.582 | 46.582 | 45.232 | -8.8818e-16 | 1.57 | 3.14 | 4.71 | 6.28 | 7.85 | 9.42 | 10.99 | 12.56 | 14.13 | 15.7 | 17.6936 | 19.6872 | 21.6808 | 23.6744 | 25.668 | 26.0964 | 26.5248 | 26.9532 | 27.3816 | 27.81 | 28.3666 | 28.9232 | 29.4798 | 30.0364 | 30.593 | 31.1496 | 31.7062 | 32.2628 | 32.8194 | 33.376 | 33.7412 | 34.1064 | 34.4716 | 34.8368 | 35.202 | 35.5672 | 35.9324 | 36.2976 | 36.6628 | 37.028 | 37.3932 | 37.7584 | 38.1236 | 38.4888 | 38.854 | 39.1475 | 39.4409 | 39.7344 | 40.0279 | 40.3213 | 40.6148 | 40.9083 | 41.2017 | 41.4952 | 41.7887 | 42.0821 | 42.3756 | 42.6691 | 42.9625 | 43.256 | 43.3369 | 43.4177 | 43.4986 | 43.5795 | 43.6603 | 43.7412 | 43.8221 | 43.9029 | 43.9838 | 44.0647 | 44.1455 | 44.2264 | 44.3073 | 44.3881 | 44.469 | 44.5499 | 44.6307 | 44.7116 | 44.7925 | 44.8733 | 44.9542 | 45.0351 | 45.1159 | 45.1968 | 45.2777 | 45.3585 | 45.4394 | 45.5203 | 45.6011 | 45.682 | 45.712 | 45.742 | 45.772 | 45.802 | 45.832 | 45.862 | 45.892 | 45.922 | 45.952 | 45.982 | 46.012 | 46.042 | 46.072 | 46.102 | 46.132 | 46.162 | 46.192 | 46.222 | 46.252 | 46.282 | 46.312 | 46.342 | 46.372 | 46.402 | 46.432 | 46.462 | 46.492 | 46.522 | 46.552 | 46.582 | 46.582 | 46.582 | 46.582 | 46.582 | 46.582 | 46.582 | 46.582 | 46.582 | 46.582 | 46.582 | 46.582 | 46.582 | 46.582 | 46.582 | 46.582 | 46.582 | 46.582 | 46.582 | 46.582 | 46.582 | 46.582 | 46.582 | 46.582 | 46.582 | 46.582 | 46.582 | 46.582 | 46.582 | 46.582 | 46.582 | 46.537 | 46.492 | 46.447 | 46.402 | 46.357 | 46.312 | 46.267 | 46.222 | 46.177 | 46.132 | 46.087 | 46.042 | 45.997 | 45.952 | 45.907 | 45.862 | 45.817 | 45.772 | 45.727 | 45.682 | 45.637 | 45.592 | 45.547 | 45.502 | 45.457 | 45.412 | 45.367 | 45.322 | 45.277 | 45.232
6.75 | 0 | 15.9167 | 26.0367 | 28.1917 | 33.84 | 39.4017 | 43.8733 | 46.3383 | 47.255 | 47.255 | 45.88 | 0 | 1.5917 | 3.1833 | 4.775 | 6.3667 | 7.9583 | 9.55 | 11.1417 | 12.7333 | 14.325 | 15.9167 | 17.9407 | 19.9647 | 21.9887 | 24.0127 | 26.0367 | 26.4677 | 26.8987 | 27.3297 | 27.7607 | 28.1917 | 28.7565 | 29.3213 | 29.8862 | 30.451 | 31.0158 | 31.5807 | 32.1455 | 32.7103 | 33.2752 | 33.84 | 34.2108 | 34.5816 | 34.9523 | 35.3231 | 35.6939 | 36.0647 | 36.4354 | 36.8062 | 37.177 | 37.5478 | 37.9186 | 38.2893 | 38.6601 | 39.0309 | 39.4017 | 39.6998 | 39.9979 | 40.296 | 40.5941 | 40.8922 | 41.1903 | 41.4884 | 41.7866 | 42.0847 | 42.3828 | 42.6809 | 42.979 | 43.2771 | 43.5752 | 43.8733 | 43.9555 | 44.0377 | 44.1198 | 44.202 | 44.2842 | 44.3663 | 44.4485 | 44.5307 | 44.6128 | 44.695 | 44.7772 | 44.8593 | 44.9415 | 45.0237 | 45.1058 | 45.188 | 45.2702 | 45.3523 | 45.4345 | 45.5167 | 45.5988 | 45.681 | 45.7632 | 45.8453 | 45.9275 | 46.0097 | 46.0918 | 46.174 | 46.2562 | 46.3383 | 46.3689 | 46.3994 | 46.43 | 46.4606 | 46.4911 | 46.5217 | 46.5522 | 46.5828 | 46.6133 | 46.6439 | 46.6744 | 46.705 | 46.7356 | 46.7661 | 46.7967 | 46.8272 | 46.8578 | 46.8883 | 46.9189 | 46.9494 | 46.98 | 47.0106 | 47.0411 | 47.0717 | 47.1022 | 47.1328 | 47.1633 | 47.1939 | 47.2244 | 47.255 | 47.255 | 47.255 | 47.255 | 47.255 | 47.255 | 47.255 | 47.255 | 47.255 | 47.255 | 47.255 | 47.255 | 47.255 | 47.255 | 47.255 | 47.255 | 47.255 | 47.255 | 47.255 | 47.255 | 47.255 | 47.255 | 47.255 | 47.255 | 47.255 | 47.255 | 47.255 | 47.255 | 47.255 | 47.255 | 47.255 | 47.2092 | 47.1633 | 47.1175 | 47.0717 | 47.0258 | 46.98 | 46.9342 | 46.8883 | 46.8425 | 46.7967 | 46.7508 | 46.705 | 46.6592 | 46.6133 | 46.5675 | 46.5217 | 46.4758 | 46.43 | 46.3842 | 46.3383 | 46.2925 | 46.2467 | 46.2008 | 46.155 | 46.1092 | 46.0633 | 46.0175 | 45.9717 | 45.9258 | 45.88
6.8 | 0 | 16.1333 | 26.4053 | 28.5733 | 34.304 | 39.9493 | 44.4907 | 46.9947 | 47.928 | 47.928 | 46.528 | 1.7764e-15 | 1.6133 | 3.2267 | 4.84 | 6.4533 | 8.0667 | 9.68 | 11.2933 | 12.9067 | 14.52 | 16.1333 | 18.1877 | 20.2421 | 22.2965 | 24.3509 | 26.4053 | 26.8389 | 27.2725 | 27.7061 | 28.1397 | 28.5733 | 29.1464 | 29.7195 | 30.2925 | 30.8656 | 31.4387 | 32.0117 | 32.5848 | 33.1579 | 33.7309 | 34.304 | 34.6804 | 35.0567 | 35.4331 | 35.8094 | 36.1858 | 36.5621 | 36.9385 | 37.3148 | 37.6912 | 38.0676 | 38.4439 | 38.8203 | 39.1966 | 39.573 | 39.9493 | 40.2521 | 40.5548 | 40.8576 | 41.1604 | 41.4631 | 41.7659 | 42.0686 | 42.3714 | 42.6741 | 42.9769 | 43.2796 | 43.5824 | 43.8852 | 44.1879 | 44.4907 | 44.5741 | 44.6576 | 44.7411 | 44.8245 | 44.908 | 44.9915 | 45.0749 | 45.1584 | 45.2419 | 45.3253 | 45.4088 | 45.4923 | 45.5757 | 45.6592 | 45.7427 | 45.8261 | 45.9096 | 45.9931 | 46.0765 | 46.16 | 46.2435 | 46.3269 | 46.4104 | 46.4939 | 46.5773 | 46.6608 | 46.7443 | 46.8277 | 46.9112 | 46.9947 | 47.0258 | 47.0569 | 47.088 | 47.1191 | 47.1502 | 47.1813 | 47.2124 | 47.2436 | 47.2747 | 47.3058 | 47.3369 | 47.368 | 47.3991 | 47.4302 | 47.4613 | 47.4924 | 47.5236 | 47.5547 | 47.5858 | 47.6169 | 47.648 | 47.6791 | 47.7102 | 47.7413 | 47.7724 | 47.8036 | 47.8347 | 47.8658 | 47.8969 | 47.928 | 47.928 | 47.928 | 47.928 | 47.928 | 47.928 | 47.928 | 47.928 | 47.928 | 47.928 | 47.928 | 47.928 | 47.928 | 47.928 | 47.928 | 47.928 | 47.928 | 47.928 | 47.928 | 47.928 | 47.928 | 47.928 | 47.928 | 47.928 | 47.928 | 47.928 | 47.928 | 47.928 | 47.928 | 47.928 | 47.928 | 47.8813 | 47.8347 | 47.788 | 47.7413 | 47.6947 | 47.648 | 47.6013 | 47.5547 | 47.508 | 47.4613 | 47.4147 | 47.368 | 47.3213 | 47.2747 | 47.228 | 47.1813 | 47.1347 | 47.088 | 47.0413 | 46.9947 | 46.948 | 46.9013 | 46.8547 | 46.808 | 46.7613 | 46.7147 | 46.668 | 46.6213 | 46.5747 | 46.528
6.85 | 0 | 16.35 | 26.774 | 28.955 | 34.768 | 40.497 | 45.108 | 47.651 | 48.601 | 48.601 | 47.176 | 0 | 1.635 | 3.27 | 4.905 | 6.54 | 8.175 | 9.81 | 11.445 | 13.08 | 14.715 | 16.35 | 18.4348 | 20.5196 | 22.6044 | 24.6892 | 26.774 | 27.2102 | 27.6464 | 28.0826 | 28.5188 | 28.955 | 29.5363 | 30.1176 | 30.6989 | 31.2802 | 31.8615 | 32.4428 | 33.0241 | 33.6054 | 34.1867 | 34.768 | 35.1499 | 35.5319 | 35.9138 | 36.2957 | 36.6777 | 37.0596 | 37.4415 | 37.8235 | 38.2054 | 38.5873 | 38.9693 | 39.3512 | 39.7331 | 40.1151 | 40.497 | 40.8044 | 41.1118 | 41.4192 | 41.7266 | 42.034 | 42.3414 | 42.6488 | 42.9562 | 43.2636 | 43.571 | 43.8784 | 44.1858 | 44.4932 | 44.8006 | 45.108 | 45.1928 | 45.2775 | 45.3623 | 45.4471 | 45.5318 | 45.6166 | 45.7014 | 45.7861 | 45.8709 | 45.9557 | 46.0404 | 46.1252 | 46.21 | 46.2947 | 46.3795 | 46.4643 | 46.549 | 46.6338 | 46.7186 | 46.8033 | 46.8881 | 46.9729 | 47.0576 | 47.1424 | 47.2272 | 47.3119 | 47.3967 | 47.4815 | 47.5662 | 47.651 | 47.6827 | 47.7143 | 47.746 | 47.7777 | 47.8093 | 47.841 | 47.8727 | 47.9043 | 47.936 | 47.9677 | 47.9993 | 48.031 | 48.0627 | 48.0943 | 48.126 | 48.1577 | 48.1893 | 48.221 | 48.2527 | 48.2843 | 48.316 | 48.3477 | 48.3793 | 48.411 | 48.4427 | 48.4743 | 48.506 | 48.5377 | 48.5693 | 48.601 | 48.601 | 48.601 | 48.601 | 48.601 | 48.601 | 48.601 | 48.601 | 48.601 | 48.601 | 48.601 | 48.601 | 48.601 | 48.601 | 48.601 | 48.601 | 48.601 | 48.601 | 48.601 | 48.601 | 48.601 | 48.601 | 48.601 | 48.601 | 48.601 | 48.601 | 48.601 | 48.601 | 48.601 | 48.601 | 48.601 | 48.5535 | 48.506 | 48.4585 | 48.411 | 48.3635 | 48.316 | 48.2685 | 48.221 | 48.1735 | 48.126 | 48.0785 | 48.031 | 47.9835 | 47.936 | 47.8885 | 47.841 | 47.7935 | 47.746 | 47.6985 | 47.651 | 47.6035 | 47.556 | 47.5085 | 47.461 | 47.4135 | 47.366 | 47.3185 | 47.271 | 47.2235 | 47.176
6.9 | 0 | 16.5667 | 27.1427 | 29.3367 | 35.232 | 41.0447 | 45.7253 | 48.3073 | 49.274 | 49.274 | 47.824 | 0 | 1.6567 | 3.3133 | 4.97 | 6.6267 | 8.2833 | 9.94 | 11.5967 | 13.2533 | 14.91 | 16.5667 | 18.6819 | 20.7971 | 22.9123 | 25.0275 | 27.1427 | 27.5815 | 28.0203 | 28.4591 | 28.8979 | 29.3367 | 29.9262 | 30.5157 | 31.1053 | 31.6948 | 32.2843 | 32.8739 | 33.4634 | 34.0529 | 34.6425 | 35.232 | 35.6195 | 36.007 | 36.3945 | 36.782 | 37.1696 | 37.5571 | 37.9446 | 38.3321 | 38.7196 | 39.1071 | 39.4946 | 39.8821 | 40.2696 | 40.6572 | 41.0447 | 41.3567 | 41.6688 | 41.9808 | 42.2928 | 42.6049 | 42.9169 | 43.229 | 43.541 | 43.8531 | 44.1651 | 44.4772 | 44.7892 | 45.1012 | 45.4133 | 45.7253 | 45.8114 | 45.8975 | 45.9835 | 46.0696 | 46.1557 | 46.2417 | 46.3278 | 46.4139 | 46.4999 | 46.586 | 46.6721 | 46.7581 | 46.8442 | 46.9303 | 47.0163 | 47.1024 | 47.1885 | 47.2745 | 47.3606 | 47.4467 | 47.5327 | 47.6188 | 47.7049 | 47.7909 | 47.877 | 47.9631 | 48.0491 | 48.1352 | 48.2213 | 48.3073 | 48.3396 | 48.3718 | 48.404 | 48.4362 | 48.4684 | 48.5007 | 48.5329 | 48.5651 | 48.5973 | 48.6296 | 48.6618 | 48.694 | 48.7262 | 48.7584 | 48.7907 | 48.8229 | 48.8551 | 48.8873 | 48.9196 | 48.9518 | 48.984 | 49.0162 | 49.0484 | 49.0807 | 49.1129 | 49.1451 | 49.1773 | 49.2096 | 49.2418 | 49.274 | 49.274 | 49.274 | 49.274 | 49.274 | 49.274 | 49.274 | 49.274 | 49.274 | 49.274 | 49.274 | 49.274 | 49.274 | 49.274 | 49.274 | 49.274 | 49.274 | 49.274 | 49.274 | 49.274 | 49.274 | 49.274 | 49.274 | 49.274 | 49.274 | 49.274 | 49.274 | 49.274 | 49.274 | 49.274 | 49.274 | 49.2257 | 49.1773 | 49.129 | 49.0807 | 49.0323 | 48.984 | 48.9357 | 48.8873 | 48.839 | 48.7907 | 48.7423 | 48.694 | 48.6457 | 48.5973 | 48.549 | 48.5007 | 48.4523 | 48.404 | 48.3557 | 48.3073 | 48.259 | 48.2107 | 48.1623 | 48.114 | 48.0657 | 48.0173 | 47.969 | 47.9207 | 47.8723 | 47.824
6.95 | 0 | 16.7833 | 27.5113 | 29.7183 | 35.696 | 41.5923 | 46.3427 | 48.9637 | 49.947 | 49.947 | 48.472 | 0 | 1.6783 | 3.3567 | 5.035 | 6.7133 | 8.3917 | 10.07 | 11.7483 | 13.4267 | 15.105 | 16.7833 | 18.9289 | 21.0745 | 23.2201 | 25.3657 | 27.5113 | 27.9527 | 28.3941 | 28.8355 | 29.2769 | 29.7183 | 30.3161 | 30.9139 | 31.5116 | 32.1094 | 32.7072 | 33.3049 | 33.9027 | 34.5005 | 35.0982 | 35.696 | 36.0891 | 36.4822 | 36.8753 | 37.2684 | 37.6614 | 38.0545 | 38.4476 | 38.8407 | 39.2338 | 39.6269 | 40.02 | 40.4131 | 40.8062 | 41.1992 | 41.5923 | 41.909 | 42.2257 | 42.5424 | 42.8591 | 43.1758 | 43.4925 | 43.8092 | 44.1258 | 44.4425 | 44.7592 | 45.0759 | 45.3926 | 45.7093 | 46.026 | 46.3427 | 46.43 | 46.5174 | 46.6048 | 46.6921 | 46.7795 | 46.8669 | 46.9542 | 47.0416 | 47.129 | 47.2163 | 47.3037 | 47.3911 | 47.4784 | 47.5658 | 47.6532 | 47.7405 | 47.8279 | 47.9153 | 48.0026 | 48.09 | 48.1774 | 48.2647 | 48.3521 | 48.4395 | 48.5268 | 48.6142 | 48.7016 | 48.7889 | 48.8763 | 48.9637 | 48.9964 | 49.0292 | 49.062 | 49.0948 | 49.1276 | 49.1603 | 49.1931 | 49.2259 | 49.2587 | 49.2914 | 49.3242 | 49.357 | 49.3898 | 49.4226 | 49.4553 | 49.4881 | 49.5209 | 49.5537 | 49.5864 | 49.6192 | 49.652 | 49.6848 | 49.7176 | 49.7503 | 49.7831 | 49.8159 | 49.8487 | 49.8814 | 49.9142 | 49.947 | 49.947 | 49.947 | 49.947 | 49.947 | 49.947 | 49.947 | 49.947 | 49.947 | 49.947 | 49.947 | 49.947 | 49.947 | 49.947 | 49.947 | 49.947 | 49.947 | 49.947 | 49.947 | 49.947 | 49.947 | 49.947 | 49.947 | 49.947 | 49.947 | 49.947 | 49.947 | 49.947 | 49.947 | 49.947 | 49.947 | 49.8978 | 49.8487 | 49.7995 | 49.7503 | 49.7012 | 49.652 | 49.6028 | 49.5537 | 49.5045 | 49.4553 | 49.4062 | 49.357 | 49.3078 | 49.2587 | 49.2095 | 49.1603 | 49.1112 | 49.062 | 49.0128 | 48.9637 | 48.9145 | 48.8653 | 48.8162 | 48.767 | 48.7178 | 48.6687 | 48.6195 | 48.5703 | 48.5212 | 48.472
7 | 0 | 17 | 27.88 | 30.1 | 36.16 | 42.14 | 46.96 | 49.62 | 50.62 | 50.62 | 49.12 | 0 | 1.7 | 3.4 | 5.1 | 6.8 | 8.5 | 10.2 | 11.9 | 13.6 | 15.3 | 17 | 19.176 | 21.352 | 23.528 | 25.704 | 27.88 | 28.324 | 28.768 | 29.212 | 29.656 | 30.1 | 30.706 | 31.312 | 31.918 | 32.524 | 33.13 | 33.736 | 34.342 | 34.948 | 35.554 | 36.16 | 36.5587 | 36.9573 | 37.356 | 37.7547 | 38.1533 | 38.552 | 38.9507 | 39.3493 | 39.748 | 40.1467 | 40.5453 | 40.944 | 41.3427 | 41.7413 | 42.14 | 42.4613 | 42.7827 | 43.104 | 43.4253 | 43.7467 | 44.068 | 44.3893 | 44.7107 | 45.032 | 45.3533 | 45.6747 | 45.996 | 46.3173 | 46.6387 | 46.96 | 47.0487 | 47.1373 | 47.226 | 47.3147 | 47.4033 | 47.492 | 47.5807 | 47.6693 | 47.758 | 47.8467 | 47.9353 | 48.024 | 48.1127 | 48.2013 | 48.29 | 48.3787 | 48.4673 | 48.556 | 48.6447 | 48.7333 | 48.822 | 48.9107 | 48.9993 | 49.088 | 49.1767 | 49.2653 | 49.354 | 49.4427 | 49.5313 | 49.62 | 49.6533 | 49.6867 | 49.72 | 49.7533 | 49.7867 | 49.82 | 49.8533 | 49.8867 | 49.92 | 49.9533 | 49.9867 | 50.02 | 50.0533 | 50.0867 | 50.12 | 50.1533 | 50.1867 | 50.22 | 50.2533 | 50.2867 | 50.32 | 50.3533 | 50.3867 | 50.42 | 50.4533 | 50.4867 | 50.52 | 50.5533 | 50.5867 | 50.62 | 50.62 | 50.62 | 50.62 | 50.62 | 50.62 | 50.62 | 50.62 | 50.62 | 50.62 | 50.62 | 50.62 | 50.62 | 50.62 | 50.62 | 50.62 | 50.62 | 50.62 | 50.62 | 50.62 | 50.62 | 50.62 | 50.62 | 50.62 | 50.62 | 50.62 | 50.62 | 50.62 | 50.62 | 50.62 | 50.62 | 50.57 | 50.52 | 50.47 | 50.42 | 50.37 | 50.32 | 50.27 | 50.22 | 50.17 | 50.12 | 50.07 | 50.02 | 49.97 | 49.92 | 49.87 | 49.82 | 49.77 | 49.72 | 49.67 | 49.62 | 49.57 | 49.52 | 49.47 | 49.42 | 49.37 | 49.32 | 49.27 | 49.22 | 49.17 | 49.12
7.05 | 0 | 17.2167 | 28.2487 | 30.4817 | 36.624 | 42.6877 | 47.5773 | 50.2763 | 51.293 | 51.293 | 49.768 | -1.7764e-15 | 1.7217 | 3.4433 | 5.165 | 6.8867 | 8.6083 | 10.33 | 12.0517 | 13.7733 | 15.495 | 17.2167 | 19.4231 | 21.6295 | 23.8359 | 26.0423 | 28.2487 | 28.6953 | 29.1419 | 29.5885 | 30.0351 | 30.4817 | 31.0959 | 31.7101 | 32.3244 | 32.9386 | 33.5528 | 34.1671 | 34.7813 | 35.3955 | 36.0098 | 36.624 | 37.0282 | 37.4325 | 37.8367 | 38.241 | 38.6452 | 39.0495 | 39.4537 | 39.858 | 40.2622 | 40.6664 | 41.0707 | 41.4749 | 41.8792 | 42.2834 | 42.6877 | 43.0136 | 43.3396 | 43.6656 | 43.9916 | 44.3176 | 44.6435 | 44.9695 | 45.2955 | 45.6215 | 45.9474 | 46.2734 | 46.5994 | 46.9254 | 47.2514 | 47.5773 | 47.6673 | 47.7573 | 47.8472 | 47.9372 | 48.0272 | 48.1171 | 48.2071 | 48.2971 | 48.387 | 48.477 | 48.567 | 48.6569 | 48.7469 | 48.8369 | 48.9268 | 49.0168 | 49.1068 | 49.1967 | 49.2867 | 49.3767 | 49.4666 | 49.5566 | 49.6466 | 49.7365 | 49.8265 | 49.9165 | 50.0064 | 50.0964 | 50.1864 | 50.2763 | 50.3102 | 50.3441 | 50.378 | 50.4119 | 50.4458 | 50.4797 | 50.5136 | 50.5474 | 50.5813 | 50.6152 | 50.6491 | 50.683 | 50.7169 | 50.7508 | 50.7847 | 50.8186 | 50.8524 | 50.8863 | 50.9202 | 50.9541 | 50.988 | 51.0219 | 51.0558 | 51.0897 | 51.1236 | 51.1574 | 51.1913 | 51.2252 | 51.2591 | 51.293 | 51.293 | 51.293 | 51.293 | 51.293 | 51.293 | 51.293 | 51.293 | 51.293 | 51.293 | 51.293 | 51.293 | 51.293 | 51.293 | 51.293 | 51.293 | 51.293 | 51.293 | 51.293 | 51.293 | 51.293 | 51.293 | 51.293 | 51.293 | 51.293 | 51.293 | 51.293 | 51.293 | 51.293 | 51.293 | 51.293 | 51.2422 | 51.1913 | 51.1405 | 51.0897 | 51.0388 | 50.988 | 50.9372 | 50.8863 | 50.8355 | 50.7847 | 50.7338 | 50.683 | 50.6322 | 50.5813 | 50.5305 | 50.4797 | 50.4288 | 50.378 | 50.3272 | 50.2763 | 50.2255 | 50.1747 | 50.1238 | 50.073 | 50.0222 | 49.9713 | 49.9205 | 49.8697 | 49.8188 | 49.768
7.1 | 0 | 17.4333 | 28.6173 | 30.8633 | 37.088 | 43.2353 | 48.1947 | 50.9327 | 51.966 | 51.966 | 50.416 | 0 | 1.7433 | 3.4867 | 5.23 | 6.9733 | 8.7167 | 10.46 | 12.2033 | 13.9467 | 15.69 | 17.4333 | 19.6701 | 21.9069 | 24.1437 | 26.3805 | 28.6173 | 29.0665 | 29.5157 | 29.9649 | 30.4141 | 30.8633 | 31.4858 | 32.1083 | 32.7307 | 33.3532 | 33.9757 | 34.5981 | 35.2206 | 35.8431 | 36.4655 | 37.088 | 37.4978 | 37.9076 | 38.3175 | 38.7273 | 39.1371 | 39.5469 | 39.9568 | 40.3666 | 40.7764 | 41.1862 | 41.596 | 42.0059 | 42.4157 | 42.8255 | 43.2353 | 43.566 | 43.8966 | 44.2272 | 44.5578 | 44.8884 | 45.2191 | 45.5497 | 45.8803 | 46.2109 | 46.5416 | 46.8722 | 47.2028 | 47.5334 | 47.864 | 48.1947 | 48.2859 | 48.3772 | 48.4685 | 48.5597 | 48.651 | 48.7423 | 48.8335 | 48.9248 | 49.0161 | 49.1073 | 49.1986 | 49.2899 | 49.3811 | 49.4724 | 49.5637 | 49.6549 | 49.7462 | 49.8375 | 49.9287 | 50.02 | 50.1113 | 50.2025 | 50.2938 | 50.3851 | 50.4763 | 50.5676 | 50.6589 | 50.7501 | 50.8414 | 50.9327 | 50.9671 | 51.0016 | 51.036 | 51.0704 | 51.1049 | 51.1393 | 51.1738 | 51.2082 | 51.2427 | 51.2771 | 51.3116 | 51.346 | 51.3804 | 51.4149 | 51.4493 | 51.4838 | 51.5182 | 51.5527 | 51.5871 | 51.6216 | 51.656 | 51.6904 | 51.7249 | 51.7593 | 51.7938 | 51.8282 | 51.8627 | 51.8971 | 51.9316 | 51.966 | 51.966 | 51.966 | 51.966 | 51.966 | 51.966 | 51.966 | 51.966 | 51.966 | 51.966 | 51.966 | 51.966 | 51.966 | 51.966 | 51.966 | 51.966 | 51.966 | 51.966 | 51.966 | 51.966 | 51.966 | 51.966 | 51.966 | 51.966 | 51.966 | 51.966 | 51.966 | 51.966 | 51.966 | 51.966 | 51.966 | 51.9143 | 51.8627 | 51.811 | 51.7593 | 51.7077 | 51.656 | 51.6043 | 51.5527 | 51.501 | 51.4493 | 51.3977 | 51.346 | 51.2943 | 51.2427 | 51.191 | 51.1393 | 51.0877 | 51.036 | 50.9843 | 50.9327 | 50.881 | 50.8293 | 50.7777 | 50.726 | 50.6743 | 50.6227 | 50.571 | 50.5193 | 50.4677 | 50.416
7.15 | 0 | 17.65 | 28.986 | 31.245 | 37.552 | 43.783 | 48.812 | 51.589 | 52.639 | 52.639 | 51.064 | 0 | 1.765 | 3.53 | 5.295 | 7.06 | 8.825 | 10.59 | 12.355 | 14.12 | 15.885 | 17.65 | 19.9172 | 22.1844 | 24.4516 | 26.7188 | 28.986 | 29.4378 | 29.8896 | 30.3414 | 30.7932 | 31.245 | 31.8757 | 32.5064 | 33.1371 | 33.7678 | 34.3985 | 35.0292 | 35.6599 | 36.2906 | 36.9213 | 37.552 | 37.9674 | 38.3828 | 38.7982 | 39.2136 | 39.629 | 40.0444 | 40.4598 | 40.8752 | 41.2906 | 41.706 | 42.1214 | 42.5368 | 42.9522 | 43.3676 | 43.783 | 44.1183 | 44.4535 | 44.7888 | 45.1241 | 45.4593 | 45.7946 | 46.1299 | 46.4651 | 46.8004 | 47.1357 | 47.4709 | 47.8062 | 48.1415 | 48.4767 | 48.812 | 48.9046 | 48.9971 | 49.0897 | 49.1823 | 49.2748 | 49.3674 | 49.46 | 49.5525 | 49.6451 | 49.7377 | 49.8302 | 49.9228 | 50.0154 | 50.1079 | 50.2005 | 50.2931 | 50.3856 | 50.4782 | 50.5708 | 50.6633 | 50.7559 | 50.8485 | 50.941 | 51.0336 | 51.1262 | 51.2187 | 51.3113 | 51.4039 | 51.4964 | 51.589 | 51.624 | 51.659 | 51.694 | 51.729 | 51.764 | 51.799 | 51.834 | 51.869 | 51.904 | 51.939 | 51.974 | 52.009 | 52.044 | 52.079 | 52.114 | 52.149 | 52.184 | 52.219 | 52.254 | 52.289 | 52.324 | 52.359 | 52.394 | 52.429 | 52.464 | 52.499 | 52.534 | 52.569 | 52.604 | 52.639 | 52.639 | 52.639 | 52.639 | 52.639 | 52.639 | 52.639 | 52.639 | 52.639 | 52.639 | 52.639 | 52.639 | 52.639 | 52.639 | 52.639 | 52.639 | 52.639 | 52.639 | 52.639 | 52.639 | 52.639 | 52.639 | 52.639 | 52.639 | 52.639 | 52.639 | 52.639 | 52.639 | 52.639 | 52.639 | 52.639 | 52.5865 | 52.534 | 52.4815 | 52.429 | 52.3765 | 52.324 | 52.2715 | 52.219 | 52.1665 | 52.114 | 52.0615 | 52.009 | 51.9565 | 51.904 | 51.8515 | 51.799 | 51.7465 | 51.694 | 51.6415 | 51.589 | 51.5365 | 51.484 | 51.4315 | 51.379 | 51.3265 | 51.274 | 51.2215 | 51.169 | 51.1165 | 51.064
7.2 | 0 | 17.8667 | 29.3547 | 31.6267 | 38.016 | 44.3307 | 49.4293 | 52.2453 | 53.312 | 53.312 | 51.712 | 0 | 1.7867 | 3.5733 | 5.36 | 7.1467 | 8.9333 | 10.72 | 12.5067 | 14.2933 | 16.08 | 17.8667 | 20.1643 | 22.4619 | 24.7595 | 27.0571 | 29.3547 | 29.8091 | 30.2635 | 30.7179 | 31.1723 | 31.6267 | 32.2656 | 32.9045 | 33.5435 | 34.1824 | 34.8213 | 35.4603 | 36.0992 | 36.7381 | 37.3771 | 38.016 | 38.437 | 38.858 | 39.2789 | 39.6999 | 40.1209 | 40.5419 | 40.9628 | 41.3838 | 41.8048 | 42.2258 | 42.6468 | 43.0677 | 43.4887 | 43.9097 | 44.3307 | 44.6706 | 45.0105 | 45.3504 | 45.6903 | 46.0302 | 46.3701 | 46.71 | 47.05 | 47.3899 | 47.7298 | 48.0697 | 48.4096 | 48.7495 | 49.0894 | 49.4293 | 49.5232 | 49.6171 | 49.7109 | 49.8048 | 49.8987 | 49.9925 | 50.0864 | 50.1803 | 50.2741 | 50.368 | 50.4619 | 50.5557 | 50.6496 | 50.7435 | 50.8373 | 50.9312 | 51.0251 | 51.1189 | 51.2128 | 51.3067 | 51.4005 | 51.4944 | 51.5883 | 51.6821 | 51.776 | 51.8699 | 51.9637 | 52.0576 | 52.1515 | 52.2453 | 52.2809 | 52.3164 | 52.352 | 52.3876 | 52.4231 | 52.4587 | 52.4942 | 52.5298 | 52.5653 | 52.6009 | 52.6364 | 52.672 | 52.7076 | 52.7431 | 52.7787 | 52.8142 | 52.8498 | 52.8853 | 52.9209 | 52.9564 | 52.992 | 53.0276 | 53.0631 | 53.0987 | 53.1342 | 53.1698 | 53.2053 | 53.2409 | 53.2764 | 53.312 | 53.312 | 53.312 | 53.312 | 53.312 | 53.312 | 53.312 | 53.312 | 53.312 | 53.312 | 53.312 | 53.312 | 53.312 | 53.312 | 53.312 | 53.312 | 53.312 | 53.312 | 53.312 | 53.312 | 53.312 | 53.312 | 53.312 | 53.312 | 53.312 | 53.312 | 53.312 | 53.312 | 53.312 | 53.312 | 53.312 | 53.2587 | 53.2053 | 53.152 | 53.0987 | 53.0453 | 52.992 | 52.9387 | 52.8853 | 52.832 | 52.7787 | 52.7253 | 52.672 | 52.6187 | 52.5653 | 52.512 | 52.4587 | 52.4053 | 52.352 | 52.2987 | 52.2453 | 52.192 | 52.1387 | 52.0853 | 52.032 | 51.9787 | 51.9253 | 51.872 | 51.8187 | 51.7653 | 51.712
7.25 | 0 | 18.0833 | 29.7233 | 32.0083 | 38.48 | 44.8783 | 50.0467 | 52.9017 | 53.985 | 53.985 | 52.36 | 0 | 1.8083 | 3.6167 | 5.425 | 7.2333 | 9.0417 | 10.85 | 12.6583 | 14.4667 | 16.275 | 18.0833 | 20.4113 | 22.7393 | 25.0673 | 27.3953 | 29.7233 | 30.1803 | 30.6373 | 31.0943 | 31.5513 | 32.0083 | 32.6555 | 33.3027 | 33.9498 | 34.597 | 35.2442 | 35.8913 | 36.5385 | 37.1857 | 37.8328 | 38.48 | 38.9066 | 39.3331 | 39.7597 | 40.1862 | 40.6128 | 41.0393 | 41.4659 | 41.8924 | 42.319 | 42.7456 | 43.1721 | 43.5987 | 44.0252 | 44.4518 | 44.8783 | 45.2229 | 45.5674 | 45.912 | 46.2566 | 46.6011 | 46.9457 | 47.2902 | 47.6348 | 47.9793 | 48.3239 | 48.6684 | 49.013 | 49.3576 | 49.7021 | 50.0467 | 50.1418 | 50.237 | 50.3322 | 50.4273 | 50.5225 | 50.6177 | 50.7128 | 50.808 | 50.9032 | 50.9983 | 51.0935 | 51.1887 | 51.2838 | 51.379 | 51.4742 | 51.5693 | 51.6645 | 51.7597 | 51.8548 | 51.95 | 52.0452 | 52.1403 | 52.2355 | 52.3307 | 52.4258 | 52.521 | 52.6162 | 52.7113 | 52.8065 | 52.9017 | 52.9378 | 52.9739 | 53.01 | 53.0461 | 53.0822 | 53.1183 | 53.1544 | 53.1906 | 53.2267 | 53.2628 | 53.2989 | 53.335 | 53.3711 | 53.4072 | 53.4433 | 53.4794 | 53.5156 | 53.5517 | 53.5878 | 53.6239 | 53.66 | 53.6961 | 53.7322 | 53.7683 | 53.8044 | 53.8406 | 53.8767 | 53.9128 | 53.9489 | 53.985 | 53.985 | 53.985 | 53.985 | 53.985 | 53.985 | 53.985 | 53.985 | 53.985 | 53.985 | 53.985 | 53.985 | 53.985 | 53.985 | 53.985 | 53.985 | 53.985 | 53.985 | 53.985 | 53.985 | 53.985 | 53.985 | 53.985 | 53.985 | 53.985 | 53.985 | 53.985 | 53.985 | 53.985 | 53.985 | 53.985 | 53.9308 | 53.8767 | 53.8225 | 53.7683 | 53.7142 | 53.66 | 53.6058 | 53.5517 | 53.4975 | 53.4433 | 53.3892 | 53.335 | 53.2808 | 53.2267 | 53.1725 | 53.1183 | 53.0642 | 53.01 | 52.9558 | 52.9017 | 52.8475 | 52.7933 | 52.7392 | 52.685 | 52.6308 | 52.5767 | 52.5225 | 52.4683 | 52.4142 | 52.36
7.3 | 0 | 18.3 | 30.092 | 32.39 | 38.944 | 45.426 | 50.664 | 53.558 | 54.658 | 54.658 | 53.008 | 0 | 1.83 | 3.66 | 5.49 | 7.32 | 9.15 | 10.98 | 12.81 | 14.64 | 16.47 | 18.3 | 20.6584 | 23.0168 | 25.3752 | 27.7336 | 30.092 | 30.5516 | 31.0112 | 31.4708 | 31.9304 | 32.39 | 33.0454 | 33.7008 | 34.3562 | 35.0116 | 35.667 | 36.3224 | 36.9778 | 37.6332 | 38.2886 | 38.944 | 39.3761 | 39.8083 | 40.2404 | 40.6725 | 41.1047 | 41.5368 | 41.9689 | 42.4011 | 42.8332 | 43.2653 | 43.6975 | 44.1296 | 44.5617 | 44.9939 | 45.426 | 45.7752 | 46.1244 | 46.4736 | 46.8228 | 47.172 | 47.5212 | 47.8704 | 48.2196 | 48.5688 | 48.918 | 49.2672 | 49.6164 | 49.9656 | 50.3148 | 50.664 | 50.7605 | 50.8569 | 50.9534 | 51.0499 | 51.1463 | 51.2428 | 51.3393 | 51.4357 | 51.5322 | 51.6287 | 51.7251 | 51.8216 | 51.9181 | 52.0145 | 52.111 | 52.2075 | 52.3039 | 52.4004 | 52.4969 | 52.5933 | 52.6898 | 52.7863 | 52.8827 | 52.9792 | 53.0757 | 53.1721 | 53.2686 | 53.3651 | 53.4615 | 53.558 | 53.5947 | 53.6313 | 53.668 | 53.7047 | 53.7413 | 53.778 | 53.8147 | 53.8513 | 53.888 | 53.9247 | 53.9613 | 53.998 | 54.0347 | 54.0713 | 54.108 | 54.1447 | 54.1813 | 54.218 | 54.2547 | 54.2913 | 54.328 | 54.3647 | 54.4013 | 54.438 | 54.4747 | 54.5113 | 54.548 | 54.5847 | 54.6213 | 54.658 | 54.658 | 54.658 | 54.658 | 54.658 | 54.658 | 54.658 | 54.658 | 54.658 | 54.658 | 54.658 | 54.658 | 54.658 | 54.658 | 54.658 | 54.658 | 54.658 | 54.658 | 54.658 | 54.658 | 54.658 | 54.658 | 54.658 | 54.658 | 54.658 | 54.658 | 54.658 | 54.658 | 54.658 | 54.658 | 54.658 | 54.603 | 54.548 | 54.493 | 54.438 | 54.383 | 54.328 | 54.273 | 54.218 | 54.163 | 54.108 | 54.053 | 53.998 | 53.943 | 53.888 | 53.833 | 53.778 | 53.723 | 53.668 | 53.613 | 53.558 | 53.503 | 53.448 | 53.393 | 53.338 | 53.283 | 53.228 | 53.173 | 53.118 | 53.063 | 53.008
7.35 | 0 | 18.5167 | 30.4607 | 32.7717 | 39.408 | 45.9737 | 51.2813 | 54.2143 | 55.331 | 55.331 | 53.656 | 0 | 1.8517 | 3.7033 | 5.555 | 7.4067 | 9.2583 | 11.11 | 12.9617 | 14.8133 | 16.665 | 18.5167 | 20.9055 | 23.2943 | 25.6831 | 28.0719 | 30.4607 | 30.9229 | 31.3851 | 31.8473 | 32.3095 | 32.7717 | 33.4353 | 34.0989 | 34.7626 | 35.4262 | 36.0898 | 36.7535 | 37.4171 | 38.0807 | 38.7444 | 39.408 | 39.8457 | 40.2834 | 40.7211 | 41.1588 | 41.5966 | 42.0343 | 42.472 | 42.9097 | 43.3474 | 43.7851 | 44.2228 | 44.6605 | 45.0982 | 45.536 | 45.9737 | 46.3275 | 46.6814 | 47.0352 | 47.389 | 47.7429 | 48.0967 | 48.4506 | 48.8044 | 49.1583 | 49.5121 | 49.866 | 50.2198 | 50.5736 | 50.9275 | 51.2813 | 51.3791 | 51.4769 | 51.5746 | 51.6724 | 51.7702 | 51.8679 | 51.9657 | 52.0635 | 52.1612 | 52.259 | 52.3568 | 52.4545 | 52.5523 | 52.6501 | 52.7478 | 52.8456 | 52.9434 | 53.0411 | 53.1389 | 53.2367 | 53.3344 | 53.4322 | 53.53 | 53.6277 | 53.7255 | 53.8233 | 53.921 | 54.0188 | 54.1166 | 54.2143 | 54.2516 | 54.2888 | 54.326 | 54.3632 | 54.4004 | 54.4377 | 54.4749 | 54.5121 | 54.5493 | 54.5866 | 54.6238 | 54.661 | 54.6982 | 54.7354 | 54.7727 | 54.8099 | 54.8471 | 54.8843 | 54.9216 | 54.9588 | 54.996 | 55.0332 | 55.0704 | 55.1077 | 55.1449 | 55.1821 | 55.2193 | 55.2566 | 55.2938 | 55.331 | 55.331 | 55.331 | 55.331 | 55.331 | 55.331 | 55.331 | 55.331 | 55.331 | 55.331 | 55.331 | 55.331 | 55.331 | 55.331 | 55.331 | 55.331 | 55.331 | 55.331 | 55.331 | 55.331 | 55.331 | 55.331 | 55.331 | 55.331 | 55.331 | 55.331 | 55.331 | 55.331 | 55.331 | 55.331 | 55.331 | 55.2752 | 55.2193 | 55.1635 | 55.1077 | 55.0518 | 54.996 | 54.9402 | 54.8843 | 54.8285 | 54.7727 | 54.7168 | 54.661 | 54.6052 | 54.5493 | 54.4935 | 54.4377 | 54.3818 | 54.326 | 54.2702 | 54.2143 | 54.1585 | 54.1027 | 54.0468 | 53.991 | 53.9352 | 53.8793 | 53.8235 | 53.7677 | 53.7118 | 53.656
7.4 | 0 | 18.7333 | 30.8293 | 33.1533 | 39.872 | 46.5213 | 51.8987 | 54.8707 | 56.004 | 56.004 | 54.304 | 0 | 1.8733 | 3.7467 | 5.62 | 7.4933 | 9.3667 | 11.24 | 13.1133 | 14.9867 | 16.86 | 18.7333 | 21.1525 | 23.5717 | 25.9909 | 28.4101 | 30.8293 | 31.2941 | 31.7589 | 32.2237 | 32.6885 | 33.1533 | 33.8252 | 34.4971 | 35.1689 | 35.8408 | 36.5127 | 37.1845 | 37.8564 | 38.5283 | 39.2001 | 39.872 | 40.3153 | 40.7586 | 41.2019 | 41.6452 | 42.0884 | 42.5317 | 42.975 | 43.4183 | 43.8616 | 44.3049 | 44.7482 | 45.1915 | 45.6348 | 46.078 | 46.5213 | 46.8798 | 47.2383 | 47.5968 | 47.9553 | 48.3138 | 48.6723 | 49.0308 | 49.3892 | 49.7477 | 50.1062 | 50.4647 | 50.8232 | 51.1817 | 51.5402 | 51.8987 | 51.9977 | 52.0968 | 52.1959 | 52.2949 | 52.394 | 52.4931 | 52.5921 | 52.6912 | 52.7903 | 52.8893 | 52.9884 | 53.0875 | 53.1865 | 53.2856 | 53.3847 | 53.4837 | 53.5828 | 53.6819 | 53.7809 | 53.88 | 53.9791 | 54.0781 | 54.1772 | 54.2763 | 54.3753 | 54.4744 | 54.5735 | 54.6725 | 54.7716 | 54.8707 | 54.9084 | 54.9462 | 54.984 | 55.0218 | 55.0596 | 55.0973 | 55.1351 | 55.1729 | 55.2107 | 55.2484 | 55.2862 | 55.324 | 55.3618 | 55.3996 | 55.4373 | 55.4751 | 55.5129 | 55.5507 | 55.5884 | 55.6262 | 55.664 | 55.7018 | 55.7396 | 55.7773 | 55.8151 | 55.8529 | 55.8907 | 55.9284 | 55.9662 | 56.004 | 56.004 | 56.004 | 56.004 | 56.004 | 56.004 | 56.004 | 56.004 | 56.004 | 56.004 | 56.004 | 56.004 | 56.004 | 56.004 | 56.004 | 56.004 | 56.004 | 56.004 | 56.004 | 56.004 | 56.004 | 56.004 | 56.004 | 56.004 | 56.004 | 56.004 | 56.004 | 56.004 | 56.004 | 56.004 | 56.004 | 55.9473 | 55.8907 | 55.834 | 55.7773 | 55.7207 | 55.664 | 55.6073 | 55.5507 | 55.494 | 55.4373 | 55.3807 | 55.324 | 55.2673 | 55.2107 | 55.154 | 55.0973 | 55.0407 | 54.984 | 54.9273 | 54.8707 | 54.814 | 54.7573 | 54.7007 | 54.644 | 54.5873 | 54.5307 | 54.474 | 54.4173 | 54.3607 | 54.304
7.45 | 0 | 18.95 | 31.198 | 33.535 | 40.336 | 47.069 | 52.516 | 55.527 | 56.677 | 56.677 | 54.952 | 0 | 1.895 | 3.79 | 5.685 | 7.58 | 9.475 | 11.37 | 13.265 | 15.16 | 17.055 | 18.95 | 21.3996 | 23.8492 | 26.2988 | 28.7484 | 31.198 | 31.6654 | 32.1328 | 32.6002 | 33.0676 | 33.535 | 34.2151 | 34.8952 | 35.5753 | 36.2554 | 36.9355 | 37.6156 | 38.2957 | 38.9758 | 39.6559 | 40.336 | 40.7849 | 41.2337 | 41.6826 | 42.1315 | 42.5803 | 43.0292 | 43.4781 | 43.9269 | 44.3758 | 44.8247 | 45.2735 | 45.7224 | 46.1713 | 46.6201 | 47.069 | 47.4321 | 47.7953 | 48.1584 | 48.5215 | 48.8847 | 49.2478 | 49.6109 | 49.9741 | 50.3372 | 50.7003 | 51.0635 | 51.4266 | 51.7897 | 52.1529 | 52.516 | 52.6164 | 52.7167 | 52.8171 | 52.9175 | 53.0178 | 53.1182 | 53.2186 | 53.3189 | 53.4193 | 53.5197 | 53.62 | 53.7204 | 53.8208 | 53.9211 | 54.0215 | 54.1219 | 54.2222 | 54.3226 | 54.423 | 54.5233 | 54.6237 | 54.7241 | 54.8244 | 54.9248 | 55.0252 | 55.1255 | 55.2259 | 55.3263 | 55.4266 | 55.527 | 55.5653 | 55.6037 | 55.642 | 55.6803 | 55.7187 | 55.757 | 55.7953 | 55.8337 | 55.872 | 55.9103 | 55.9487 | 55.987 | 56.0253 | 56.0637 | 56.102 | 56.1403 | 56.1787 | 56.217 | 56.2553 | 56.2937 | 56.332 | 56.3703 | 56.4087 | 56.447 | 56.4853 | 56.5237 | 56.562 | 56.6003 | 56.6387 | 56.677 | 56.677 | 56.677 | 56.677 | 56.677 | 56.677 | 56.677 | 56.677 | 56.677 | 56.677 | 56.677 | 56.677 | 56.677 | 56.677 | 56.677 | 56.677 | 56.677 | 56.677 | 56.677 | 56.677 | 56.677 | 56.677 | 56.677 | 56.677 | 56.677 | 56.677 | 56.677 | 56.677 | 56.677 | 56.677 | 56.677 | 56.6195 | 56.562 | 56.5045 | 56.447 | 56.3895 | 56.332 | 56.2745 | 56.217 | 56.1595 | 56.102 | 56.0445 | 55.987 | 55.9295 | 55.872 | 55.8145 | 55.757 | 55.6995 | 55.642 | 55.5845 | 55.527 | 55.4695 | 55.412 | 55.3545 | 55.297 | 55.2395 | 55.182 | 55.1245 | 55.067 | 55.0095 | 54.952
7.5 | 0 | 19.1667 | 31.5667 | 33.9167 | 40.8 | 47.6167 | 53.1333 | 56.1833 | 57.35 | 57.35 | 55.6 | -1.7764e-15 | 1.9167 | 3.8333 | 5.75 | 7.6667 | 9.5833 | 11.5 | 13.4167 | 15.3333 | 17.25 | 19.1667 | 21.6467 | 24.1267 | 26.6067 | 29.0867 | 31.5667 | 32.0367 | 32.5067 | 32.9767 | 33.4467 | 33.9167 | 34.605 | 35.2933 | 35.9817 | 36.67 | 37.3583 | 38.0467 | 38.735 | 39.4233 | 40.1117 | 40.8 | 41.2544 | 41.7089 | 42.1633 | 42.6178 | 43.0722 | 43.5267 | 43.9811 | 44.4356 | 44.89 | 45.3444 | 45.7989 | 46.2533 | 46.7078 | 47.1622 | 47.6167 | 47.9844 | 48.3522 | 48.72 | 49.0878 | 49.4556 | 49.8233 | 50.1911 | 50.5589 | 50.9267 | 51.2944 | 51.6622 | 52.03 | 52.3978 | 52.7656 | 53.1333 | 53.235 | 53.3367 | 53.4383 | 53.54 | 53.6417 | 53.7433 | 53.845 | 53.9467 | 54.0483 | 54.15 | 54.2517 | 54.3533 | 54.455 | 54.5567 | 54.6583 | 54.76 | 54.8617 | 54.9633 | 55.065 | 55.1667 | 55.2683 | 55.37 | 55.4717 | 55.5733 | 55.675 | 55.7767 | 55.8783 | 55.98 | 56.0817 | 56.1833 | 56.2222 | 56.2611 | 56.3 | 56.3389 | 56.3778 | 56.4167 | 56.4556 | 56.4944 | 56.5333 | 56.5722 | 56.6111 | 56.65 | 56.6889 | 56.7278 | 56.7667 | 56.8056 | 56.8444 | 56.8833 | 56.9222 | 56.9611 | 57 | 57.0389 | 57.0778 | 57.1167 | 57.1556 | 57.1944 | 57.2333 | 57.2722 | 57.3111 | 57.35 | 57.35 | 57.35 | 57.35 | 57.35 | 57.35 | 57.35 | 57.35 | 57.35 | 57.35 | 57.35 | 57.35 | 57.35 | 57.35 | 57.35 | 57.35 | 57.35 | 57.35 | 57.35 | 57.35 | 57.35 | 57.35 | 57.35 | 57.35 | 57.35 | 57.35 | 57.35 | 57.35 | 57.35 | 57.35 | 57.35 | 57.2917 | 57.2333 | 57.175 | 57.1167 | 57.0583 | 57 | 56.9417 | 56.8833 | 56.825 | 56.7667 | 56.7083 | 56.65 | 56.5917 | 56.5333 | 56.475 | 56.4167 | 56.3583 | 56.3 | 56.2417 | 56.1833 | 56.125 | 56.0667 | 56.0083 | 55.95 | 55.8917 | 55.8333 | 55.775 | 55.7167 | 55.6583 | 55.6
7.55 | 0 | 19.3833 | 31.9353 | 34.2983 | 41.264 | 48.1643 | 53.7507 | 56.8397 | 58.023 | 58.023 | 56.248 | 0 | 1.9383 | 3.8767 | 5.815 | 7.7533 | 9.6917 | 11.63 | 13.5683 | 15.5067 | 17.445 | 19.3833 | 21.8937 | 24.4041 | 26.9145 | 29.4249 | 31.9353 | 32.4079 | 32.8805 | 33.3531 | 33.8257 | 34.2983 | 34.9949 | 35.6915 | 36.388 | 37.0846 | 37.7812 | 38.4777 | 39.1743 | 39.8709 | 40.5674 | 41.264 | 41.724 | 42.184 | 42.6441 | 43.1041 | 43.5641 | 44.0241 | 44.4842 | 44.9442 | 45.4042 | 45.8642 | 46.3242 | 46.7843 | 47.2443 | 47.7043 | 48.1643 | 48.5368 | 48.9092 | 49.2816 | 49.654 | 50.0264 | 50.3989 | 50.7713 | 51.1437 | 51.5161 | 51.8886 | 52.261 | 52.6334 | 53.0058 | 53.3782 | 53.7507 | 53.8536 | 53.9566 | 54.0596 | 54.1625 | 54.2655 | 54.3685 | 54.4714 | 54.5744 | 54.6774 | 54.7803 | 54.8833 | 54.9863 | 55.0892 | 55.1922 | 55.2952 | 55.3981 | 55.5011 | 55.6041 | 55.707 | 55.81 | 55.913 | 56.0159 | 56.1189 | 56.2219 | 56.3248 | 56.4278 | 56.5308 | 56.6337 | 56.7367 | 56.8397 | 56.8791 | 56.9186 | 56.958 | 56.9974 | 57.0369 | 57.0763 | 57.1158 | 57.1552 | 57.1947 | 57.2341 | 57.2736 | 57.313 | 57.3524 | 57.3919 | 57.4313 | 57.4708 | 57.5102 | 57.5497 | 57.5891 | 57.6286 | 57.668 | 57.7074 | 57.7469 | 57.7863 | 57.8258 | 57.8652 | 57.9047 | 57.9441 | 57.9836 | 58.023 | 58.023 | 58.023 | 58.023 | 58.023 | 58.023 | 58.023 | 58.023 | 58.023 | 58.023 | 58.023 | 58.023 | 58.023 | 58.023 | 58.023 | 58.023 | 58.023 | 58.023 | 58.023 | 58.023 | 58.023 | 58.023 | 58.023 | 58.023 | 58.023 | 58.023 | 58.023 | 58.023 | 58.023 | 58.023 | 58.023 | 57.9638 | 57.9047 | 57.8455 | 57.7863 | 57.7272 | 57.668 | 57.6088 | 57.5497 | 57.4905 | 57.4313 | 57.3722 | 57.313 | 57.2538 | 57.1947 | 57.1355 | 57.0763 | 57.0172 | 56.958 | 56.8988 | 56.8397 | 56.7805 | 56.7213 | 56.6622 | 56.603 | 56.5438 | 56.4847 | 56.4255 | 56.3663 | 56.3072 | 56.248
7.6 | 0 | 19.6 | 32.304 | 34.68 | 41.728 | 48.712 | 54.368 | 57.496 | 58.696 | 58.696 | 56.896 | 0 | 1.96 | 3.92 | 5.88 | 7.84 | 9.8 | 11.76 | 13.72 | 15.68 | 17.64 | 19.6 | 22.1408 | 24.6816 | 27.2224 | 29.7632 | 32.304 | 32.7792 | 33.2544 | 33.7296 | 34.2048 | 34.68 | 35.3848 | 36.0896 | 36.7944 | 37.4992 | 38.204 | 38.9088 | 39.6136 | 40.3184 | 41.0232 | 41.728 | 42.1936 | 42.6592 | 43.1248 | 43.5904 | 44.056 | 44.5216 | 44.9872 | 45.4528 | 45.9184 | 46.384 | 46.8496 | 47.3152 | 47.7808 | 48.2464 | 48.712 | 49.0891 | 49.4661 | 49.8432 | 50.2203 | 50.5973 | 50.9744 | 51.3515 | 51.7285 | 52.1056 | 52.4827 | 52.8597 | 53.2368 | 53.6139 | 53.9909 | 54.368 | 54.4723 | 54.5765 | 54.6808 | 54.7851 | 54.8893 | 54.9936 | 55.0979 | 55.2021 | 55.3064 | 55.4107 | 55.5149 | 55.6192 | 55.7235 | 55.8277 | 55.932 | 56.0363 | 56.1405 | 56.2448 | 56.3491 | 56.4533 | 56.5576 | 56.6619 | 56.7661 | 56.8704 | 56.9747 | 57.0789 | 57.1832 | 57.2875 | 57.3917 | 57.496 | 57.536 | 57.576 | 57.616 | 57.656 | 57.696 | 57.736 | 57.776 | 57.816 | 57.856 | 57.896 | 57.936 | 57.976 | 58.016 | 58.056 | 58.096 | 58.136 | 58.176 | 58.216 | 58.256 | 58.296 | 58.336 | 58.376 | 58.416 | 58.456 | 58.496 | 58.536 | 58.576 | 58.616 | 58.656 | 58.696 | 58.696 | 58.696 | 58.696 | 58.696 | 58.696 | 58.696 | 58.696 | 58.696 | 58.696 | 58.696 | 58.696 | 58.696 | 58.696 | 58.696 | 58.696 | 58.696 | 58.696 | 58.696 | 58.696 | 58.696 | 58.696 | 58.696 | 58.696 | 58.696 | 58.696 | 58.696 | 58.696 | 58.696 | 58.696 | 58.696 | 58.636 | 58.576 | 58.516 | 58.456 | 58.396 | 58.336 | 58.276 | 58.216 | 58.156 | 58.096 | 58.036 | 57.976 | 57.916 | 57.856 | 57.796 | 57.736 | 57.676 | 57.616 | 57.556 | 57.496 | 57.436 | 57.376 | 57.316 | 57.256 | 57.196 | 57.136 | 57.076 | 57.016 | 56.956 | 56.896
7.65 | 0 | 19.8167 | 32.6727 | 35.0617 | 42.192 | 49.2597 | 54.9853 | 58.1523 | 59.369 | 59.369 | 57.544 | 1.7764e-15 | 1.9817 | 3.9633 | 5.945 | 7.9267 | 9.9083 | 11.89 | 13.8717 | 15.8533 | 17.835 | 19.8167 | 22.3879 | 24.9591 | 27.5303 | 30.1015 | 32.6727 | 33.1505 | 33.6283 | 34.1061 | 34.5839 | 35.0617 | 35.7747 | 36.4877 | 37.2008 | 37.9138 | 38.6268 | 39.3399 | 40.0529 | 40.7659 | 41.479 | 42.192 | 42.6632 | 43.1344 | 43.6055 | 44.0767 | 44.5479 | 45.0191 | 45.4902 | 45.9614 | 46.4326 | 46.9038 | 47.375 | 47.8461 | 48.3173 | 48.7885 | 49.2597 | 49.6414 | 50.0231 | 50.4048 | 50.7865 | 51.1682 | 51.5499 | 51.9316 | 52.3134 | 52.6951 | 53.0768 | 53.4585 | 53.8402 | 54.2219 | 54.6036 | 54.9853 | 55.0909 | 55.1965 | 55.302 | 55.4076 | 55.5132 | 55.6187 | 55.7243 | 55.8299 | 55.9354 | 56.041 | 56.1466 | 56.2521 | 56.3577 | 56.4633 | 56.5688 | 56.6744 | 56.78 | 56.8855 | 56.9911 | 57.0967 | 57.2022 | 57.3078 | 57.4134 | 57.5189 | 57.6245 | 57.7301 | 57.8356 | 57.9412 | 58.0468 | 58.1523 | 58.1929 | 58.2334 | 58.274 | 58.3146 | 58.3551 | 58.3957 | 58.4362 | 58.4768 | 58.5173 | 58.5579 | 58.5984 | 58.639 | 58.6796 | 58.7201 | 58.7607 | 58.8012 | 58.8418 | 58.8823 | 58.9229 | 58.9634 | 59.004 | 59.0446 | 59.0851 | 59.1257 | 59.1662 | 59.2068 | 59.2473 | 59.2879 | 59.3284 | 59.369 | 59.369 | 59.369 | 59.369 | 59.369 | 59.369 | 59.369 | 59.369 | 59.369 | 59.369 | 59.369 | 59.369 | 59.369 | 59.369 | 59.369 | 59.369 | 59.369 | 59.369 | 59.369 | 59.369 | 59.369 | 59.369 | 59.369 | 59.369 | 59.369 | 59.369 | 59.369 | 59.369 | 59.369 | 59.369 | 59.369 | 59.3082 | 59.2473 | 59.1865 | 59.1257 | 59.0648 | 59.004 | 58.9432 | 58.8823 | 58.8215 | 58.7607 | 58.6998 | 58.639 | 58.5782 | 58.5173 | 58.4565 | 58.3957 | 58.3348 | 58.274 | 58.2132 | 58.1523 | 58.0915 | 58.0307 | 57.9698 | 57.909 | 57.8482 | 57.7873 | 57.7265 | 57.6657 | 57.6048 | 57.544
7.7 | 0 | 20.0333 | 33.0413 | 35.4433 | 42.656 | 49.8073 | 55.6027 | 58.8087 | 60.042 | 60.042 | 58.192 | 0 | 2.0033 | 4.0067 | 6.01 | 8.0133 | 10.0167 | 12.02 | 14.0233 | 16.0267 | 18.03 | 20.0333 | 22.6349 | 25.2365 | 27.8381 | 30.4397 | 33.0413 | 33.5217 | 34.0021 | 34.4825 | 34.9629 | 35.4433 | 36.1646 | 36.8859 | 37.6071 | 38.3284 | 39.0497 | 39.7709 | 40.4922 | 41.2135 | 41.9347 | 42.656 | 43.1328 | 43.6095 | 44.0863 | 44.563 | 45.0398 | 45.5165 | 45.9933 | 46.47 | 46.9468 | 47.4236 | 47.9003 | 48.3771 | 48.8538 | 49.3306 | 49.8073 | 50.1937 | 50.58 | 50.9664 | 51.3528 | 51.7391 | 52.1255 | 52.5118 | 52.8982 | 53.2845 | 53.6709 | 54.0572 | 54.4436 | 54.83 | 55.2163 | 55.6027 | 55.7095 | 55.8164 | 55.9233 | 56.0301 | 56.137 | 56.2439 | 56.3507 | 56.4576 | 56.5645 | 56.6713 | 56.7782 | 56.8851 | 56.9919 | 57.0988 | 57.2057 | 57.3125 | 57.4194 | 57.5263 | 57.6331 | 57.74 | 57.8469 | 57.9537 | 58.0606 | 58.1675 | 58.2743 | 58.3812 | 58.4881 | 58.5949 | 58.7018 | 58.8087 | 58.8498 | 58.8909 | 58.932 | 58.9731 | 59.0142 | 59.0553 | 59.0964 | 59.1376 | 59.1787 | 59.2198 | 59.2609 | 59.302 | 59.3431 | 59.3842 | 59.4253 | 59.4664 | 59.5076 | 59.5487 | 59.5898 | 59.6309 | 59.672 | 59.7131 | 59.7542 | 59.7953 | 59.8364 | 59.8776 | 59.9187 | 59.9598 | 60.0009 | 60.042 | 60.042 | 60.042 | 60.042 | 60.042 | 60.042 | 60.042 | 60.042 | 60.042 | 60.042 | 60.042 | 60.042 | 60.042 | 60.042 | 60.042 | 60.042 | 60.042 | 60.042 | 60.042 | 60.042 | 60.042 | 60.042 | 60.042 | 60.042 | 60.042 | 60.042 | 60.042 | 60.042 | 60.042 | 60.042 | 60.042 | 59.9803 | 59.9187 | 59.857 | 59.7953 | 59.7337 | 59.672 | 59.6103 | 59.5487 | 59.487 | 59.4253 | 59.3637 | 59.302 | 59.2403 | 59.1787 | 59.117 | 59.0553 | 58.9937 | 58.932 | 58.8703 | 58.8087 | 58.747 | 58.6853 | 58.6237 | 58.562 | 58.5003 | 58.4387 | 58.377 | 58.3153 | 58.2537 | 58.192
7.75 | 0 | 20.25 | 33.41 | 35.825 | 43.12 | 50.355 | 56.22 | 59.465 | 60.715 | 60.715 | 58.84 | -1.7764e-15 | 2.025 | 4.05 | 6.075 | 8.1 | 10.125 | 12.15 | 14.175 | 16.2 | 18.225 | 20.25 | 22.882 | 25.514 | 28.146 | 30.778 | 33.41 | 33.893 | 34.376 | 34.859 | 35.342 | 35.825 | 36.5545 | 37.284 | 38.0135 | 38.743 | 39.4725 | 40.202 | 40.9315 | 41.661 | 42.3905 | 43.12 | 43.6023 | 44.0847 | 44.567 | 45.0493 | 45.5317 | 46.014 | 46.4963 | 46.9787 | 47.461 | 47.9433 | 48.4257 | 48.908 | 49.3903 | 49.8727 | 50.355 | 50.746 | 51.137 | 51.528 | 51.919 | 52.31 | 52.701 | 53.092 | 53.483 | 53.874 | 54.265 | 54.656 | 55.047 | 55.438 | 55.829 | 56.22 | 56.3282 | 56.4363 | 56.5445 | 56.6527 | 56.7608 | 56.869 | 56.9772 | 57.0853 | 57.1935 | 57.3017 | 57.4098 | 57.518 | 57.6262 | 57.7343 | 57.8425 | 57.9507 | 58.0588 | 58.167 | 58.2752 | 58.3833 | 58.4915 | 58.5997 | 58.7078 | 58.816 | 58.9242 | 59.0323 | 59.1405 | 59.2487 | 59.3568 | 59.465 | 59.5067 | 59.5483 | 59.59 | 59.6317 | 59.6733 | 59.715 | 59.7567 | 59.7983 | 59.84 | 59.8817 | 59.9233 | 59.965 | 60.0067 | 60.0483 | 60.09 | 60.1317 | 60.1733 | 60.215 | 60.2567 | 60.2983 | 60.34 | 60.3817 | 60.4233 | 60.465 | 60.5067 | 60.5483 | 60.59 | 60.6317 | 60.6733 | 60.715 | 60.715 | 60.715 | 60.715 | 60.715 | 60.715 | 60.715 | 60.715 | 60.715 | 60.715 | 60.715 | 60.715 | 60.715 | 60.715 | 60.715 | 60.715 | 60.715 | 60.715 | 60.715 | 60.715 | 60.715 | 60.715 | 60.715 | 60.715 | 60.715 | 60.715 | 60.715 | 60.715 | 60.715 | 60.715 | 60.715 | 60.6525 | 60.59 | 60.5275 | 60.465 | 60.4025 | 60.34 | 60.2775 | 60.215 | 60.1525 | 60.09 | 60.0275 | 59.965 | 59.9025 | 59.84 | 59.7775 | 59.715 | 59.6525 | 59.59 | 59.5275 | 59.465 | 59.4025 | 59.34 | 59.2775 | 59.215 | 59.1525 | 59.09 | 59.0275 | 58.965 | 58.9025 | 58.84
7.8 | 0 | 20.4667 | 33.7787 | 36.2067 | 43.584 | 50.9027 | 56.8373 | 60.1213 | 61.388 | 61.388 | 59.488 | 0 | 2.0467 | 4.0933 | 6.14 | 8.1867 | 10.2333 | 12.28 | 14.3267 | 16.3733 | 18.42 | 20.4667 | 23.1291 | 25.7915 | 28.4539 | 31.1163 | 33.7787 | 34.2643 | 34.7499 | 35.2355 | 35.7211 | 36.2067 | 36.9444 | 37.6821 | 38.4199 | 39.1576 | 39.8953 | 40.6331 | 41.3708 | 42.1085 | 42.8463 | 43.584 | 44.0719 | 44.5598 | 45.0477 | 45.5356 | 46.0236 | 46.5115 | 46.9994 | 47.4873 | 47.9752 | 48.4631 | 48.951 | 49.4389 | 49.9268 | 50.4148 | 50.9027 | 51.2983 | 51.694 | 52.0896 | 52.4852 | 52.8809 | 53.2765 | 53.6722 | 54.0678 | 54.4635 | 54.8591 | 55.2548 | 55.6504 | 56.046 | 56.4417 | 56.8373 | 56.9468 | 57.0563 | 57.1657 | 57.2752 | 57.3847 | 57.4941 | 57.6036 | 57.7131 | 57.8225 | 57.932 | 58.0415 | 58.1509 | 58.2604 | 58.3699 | 58.4793 | 58.5888 | 58.6983 | 58.8077 | 58.9172 | 59.0267 | 59.1361 | 59.2456 | 59.3551 | 59.4645 | 59.574 | 59.6835 | 59.7929 | 59.9024 | 60.0119 | 60.1213 | 60.1636 | 60.2058 | 60.248 | 60.2902 | 60.3324 | 60.3747 | 60.4169 | 60.4591 | 60.5013 | 60.5436 | 60.5858 | 60.628 | 60.6702 | 60.7124 | 60.7547 | 60.7969 | 60.8391 | 60.8813 | 60.9236 | 60.9658 | 61.008 | 61.0502 | 61.0924 | 61.1347 | 61.1769 | 61.2191 | 61.2613 | 61.3036 | 61.3458 | 61.388 | 61.388 | 61.388 | 61.388 | 61.388 | 61.388 | 61.388 | 61.388 | 61.388 | 61.388 | 61.388 | 61.388 | 61.388 | 61.388 | 61.388 | 61.388 | 61.388 | 61.388 | 61.388 | 61.388 | 61.388 | 61.388 | 61.388 | 61.388 | 61.388 | 61.388 | 61.388 | 61.388 | 61.388 | 61.388 | 61.388 | 61.3247 | 61.2613 | 61.198 | 61.1347 | 61.0713 | 61.008 | 60.9447 | 60.8813 | 60.818 | 60.7547 | 60.6913 | 60.628 | 60.5647 | 60.5013 | 60.438 | 60.3747 | 60.3113 | 60.248 | 60.1847 | 60.1213 | 60.058 | 59.9947 | 59.9313 | 59.868 | 59.8047 | 59.7413 | 59.678 | 59.6147 | 59.5513 | 59.488
7.85 | 0 | 20.6833 | 34.1473 | 36.5883 | 44.048 | 51.4503 | 57.4547 | 60.7777 | 62.061 | 62.061 | 60.136 | 0 | 2.0683 | 4.1367 | 6.205 | 8.2733 | 10.3417 | 12.41 | 14.4783 | 16.5467 | 18.615 | 20.6833 | 23.3761 | 26.0689 | 28.7617 | 31.4545 | 34.1473 | 34.6355 | 35.1237 | 35.6119 | 36.1001 | 36.5883 | 37.3343 | 38.0803 | 38.8262 | 39.5722 | 40.3182 | 41.0641 | 41.8101 | 42.5561 | 43.302 | 44.048 | 44.5415 | 45.035 | 45.5285 | 46.022 | 46.5154 | 47.0089 | 47.5024 | 47.9959 | 48.4894 | 48.9829 | 49.4764 | 49.9699 | 50.4634 | 50.9568 | 51.4503 | 51.8506 | 52.2509 | 52.6512 | 53.0515 | 53.4518 | 53.8521 | 54.2524 | 54.6526 | 55.0529 | 55.4532 | 55.8535 | 56.2538 | 56.6541 | 57.0544 | 57.4547 | 57.5654 | 57.6762 | 57.787 | 57.8977 | 58.0085 | 58.1193 | 58.23 | 58.3408 | 58.4516 | 58.5623 | 58.6731 | 58.7839 | 58.8946 | 59.0054 | 59.1162 | 59.2269 | 59.3377 | 59.4485 | 59.5592 | 59.67 | 59.7808 | 59.8915 | 60.0023 | 60.1131 | 60.2238 | 60.3346 | 60.4454 | 60.5561 | 60.6669 | 60.7777 | 60.8204 | 60.8632 | 60.906 | 60.9488 | 60.9916 | 61.0343 | 61.0771 | 61.1199 | 61.1627 | 61.2054 | 61.2482 | 61.291 | 61.3338 | 61.3766 | 61.4193 | 61.4621 | 61.5049 | 61.5477 | 61.5904 | 61.6332 | 61.676 | 61.7188 | 61.7616 | 61.8043 | 61.8471 | 61.8899 | 61.9327 | 61.9754 | 62.0182 | 62.061 | 62.061 | 62.061 | 62.061 | 62.061 | 62.061 | 62.061 | 62.061 | 62.061 | 62.061 | 62.061 | 62.061 | 62.061 | 62.061 | 62.061 | 62.061 | 62.061 | 62.061 | 62.061 | 62.061 | 62.061 | 62.061 | 62.061 | 62.061 | 62.061 | 62.061 | 62.061 | 62.061 | 62.061 | 62.061 | 62.061 | 61.9968 | 61.9327 | 61.8685 | 61.8043 | 61.7402 | 61.676 | 61.6118 | 61.5477 | 61.4835 | 61.4193 | 61.3552 | 61.291 | 61.2268 | 61.1627 | 61.0985 | 61.0343 | 60.9702 | 60.906 | 60.8418 | 60.7777 | 60.7135 | 60.6493 | 60.5852 | 60.521 | 60.4568 | 60.3927 | 60.3285 | 60.2643 | 60.2002 | 60.136
7.9 | 0 | 20.9 | 34.516 | 36.97 | 44.512 | 51.998 | 58.072 | 61.434 | 62.734 | 62.734 | 60.784 | -1.7764e-15 | 2.09 | 4.18 | 6.27 | 8.36 | 10.45 | 12.54 | 14.63 | 16.72 | 18.81 | 20.9 | 23.6232 | 26.3464 | 29.0696 | 31.7928 | 34.516 | 35.0068 | 35.4976 | 35.9884 | 36.4792 | 36.97 | 37.7242 | 38.4784 | 39.2326 | 39.9868 | 40.741 | 41.4952 | 42.2494 | 43.0036 | 43.7578 | 44.512 | 45.0111 | 45.5101 | 46.0092 | 46.5083 | 47.0073 | 47.5064 | 48.0055 | 48.5045 | 49.0036 | 49.5027 | 50.0017 | 50.5008 | 50.9999 | 51.4989 | 51.998 | 52.4029 | 52.8079 | 53.2128 | 53.6177 | 54.0227 | 54.4276 | 54.8325 | 55.2375 | 55.6424 | 56.0473 | 56.4523 | 56.8572 | 57.2621 | 57.6671 | 58.072 | 58.1841 | 58.2961 | 58.4082 | 58.5203 | 58.6323 | 58.7444 | 58.8565 | 58.9685 | 59.0806 | 59.1927 | 59.3047 | 59.4168 | 59.5289 | 59.6409 | 59.753 | 59.8651 | 59.9771 | 60.0892 | 60.2013 | 60.3133 | 60.4254 | 60.5375 | 60.6495 | 60.7616 | 60.8737 | 60.9857 | 61.0978 | 61.2099 | 61.3219 | 61.434 | 61.4773 | 61.5207 | 61.564 | 61.6073 | 61.6507 | 61.694 | 61.7373 | 61.7807 | 61.824 | 61.8673 | 61.9107 | 61.954 | 61.9973 | 62.0407 | 62.084 | 62.1273 | 62.1707 | 62.214 | 62.2573 | 62.3007 | 62.344 | 62.3873 | 62.4307 | 62.474 | 62.5173 | 62.5607 | 62.604 | 62.6473 | 62.6907 | 62.734 | 62.734 | 62.734 | 62.734 | 62.734 | 62.734 | 62.734 | 62.734 | 62.734 | 62.734 | 62.734 | 62.734 | 62.734 | 62.734 | 62.734 | 62.734 | 62.734 | 62.734 | 62.734 | 62.734 | 62.734 | 62.734 | 62.734 | 62.734 | 62.734 | 62.734 | 62.734 | 62.734 | 62.734 | 62.734 | 62.734 | 62.669 | 62.604 | 62.539 | 62.474 | 62.409 | 62.344 | 62.279 | 62.214 | 62.149 | 62.084 | 62.019 | 61.954 | 61.889 | 61.824 | 61.759 | 61.694 | 61.629 | 61.564 | 61.499 | 61.434 | 61.369 | 61.304 | 61.239 | 61.174 | 61.109 | 61.044 | 60.979 | 60.914 | 60.849 | 60.784
7.95 | 0 | 21.1167 | 34.8847 | 37.3517 | 44.976 | 52.5457 | 58.6893 | 62.0903 | 63.407 | 63.407 | 61.432 | 1.7764e-15 | 2.1117 | 4.2233 | 6.335 | 8.4467 | 10.5583 | 12.67 | 14.7817 | 16.8933 | 19.005 | 21.1167 | 23.8703 | 26.6239 | 29.3775 | 32.1311 | 34.8847 | 35.3781 | 35.8715 | 36.3649 | 36.8583 | 37.3517 | 38.1141 | 38.8765 | 39.639 | 40.4014 | 41.1638 | 41.9263 | 42.6887 | 43.4511 | 44.2136 | 44.976 | 45.4806 | 45.9853 | 46.4899 | 46.9946 | 47.4992 | 48.0039 | 48.5085 | 49.0132 | 49.5178 | 50.0224 | 50.5271 | 51.0317 | 51.5364 | 52.041 | 52.5457 | 52.9552 | 53.3648 | 53.7744 | 54.184 | 54.5936 | 55.0031 | 55.4127 | 55.8223 | 56.2319 | 56.6414 | 57.051 | 57.4606 | 57.8702 | 58.2798 | 58.6893 | 58.8027 | 58.9161 | 59.0294 | 59.1428 | 59.2562 | 59.3695 | 59.4829 | 59.5963 | 59.7096 | 59.823 | 59.9364 | 60.0497 | 60.1631 | 60.2765 | 60.3898 | 60.5032 | 60.6166 | 60.7299 | 60.8433 | 60.9567 | 61.07 | 61.1834 | 61.2968 | 61.4101 | 61.5235 | 61.6369 | 61.7502 | 61.8636 | 61.977 | 62.0903 | 62.1342 | 62.1781 | 62.222 | 62.2659 | 62.3098 | 62.3537 | 62.3976 | 62.4414 | 62.4853 | 62.5292 | 62.5731 | 62.617 | 62.6609 | 62.7048 | 62.7487 | 62.7926 | 62.8364 | 62.8803 | 62.9242 | 62.9681 | 63.012 | 63.0559 | 63.0998 | 63.1437 | 63.1876 | 63.2314 | 63.2753 | 63.3192 | 63.3631 | 63.407 | 63.407 | 63.407 | 63.407 | 63.407 | 63.407 | 63.407 | 63.407 | 63.407 | 63.407 | 63.407 | 63.407 | 63.407 | 63.407 | 63.407 | 63.407 | 63.407 | 63.407 | 63.407 | 63.407 | 63.407 | 63.407 | 63.407 | 63.407 | 63.407 | 63.407 | 63.407 | 63.407 | 63.407 | 63.407 | 63.407 | 63.3412 | 63.2753 | 63.2095 | 63.1437 | 63.0778 | 63.012 | 62.9462 | 62.8803 | 62.8145 | 62.7487 | 62.6828 | 62.617 | 62.5512 | 62.4853 | 62.4195 | 62.3537 | 62.2878 | 62.222 | 62.1562 | 62.0903 | 62.0245 | 61.9587 | 61.8928 | 61.827 | 61.7612 | 61.6953 | 61.6295 | 61.5637 | 61.4978 | 61.432
8 | 0 | 21.3333 | 35.2533 | 37.7333 | 45.44 | 53.0933 | 59.3067 | 62.7467 | 64.08 | 64.08 | 62.08 | 0 | 2.1333 | 4.2667 | 6.4 | 8.5333 | 10.6667 | 12.8 | 14.9333 | 17.0667 | 19.2 | 21.3333 | 24.1173 | 26.9013 | 29.6853 | 32.4693 | 35.2533 | 35.7493 | 36.2453 | 36.7413 | 37.2373 | 37.7333 | 38.504 | 39.2747 | 40.0453 | 40.816 | 41.5867 | 42.3573 | 43.128 | 43.8987 | 44.6693 | 45.44 | 45.9502 | 46.4604 | 46.9707 | 47.4809 | 47.9911 | 48.5013 | 49.0116 | 49.5218 | 50.032 | 50.5422 | 51.0524 | 51.5627 | 52.0729 | 52.5831 | 53.0933 | 53.5076 | 53.9218 | 54.336 | 54.7502 | 55.1644 | 55.5787 | 55.9929 | 56.4071 | 56.8213 | 57.2356 | 57.6498 | 58.064 | 58.4782 | 58.8924 | 59.3067 | 59.4213 | 59.536 | 59.6507 | 59.7653 | 59.88 | 59.9947 | 60.1093 | 60.224 | 60.3387 | 60.4533 | 60.568 | 60.6827 | 60.7973 | 60.912 | 61.0267 | 61.1413 | 61.256 | 61.3707 | 61.4853 | 61.6 | 61.7147 | 61.8293 | 61.944 | 62.0587 | 62.1733 | 62.288 | 62.4027 | 62.5173 | 62.632 | 62.7467 | 62.7911 | 62.8356 | 62.88 | 62.9244 | 62.9689 | 63.0133 | 63.0578 | 63.1022 | 63.1467 | 63.1911 | 63.2356 | 63.28 | 63.3244 | 63.3689 | 63.4133 | 63.4578 | 63.5022 | 63.5467 | 63.5911 | 63.6356 | 63.68 | 63.7244 | 63.7689 | 63.8133 | 63.8578 | 63.9022 | 63.9467 | 63.9911 | 64.0356 | 64.08 | 64.08 | 64.08 | 64.08 | 64.08 | 64.08 | 64.08 | 64.08 | 64.08 | 64.08 | 64.08 | 64.08 | 64.08 | 64.08 | 64.08 | 64.08 | 64.08 | 64.08 | 64.08 | 64.08 | 64.08 | 64.08 | 64.08 | 64.08 | 64.08 | 64.08 | 64.08 | 64.08 | 64.08 | 64.08 | 64.08 | 64.0133 | 63.9467 | 63.88 | 63.8133 | 63.7467 | 63.68 | 63.6133 | 63.5467 | 63.48 | 63.4133 | 63.3467 | 63.28 | 63.2133 | 63.1467 | 63.08 | 63.0133 | 62.9467 | 62.88 | 62.8133 | 62.7467 | 62.68 | 62.6133 | 62.5467 | 62.48 | 62.4133 | 62.3467 | 62.28 | 62.2133 | 62.1467 | 62.08
8.05 | 0 | 21.55 | 35.622 | 38.115 | 45.904 | 53.641 | 59.924 | 63.403 | 64.753 | 64.753 | 62.728 | 0 | 2.155 | 4.31 | 6.465 | 8.62 | 10.775 | 12.93 | 15.085 | 17.24 | 19.395 | 21.55 | 24.3644 | 27.1788 | 29.9932 | 32.8076 | 35.622 | 36.1206 | 36.6192 | 37.1178 | 37.6164 | 38.115 | 38.8939 | 39.6728 | 40.4517 | 41.2306 | 42.0095 | 42.7884 | 43.5673 | 44.3462 | 45.1251 | 45.904 | 46.4198 | 46.9356 | 47.4514 | 47.9672 | 48.483 | 48.9988 | 49.5146 | 50.0304 | 50.5462 | 51.062 | 51.5778 | 52.0936 | 52.6094 | 53.1252 | 53.641 | 54.0599 | 54.4787 | 54.8976 | 55.3165 | 55.7353 | 56.1542 | 56.5731 | 56.9919 | 57.4108 | 57.8297 | 58.2485 | 58.6674 | 59.0863 | 59.5051 | 59.924 | 60.04 | 60.1559 | 60.2719 | 60.3879 | 60.5038 | 60.6198 | 60.7358 | 60.8517 | 60.9677 | 61.0837 | 61.1996 | 61.3156 | 61.4316 | 61.5475 | 61.6635 | 61.7795 | 61.8954 | 62.0114 | 62.1274 | 62.2433 | 62.3593 | 62.4753 | 62.5912 | 62.7072 | 62.8232 | 62.9391 | 63.0551 | 63.1711 | 63.287 | 63.403 | 63.448 | 63.493 | 63.538 | 63.583 | 63.628 | 63.673 | 63.718 | 63.763 | 63.808 | 63.853 | 63.898 | 63.943 | 63.988 | 64.033 | 64.078 | 64.123 | 64.168 | 64.213 | 64.258 | 64.303 | 64.348 | 64.393 | 64.438 | 64.483 | 64.528 | 64.573 | 64.618 | 64.663 | 64.708 | 64.753 | 64.753 | 64.753 | 64.753 | 64.753 | 64.753 | 64.753 | 64.753 | 64.753 | 64.753 | 64.753 | 64.753 | 64.753 | 64.753 | 64.753 | 64.753 | 64.753 | 64.753 | 64.753 | 64.753 | 64.753 | 64.753 | 64.753 | 64.753 | 64.753 | 64.753 | 64.753 | 64.753 | 64.753 | 64.753 | 64.753 | 64.6855 | 64.618 | 64.5505 | 64.483 | 64.4155 | 64.348 | 64.2805 | 64.213 | 64.1455 | 64.078 | 64.0105 | 63.943 | 63.8755 | 63.808 | 63.7405 | 63.673 | 63.6055 | 63.538 | 63.4705 | 63.403 | 63.3355 | 63.268 | 63.2005 | 63.133 | 63.0655 | 62.998 | 62.9305 | 62.863 | 62.7955 | 62.728
8.1 | 0 | 21.7667 | 35.9907 | 38.4967 | 46.368 | 54.1887 | 60.5413 | 64.0593 | 65.426 | 65.426 | 63.376 | 0 | 2.1767 | 4.3533 | 6.53 | 8.7067 | 10.8833 | 13.06 | 15.2367 | 17.4133 | 19.59 | 21.7667 | 24.6115 | 27.4563 | 30.3011 | 33.1459 | 35.9907 | 36.4919 | 36.9931 | 37.4943 | 37.9955 | 38.4967 | 39.2838 | 40.0709 | 40.8581 | 41.6452 | 42.4323 | 43.2195 | 44.0066 | 44.7937 | 45.5809 | 46.368 | 46.8894 | 47.4108 | 47.9321 | 48.4535 | 48.9749 | 49.4963 | 50.0176 | 50.539 | 51.0604 | 51.5818 | 52.1032 | 52.6245 | 53.1459 | 53.6673 | 54.1887 | 54.6122 | 55.0357 | 55.4592 | 55.8827 | 56.3062 | 56.7297 | 57.1532 | 57.5768 | 58.0003 | 58.4238 | 58.8473 | 59.2708 | 59.6943 | 60.1178 | 60.5413 | 60.6586 | 60.7759 | 60.8931 | 61.0104 | 61.1277 | 61.2449 | 61.3622 | 61.4795 | 61.5967 | 61.714 | 61.8313 | 61.9485 | 62.0658 | 62.1831 | 62.3003 | 62.4176 | 62.5349 | 62.6521 | 62.7694 | 62.8867 | 63.0039 | 63.1212 | 63.2385 | 63.3557 | 63.473 | 63.5903 | 63.7075 | 63.8248 | 63.9421 | 64.0593 | 64.1049 | 64.1504 | 64.196 | 64.2416 | 64.2871 | 64.3327 | 64.3782 | 64.4238 | 64.4693 | 64.5149 | 64.5604 | 64.606 | 64.6516 | 64.6971 | 64.7427 | 64.7882 | 64.8338 | 64.8793 | 64.9249 | 64.9704 | 65.016 | 65.0616 | 65.1071 | 65.1527 | 65.1982 | 65.2438 | 65.2893 | 65.3349 | 65.3804 | 65.426 | 65.426 | 65.426 | 65.426 | 65.426 | 65.426 | 65.426 | 65.426 | 65.426 | 65.426 | 65.426 | 65.426 | 65.426 | 65.426 | 65.426 | 65.426 | 65.426 | 65.426 | 65.426 | 65.426 | 65.426 | 65.426 | 65.426 | 65.426 | 65.426 | 65.426 | 65.426 | 65.426 | 65.426 | 65.426 | 65.426 | 65.3577 | 65.2893 | 65.221 | 65.1527 | 65.0843 | 65.016 | 64.9477 | 64.8793 | 64.811 | 64.7427 | 64.6743 | 64.606 | 64.5377 | 64.4693 | 64.401 | 64.3327 | 64.2643 | 64.196 | 64.1277 | 64.0593 | 63.991 | 63.9227 | 63.8543 | 63.786 | 63.7177 | 63.6493 | 63.581 | 63.5127 | 63.4443 | 63.376
8.15 | 0 | 21.9833 | 36.3593 | 38.8783 | 46.832 | 54.7363 | 61.1587 | 64.7157 | 66.099 | 66.099 | 64.024 | 0 | 2.1983 | 4.3967 | 6.595 | 8.7933 | 10.9917 | 13.19 | 15.3883 | 17.5867 | 19.785 | 21.9833 | 24.8585 | 27.7337 | 30.6089 | 33.4841 | 36.3593 | 36.8631 | 37.3669 | 37.8707 | 38.3745 | 38.8783 | 39.6737 | 40.4691 | 41.2644 | 42.0598 | 42.8552 | 43.6505 | 44.4459 | 45.2413 | 46.0366 | 46.832 | 47.359 | 47.8859 | 48.4129 | 48.9398 | 49.4668 | 49.9937 | 50.5207 | 51.0476 | 51.5746 | 52.1016 | 52.6285 | 53.1555 | 53.6824 | 54.2094 | 54.7363 | 55.1645 | 55.5926 | 56.0208 | 56.449 | 56.8771 | 57.3053 | 57.7334 | 58.1616 | 58.5897 | 59.0179 | 59.446 | 59.8742 | 60.3024 | 60.7305 | 61.1587 | 61.2772 | 61.3958 | 61.5144 | 61.6329 | 61.7515 | 61.8701 | 61.9886 | 62.1072 | 62.2258 | 62.3443 | 62.4629 | 62.5815 | 62.7 | 62.8186 | 62.9372 | 63.0557 | 63.1743 | 63.2929 | 63.4114 | 63.53 | 63.6486 | 63.7671 | 63.8857 | 64.0043 | 64.1228 | 64.2414 | 64.36 | 64.4785 | 64.5971 | 64.7157 | 64.7618 | 64.8079 | 64.854 | 64.9001 | 64.9462 | 64.9923 | 65.0384 | 65.0846 | 65.1307 | 65.1768 | 65.2229 | 65.269 | 65.3151 | 65.3612 | 65.4073 | 65.4534 | 65.4996 | 65.5457 | 65.5918 | 65.6379 | 65.684 | 65.7301 | 65.7762 | 65.8223 | 65.8684 | 65.9146 | 65.9607 | 66.0068 | 66.0529 | 66.099 | 66.099 | 66.099 | 66.099 | 66.099 | 66.099 | 66.099 | 66.099 | 66.099 | 66.099 | 66.099 | 66.099 | 66.099 | 66.099 | 66.099 | 66.099 | 66.099 | 66.099 | 66.099 | 66.099 | 66.099 | 66.099 | 66.099 | 66.099 | 66.099 | 66.099 | 66.099 | 66.099 | 66.099 | 66.099 | 66.099 | 66.0298 | 65.9607 | 65.8915 | 65.8223 | 65.7532 | 65.684 | 65.6148 | 65.5457 | 65.4765 | 65.4073 | 65.3382 | 65.269 | 65.1998 | 65.1307 | 65.0615 | 64.9923 | 64.9232 | 64.854 | 64.7848 | 64.7157 | 64.6465 | 64.5773 | 64.5082 | 64.439 | 64.3698 | 64.3007 | 64.2315 | 64.1623 | 64.0932 | 64.024
8.2 | 0 | 22.2 | 36.728 | 39.26 | 47.296 | 55.284 | 61.776 | 65.372 | 66.772 | 66.772 | 64.672 | 0 | 2.22 | 4.44 | 6.66 | 8.88 | 11.1 | 13.32 | 15.54 | 17.76 | 19.98 | 22.2 | 25.1056 | 28.0112 | 30.9168 | 33.8224 | 36.728 | 37.2344 | 37.7408 | 38.2472 | 38.7536 | 39.26 | 40.0636 | 40.8672 | 41.6708 | 42.4744 | 43.278 | 44.0816 | 44.8852 | 45.6888 | 46.4924 | 47.296 | 47.8285 | 48.3611 | 48.8936 | 49.4261 | 49.9587 | 50.4912 | 51.0237 | 51.5563 | 52.0888 | 52.6213 | 53.1539 | 53.6864 | 54.2189 | 54.7515 | 55.284 | 55.7168 | 56.1496 | 56.5824 | 57.0152 | 57.448 | 57.8808 | 58.3136 | 58.7464 | 59.1792 | 59.612 | 60.0448 | 60.4776 | 60.9104 | 61.3432 | 61.776 | 61.8959 | 62.0157 | 62.1356 | 62.2555 | 62.3753 | 62.4952 | 62.6151 | 62.7349 | 62.8548 | 62.9747 | 63.0945 | 63.2144 | 63.3343 | 63.4541 | 63.574 | 63.6939 | 63.8137 | 63.9336 | 64.0535 | 64.1733 | 64.2932 | 64.4131 | 64.5329 | 64.6528 | 64.7727 | 64.8925 | 65.0124 | 65.1323 | 65.2521 | 65.372 | 65.4187 | 65.4653 | 65.512 | 65.5587 | 65.6053 | 65.652 | 65.6987 | 65.7453 | 65.792 | 65.8387 | 65.8853 | 65.932 | 65.9787 | 66.0253 | 66.072 | 66.1187 | 66.1653 | 66.212 | 66.2587 | 66.3053 | 66.352 | 66.3987 | 66.4453 | 66.492 | 66.5387 | 66.5853 | 66.632 | 66.6787 | 66.7253 | 66.772 | 66.772 | 66.772 | 66.772 | 66.772 | 66.772 | 66.772 | 66.772 | 66.772 | 66.772 | 66.772 | 66.772 | 66.772 | 66.772 | 66.772 | 66.772 | 66.772 | 66.772 | 66.772 | 66.772 | 66.772 | 66.772 | 66.772 | 66.772 | 66.772 | 66.772 | 66.772 | 66.772 | 66.772 | 66.772 | 66.772 | 66.702 | 66.632 | 66.562 | 66.492 | 66.422 | 66.352 | 66.282 | 66.212 | 66.142 | 66.072 | 66.002 | 65.932 | 65.862 | 65.792 | 65.722 | 65.652 | 65.582 | 65.512 | 65.442 | 65.372 | 65.302 | 65.232 | 65.162 | 65.092 | 65.022 | 64.952 | 64.882 | 64.812 | 64.742 | 64.672
8.25 | 0 | 22.4167 | 37.0967 | 39.6417 | 47.76 | 55.8317 | 62.3933 | 66.0283 | 67.445 | 67.445 | 65.32 | 0 | 2.2417 | 4.4833 | 6.725 | 8.9667 | 11.2083 | 13.45 | 15.6917 | 17.9333 | 20.175 | 22.4167 | 25.3527 | 28.2887 | 31.2247 | 34.1607 | 37.0967 | 37.6057 | 38.1147 | 38.6237 | 39.1327 | 39.6417 | 40.4535 | 41.2653 | 42.0772 | 42.889 | 43.7008 | 44.5127 | 45.3245 | 46.1363 | 46.9482 | 47.76 | 48.2981 | 48.8362 | 49.3743 | 49.9124 | 50.4506 | 50.9887 | 51.5268 | 52.0649 | 52.603 | 53.1411 | 53.6792 | 54.2173 | 54.7554 | 55.2936 | 55.8317 | 56.2691 | 56.7066 | 57.144 | 57.5814 | 58.0189 | 58.4563 | 58.8938 | 59.3312 | 59.7687 | 60.2061 | 60.6436 | 61.081 | 61.5184 | 61.9559 | 62.3933 | 62.5145 | 62.6357 | 62.7568 | 62.878 | 62.9992 | 63.1203 | 63.2415 | 63.3627 | 63.4838 | 63.605 | 63.7262 | 63.8473 | 63.9685 | 64.0897 | 64.2108 | 64.332 | 64.4532 | 64.5743 | 64.6955 | 64.8167 | 64.9378 | 65.059 | 65.1802 | 65.3013 | 65.4225 | 65.5437 | 65.6648 | 65.786 | 65.9072 | 66.0283 | 66.0756 | 66.1228 | 66.17 | 66.2172 | 66.2644 | 66.3117 | 66.3589 | 66.4061 | 66.4533 | 66.5006 | 66.5478 | 66.595 | 66.6422 | 66.6894 | 66.7367 | 66.7839 | 66.8311 | 66.8783 | 66.9256 | 66.9728 | 67.02 | 67.0672 | 67.1144 | 67.1617 | 67.2089 | 67.2561 | 67.3033 | 67.3506 | 67.3978 | 67.445 | 67.445 | 67.445 | 67.445 | 67.445 | 67.445 | 67.445 | 67.445 | 67.445 | 67.445 | 67.445 | 67.445 | 67.445 | 67.445 | 67.445 | 67.445 | 67.445 | 67.445 | 67.445 | 67.445 | 67.445 | 67.445 | 67.445 | 67.445 | 67.445 | 67.445 | 67.445 | 67.445 | 67.445 | 67.445 | 67.445 | 67.3742 | 67.3033 | 67.2325 | 67.1617 | 67.0908 | 67.02 | 66.9492 | 66.8783 | 66.8075 | 66.7367 | 66.6658 | 66.595 | 66.5242 | 66.4533 | 66.3825 | 66.3117 | 66.2408 | 66.17 | 66.0992 | 66.0283 | 65.9575 | 65.8867 | 65.8158 | 65.745 | 65.6742 | 65.6033 | 65.5325 | 65.4617 | 65.3908 | 65.32
8.3 | 0 | 22.6333 | 37.4653 | 40.0233 | 48.224 | 56.3793 | 63.0107 | 66.6847 | 68.118 | 68.118 | 65.968 | 0 | 2.2633 | 4.5267 | 6.79 | 9.0533 | 11.3167 | 13.58 | 15.8433 | 18.1067 | 20.37 | 22.6333 | 25.5997 | 28.5661 | 31.5325 | 34.4989 | 37.4653 | 37.9769 | 38.4885 | 39.0001 | 39.5117 | 40.0233 | 40.8434 | 41.6635 | 42.4835 | 43.3036 | 44.1237 | 44.9437 | 45.7638 | 46.5839 | 47.4039 | 48.224 | 48.7677 | 49.3114 | 49.8551 | 50.3988 | 50.9424 | 51.4861 | 52.0298 | 52.5735 | 53.1172 | 53.6609 | 54.2046 | 54.7483 | 55.292 | 55.8356 | 56.3793 | 56.8214 | 57.2635 | 57.7056 | 58.1477 | 58.5898 | 59.0319 | 59.474 | 59.916 | 60.3581 | 60.8002 | 61.2423 | 61.6844 | 62.1265 | 62.5686 | 63.0107 | 63.1331 | 63.2556 | 63.3781 | 63.5005 | 63.623 | 63.7455 | 63.8679 | 63.9904 | 64.1129 | 64.2353 | 64.3578 | 64.4803 | 64.6027 | 64.7252 | 64.8477 | 64.9701 | 65.0926 | 65.2151 | 65.3375 | 65.46 | 65.5825 | 65.7049 | 65.8274 | 65.9499 | 66.0723 | 66.1948 | 66.3173 | 66.4397 | 66.5622 | 66.6847 | 66.7324 | 66.7802 | 66.828 | 66.8758 | 66.9236 | 66.9713 | 67.0191 | 67.0669 | 67.1147 | 67.1624 | 67.2102 | 67.258 | 67.3058 | 67.3536 | 67.4013 | 67.4491 | 67.4969 | 67.5447 | 67.5924 | 67.6402 | 67.688 | 67.7358 | 67.7836 | 67.8313 | 67.8791 | 67.9269 | 67.9747 | 68.0224 | 68.0702 | 68.118 | 68.118 | 68.118 | 68.118 | 68.118 | 68.118 | 68.118 | 68.118 | 68.118 | 68.118 | 68.118 | 68.118 | 68.118 | 68.118 | 68.118 | 68.118 | 68.118 | 68.118 | 68.118 | 68.118 | 68.118 | 68.118 | 68.118 | 68.118 | 68.118 | 68.118 | 68.118 | 68.118 | 68.118 | 68.118 | 68.118 | 68.0463 | 67.9747 | 67.903 | 67.8313 | 67.7597 | 67.688 | 67.6163 | 67.5447 | 67.473 | 67.4013 | 67.3297 | 67.258 | 67.1863 | 67.1147 | 67.043 | 66.9713 | 66.8997 | 66.828 | 66.7563 | 66.6847 | 66.613 | 66.5413 | 66.4697 | 66.398 | 66.3263 | 66.2547 | 66.183 | 66.1113 | 66.0397 | 65.968
8.35 | 0 | 22.85 | 37.834 | 40.405 | 48.688 | 56.927 | 63.628 | 67.341 | 68.791 | 68.791 | 66.616 | 0 | 2.285 | 4.57 | 6.855 | 9.14 | 11.425 | 13.71 | 15.995 | 18.28 | 20.565 | 22.85 | 25.8468 | 28.8436 | 31.8404 | 34.8372 | 37.834 | 38.3482 | 38.8624 | 39.3766 | 39.8908 | 40.405 | 41.2333 | 42.0616 | 42.8899 | 43.7182 | 44.5465 | 45.3748 | 46.2031 | 47.0314 | 47.8597 | 48.688 | 49.2373 | 49.7865 | 50.3358 | 50.8851 | 51.4343 | 51.9836 | 52.5329 | 53.0821 | 53.6314 | 54.1807 | 54.7299 | 55.2792 | 55.8285 | 56.3777 | 56.927 | 57.3737 | 57.8205 | 58.2672 | 58.7139 | 59.1607 | 59.6074 | 60.0541 | 60.5009 | 60.9476 | 61.3943 | 61.8411 | 62.2878 | 62.7345 | 63.1813 | 63.628 | 63.7518 | 63.8755 | 63.9993 | 64.1231 | 64.2468 | 64.3706 | 64.4944 | 64.6181 | 64.7419 | 64.8657 | 64.9894 | 65.1132 | 65.237 | 65.3607 | 65.4845 | 65.6083 | 65.732 | 65.8558 | 65.9796 | 66.1033 | 66.2271 | 66.3509 | 66.4746 | 66.5984 | 66.7222 | 66.8459 | 66.9697 | 67.0935 | 67.2172 | 67.341 | 67.3893 | 67.4377 | 67.486 | 67.5343 | 67.5827 | 67.631 | 67.6793 | 67.7277 | 67.776 | 67.8243 | 67.8727 | 67.921 | 67.9693 | 68.0177 | 68.066 | 68.1143 | 68.1627 | 68.211 | 68.2593 | 68.3077 | 68.356 | 68.4043 | 68.4527 | 68.501 | 68.5493 | 68.5977 | 68.646 | 68.6943 | 68.7427 | 68.791 | 68.791 | 68.791 | 68.791 | 68.791 | 68.791 | 68.791 | 68.791 | 68.791 | 68.791 | 68.791 | 68.791 | 68.791 | 68.791 | 68.791 | 68.791 | 68.791 | 68.791 | 68.791 | 68.791 | 68.791 | 68.791 | 68.791 | 68.791 | 68.791 | 68.791 | 68.791 | 68.791 | 68.791 | 68.791 | 68.791 | 68.7185 | 68.646 | 68.5735 | 68.501 | 68.4285 | 68.356 | 68.2835 | 68.211 | 68.1385 | 68.066 | 67.9935 | 67.921 | 67.8485 | 67.776 | 67.7035 | 67.631 | 67.5585 | 67.486 | 67.4135 | 67.341 | 67.2685 | 67.196 | 67.1235 | 67.051 | 66.9785 | 66.906 | 66.8335 | 66.761 | 66.6885 | 66.616
8.4 | 0 | 23.0667 | 38.2027 | 40.7867 | 49.152 | 57.4747 | 64.2453 | 67.9973 | 69.464 | 69.464 | 67.264 | 0 | 2.3067 | 4.6133 | 6.92 | 9.2267 | 11.5333 | 13.84 | 16.1467 | 18.4533 | 20.76 | 23.0667 | 26.0939 | 29.1211 | 32.1483 | 35.1755 | 38.2027 | 38.7195 | 39.2363 | 39.7531 | 40.2699 | 40.7867 | 41.6232 | 42.4597 | 43.2963 | 44.1328 | 44.9693 | 45.8059 | 46.6424 | 47.4789 | 48.3155 | 49.152 | 49.7068 | 50.2617 | 50.8165 | 51.3714 | 51.9262 | 52.4811 | 53.0359 | 53.5908 | 54.1456 | 54.7004 | 55.2553 | 55.8101 | 56.365 | 56.9198 | 57.4747 | 57.926 | 58.3774 | 58.8288 | 59.2802 | 59.7316 | 60.1829 | 60.6343 | 61.0857 | 61.5371 | 61.9884 | 62.4398 | 62.8912 | 63.3426 | 63.794 | 64.2453 | 64.3704 | 64.4955 | 64.6205 | 64.7456 | 64.8707 | 64.9957 | 65.1208 | 65.2459 | 65.3709 | 65.496 | 65.6211 | 65.7461 | 65.8712 | 65.9963 | 66.1213 | 66.2464 | 66.3715 | 66.4965 | 66.6216 | 66.7467 | 66.8717 | 66.9968 | 67.1219 | 67.2469 | 67.372 | 67.4971 | 67.6221 | 67.7472 | 67.8723 | 67.9973 | 68.0462 | 68.0951 | 68.144 | 68.1929 | 68.2418 | 68.2907 | 68.3396 | 68.3884 | 68.4373 | 68.4862 | 68.5351 | 68.584 | 68.6329 | 68.6818 | 68.7307 | 68.7796 | 68.8284 | 68.8773 | 68.9262 | 68.9751 | 69.024 | 69.0729 | 69.1218 | 69.1707 | 69.2196 | 69.2684 | 69.3173 | 69.3662 | 69.4151 | 69.464 | 69.464 | 69.464 | 69.464 | 69.464 | 69.464 | 69.464 | 69.464 | 69.464 | 69.464 | 69.464 | 69.464 | 69.464 | 69.464 | 69.464 | 69.464 | 69.464 | 69.464 | 69.464 | 69.464 | 69.464 | 69.464 | 69.464 | 69.464 | 69.464 | 69.464 | 69.464 | 69.464 | 69.464 | 69.464 | 69.464 | 69.3907 | 69.3173 | 69.244 | 69.1707 | 69.0973 | 69.024 | 68.9507 | 68.8773 | 68.804 | 68.7307 | 68.6573 | 68.584 | 68.5107 | 68.4373 | 68.364 | 68.2907 | 68.2173 | 68.144 | 68.0707 | 67.9973 | 67.924 | 67.8507 | 67.7773 | 67.704 | 67.6307 | 67.5573 | 67.484 | 67.4107 | 67.3373 | 67.264
8.45 | 0 | 23.2833 | 38.5713 | 41.1683 | 49.616 | 58.0223 | 64.8627 | 68.6537 | 70.137 | 70.137 | 67.912 | 1.7764e-15 | 2.3283 | 4.6567 | 6.985 | 9.3133 | 11.6417 | 13.97 | 16.2983 | 18.6267 | 20.955 | 23.2833 | 26.3409 | 29.3985 | 32.4561 | 35.5137 | 38.5713 | 39.0907 | 39.6101 | 40.1295 | 40.6489 | 41.1683 | 42.0131 | 42.8579 | 43.7026 | 44.5474 | 45.3922 | 46.2369 | 47.0817 | 47.9265 | 48.7712 | 49.616 | 50.1764 | 50.7368 | 51.2973 | 51.8577 | 52.4181 | 52.9785 | 53.539 | 54.0994 | 54.6598 | 55.2202 | 55.7806 | 56.3411 | 56.9015 | 57.4619 | 58.0223 | 58.4784 | 58.9344 | 59.3904 | 59.8464 | 60.3024 | 60.7585 | 61.2145 | 61.6705 | 62.1265 | 62.5826 | 63.0386 | 63.4946 | 63.9506 | 64.4066 | 64.8627 | 64.989 | 65.1154 | 65.2418 | 65.3681 | 65.4945 | 65.6209 | 65.7472 | 65.8736 | 66 | 66.1263 | 66.2527 | 66.3791 | 66.5054 | 66.6318 | 66.7582 | 66.8845 | 67.0109 | 67.1373 | 67.2636 | 67.39 | 67.5164 | 67.6427 | 67.7691 | 67.8955 | 68.0218 | 68.1482 | 68.2746 | 68.4009 | 68.5273 | 68.6537 | 68.7031 | 68.7526 | 68.802 | 68.8514 | 68.9009 | 68.9503 | 68.9998 | 69.0492 | 69.0987 | 69.1481 | 69.1976 | 69.247 | 69.2964 | 69.3459 | 69.3953 | 69.4448 | 69.4942 | 69.5437 | 69.5931 | 69.6426 | 69.692 | 69.7414 | 69.7909 | 69.8403 | 69.8898 | 69.9392 | 69.9887 | 70.0381 | 70.0876 | 70.137 | 70.137 | 70.137 | 70.137 | 70.137 | 70.137 | 70.137 | 70.137 | 70.137 | 70.137 | 70.137 | 70.137 | 70.137 | 70.137 | 70.137 | 70.137 | 70.137 | 70.137 | 70.137 | 70.137 | 70.137 | 70.137 | 70.137 | 70.137 | 70.137 | 70.137 | 70.137 | 70.137 | 70.137 | 70.137 | 70.137 | 70.0628 | 69.9887 | 69.9145 | 69.8403 | 69.7662 | 69.692 | 69.6178 | 69.5437 | 69.4695 | 69.3953 | 69.3212 | 69.247 | 69.1728 | 69.0987 | 69.0245 | 68.9503 | 68.8762 | 68.802 | 68.7278 | 68.6537 | 68.5795 | 68.5053 | 68.4312 | 68.357 | 68.2828 | 68.2087 | 68.1345 | 68.0603 | 67.9862 | 67.912
8.5 | 0 | 23.5 | 38.94 | 41.55 | 50.08 | 58.57 | 65.48 | 69.31 | 70.81 | 70.81 | 68.56 | 0 | 2.35 | 4.7 | 7.05 | 9.4 | 11.75 | 14.1 | 16.45 | 18.8 | 21.15 | 23.5 | 26.588 | 29.676 | 32.764 | 35.852 | 38.94 | 39.462 | 39.984 | 40.506 | 41.028 | 41.55 | 42.403 | 43.256 | 44.109 | 44.962 | 45.815 | 46.668 | 47.521 | 48.374 | 49.227 | 50.08 | 50.646 | 51.212 | 51.778 | 52.344 | 52.91 | 53.476 | 54.042 | 54.608 | 55.174 | 55.74 | 56.306 | 56.872 | 57.438 | 58.004 | 58.57 | 59.0307 | 59.4913 | 59.952 | 60.4127 | 60.8733 | 61.334 | 61.7947 | 62.2553 | 62.716 | 63.1767 | 63.6373 | 64.098 | 64.5587 | 65.0193 | 65.48 | 65.6077 | 65.7353 | 65.863 | 65.9907 | 66.1183 | 66.246 | 66.3737 | 66.5013 | 66.629 | 66.7567 | 66.8843 | 67.012 | 67.1397 | 67.2673 | 67.395 | 67.5227 | 67.6503 | 67.778 | 67.9057 | 68.0333 | 68.161 | 68.2887 | 68.4163 | 68.544 | 68.6717 | 68.7993 | 68.927 | 69.0547 | 69.1823 | 69.31 | 69.36 | 69.41 | 69.46 | 69.51 | 69.56 | 69.61 | 69.66 | 69.71 | 69.76 | 69.81 | 69.86 | 69.91 | 69.96 | 70.01 | 70.06 | 70.11 | 70.16 | 70.21 | 70.26 | 70.31 | 70.36 | 70.41 | 70.46 | 70.51 | 70.56 | 70.61 | 70.66 | 70.71 | 70.76 | 70.81 | 70.81 | 70.81 | 70.81 | 70.81 | 70.81 | 70.81 | 70.81 | 70.81 | 70.81 | 70.81 | 70.81 | 70.81 | 70.81 | 70.81 | 70.81 | 70.81 | 70.81 | 70.81 | 70.81 | 70.81 | 70.81 | 70.81 | 70.81 | 70.81 | 70.81 | 70.81 | 70.81 | 70.81 | 70.81 | 70.81 | 70.735 | 70.66 | 70.585 | 70.51 | 70.435 | 70.36 | 70.285 | 70.21 | 70.135 | 70.06 | 69.985 | 69.91 | 69.835 | 69.76 | 69.685 | 69.61 | 69.535 | 69.46 | 69.385 | 69.31 | 69.235 | 69.16 | 69.085 | 69.01 | 68.935 | 68.86 | 68.785 | 68.71 | 68.635 | 68.56
8.55 | 0 | 23.7167 | 39.3087 | 41.9317 | 50.544 | 59.1177 | 66.0973 | 69.9663 | 71.483 | 71.483 | 69.208 | -1.7764e-15 | 2.3717 | 4.7433 | 7.115 | 9.4867 | 11.8583 | 14.23 | 16.6017 | 18.9733 | 21.345 | 23.7167 | 26.8351 | 29.9535 | 33.0719 | 36.1903 | 39.3087 | 39.8333 | 40.3579 | 40.8825 | 41.4071 | 41.9317 | 42.7929 | 43.6541 | 44.5154 | 45.3766 | 46.2378 | 47.0991 | 47.9603 | 48.8215 | 49.6828 | 50.544 | 51.1156 | 51.6872 | 52.2587 | 52.8303 | 53.4019 | 53.9735 | 54.545 | 55.1166 | 55.6882 | 56.2598 | 56.8314 | 57.4029 | 57.9745 | 58.5461 | 59.1177 | 59.583 | 60.0483 | 60.5136 | 60.9789 | 61.4442 | 61.9095 | 62.3748 | 62.8402 | 63.3055 | 63.7708 | 64.2361 | 64.7014 | 65.1667 | 65.632 | 66.0973 | 66.2263 | 66.3553 | 66.4842 | 66.6132 | 66.7422 | 66.8711 | 67.0001 | 67.1291 | 67.258 | 67.387 | 67.516 | 67.6449 | 67.7739 | 67.9029 | 68.0318 | 68.1608 | 68.2898 | 68.4187 | 68.5477 | 68.6767 | 68.8056 | 68.9346 | 69.0636 | 69.1925 | 69.3215 | 69.4505 | 69.5794 | 69.7084 | 69.8374 | 69.9663 | 70.0169 | 70.0674 | 70.118 | 70.1686 | 70.2191 | 70.2697 | 70.3202 | 70.3708 | 70.4213 | 70.4719 | 70.5224 | 70.573 | 70.6236 | 70.6741 | 70.7247 | 70.7752 | 70.8258 | 70.8763 | 70.9269 | 70.9774 | 71.028 | 71.0786 | 71.1291 | 71.1797 | 71.2302 | 71.2808 | 71.3313 | 71.3819 | 71.4324 | 71.483 | 71.483 | 71.483 | 71.483 | 71.483 | 71.483 | 71.483 | 71.483 | 71.483 | 71.483 | 71.483 | 71.483 | 71.483 | 71.483 | 71.483 | 71.483 | 71.483 | 71.483 | 71.483 | 71.483 | 71.483 | 71.483 | 71.483 | 71.483 | 71.483 | 71.483 | 71.483 | 71.483 | 71.483 | 71.483 | 71.483 | 71.4072 | 71.3313 | 71.2555 | 71.1797 | 71.1038 | 71.028 | 70.9522 | 70.8763 | 70.8005 | 70.7247 | 70.6488 | 70.573 | 70.4972 | 70.4213 | 70.3455 | 70.2697 | 70.1938 | 70.118 | 70.0422 | 69.9663 | 69.8905 | 69.8147 | 69.7388 | 69.663 | 69.5872 | 69.5113 | 69.4355 | 69.3597 | 69.2838 | 69.208
8.6 | 0 | 23.9333 | 39.6773 | 42.3133 | 51.008 | 59.6653 | 66.7147 | 70.6227 | 72.156 | 72.156 | 69.856 | 0 | 2.3933 | 4.7867 | 7.18 | 9.5733 | 11.9667 | 14.36 | 16.7533 | 19.1467 | 21.54 | 23.9333 | 27.0821 | 30.2309 | 33.3797 | 36.5285 | 39.6773 | 40.2045 | 40.7317 | 41.2589 | 41.7861 | 42.3133 | 43.1828 | 44.0523 | 44.9217 | 45.7912 | 46.6607 | 47.5301 | 48.3996 | 49.2691 | 50.1385 | 51.008 | 51.5852 | 52.1623 | 52.7395 | 53.3166 | 53.8938 | 54.4709 | 55.0481 | 55.6252 | 56.2024 | 56.7796 | 57.3567 | 57.9339 | 58.511 | 59.0882 | 59.6653 | 60.1353 | 60.6052 | 61.0752 | 61.5452 | 62.0151 | 62.4851 | 62.955 | 63.425 | 63.8949 | 64.3649 | 64.8348 | 65.3048 | 65.7748 | 66.2447 | 66.7147 | 66.8449 | 66.9752 | 67.1055 | 67.2357 | 67.366 | 67.4963 | 67.6265 | 67.7568 | 67.8871 | 68.0173 | 68.1476 | 68.2779 | 68.4081 | 68.5384 | 68.6687 | 68.7989 | 68.9292 | 69.0595 | 69.1897 | 69.32 | 69.4503 | 69.5805 | 69.7108 | 69.8411 | 69.9713 | 70.1016 | 70.2319 | 70.3621 | 70.4924 | 70.6227 | 70.6738 | 70.7249 | 70.776 | 70.8271 | 70.8782 | 70.9293 | 70.9804 | 71.0316 | 71.0827 | 71.1338 | 71.1849 | 71.236 | 71.2871 | 71.3382 | 71.3893 | 71.4404 | 71.4916 | 71.5427 | 71.5938 | 71.6449 | 71.696 | 71.7471 | 71.7982 | 71.8493 | 71.9004 | 71.9516 | 72.0027 | 72.0538 | 72.1049 | 72.156 | 72.156 | 72.156 | 72.156 | 72.156 | 72.156 | 72.156 | 72.156 | 72.156 | 72.156 | 72.156 | 72.156 | 72.156 | 72.156 | 72.156 | 72.156 | 72.156 | 72.156 | 72.156 | 72.156 | 72.156 | 72.156 | 72.156 | 72.156 | 72.156 | 72.156 | 72.156 | 72.156 | 72.156 | 72.156 | 72.156 | 72.0793 | 72.0027 | 71.926 | 71.8493 | 71.7727 | 71.696 | 71.6193 | 71.5427 | 71.466 | 71.3893 | 71.3127 | 71.236 | 71.1593 | 71.0827 | 71.006 | 70.9293 | 70.8527 | 70.776 | 70.6993 | 70.6227 | 70.546 | 70.4693 | 70.3927 | 70.316 | 70.2393 | 70.1627 | 70.086 | 70.0093 | 69.9327 | 69.856
8.65 | 0 | 24.15 | 40.046 | 42.695 | 51.472 | 60.213 | 67.332 | 71.279 | 72.829 | 72.829 | 70.504 | 1.7764e-15 | 2.415 | 4.83 | 7.245 | 9.66 | 12.075 | 14.49 | 16.905 | 19.32 | 21.735 | 24.15 | 27.3292 | 30.5084 | 33.6876 | 36.8668 | 40.046 | 40.5758 | 41.1056 | 41.6354 | 42.1652 | 42.695 | 43.5727 | 44.4504 | 45.3281 | 46.2058 | 47.0835 | 47.9612 | 48.8389 | 49.7166 | 50.5943 | 51.472 | 52.0547 | 52.6375 | 53.2202 | 53.8029 | 54.3857 | 54.9684 | 55.5511 | 56.1339 | 56.7166 | 57.2993 | 57.8821 | 58.4648 | 59.0475 | 59.6303 | 60.213 | 60.6876 | 61.1622 | 61.6368 | 62.1114 | 62.586 | 63.0606 | 63.5352 | 64.0098 | 64.4844 | 64.959 | 65.4336 | 65.9082 | 66.3828 | 66.8574 | 67.332 | 67.4636 | 67.5951 | 67.7267 | 67.8583 | 67.9898 | 68.1214 | 68.253 | 68.3845 | 68.5161 | 68.6477 | 68.7792 | 68.9108 | 69.0424 | 69.1739 | 69.3055 | 69.4371 | 69.5686 | 69.7002 | 69.8318 | 69.9633 | 70.0949 | 70.2265 | 70.358 | 70.4896 | 70.6212 | 70.7527 | 70.8843 | 71.0159 | 71.1474 | 71.279 | 71.3307 | 71.3823 | 71.434 | 71.4857 | 71.5373 | 71.589 | 71.6407 | 71.6923 | 71.744 | 71.7957 | 71.8473 | 71.899 | 71.9507 | 72.0023 | 72.054 | 72.1057 | 72.1573 | 72.209 | 72.2607 | 72.3123 | 72.364 | 72.4157 | 72.4673 | 72.519 | 72.5707 | 72.6223 | 72.674 | 72.7257 | 72.7773 | 72.829 | 72.829 | 72.829 | 72.829 | 72.829 | 72.829 | 72.829 | 72.829 | 72.829 | 72.829 | 72.829 | 72.829 | 72.829 | 72.829 | 72.829 | 72.829 | 72.829 | 72.829 | 72.829 | 72.829 | 72.829 | 72.829 | 72.829 | 72.829 | 72.829 | 72.829 | 72.829 | 72.829 | 72.829 | 72.829 | 72.829 | 72.7515 | 72.674 | 72.5965 | 72.519 | 72.4415 | 72.364 | 72.2865 | 72.209 | 72.1315 | 72.054 | 71.9765 | 71.899 | 71.8215 | 71.744 | 71.6665 | 71.589 | 71.5115 | 71.434 | 71.3565 | 71.279 | 71.2015 | 71.124 | 71.0465 | 70.969 | 70.8915 | 70.814 | 70.7365 | 70.659 | 70.5815 | 70.504
8.7 | 0 | 24.3667 | 40.4147 | 43.0767 | 51.936 | 60.7607 | 67.9493 | 71.9353 | 73.502 | 73.502 | 71.152 | 0 | 2.4367 | 4.8733 | 7.31 | 9.7467 | 12.1833 | 14.62 | 17.0567 | 19.4933 | 21.93 | 24.3667 | 27.5763 | 30.7859 | 33.9955 | 37.2051 | 40.4147 | 40.9471 | 41.4795 | 42.0119 | 42.5443 | 43.0767 | 43.9626 | 44.8485 | 45.7345 | 46.6204 | 47.5063 | 48.3923 | 49.2782 | 50.1641 | 51.0501 | 51.936 | 52.5243 | 53.1126 | 53.7009 | 54.2892 | 54.8776 | 55.4659 | 56.0542 | 56.6425 | 57.2308 | 57.8191 | 58.4074 | 58.9957 | 59.584 | 60.1724 | 60.7607 | 61.2399 | 61.7192 | 62.1984 | 62.6776 | 63.1569 | 63.6361 | 64.1154 | 64.5946 | 65.0739 | 65.5531 | 66.0324 | 66.5116 | 66.9908 | 67.4701 | 67.9493 | 68.0822 | 68.2151 | 68.3479 | 68.4808 | 68.6137 | 68.7465 | 68.8794 | 69.0123 | 69.1451 | 69.278 | 69.4109 | 69.5437 | 69.6766 | 69.8095 | 69.9423 | 70.0752 | 70.2081 | 70.3409 | 70.4738 | 70.6067 | 70.7395 | 70.8724 | 71.0053 | 71.1381 | 71.271 | 71.4039 | 71.5367 | 71.6696 | 71.8025 | 71.9353 | 71.9876 | 72.0398 | 72.092 | 72.1442 | 72.1964 | 72.2487 | 72.3009 | 72.3531 | 72.4053 | 72.4576 | 72.5098 | 72.562 | 72.6142 | 72.6664 | 72.7187 | 72.7709 | 72.8231 | 72.8753 | 72.9276 | 72.9798 | 73.032 | 73.0842 | 73.1364 | 73.1887 | 73.2409 | 73.2931 | 73.3453 | 73.3976 | 73.4498 | 73.502 | 73.502 | 73.502 | 73.502 | 73.502 | 73.502 | 73.502 | 73.502 | 73.502 | 73.502 | 73.502 | 73.502 | 73.502 | 73.502 | 73.502 | 73.502 | 73.502 | 73.502 | 73.502 | 73.502 | 73.502 | 73.502 | 73.502 | 73.502 | 73.502 | 73.502 | 73.502 | 73.502 | 73.502 | 73.502 | 73.502 | 73.4237 | 73.3453 | 73.267 | 73.1887 | 73.1103 | 73.032 | 72.9537 | 72.8753 | 72.797 | 72.7187 | 72.6403 | 72.562 | 72.4837 | 72.4053 | 72.327 | 72.2487 | 72.1703 | 72.092 | 72.0137 | 71.9353 | 71.857 | 71.7787 | 71.7003 | 71.622 | 71.5437 | 71.4653 | 71.387 | 71.3087 | 71.2303 | 71.152
8.75 | 0 | 24.5833 | 40.7833 | 43.4583 | 52.4 | 61.3083 | 68.5667 | 72.5917 | 74.175 | 74.175 | 71.8 | 0 | 2.4583 | 4.9167 | 7.375 | 9.8333 | 12.2917 | 14.75 | 17.2083 | 19.6667 | 22.125 | 24.5833 | 27.8233 | 31.0633 | 34.3033 | 37.5433 | 40.7833 | 41.3183 | 41.8533 | 42.3883 | 42.9233 | 43.4583 | 44.3525 | 45.2467 | 46.1408 | 47.035 | 47.9292 | 48.8233 | 49.7175 | 50.6117 | 51.5058 | 52.4 | 52.9939 | 53.5878 | 54.1817 | 54.7756 | 55.3694 | 55.9633 | 56.5572 | 57.1511 | 57.745 | 58.3389 | 58.9328 | 59.5267 | 60.1206 | 60.7144 | 61.3083 | 61.7922 | 62.2761 | 62.76 | 63.2439 | 63.7278 | 64.2117 | 64.6956 | 65.1794 | 65.6633 | 66.1472 | 66.6311 | 67.115 | 67.5989 | 68.0828 | 68.5667 | 68.7008 | 68.835 | 68.9692 | 69.1033 | 69.2375 | 69.3717 | 69.5058 | 69.64 | 69.7742 | 69.9083 | 70.0425 | 70.1767 | 70.3108 | 70.445 | 70.5792 | 70.7133 | 70.8475 | 70.9817 | 71.1158 | 71.25 | 71.3842 | 71.5183 | 71.6525 | 71.7867 | 71.9208 | 72.055 | 72.1892 | 72.3233 | 72.4575 | 72.5917 | 72.6444 | 72.6972 | 72.75 | 72.8028 | 72.8556 | 72.9083 | 72.9611 | 73.0139 | 73.0667 | 73.1194 | 73.1722 | 73.225 | 73.2778 | 73.3306 | 73.3833 | 73.4361 | 73.4889 | 73.5417 | 73.5944 | 73.6472 | 73.7 | 73.7528 | 73.8056 | 73.8583 | 73.9111 | 73.9639 | 74.0167 | 74.0694 | 74.1222 | 74.175 | 74.175 | 74.175 | 74.175 | 74.175 | 74.175 | 74.175 | 74.175 | 74.175 | 74.175 | 74.175 | 74.175 | 74.175 | 74.175 | 74.175 | 74.175 | 74.175 | 74.175 | 74.175 | 74.175 | 74.175 | 74.175 | 74.175 | 74.175 | 74.175 | 74.175 | 74.175 | 74.175 | 74.175 | 74.175 | 74.175 | 74.0958 | 74.0167 | 73.9375 | 73.8583 | 73.7792 | 73.7 | 73.6208 | 73.5417 | 73.4625 | 73.3833 | 73.3042 | 73.225 | 73.1458 | 73.0667 | 72.9875 | 72.9083 | 72.8292 | 72.75 | 72.6708 | 72.5917 | 72.5125 | 72.4333 | 72.3542 | 72.275 | 72.1958 | 72.1167 | 72.0375 | 71.9583 | 71.8792 | 71.8
8.8 | 0 | 24.8 | 41.152 | 43.84 | 52.864 | 61.856 | 69.184 | 73.248 | 74.848 | 74.848 | 72.448 | 0 | 2.48 | 4.96 | 7.44 | 9.92 | 12.4 | 14.88 | 17.36 | 19.84 | 22.32 | 24.8 | 28.0704 | 31.3408 | 34.6112 | 37.8816 | 41.152 | 41.6896 | 42.2272 | 42.7648 | 43.3024 | 43.84 | 44.7424 | 45.6448 | 46.5472 | 47.4496 | 48.352 | 49.2544 | 50.1568 | 51.0592 | 51.9616 | 52.864 | 53.4635 | 54.0629 | 54.6624 | 55.2619 | 55.8613 | 56.4608 | 57.0603 | 57.6597 | 58.2592 | 58.8587 | 59.4581 | 60.0576 | 60.6571 | 61.2565 | 61.856 | 62.3445 | 62.8331 | 63.3216 | 63.8101 | 64.2987 | 64.7872 | 65.2757 | 65.7643 | 66.2528 | 66.7413 | 67.2299 | 67.7184 | 68.2069 | 68.6955 | 69.184 | 69.3195 | 69.4549 | 69.5904 | 69.7259 | 69.8613 | 69.9968 | 70.1323 | 70.2677 | 70.4032 | 70.5387 | 70.6741 | 70.8096 | 70.9451 | 71.0805 | 71.216 | 71.3515 | 71.4869 | 71.6224 | 71.7579 | 71.8933 | 72.0288 | 72.1643 | 72.2997 | 72.4352 | 72.5707 | 72.7061 | 72.8416 | 72.9771 | 73.1125 | 73.248 | 73.3013 | 73.3547 | 73.408 | 73.4613 | 73.5147 | 73.568 | 73.6213 | 73.6747 | 73.728 | 73.7813 | 73.8347 | 73.888 | 73.9413 | 73.9947 | 74.048 | 74.1013 | 74.1547 | 74.208 | 74.2613 | 74.3147 | 74.368 | 74.4213 | 74.4747 | 74.528 | 74.5813 | 74.6347 | 74.688 | 74.7413 | 74.7947 | 74.848 | 74.848 | 74.848 | 74.848 | 74.848 | 74.848 | 74.848 | 74.848 | 74.848 | 74.848 | 74.848 | 74.848 | 74.848 | 74.848 | 74.848 | 74.848 | 74.848 | 74.848 | 74.848 | 74.848 | 74.848 | 74.848 | 74.848 | 74.848 | 74.848 | 74.848 | 74.848 | 74.848 | 74.848 | 74.848 | 74.848 | 74.768 | 74.688 | 74.608 | 74.528 | 74.448 | 74.368 | 74.288 | 74.208 | 74.128 | 74.048 | 73.968 | 73.888 | 73.808 | 73.728 | 73.648 | 73.568 | 73.488 | 73.408 | 73.328 | 73.248 | 73.168 | 73.088 | 73.008 | 72.928 | 72.848 | 72.768 | 72.688 | 72.608 | 72.528 | 72.448
8.85 | 0 | 25.0167 | 41.5207 | 44.2217 | 53.328 | 62.4037 | 69.8013 | 73.9043 | 75.521 | 75.521 | 73.096 | 1.7764e-15 | 2.5017 | 5.0033 | 7.505 | 10.0067 | 12.5083 | 15.01 | 17.5117 | 20.0133 | 22.515 | 25.0167 | 28.3175 | 31.6183 | 34.9191 | 38.2199 | 41.5207 | 42.0609 | 42.6011 | 43.1413 | 43.6815 | 44.2217 | 45.1323 | 46.0429 | 46.9536 | 47.8642 | 48.7748 | 49.6855 | 50.5961 | 51.5067 | 52.4174 | 53.328 | 53.933 | 54.5381 | 55.1431 | 55.7482 | 56.3532 | 56.9583 | 57.5633 | 58.1684 | 58.7734 | 59.3784 | 59.9835 | 60.5885 | 61.1936 | 61.7986 | 62.4037 | 62.8968 | 63.39 | 63.8832 | 64.3764 | 64.8696 | 65.3627 | 65.8559 | 66.3491 | 66.8423 | 67.3354 | 67.8286 | 68.3218 | 68.815 | 69.3082 | 69.8013 | 69.9381 | 70.0749 | 70.2116 | 70.3484 | 70.4852 | 70.6219 | 70.7587 | 70.8955 | 71.0322 | 71.169 | 71.3058 | 71.4425 | 71.5793 | 71.7161 | 71.8528 | 71.9896 | 72.1264 | 72.2631 | 72.3999 | 72.5367 | 72.6734 | 72.8102 | 72.947 | 73.0837 | 73.2205 | 73.3573 | 73.494 | 73.6308 | 73.7676 | 73.9043 | 73.9582 | 74.0121 | 74.066 | 74.1199 | 74.1738 | 74.2277 | 74.2816 | 74.3354 | 74.3893 | 74.4432 | 74.4971 | 74.551 | 74.6049 | 74.6588 | 74.7127 | 74.7666 | 74.8204 | 74.8743 | 74.9282 | 74.9821 | 75.036 | 75.0899 | 75.1438 | 75.1977 | 75.2516 | 75.3054 | 75.3593 | 75.4132 | 75.4671 | 75.521 | 75.521 | 75.521 | 75.521 | 75.521 | 75.521 | 75.521 | 75.521 | 75.521 | 75.521 | 75.521 | 75.521 | 75.521 | 75.521 | 75.521 | 75.521 | 75.521 | 75.521 | 75.521 | 75.521 | 75.521 | 75.521 | 75.521 | 75.521 | 75.521 | 75.521 | 75.521 | 75.521 | 75.521 | 75.521 | 75.521 | 75.4402 | 75.3593 | 75.2785 | 75.1977 | 75.1168 | 75.036 | 74.9552 | 74.8743 | 74.7935 | 74.7127 | 74.6318 | 74.551 | 74.4702 | 74.3893 | 74.3085 | 74.2277 | 74.1468 | 74.066 | 73.9852 | 73.9043 | 73.8235 | 73.7427 | 73.6618 | 73.581 | 73.5002 | 73.4193 | 73.3385 | 73.2577 | 73.1768 | 73.096
8.9 | 0 | 25.2333 | 41.8893 | 44.6033 | 53.792 | 62.9513 | 70.4187 | 74.5607 | 76.194 | 76.194 | 73.744 | 0 | 2.5233 | 5.0467 | 7.57 | 10.0933 | 12.6167 | 15.14 | 17.6633 | 20.1867 | 22.71 | 25.2333 | 28.5645 | 31.8957 | 35.2269 | 38.5581 | 41.8893 | 42.4321 | 42.9749 | 43.5177 | 44.0605 | 44.6033 | 45.5222 | 46.4411 | 47.3599 | 48.2788 | 49.1977 | 50.1165 | 51.0354 | 51.9543 | 52.8731 | 53.792 | 54.4026 | 55.0132 | 55.6239 | 56.2345 | 56.8451 | 57.4557 | 58.0664 | 58.677 | 59.2876 | 59.8982 | 60.5088 | 61.1195 | 61.7301 | 62.3407 | 62.9513 | 63.4492 | 63.947 | 64.4448 | 64.9426 | 65.4404 | 65.9383 | 66.4361 | 66.9339 | 67.4317 | 67.9296 | 68.4274 | 68.9252 | 69.423 | 69.9208 | 70.4187 | 70.5567 | 70.6948 | 70.8329 | 70.9709 | 71.109 | 71.2471 | 71.3851 | 71.5232 | 71.6613 | 71.7993 | 71.9374 | 72.0755 | 72.2135 | 72.3516 | 72.4897 | 72.6277 | 72.7658 | 72.9039 | 73.0419 | 73.18 | 73.3181 | 73.4561 | 73.5942 | 73.7323 | 73.8703 | 74.0084 | 74.1465 | 74.2845 | 74.4226 | 74.5607 | 74.6151 | 74.6696 | 74.724 | 74.7784 | 74.8329 | 74.8873 | 74.9418 | 74.9962 | 75.0507 | 75.1051 | 75.1596 | 75.214 | 75.2684 | 75.3229 | 75.3773 | 75.4318 | 75.4862 | 75.5407 | 75.5951 | 75.6496 | 75.704 | 75.7584 | 75.8129 | 75.8673 | 75.9218 | 75.9762 | 76.0307 | 76.0851 | 76.1396 | 76.194 | 76.194 | 76.194 | 76.194 | 76.194 | 76.194 | 76.194 | 76.194 | 76.194 | 76.194 | 76.194 | 76.194 | 76.194 | 76.194 | 76.194 | 76.194 | 76.194 | 76.194 | 76.194 | 76.194 | 76.194 | 76.194 | 76.194 | 76.194 | 76.194 | 76.194 | 76.194 | 76.194 | 76.194 | 76.194 | 76.194 | 76.1123 | 76.0307 | 75.949 | 75.8673 | 75.7857 | 75.704 | 75.6223 | 75.5407 | 75.459 | 75.3773 | 75.2957 | 75.214 | 75.1323 | 75.0507 | 74.969 | 74.8873 | 74.8057 | 74.724 | 74.6423 | 74.5607 | 74.479 | 74.3973 | 74.3157 | 74.234 | 74.1523 | 74.0707 | 73.989 | 73.9073 | 73.8257 | 73.744
8.95 | 0 | 25.45 | 42.258 | 44.985 | 54.256 | 63.499 | 71.036 | 75.217 | 76.867 | 76.867 | 74.392 | -1.7764e-15 | 2.545 | 5.09 | 7.635 | 10.18 | 12.725 | 15.27 | 17.815 | 20.36 | 22.905 | 25.45 | 28.8116 | 32.1732 | 35.5348 | 38.8964 | 42.258 | 42.8034 | 43.3488 | 43.8942 | 44.4396 | 44.985 | 45.9121 | 46.8392 | 47.7663 | 48.6934 | 49.6205 | 50.5476 | 51.4747 | 52.4018 | 53.3289 | 54.256 | 54.8722 | 55.4884 | 56.1046 | 56.7208 | 57.337 | 57.9532 | 58.5694 | 59.1856 | 59.8018 | 60.418 | 61.0342 | 61.6504 | 62.2666 | 62.8828 | 63.499 | 64.0015 | 64.5039 | 65.0064 | 65.5089 | 66.0113 | 66.5138 | 67.0163 | 67.5187 | 68.0212 | 68.5237 | 69.0261 | 69.5286 | 70.0311 | 70.5335 | 71.036 | 71.1754 | 71.3147 | 71.4541 | 71.5935 | 71.7328 | 71.8722 | 72.0116 | 72.1509 | 72.2903 | 72.4297 | 72.569 | 72.7084 | 72.8478 | 72.9871 | 73.1265 | 73.2659 | 73.4052 | 73.5446 | 73.684 | 73.8233 | 73.9627 | 74.1021 | 74.2414 | 74.3808 | 74.5202 | 74.6595 | 74.7989 | 74.9383 | 75.0776 | 75.217 | 75.272 | 75.327 | 75.382 | 75.437 | 75.492 | 75.547 | 75.602 | 75.657 | 75.712 | 75.767 | 75.822 | 75.877 | 75.932 | 75.987 | 76.042 | 76.097 | 76.152 | 76.207 | 76.262 | 76.317 | 76.372 | 76.427 | 76.482 | 76.537 | 76.592 | 76.647 | 76.702 | 76.757 | 76.812 | 76.867 | 76.867 | 76.867 | 76.867 | 76.867 | 76.867 | 76.867 | 76.867 | 76.867 | 76.867 | 76.867 | 76.867 | 76.867 | 76.867 | 76.867 | 76.867 | 76.867 | 76.867 | 76.867 | 76.867 | 76.867 | 76.867 | 76.867 | 76.867 | 76.867 | 76.867 | 76.867 | 76.867 | 76.867 | 76.867 | 76.867 | 76.7845 | 76.702 | 76.6195 | 76.537 | 76.4545 | 76.372 | 76.2895 | 76.207 | 76.1245 | 76.042 | 75.9595 | 75.877 | 75.7945 | 75.712 | 75.6295 | 75.547 | 75.4645 | 75.382 | 75.2995 | 75.217 | 75.1345 | 75.052 | 74.9695 | 74.887 | 74.8045 | 74.722 | 74.6395 | 74.557 | 74.4745 | 74.392
9 | 0 | 25.6667 | 42.6267 | 45.3667 | 54.72 | 64.0467 | 71.6533 | 75.8733 | 77.54 | 77.54 | 75.04 | 1.7764e-15 | 2.5667 | 5.1333 | 7.7 | 10.2667 | 12.8333 | 15.4 | 17.9667 | 20.5333 | 23.1 | 25.6667 | 29.0587 | 32.4507 | 35.8427 | 39.2347 | 42.6267 | 43.1747 | 43.7227 | 44.2707 | 44.8187 | 45.3667 | 46.302 | 47.2373 | 48.1727 | 49.108 | 50.0433 | 50.9787 | 51.914 | 52.8493 | 53.7847 | 54.72 | 55.3418 | 55.9636 | 56.5853 | 57.2071 | 57.8289 | 58.4507 | 59.0724 | 59.6942 | 60.316 | 60.9378 | 61.5596 | 62.1813 | 62.8031 | 63.4249 | 64.0467 | 64.5538 | 65.0609 | 65.568 | 66.0751 | 66.5822 | 67.0893 | 67.5964 | 68.1036 | 68.6107 | 69.1178 | 69.6249 | 70.132 | 70.6391 | 71.1462 | 71.6533 | 71.794 | 71.9347 | 72.0753 | 72.216 | 72.3567 | 72.4973 | 72.638 | 72.7787 | 72.9193 | 73.06 | 73.2007 | 73.3413 | 73.482 | 73.6227 | 73.7633 | 73.904 | 74.0447 | 74.1853 | 74.326 | 74.4667 | 74.6073 | 74.748 | 74.8887 | 75.0293 | 75.17 | 75.3107 | 75.4513 | 75.592 | 75.7327 | 75.8733 | 75.9289 | 75.9844 | 76.04 | 76.0956 | 76.1511 | 76.2067 | 76.2622 | 76.3178 | 76.3733 | 76.4289 | 76.4844 | 76.54 | 76.5956 | 76.6511 | 76.7067 | 76.7622 | 76.8178 | 76.8733 | 76.9289 | 76.9844 | 77.04 | 77.0956 | 77.1511 | 77.2067 | 77.2622 | 77.3178 | 77.3733 | 77.4289 | 77.4844 | 77.54 | 77.54 | 77.54 | 77.54 | 77.54 | 77.54 | 77.54 | 77.54 | 77.54 | 77.54 | 77.54 | 77.54 | 77.54 | 77.54 | 77.54 | 77.54 | 77.54 | 77.54 | 77.54 | 77.54 | 77.54 | 77.54 | 77.54 | 77.54 | 77.54 | 77.54 | 77.54 | 77.54 | 77.54 | 77.54 | 77.54 | 77.4567 | 77.3733 | 77.29 | 77.2067 | 77.1233 | 77.04 | 76.9567 | 76.8733 | 76.79 | 76.7067 | 76.6233 | 76.54 | 76.4567 | 76.3733 | 76.29 | 76.2067 | 76.1233 | 76.04 | 75.9567 | 75.8733 | 75.79 | 75.7067 | 75.6233 | 75.54 | 75.4567 | 75.3733 | 75.29 | 75.2067 | 75.1233 | 75.04
9.05 | 0 | 25.8833 | 42.9953 | 45.7483 | 55.184 | 64.5943 | 72.2707 | 76.5297 | 78.213 | 78.213 | 75.688 | 1.7764e-15 | 2.5883 | 5.1767 | 7.765 | 10.3533 | 12.9417 | 15.53 | 18.1183 | 20.7067 | 23.295 | 25.8833 | 29.3057 | 32.7281 | 36.1505 | 39.5729 | 42.9953 | 43.5459 | 44.0965 | 44.6471 | 45.1977 | 45.7483 | 46.6919 | 47.6355 | 48.579 | 49.5226 | 50.4662 | 51.4097 | 52.3533 | 53.2969 | 54.2404 | 55.184 | 55.8114 | 56.4387 | 57.0661 | 57.6934 | 58.3208 | 58.9481 | 59.5755 | 60.2028 | 60.8302 | 61.4576 | 62.0849 | 62.7123 | 63.3396 | 63.967 | 64.5943 | 65.1061 | 65.6178 | 66.1296 | 66.6414 | 67.1531 | 67.6649 | 68.1766 | 68.6884 | 69.2001 | 69.7119 | 70.2236 | 70.7354 | 71.2472 | 71.7589 | 72.2707 | 72.4126 | 72.5546 | 72.6966 | 72.8385 | 72.9805 | 73.1225 | 73.2644 | 73.4064 | 73.5484 | 73.6903 | 73.8323 | 73.9743 | 74.1162 | 74.2582 | 74.4002 | 74.5421 | 74.6841 | 74.8261 | 74.968 | 75.11 | 75.252 | 75.3939 | 75.5359 | 75.6779 | 75.8198 | 75.9618 | 76.1038 | 76.2457 | 76.3877 | 76.5297 | 76.5858 | 76.6419 | 76.698 | 76.7541 | 76.8102 | 76.8663 | 76.9224 | 76.9786 | 77.0347 | 77.0908 | 77.1469 | 77.203 | 77.2591 | 77.3152 | 77.3713 | 77.4274 | 77.4836 | 77.5397 | 77.5958 | 77.6519 | 77.708 | 77.7641 | 77.8202 | 77.8763 | 77.9324 | 77.9886 | 78.0447 | 78.1008 | 78.1569 | 78.213 | 78.213 | 78.213 | 78.213 | 78.213 | 78.213 | 78.213 | 78.213 | 78.213 | 78.213 | 78.213 | 78.213 | 78.213 | 78.213 | 78.213 | 78.213 | 78.213 | 78.213 | 78.213 | 78.213 | 78.213 | 78.213 | 78.213 | 78.213 | 78.213 | 78.213 | 78.213 | 78.213 | 78.213 | 78.213 | 78.213 | 78.1288 | 78.0447 | 77.9605 | 77.8763 | 77.7922 | 77.708 | 77.6238 | 77.5397 | 77.4555 | 77.3713 | 77.2872 | 77.203 | 77.1188 | 77.0347 | 76.9505 | 76.8663 | 76.7822 | 76.698 | 76.6138 | 76.5297 | 76.4455 | 76.3613 | 76.2772 | 76.193 | 76.1088 | 76.0247 | 75.9405 | 75.8563 | 75.7722 | 75.688
9.1 | 0 | 26.1 | 43.364 | 46.13 | 55.648 | 65.142 | 72.888 | 77.186 | 78.886 | 78.886 | 76.336 | 1.7764e-15 | 2.61 | 5.22 | 7.83 | 10.44 | 13.05 | 15.66 | 18.27 | 20.88 | 23.49 | 26.1 | 29.5528 | 33.0056 | 36.4584 | 39.9112 | 43.364 | 43.9172 | 44.4704 | 45.0236 | 45.5768 | 46.13 | 47.0818 | 48.0336 | 48.9854 | 49.9372 | 50.889 | 51.8408 | 52.7926 | 53.7444 | 54.6962 | 55.648 | 56.2809 | 56.9139 | 57.5468 | 58.1797 | 58.8127 | 59.4456 | 60.0785 | 60.7115 | 61.3444 | 61.9773 | 62.6103 | 63.2432 | 63.8761 | 64.5091 | 65.142 | 65.6584 | 66.1748 | 66.6912 | 67.2076 | 67.724 | 68.2404 | 68.7568 | 69.2732 | 69.7896 | 70.306 | 70.8224 | 71.3388 | 71.8552 | 72.3716 | 72.888 | 73.0313 | 73.1745 | 73.3178 | 73.4611 | 73.6043 | 73.7476 | 73.8909 | 74.0341 | 74.1774 | 74.3207 | 74.4639 | 74.6072 | 74.7505 | 74.8937 | 75.037 | 75.1803 | 75.3235 | 75.4668 | 75.6101 | 75.7533 | 75.8966 | 76.0399 | 76.1831 | 76.3264 | 76.4697 | 76.6129 | 76.7562 | 76.8995 | 77.0427 | 77.186 | 77.2427 | 77.2993 | 77.356 | 77.4127 | 77.4693 | 77.526 | 77.5827 | 77.6393 | 77.696 | 77.7527 | 77.8093 | 77.866 | 77.9227 | 77.9793 | 78.036 | 78.0927 | 78.1493 | 78.206 | 78.2627 | 78.3193 | 78.376 | 78.4327 | 78.4893 | 78.546 | 78.6027 | 78.6593 | 78.716 | 78.7727 | 78.8293 | 78.886 | 78.886 | 78.886 | 78.886 | 78.886 | 78.886 | 78.886 | 78.886 | 78.886 | 78.886 | 78.886 | 78.886 | 78.886 | 78.886 | 78.886 | 78.886 | 78.886 | 78.886 | 78.886 | 78.886 | 78.886 | 78.886 | 78.886 | 78.886 | 78.886 | 78.886 | 78.886 | 78.886 | 78.886 | 78.886 | 78.886 | 78.801 | 78.716 | 78.631 | 78.546 | 78.461 | 78.376 | 78.291 | 78.206 | 78.121 | 78.036 | 77.951 | 77.866 | 77.781 | 77.696 | 77.611 | 77.526 | 77.441 | 77.356 | 77.271 | 77.186 | 77.101 | 77.016 | 76.931 | 76.846 | 76.761 | 76.676 | 76.591 | 76.506 | 76.421 | 76.336
9.15 | 0 | 26.3167 | 43.7327 | 46.5117 | 56.112 | 65.6897 | 73.5053 | 77.8423 | 79.559 | 79.559 | 76.984 | -1.7764e-15 | 2.6317 | 5.2633 | 7.895 | 10.5267 | 13.1583 | 15.79 | 18.4217 | 21.0533 | 23.685 | 26.3167 | 29.7999 | 33.2831 | 36.7663 | 40.2495 | 43.7327 | 44.2885 | 44.8443 | 45.4001 | 45.9559 | 46.5117 | 47.4717 | 48.4317 | 49.3918 | 50.3518 | 51.3118 | 52.2719 | 53.2319 | 54.1919 | 55.152 | 56.112 | 56.7505 | 57.389 | 58.0275 | 58.666 | 59.3046 | 59.9431 | 60.5816 | 61.2201 | 61.8586 | 62.4971 | 63.1356 | 63.7741 | 64.4126 | 65.0512 | 65.6897 | 66.2107 | 66.7318 | 67.2528 | 67.7738 | 68.2949 | 68.8159 | 69.337 | 69.858 | 70.3791 | 70.9001 | 71.4212 | 71.9422 | 72.4632 | 72.9843 | 73.5053 | 73.6499 | 73.7945 | 73.939 | 74.0836 | 74.2282 | 74.3727 | 74.5173 | 74.6619 | 74.8064 | 74.951 | 75.0956 | 75.2401 | 75.3847 | 75.5293 | 75.6738 | 75.8184 | 75.963 | 76.1075 | 76.2521 | 76.3967 | 76.5412 | 76.6858 | 76.8304 | 76.9749 | 77.1195 | 77.2641 | 77.4086 | 77.5532 | 77.6978 | 77.8423 | 77.8996 | 77.9568 | 78.014 | 78.0712 | 78.1284 | 78.1857 | 78.2429 | 78.3001 | 78.3573 | 78.4146 | 78.4718 | 78.529 | 78.5862 | 78.6434 | 78.7007 | 78.7579 | 78.8151 | 78.8723 | 78.9296 | 78.9868 | 79.044 | 79.1012 | 79.1584 | 79.2157 | 79.2729 | 79.3301 | 79.3873 | 79.4446 | 79.5018 | 79.559 | 79.559 | 79.559 | 79.559 | 79.559 | 79.559 | 79.559 | 79.559 | 79.559 | 79.559 | 79.559 | 79.559 | 79.559 | 79.559 | 79.559 | 79.559 | 79.559 | 79.559 | 79.559 | 79.559 | 79.559 | 79.559 | 79.559 | 79.559 | 79.559 | 79.559 | 79.559 | 79.559 | 79.559 | 79.559 | 79.559 | 79.4732 | 79.3873 | 79.3015 | 79.2157 | 79.1298 | 79.044 | 78.9582 | 78.8723 | 78.7865 | 78.7007 | 78.6148 | 78.529 | 78.4432 | 78.3573 | 78.2715 | 78.1857 | 78.0998 | 78.014 | 77.9282 | 77.8423 | 77.7565 | 77.6707 | 77.5848 | 77.499 | 77.4132 | 77.3273 | 77.2415 | 77.1557 | 77.0698 | 76.984
9.2 | 0 | 26.5333 | 44.1013 | 46.8933 | 56.576 | 66.2373 | 74.1227 | 78.4987 | 80.232 | 80.232 | 77.632 | 0 | 2.6533 | 5.3067 | 7.96 | 10.6133 | 13.2667 | 15.92 | 18.5733 | 21.2267 | 23.88 | 26.5333 | 30.0469 | 33.5605 | 37.0741 | 40.5877 | 44.1013 | 44.6597 | 45.2181 | 45.7765 | 46.3349 | 46.8933 | 47.8616 | 48.8299 | 49.7981 | 50.7664 | 51.7347 | 52.7029 | 53.6712 | 54.6395 | 55.6077 | 56.576 | 57.2201 | 57.8642 | 58.5083 | 59.1524 | 59.7964 | 60.4405 | 61.0846 | 61.7287 | 62.3728 | 63.0169 | 63.661 | 64.3051 | 64.9492 | 65.5932 | 66.2373 | 66.763 | 67.2887 | 67.8144 | 68.3401 | 68.8658 | 69.3915 | 69.9172 | 70.4428 | 70.9685 | 71.4942 | 72.0199 | 72.5456 | 73.0713 | 73.597 | 74.1227 | 74.2685 | 74.4144 | 74.5603 | 74.7061 | 74.852 | 74.9979 | 75.1437 | 75.2896 | 75.4355 | 75.5813 | 75.7272 | 75.8731 | 76.0189 | 76.1648 | 76.3107 | 76.4565 | 76.6024 | 76.7483 | 76.8941 | 77.04 | 77.1859 | 77.3317 | 77.4776 | 77.6235 | 77.7693 | 77.9152 | 78.0611 | 78.2069 | 78.3528 | 78.4987 | 78.5564 | 78.6142 | 78.672 | 78.7298 | 78.7876 | 78.8453 | 78.9031 | 78.9609 | 79.0187 | 79.0764 | 79.1342 | 79.192 | 79.2498 | 79.3076 | 79.3653 | 79.4231 | 79.4809 | 79.5387 | 79.5964 | 79.6542 | 79.712 | 79.7698 | 79.8276 | 79.8853 | 79.9431 | 80.0009 | 80.0587 | 80.1164 | 80.1742 | 80.232 | 80.232 | 80.232 | 80.232 | 80.232 | 80.232 | 80.232 | 80.232 | 80.232 | 80.232 | 80.232 | 80.232 | 80.232 | 80.232 | 80.232 | 80.232 | 80.232 | 80.232 | 80.232 | 80.232 | 80.232 | 80.232 | 80.232 | 80.232 | 80.232 | 80.232 | 80.232 | 80.232 | 80.232 | 80.232 | 80.232 | 80.1453 | 80.0587 | 79.972 | 79.8853 | 79.7987 | 79.712 | 79.6253 | 79.5387 | 79.452 | 79.3653 | 79.2787 | 79.192 | 79.1053 | 79.0187 | 78.932 | 78.8453 | 78.7587 | 78.672 | 78.5853 | 78.4987 | 78.412 | 78.3253 | 78.2387 | 78.152 | 78.0653 | 77.9787 | 77.892 | 77.8053 | 77.7187 | 77.632
9.25 | 0 | 26.75 | 44.47 | 47.275 | 57.04 | 66.785 | 74.74 | 79.155 | 80.905 | 80.905 | 78.28 | 0 | 2.675 | 5.35 | 8.025 | 10.7 | 13.375 | 16.05 | 18.725 | 21.4 | 24.075 | 26.75 | 30.294 | 33.838 | 37.382 | 40.926 | 44.47 | 45.031 | 45.592 | 46.153 | 46.714 | 47.275 | 48.2515 | 49.228 | 50.2045 | 51.181 | 52.1575 | 53.134 | 54.1105 | 55.087 | 56.0635 | 57.04 | 57.6897 | 58.3393 | 58.989 | 59.6387 | 60.2883 | 60.938 | 61.5877 | 62.2373 | 62.887 | 63.5367 | 64.1863 | 64.836 | 65.4857 | 66.1353 | 66.785 | 67.3153 | 67.8457 | 68.376 | 68.9063 | 69.4367 | 69.967 | 70.4973 | 71.0277 | 71.558 | 72.0883 | 72.6187 | 73.149 | 73.6793 | 74.2097 | 74.74 | 74.8872 | 75.0343 | 75.1815 | 75.3287 | 75.4758 | 75.623 | 75.7702 | 75.9173 | 76.0645 | 76.2117 | 76.3588 | 76.506 | 76.6532 | 76.8003 | 76.9475 | 77.0947 | 77.2418 | 77.389 | 77.5362 | 77.6833 | 77.8305 | 77.9777 | 78.1248 | 78.272 | 78.4192 | 78.5663 | 78.7135 | 78.8607 | 79.0078 | 79.155 | 79.2133 | 79.2717 | 79.33 | 79.3883 | 79.4467 | 79.505 | 79.5633 | 79.6217 | 79.68 | 79.7383 | 79.7967 | 79.855 | 79.9133 | 79.9717 | 80.03 | 80.0883 | 80.1467 | 80.205 | 80.2633 | 80.3217 | 80.38 | 80.4383 | 80.4967 | 80.555 | 80.6133 | 80.6717 | 80.73 | 80.7883 | 80.8467 | 80.905 | 80.905 | 80.905 | 80.905 | 80.905 | 80.905 | 80.905 | 80.905 | 80.905 | 80.905 | 80.905 | 80.905 | 80.905 | 80.905 | 80.905 | 80.905 | 80.905 | 80.905 | 80.905 | 80.905 | 80.905 | 80.905 | 80.905 | 80.905 | 80.905 | 80.905 | 80.905 | 80.905 | 80.905 | 80.905 | 80.905 | 80.8175 | 80.73 | 80.6425 | 80.555 | 80.4675 | 80.38 | 80.2925 | 80.205 | 80.1175 | 80.03 | 79.9425 | 79.855 | 79.7675 | 79.68 | 79.5925 | 79.505 | 79.4175 | 79.33 | 79.2425 | 79.155 | 79.0675 | 78.98 | 78.8925 | 78.805 | 78.7175 | 78.63 | 78.5425 | 78.455 | 78.3675 | 78.28
9.3 | 0 | 26.9667 | 44.8387 | 47.6567 | 57.504 | 67.3327 | 75.3573 | 79.8113 | 81.578 | 81.578 | 78.928 | 0 | 2.6967 | 5.3933 | 8.09 | 10.7867 | 13.4833 | 16.18 | 18.8767 | 21.5733 | 24.27 | 26.9667 | 30.5411 | 34.1155 | 37.6899 | 41.2643 | 44.8387 | 45.4023 | 45.9659 | 46.5295 | 47.0931 | 47.6567 | 48.6414 | 49.6261 | 50.6109 | 51.5956 | 52.5803 | 53.5651 | 54.5498 | 55.5345 | 56.5193 | 57.504 | 58.1592 | 58.8145 | 59.4697 | 60.125 | 60.7802 | 61.4355 | 62.0907 | 62.746 | 63.4012 | 64.0564 | 64.7117 | 65.3669 | 66.0222 | 66.6774 | 67.3327 | 67.8676 | 68.4026 | 68.9376 | 69.4726 | 70.0076 | 70.5425 | 71.0775 | 71.6125 | 72.1475 | 72.6824 | 73.2174 | 73.7524 | 74.2874 | 74.8224 | 75.3573 | 75.5058 | 75.6543 | 75.8027 | 75.9512 | 76.0997 | 76.2481 | 76.3966 | 76.5451 | 76.6935 | 76.842 | 76.9905 | 77.1389 | 77.2874 | 77.4359 | 77.5843 | 77.7328 | 77.8813 | 78.0297 | 78.1782 | 78.3267 | 78.4751 | 78.6236 | 78.7721 | 78.9205 | 79.069 | 79.2175 | 79.3659 | 79.5144 | 79.6629 | 79.8113 | 79.8702 | 79.9291 | 79.988 | 80.0469 | 80.1058 | 80.1647 | 80.2236 | 80.2824 | 80.3413 | 80.4002 | 80.4591 | 80.518 | 80.5769 | 80.6358 | 80.6947 | 80.7536 | 80.8124 | 80.8713 | 80.9302 | 80.9891 | 81.048 | 81.1069 | 81.1658 | 81.2247 | 81.2836 | 81.3424 | 81.4013 | 81.4602 | 81.5191 | 81.578 | 81.578 | 81.578 | 81.578 | 81.578 | 81.578 | 81.578 | 81.578 | 81.578 | 81.578 | 81.578 | 81.578 | 81.578 | 81.578 | 81.578 | 81.578 | 81.578 | 81.578 | 81.578 | 81.578 | 81.578 | 81.578 | 81.578 | 81.578 | 81.578 | 81.578 | 81.578 | 81.578 | 81.578 | 81.578 | 81.578 | 81.4897 | 81.4013 | 81.313 | 81.2247 | 81.1363 | 81.048 | 80.9597 | 80.8713 | 80.783 | 80.6947 | 80.6063 | 80.518 | 80.4297 | 80.3413 | 80.253 | 80.1647 | 80.0763 | 79.988 | 79.8997 | 79.8113 | 79.723 | 79.6347 | 79.5463 | 79.458 | 79.3697 | 79.2813 | 79.193 | 79.1047 | 79.0163 | 78.928
9.35 | 0 | 27.1833 | 45.2073 | 48.0383 | 57.968 | 67.8803 | 75.9747 | 80.4677 | 82.251 | 82.251 | 79.576 | 0 | 2.7183 | 5.4367 | 8.155 | 10.8733 | 13.5917 | 16.31 | 19.0283 | 21.7467 | 24.465 | 27.1833 | 30.7881 | 34.3929 | 37.9977 | 41.6025 | 45.2073 | 45.7735 | 46.3397 | 46.9059 | 47.4721 | 48.0383 | 49.0313 | 50.0243 | 51.0172 | 52.0102 | 53.0032 | 53.9961 | 54.9891 | 55.9821 | 56.975 | 57.968 | 58.6288 | 59.2896 | 59.9505 | 60.6113 | 61.2721 | 61.9329 | 62.5938 | 63.2546 | 63.9154 | 64.5762 | 65.237 | 65.8979 | 66.5587 | 67.2195 | 67.8803 | 68.42 | 68.9596 | 69.4992 | 70.0388 | 70.5784 | 71.1181 | 71.6577 | 72.1973 | 72.7369 | 73.2766 | 73.8162 | 74.3558 | 74.8954 | 75.435 | 75.9747 | 76.1244 | 76.2742 | 76.424 | 76.5737 | 76.7235 | 76.8733 | 77.023 | 77.1728 | 77.3226 | 77.4723 | 77.6221 | 77.7719 | 77.9216 | 78.0714 | 78.2212 | 78.3709 | 78.5207 | 78.6705 | 78.8202 | 78.97 | 79.1198 | 79.2695 | 79.4193 | 79.5691 | 79.7188 | 79.8686 | 80.0184 | 80.1681 | 80.3179 | 80.4677 | 80.5271 | 80.5866 | 80.646 | 80.7054 | 80.7649 | 80.8243 | 80.8838 | 80.9432 | 81.0027 | 81.0621 | 81.1216 | 81.181 | 81.2404 | 81.2999 | 81.3593 | 81.4188 | 81.4782 | 81.5377 | 81.5971 | 81.6566 | 81.716 | 81.7754 | 81.8349 | 81.8943 | 81.9538 | 82.0132 | 82.0727 | 82.1321 | 82.1916 | 82.251 | 82.251 | 82.251 | 82.251 | 82.251 | 82.251 | 82.251 | 82.251 | 82.251 | 82.251 | 82.251 | 82.251 | 82.251 | 82.251 | 82.251 | 82.251 | 82.251 | 82.251 | 82.251 | 82.251 | 82.251 | 82.251 | 82.251 | 82.251 | 82.251 | 82.251 | 82.251 | 82.251 | 82.251 | 82.251 | 82.251 | 82.1618 | 82.0727 | 81.9835 | 81.8943 | 81.8052 | 81.716 | 81.6268 | 81.5377 | 81.4485 | 81.3593 | 81.2702 | 81.181 | 81.0918 | 81.0027 | 80.9135 | 80.8243 | 80.7352 | 80.646 | 80.5568 | 80.4677 | 80.3785 | 80.2893 | 80.2002 | 80.111 | 80.0218 | 79.9327 | 79.8435 | 79.7543 | 79.6652 | 79.576
9.4 | 0 | 27.4 | 45.576 | 48.42 | 58.432 | 68.428 | 76.592 | 81.124 | 82.924 | 82.924 | 80.224 | 0 | 2.74 | 5.48 | 8.22 | 10.96 | 13.7 | 16.44 | 19.18 | 21.92 | 24.66 | 27.4 | 31.0352 | 34.6704 | 38.3056 | 41.9408 | 45.576 | 46.1448 | 46.7136 | 47.2824 | 47.8512 | 48.42 | 49.4212 | 50.4224 | 51.4236 | 52.4248 | 53.426 | 54.4272 | 55.4284 | 56.4296 | 57.4308 | 58.432 | 59.0984 | 59.7648 | 60.4312 | 61.0976 | 61.764 | 62.4304 | 63.0968 | 63.7632 | 64.4296 | 65.096 | 65.7624 | 66.4288 | 67.0952 | 67.7616 | 68.428 | 68.9723 | 69.5165 | 70.0608 | 70.6051 | 71.1493 | 71.6936 | 72.2379 | 72.7821 | 73.3264 | 73.8707 | 74.4149 | 74.9592 | 75.5035 | 76.0477 | 76.592 | 76.7431 | 76.8941 | 77.0452 | 77.1963 | 77.3473 | 77.4984 | 77.6495 | 77.8005 | 77.9516 | 78.1027 | 78.2537 | 78.4048 | 78.5559 | 78.7069 | 78.858 | 79.0091 | 79.1601 | 79.3112 | 79.4623 | 79.6133 | 79.7644 | 79.9155 | 80.0665 | 80.2176 | 80.3687 | 80.5197 | 80.6708 | 80.8219 | 80.9729 | 81.124 | 81.184 | 81.244 | 81.304 | 81.364 | 81.424 | 81.484 | 81.544 | 81.604 | 81.664 | 81.724 | 81.784 | 81.844 | 81.904 | 81.964 | 82.024 | 82.084 | 82.144 | 82.204 | 82.264 | 82.324 | 82.384 | 82.444 | 82.504 | 82.564 | 82.624 | 82.684 | 82.744 | 82.804 | 82.864 | 82.924 | 82.924 | 82.924 | 82.924 | 82.924 | 82.924 | 82.924 | 82.924 | 82.924 | 82.924 | 82.924 | 82.924 | 82.924 | 82.924 | 82.924 | 82.924 | 82.924 | 82.924 | 82.924 | 82.924 | 82.924 | 82.924 | 82.924 | 82.924 | 82.924 | 82.924 | 82.924 | 82.924 | 82.924 | 82.924 | 82.924 | 82.834 | 82.744 | 82.654 | 82.564 | 82.474 | 82.384 | 82.294 | 82.204 | 82.114 | 82.024 | 81.934 | 81.844 | 81.754 | 81.664 | 81.574 | 81.484 | 81.394 | 81.304 | 81.214 | 81.124 | 81.034 | 80.944 | 80.854 | 80.764 | 80.674 | 80.584 | 80.494 | 80.404 | 80.314 | 80.224
9.45 | 0 | 27.6167 | 45.9447 | 48.8017 | 58.896 | 68.9757 | 77.2093 | 81.7803 | 83.597 | 83.597 | 80.872 | 0 | 2.7617 | 5.5233 | 8.285 | 11.0467 | 13.8083 | 16.57 | 19.3317 | 22.0933 | 24.855 | 27.6167 | 31.2823 | 34.9479 | 38.6135 | 42.2791 | 45.9447 | 46.5161 | 47.0875 | 47.6589 | 48.2303 | 48.8017 | 49.8111 | 50.8205 | 51.83 | 52.8394 | 53.8488 | 54.8583 | 55.8677 | 56.8771 | 57.8866 | 58.896 | 59.568 | 60.24 | 60.9119 | 61.5839 | 62.2559 | 62.9279 | 63.5998 | 64.2718 | 64.9438 | 65.6158 | 66.2878 | 66.9597 | 67.6317 | 68.3037 | 68.9757 | 69.5246 | 70.0735 | 70.6224 | 71.1713 | 71.7202 | 72.2691 | 72.818 | 73.367 | 73.9159 | 74.4648 | 75.0137 | 75.5626 | 76.1115 | 76.6604 | 77.2093 | 77.3617 | 77.5141 | 77.6664 | 77.8188 | 77.9712 | 78.1235 | 78.2759 | 78.4283 | 78.5806 | 78.733 | 78.8854 | 79.0377 | 79.1901 | 79.3425 | 79.4948 | 79.6472 | 79.7996 | 79.9519 | 80.1043 | 80.2567 | 80.409 | 80.5614 | 80.7138 | 80.8661 | 81.0185 | 81.1709 | 81.3232 | 81.4756 | 81.628 | 81.7803 | 81.8409 | 81.9014 | 81.962 | 82.0226 | 82.0831 | 82.1437 | 82.2042 | 82.2648 | 82.3253 | 82.3859 | 82.4464 | 82.507 | 82.5676 | 82.6281 | 82.6887 | 82.7492 | 82.8098 | 82.8703 | 82.9309 | 82.9914 | 83.052 | 83.1126 | 83.1731 | 83.2337 | 83.2942 | 83.3548 | 83.4153 | 83.4759 | 83.5364 | 83.597 | 83.597 | 83.597 | 83.597 | 83.597 | 83.597 | 83.597 | 83.597 | 83.597 | 83.597 | 83.597 | 83.597 | 83.597 | 83.597 | 83.597 | 83.597 | 83.597 | 83.597 | 83.597 | 83.597 | 83.597 | 83.597 | 83.597 | 83.597 | 83.597 | 83.597 | 83.597 | 83.597 | 83.597 | 83.597 | 83.597 | 83.5062 | 83.4153 | 83.3245 | 83.2337 | 83.1428 | 83.052 | 82.9612 | 82.8703 | 82.7795 | 82.6887 | 82.5978 | 82.507 | 82.4162 | 82.3253 | 82.2345 | 82.1437 | 82.0528 | 81.962 | 81.8712 | 81.7803 | 81.6895 | 81.5987 | 81.5078 | 81.417 | 81.3262 | 81.2353 | 81.1445 | 81.0537 | 80.9628 | 80.872
9.5 | 0 | 27.8333 | 46.3133 | 49.1833 | 59.36 | 69.5233 | 77.8267 | 82.4367 | 84.27 | 84.27 | 81.52 | -1.7764e-15 | 2.7833 | 5.5667 | 8.35 | 11.1333 | 13.9167 | 16.7 | 19.4833 | 22.2667 | 25.05 | 27.8333 | 31.5293 | 35.2253 | 38.9213 | 42.6173 | 46.3133 | 46.8873 | 47.4613 | 48.0353 | 48.6093 | 49.1833 | 50.201 | 51.2187 | 52.2363 | 53.254 | 54.2717 | 55.2893 | 56.307 | 57.3247 | 58.3423 | 59.36 | 60.0376 | 60.7151 | 61.3927 | 62.0702 | 62.7478 | 63.4253 | 64.1029 | 64.7804 | 65.458 | 66.1356 | 66.8131 | 67.4907 | 68.1682 | 68.8458 | 69.5233 | 70.0769 | 70.6304 | 71.184 | 71.7376 | 72.2911 | 72.8447 | 73.3982 | 73.9518 | 74.5053 | 75.0589 | 75.6124 | 76.166 | 76.7196 | 77.2731 | 77.8267 | 77.9803 | 78.134 | 78.2877 | 78.4413 | 78.595 | 78.7487 | 78.9023 | 79.056 | 79.2097 | 79.3633 | 79.517 | 79.6707 | 79.8243 | 79.978 | 80.1317 | 80.2853 | 80.439 | 80.5927 | 80.7463 | 80.9 | 81.0537 | 81.2073 | 81.361 | 81.5147 | 81.6683 | 81.822 | 81.9757 | 82.1293 | 82.283 | 82.4367 | 82.4978 | 82.5589 | 82.62 | 82.6811 | 82.7422 | 82.8033 | 82.8644 | 82.9256 | 82.9867 | 83.0478 | 83.1089 | 83.17 | 83.2311 | 83.2922 | 83.3533 | 83.4144 | 83.4756 | 83.5367 | 83.5978 | 83.6589 | 83.72 | 83.7811 | 83.8422 | 83.9033 | 83.9644 | 84.0256 | 84.0867 | 84.1478 | 84.2089 | 84.27 | 84.27 | 84.27 | 84.27 | 84.27 | 84.27 | 84.27 | 84.27 | 84.27 | 84.27 | 84.27 | 84.27 | 84.27 | 84.27 | 84.27 | 84.27 | 84.27 | 84.27 | 84.27 | 84.27 | 84.27 | 84.27 | 84.27 | 84.27 | 84.27 | 84.27 | 84.27 | 84.27 | 84.27 | 84.27 | 84.27 | 84.1783 | 84.0867 | 83.995 | 83.9033 | 83.8117 | 83.72 | 83.6283 | 83.5367 | 83.445 | 83.3533 | 83.2617 | 83.17 | 83.0783 | 82.9867 | 82.895 | 82.8033 | 82.7117 | 82.62 | 82.5283 | 82.4367 | 82.345 | 82.2533 | 82.1617 | 82.07 | 81.9783 | 81.8867 | 81.795 | 81.7033 | 81.6117 | 81.52
9.55 | 0 | 28.05 | 46.682 | 49.565 | 59.824 | 70.071 | 78.444 | 83.093 | 84.943 | 84.943 | 82.168 | -1.7764e-15 | 2.805 | 5.61 | 8.415 | 11.22 | 14.025 | 16.83 | 19.635 | 22.44 | 25.245 | 28.05 | 31.7764 | 35.5028 | 39.2292 | 42.9556 | 46.682 | 47.2586 | 47.8352 | 48.4118 | 48.9884 | 49.565 | 50.5909 | 51.6168 | 52.6427 | 53.6686 | 54.6945 | 55.7204 | 56.7463 | 57.7722 | 58.7981 | 59.824 | 60.5071 | 61.1903 | 61.8734 | 62.5565 | 63.2397 | 63.9228 | 64.6059 | 65.2891 | 65.9722 | 66.6553 | 67.3385 | 68.0216 | 68.7047 | 69.3879 | 70.071 | 70.6292 | 71.1874 | 71.7456 | 72.3038 | 72.862 | 73.4202 | 73.9784 | 74.5366 | 75.0948 | 75.653 | 76.2112 | 76.7694 | 77.3276 | 77.8858 | 78.444 | 78.599 | 78.7539 | 78.9089 | 79.0639 | 79.2188 | 79.3738 | 79.5288 | 79.6837 | 79.8387 | 79.9937 | 80.1486 | 80.3036 | 80.4586 | 80.6135 | 80.7685 | 80.9235 | 81.0784 | 81.2334 | 81.3884 | 81.5433 | 81.6983 | 81.8533 | 82.0082 | 82.1632 | 82.3182 | 82.4731 | 82.6281 | 82.7831 | 82.938 | 83.093 | 83.1547 | 83.2163 | 83.278 | 83.3397 | 83.4013 | 83.463 | 83.5247 | 83.5863 | 83.648 | 83.7097 | 83.7713 | 83.833 | 83.8947 | 83.9563 | 84.018 | 84.0797 | 84.1413 | 84.203 | 84.2647 | 84.3263 | 84.388 | 84.4497 | 84.5113 | 84.573 | 84.6347 | 84.6963 | 84.758 | 84.8197 | 84.8813 | 84.943 | 84.943 | 84.943 | 84.943 | 84.943 | 84.943 | 84.943 | 84.943 | 84.943 | 84.943 | 84.943 | 84.943 | 84.943 | 84.943 | 84.943 | 84.943 | 84.943 | 84.943 | 84.943 | 84.943 | 84.943 | 84.943 | 84.943 | 84.943 | 84.943 | 84.943 | 84.943 | 84.943 | 84.943 | 84.943 | 84.943 | 84.8505 | 84.758 | 84.6655 | 84.573 | 84.4805 | 84.388 | 84.2955 | 84.203 | 84.1105 | 84.018 | 83.9255 | 83.833 | 83.7405 | 83.648 | 83.5555 | 83.463 | 83.3705 | 83.278 | 83.1855 | 83.093 | 83.0005 | 82.908 | 82.8155 | 82.723 | 82.6305 | 82.538 | 82.4455 | 82.353 | 82.2605 | 82.168
9.6 | 0 | 28.2667 | 47.0507 | 49.9467 | 60.288 | 70.6187 | 79.0613 | 83.7493 | 85.616 | 85.616 | 82.816 | -1.7764e-15 | 2.8267 | 5.6533 | 8.48 | 11.3067 | 14.1333 | 16.96 | 19.7867 | 22.6133 | 25.44 | 28.2667 | 32.0235 | 35.7803 | 39.5371 | 43.2939 | 47.0507 | 47.6299 | 48.2091 | 48.7883 | 49.3675 | 49.9467 | 50.9808 | 52.0149 | 53.0491 | 54.0832 | 55.1173 | 56.1515 | 57.1856 | 58.2197 | 59.2539 | 60.288 | 60.9767 | 61.6654 | 62.3541 | 63.0428 | 63.7316 | 64.4203 | 65.109 | 65.7977 | 66.4864 | 67.1751 | 67.8638 | 68.5525 | 69.2412 | 69.93 | 70.6187 | 71.1815 | 71.7444 | 72.3072 | 72.87 | 73.4329 | 73.9957 | 74.5586 | 75.1214 | 75.6843 | 76.2471 | 76.81 | 77.3728 | 77.9356 | 78.4985 | 79.0613 | 79.2176 | 79.3739 | 79.5301 | 79.6864 | 79.8427 | 79.9989 | 80.1552 | 80.3115 | 80.4677 | 80.624 | 80.7803 | 80.9365 | 81.0928 | 81.2491 | 81.4053 | 81.5616 | 81.7179 | 81.8741 | 82.0304 | 82.1867 | 82.3429 | 82.4992 | 82.6555 | 82.8117 | 82.968 | 83.1243 | 83.2805 | 83.4368 | 83.5931 | 83.7493 | 83.8116 | 83.8738 | 83.936 | 83.9982 | 84.0604 | 84.1227 | 84.1849 | 84.2471 | 84.3093 | 84.3716 | 84.4338 | 84.496 | 84.5582 | 84.6204 | 84.6827 | 84.7449 | 84.8071 | 84.8693 | 84.9316 | 84.9938 | 85.056 | 85.1182 | 85.1804 | 85.2427 | 85.3049 | 85.3671 | 85.4293 | 85.4916 | 85.5538 | 85.616 | 85.616 | 85.616 | 85.616 | 85.616 | 85.616 | 85.616 | 85.616 | 85.616 | 85.616 | 85.616 | 85.616 | 85.616 | 85.616 | 85.616 | 85.616 | 85.616 | 85.616 | 85.616 | 85.616 | 85.616 | 85.616 | 85.616 | 85.616 | 85.616 | 85.616 | 85.616 | 85.616 | 85.616 | 85.616 | 85.616 | 85.5227 | 85.4293 | 85.336 | 85.2427 | 85.1493 | 85.056 | 84.9627 | 84.8693 | 84.776 | 84.6827 | 84.5893 | 84.496 | 84.4027 | 84.3093 | 84.216 | 84.1227 | 84.0293 | 83.936 | 83.8427 | 83.7493 | 83.656 | 83.5627 | 83.4693 | 83.376 | 83.2827 | 83.1893 | 83.096 | 83.0027 | 82.9093 | 82.816
9.65 | 0 | 28.4833 | 47.4193 | 50.3283 | 60.752 | 71.1663 | 79.6787 | 84.4057 | 86.289 | 86.289 | 83.464 | 1.7764e-15 | 2.8483 | 5.6967 | 8.545 | 11.3933 | 14.2417 | 17.09 | 19.9383 | 22.7867 | 25.635 | 28.4833 | 32.2705 | 36.0577 | 39.8449 | 43.6321 | 47.4193 | 48.0011 | 48.5829 | 49.1647 | 49.7465 | 50.3283 | 51.3707 | 52.4131 | 53.4554 | 54.4978 | 55.5402 | 56.5825 | 57.6249 | 58.6673 | 59.7096 | 60.752 | 61.4463 | 62.1406 | 62.8349 | 63.5292 | 64.2234 | 64.9177 | 65.612 | 66.3063 | 67.0006 | 67.6949 | 68.3892 | 69.0835 | 69.7778 | 70.472 | 71.1663 | 71.7338 | 72.3013 | 72.8688 | 73.4363 | 74.0038 | 74.5713 | 75.1388 | 75.7062 | 76.2737 | 76.8412 | 77.4087 | 77.9762 | 78.5437 | 79.1112 | 79.6787 | 79.8362 | 79.9938 | 80.1514 | 80.3089 | 80.4665 | 80.6241 | 80.7816 | 80.9392 | 81.0968 | 81.2543 | 81.4119 | 81.5695 | 81.727 | 81.8846 | 82.0422 | 82.1997 | 82.3573 | 82.5149 | 82.6724 | 82.83 | 82.9876 | 83.1451 | 83.3027 | 83.4603 | 83.6178 | 83.7754 | 83.933 | 84.0905 | 84.2481 | 84.4057 | 84.4684 | 84.5312 | 84.594 | 84.6568 | 84.7196 | 84.7823 | 84.8451 | 84.9079 | 84.9707 | 85.0334 | 85.0962 | 85.159 | 85.2218 | 85.2846 | 85.3473 | 85.4101 | 85.4729 | 85.5357 | 85.5984 | 85.6612 | 85.724 | 85.7868 | 85.8496 | 85.9123 | 85.9751 | 86.0379 | 86.1007 | 86.1634 | 86.2262 | 86.289 | 86.289 | 86.289 | 86.289 | 86.289 | 86.289 | 86.289 | 86.289 | 86.289 | 86.289 | 86.289 | 86.289 | 86.289 | 86.289 | 86.289 | 86.289 | 86.289 | 86.289 | 86.289 | 86.289 | 86.289 | 86.289 | 86.289 | 86.289 | 86.289 | 86.289 | 86.289 | 86.289 | 86.289 | 86.289 | 86.289 | 86.1948 | 86.1007 | 86.0065 | 85.9123 | 85.8182 | 85.724 | 85.6298 | 85.5357 | 85.4415 | 85.3473 | 85.2532 | 85.159 | 85.0648 | 84.9707 | 84.8765 | 84.7823 | 84.6882 | 84.594 | 84.4998 | 84.4057 | 84.3115 | 84.2173 | 84.1232 | 84.029 | 83.9348 | 83.8407 | 83.7465 | 83.6523 | 83.5582 | 83.464
9.7 | 0 | 28.7 | 47.788 | 50.71 | 61.216 | 71.714 | 80.296 | 85.062 | 86.962 | 86.962 | 84.112 | 0 | 2.87 | 5.74 | 8.61 | 11.48 | 14.35 | 17.22 | 20.09 | 22.96 | 25.83 | 28.7 | 32.5176 | 36.3352 | 40.1528 | 43.9704 | 47.788 | 48.3724 | 48.9568 | 49.5412 | 50.1256 | 50.71 | 51.7606 | 52.8112 | 53.8618 | 54.9124 | 55.963 | 57.0136 | 58.0642 | 59.1148 | 60.1654 | 61.216 | 61.9159 | 62.6157 | 63.3156 | 64.0155 | 64.7153 | 65.4152 | 66.1151 | 66.8149 | 67.5148 | 68.2147 | 68.9145 | 69.6144 | 70.3143 | 71.0141 | 71.714 | 72.2861 | 72.8583 | 73.4304 | 74.0025 | 74.5747 | 75.1468 | 75.7189 | 76.2911 | 76.8632 | 77.4353 | 78.0075 | 78.5796 | 79.1517 | 79.7239 | 80.296 | 80.4549 | 80.6137 | 80.7726 | 80.9315 | 81.0903 | 81.2492 | 81.4081 | 81.5669 | 81.7258 | 81.8847 | 82.0435 | 82.2024 | 82.3613 | 82.5201 | 82.679 | 82.8379 | 82.9967 | 83.1556 | 83.3145 | 83.4733 | 83.6322 | 83.7911 | 83.9499 | 84.1088 | 84.2677 | 84.4265 | 84.5854 | 84.7443 | 84.9031 | 85.062 | 85.1253 | 85.1887 | 85.252 | 85.3153 | 85.3787 | 85.442 | 85.5053 | 85.5687 | 85.632 | 85.6953 | 85.7587 | 85.822 | 85.8853 | 85.9487 | 86.012 | 86.0753 | 86.1387 | 86.202 | 86.2653 | 86.3287 | 86.392 | 86.4553 | 86.5187 | 86.582 | 86.6453 | 86.7087 | 86.772 | 86.8353 | 86.8987 | 86.962 | 86.962 | 86.962 | 86.962 | 86.962 | 86.962 | 86.962 | 86.962 | 86.962 | 86.962 | 86.962 | 86.962 | 86.962 | 86.962 | 86.962 | 86.962 | 86.962 | 86.962 | 86.962 | 86.962 | 86.962 | 86.962 | 86.962 | 86.962 | 86.962 | 86.962 | 86.962 | 86.962 | 86.962 | 86.962 | 86.962 | 86.867 | 86.772 | 86.677 | 86.582 | 86.487 | 86.392 | 86.297 | 86.202 | 86.107 | 86.012 | 85.917 | 85.822 | 85.727 | 85.632 | 85.537 | 85.442 | 85.347 | 85.252 | 85.157 | 85.062 | 84.967 | 84.872 | 84.777 | 84.682 | 84.587 | 84.492 | 84.397 | 84.302 | 84.207 | 84.112
9.75 | 0 | 28.9167 | 48.1567 | 51.0917 | 61.68 | 72.2617 | 80.9133 | 85.7183 | 87.635 | 87.635 | 84.76 | 0 | 2.8917 | 5.7833 | 8.675 | 11.5667 | 14.4583 | 17.35 | 20.2417 | 23.1333 | 26.025 | 28.9167 | 32.7647 | 36.6127 | 40.4607 | 44.3087 | 48.1567 | 48.7437 | 49.3307 | 49.9177 | 50.5047 | 51.0917 | 52.1505 | 53.2093 | 54.2682 | 55.327 | 56.3858 | 57.4447 | 58.5035 | 59.5623 | 60.6212 | 61.68 | 62.3854 | 63.0909 | 63.7963 | 64.5018 | 65.2072 | 65.9127 | 66.6181 | 67.3236 | 68.029 | 68.7344 | 69.4399 | 70.1453 | 70.8508 | 71.5562 | 72.2617 | 72.8384 | 73.4152 | 73.992 | 74.5688 | 75.1456 | 75.7223 | 76.2991 | 76.8759 | 77.4527 | 78.0294 | 78.6062 | 79.183 | 79.7598 | 80.3366 | 80.9133 | 81.0735 | 81.2337 | 81.3938 | 81.554 | 81.7142 | 81.8743 | 82.0345 | 82.1947 | 82.3548 | 82.515 | 82.6752 | 82.8353 | 82.9955 | 83.1557 | 83.3158 | 83.476 | 83.6362 | 83.7963 | 83.9565 | 84.1167 | 84.2768 | 84.437 | 84.5972 | 84.7573 | 84.9175 | 85.0777 | 85.2378 | 85.398 | 85.5582 | 85.7183 | 85.7822 | 85.8461 | 85.91 | 85.9739 | 86.0378 | 86.1017 | 86.1656 | 86.2294 | 86.2933 | 86.3572 | 86.4211 | 86.485 | 86.5489 | 86.6128 | 86.6767 | 86.7406 | 86.8044 | 86.8683 | 86.9322 | 86.9961 | 87.06 | 87.1239 | 87.1878 | 87.2517 | 87.3156 | 87.3794 | 87.4433 | 87.5072 | 87.5711 | 87.635 | 87.635 | 87.635 | 87.635 | 87.635 | 87.635 | 87.635 | 87.635 | 87.635 | 87.635 | 87.635 | 87.635 | 87.635 | 87.635 | 87.635 | 87.635 | 87.635 | 87.635 | 87.635 | 87.635 | 87.635 | 87.635 | 87.635 | 87.635 | 87.635 | 87.635 | 87.635 | 87.635 | 87.635 | 87.635 | 87.635 | 87.5392 | 87.4433 | 87.3475 | 87.2517 | 87.1558 | 87.06 | 86.9642 | 86.8683 | 86.7725 | 86.6767 | 86.5808 | 86.485 | 86.3892 | 86.2933 | 86.1975 | 86.1017 | 86.0058 | 85.91 | 85.8142 | 85.7183 | 85.6225 | 85.5267 | 85.4308 | 85.335 | 85.2392 | 85.1433 | 85.0475 | 84.9517 | 84.8558 | 84.76
9.8 | 0 | 29.1333 | 48.5253 | 51.4733 | 62.144 | 72.8093 | 81.5307 | 86.3747 | 88.308 | 88.308 | 85.408 | 0 | 2.9133 | 5.8267 | 8.74 | 11.6533 | 14.5667 | 17.48 | 20.3933 | 23.3067 | 26.22 | 29.1333 | 33.0117 | 36.8901 | 40.7685 | 44.6469 | 48.5253 | 49.1149 | 49.7045 | 50.2941 | 50.8837 | 51.4733 | 52.5404 | 53.6075 | 54.6745 | 55.7416 | 56.8087 | 57.8757 | 58.9428 | 60.0099 | 61.0769 | 62.144 | 62.855 | 63.566 | 64.2771 | 64.9881 | 65.6991 | 66.4101 | 67.1212 | 67.8322 | 68.5432 | 69.2542 | 69.9652 | 70.6763 | 71.3873 | 72.0983 | 72.8093 | 73.3908 | 73.9722 | 74.5536 | 75.135 | 75.7164 | 76.2979 | 76.8793 | 77.4607 | 78.0421 | 78.6236 | 79.205 | 79.7864 | 80.3678 | 80.9492 | 81.5307 | 81.6921 | 81.8536 | 82.0151 | 82.1765 | 82.338 | 82.4995 | 82.6609 | 82.8224 | 82.9839 | 83.1453 | 83.3068 | 83.4683 | 83.6297 | 83.7912 | 83.9527 | 84.1141 | 84.2756 | 84.4371 | 84.5985 | 84.76 | 84.9215 | 85.0829 | 85.2444 | 85.4059 | 85.5673 | 85.7288 | 85.8903 | 86.0517 | 86.2132 | 86.3747 | 86.4391 | 86.5036 | 86.568 | 86.6324 | 86.6969 | 86.7613 | 86.8258 | 86.8902 | 86.9547 | 87.0191 | 87.0836 | 87.148 | 87.2124 | 87.2769 | 87.3413 | 87.4058 | 87.4702 | 87.5347 | 87.5991 | 87.6636 | 87.728 | 87.7924 | 87.8569 | 87.9213 | 87.9858 | 88.0502 | 88.1147 | 88.1791 | 88.2436 | 88.308 | 88.308 | 88.308 | 88.308 | 88.308 | 88.308 | 88.308 | 88.308 | 88.308 | 88.308 | 88.308 | 88.308 | 88.308 | 88.308 | 88.308 | 88.308 | 88.308 | 88.308 | 88.308 | 88.308 | 88.308 | 88.308 | 88.308 | 88.308 | 88.308 | 88.308 | 88.308 | 88.308 | 88.308 | 88.308 | 88.308 | 88.2113 | 88.1147 | 88.018 | 87.9213 | 87.8247 | 87.728 | 87.6313 | 87.5347 | 87.438 | 87.3413 | 87.2447 | 87.148 | 87.0513 | 86.9547 | 86.858 | 86.7613 | 86.6647 | 86.568 | 86.4713 | 86.3747 | 86.278 | 86.1813 | 86.0847 | 85.988 | 85.8913 | 85.7947 | 85.698 | 85.6013 | 85.5047 | 85.408
9.85 | 0 | 29.35 | 48.894 | 51.855 | 62.608 | 73.357 | 82.148 | 87.031 | 88.981 | 88.981 | 86.056 | -1.7764e-15 | 2.935 | 5.87 | 8.805 | 11.74 | 14.675 | 17.61 | 20.545 | 23.48 | 26.415 | 29.35 | 33.2588 | 37.1676 | 41.0764 | 44.9852 | 48.894 | 49.4862 | 50.0784 | 50.6706 | 51.2628 | 51.855 | 52.9303 | 54.0056 | 55.0809 | 56.1562 | 57.2315 | 58.3068 | 59.3821 | 60.4574 | 61.5327 | 62.608 | 63.3246 | 64.0412 | 64.7578 | 65.4744 | 66.191 | 66.9076 | 67.6242 | 68.3408 | 69.0574 | 69.774 | 70.4906 | 71.2072 | 71.9238 | 72.6404 | 73.357 | 73.9431 | 74.5291 | 75.1152 | 75.7013 | 76.2873 | 76.8734 | 77.4595 | 78.0455 | 78.6316 | 79.2177 | 79.8037 | 80.3898 | 80.9759 | 81.5619 | 82.148 | 82.3108 | 82.4735 | 82.6363 | 82.7991 | 82.9618 | 83.1246 | 83.2874 | 83.4501 | 83.6129 | 83.7757 | 83.9384 | 84.1012 | 84.264 | 84.4267 | 84.5895 | 84.7523 | 84.915 | 85.0778 | 85.2406 | 85.4033 | 85.5661 | 85.7289 | 85.8916 | 86.0544 | 86.2172 | 86.3799 | 86.5427 | 86.7055 | 86.8682 | 87.031 | 87.096 | 87.161 | 87.226 | 87.291 | 87.356 | 87.421 | 87.486 | 87.551 | 87.616 | 87.681 | 87.746 | 87.811 | 87.876 | 87.941 | 88.006 | 88.071 | 88.136 | 88.201 | 88.266 | 88.331 | 88.396 | 88.461 | 88.526 | 88.591 | 88.656 | 88.721 | 88.786 | 88.851 | 88.916 | 88.981 | 88.981 | 88.981 | 88.981 | 88.981 | 88.981 | 88.981 | 88.981 | 88.981 | 88.981 | 88.981 | 88.981 | 88.981 | 88.981 | 88.981 | 88.981 | 88.981 | 88.981 | 88.981 | 88.981 | 88.981 | 88.981 | 88.981 | 88.981 | 88.981 | 88.981 | 88.981 | 88.981 | 88.981 | 88.981 | 88.981 | 88.8835 | 88.786 | 88.6885 | 88.591 | 88.4935 | 88.396 | 88.2985 | 88.201 | 88.1035 | 88.006 | 87.9085 | 87.811 | 87.7135 | 87.616 | 87.5185 | 87.421 | 87.3235 | 87.226 | 87.1285 | 87.031 | 86.9335 | 86.836 | 86.7385 | 86.641 | 86.5435 | 86.446 | 86.3485 | 86.251 | 86.1535 | 86.056
9.9 | 0 | 29.5667 | 49.2627 | 52.2367 | 63.072 | 73.9047 | 82.7653 | 87.6873 | 89.654 | 89.654 | 86.704 | -1.7764e-15 | 2.9567 | 5.9133 | 8.87 | 11.8267 | 14.7833 | 17.74 | 20.6967 | 23.6533 | 26.61 | 29.5667 | 33.5059 | 37.4451 | 41.3843 | 45.3235 | 49.2627 | 49.8575 | 50.4523 | 51.0471 | 51.6419 | 52.2367 | 53.3202 | 54.4037 | 55.4873 | 56.5708 | 57.6543 | 58.7379 | 59.8214 | 60.9049 | 61.9885 | 63.072 | 63.7942 | 64.5164 | 65.2385 | 65.9607 | 66.6829 | 67.4051 | 68.1272 | 68.8494 | 69.5716 | 70.2938 | 71.016 | 71.7381 | 72.4603 | 73.1825 | 73.9047 | 74.4954 | 75.0861 | 75.6768 | 76.2675 | 76.8582 | 77.4489 | 78.0396 | 78.6304 | 79.2211 | 79.8118 | 80.4025 | 80.9932 | 81.5839 | 82.1746 | 82.7653 | 82.9294 | 83.0935 | 83.2575 | 83.4216 | 83.5857 | 83.7497 | 83.9138 | 84.0779 | 84.2419 | 84.406 | 84.5701 | 84.7341 | 84.8982 | 85.0623 | 85.2263 | 85.3904 | 85.5545 | 85.7185 | 85.8826 | 86.0467 | 86.2107 | 86.3748 | 86.5389 | 86.7029 | 86.867 | 87.0311 | 87.1951 | 87.3592 | 87.5233 | 87.6873 | 87.7529 | 87.8184 | 87.884 | 87.9496 | 88.0151 | 88.0807 | 88.1462 | 88.2118 | 88.2773 | 88.3429 | 88.4084 | 88.474 | 88.5396 | 88.6051 | 88.6707 | 88.7362 | 88.8018 | 88.8673 | 88.9329 | 88.9984 | 89.064 | 89.1296 | 89.1951 | 89.2607 | 89.3262 | 89.3918 | 89.4573 | 89.5229 | 89.5884 | 89.654 | 89.654 | 89.654 | 89.654 | 89.654 | 89.654 | 89.654 | 89.654 | 89.654 | 89.654 | 89.654 | 89.654 | 89.654 | 89.654 | 89.654 | 89.654 | 89.654 | 89.654 | 89.654 | 89.654 | 89.654 | 89.654 | 89.654 | 89.654 | 89.654 | 89.654 | 89.654 | 89.654 | 89.654 | 89.654 | 89.654 | 89.5557 | 89.4573 | 89.359 | 89.2607 | 89.1623 | 89.064 | 88.9657 | 88.8673 | 88.769 | 88.6707 | 88.5723 | 88.474 | 88.3757 | 88.2773 | 88.179 | 88.0807 | 87.9823 | 87.884 | 87.7857 | 87.6873 | 87.589 | 87.4907 | 87.3923 | 87.294 | 87.1957 | 87.0973 | 86.999 | 86.9007 | 86.8023 | 86.704
9.95 | 0 | 29.7833 | 49.6313 | 52.6183 | 63.536 | 74.4523 | 83.3827 | 88.3437 | 90.327 | 90.327 | 87.352 | -1.7764e-15 | 2.9783 | 5.9567 | 8.935 | 11.9133 | 14.8917 | 17.87 | 20.8483 | 23.8267 | 26.805 | 29.7833 | 33.7529 | 37.7225 | 41.6921 | 45.6617 | 49.6313 | 50.2287 | 50.8261 | 51.4235 | 52.0209 | 52.6183 | 53.7101 | 54.8019 | 55.8936 | 56.9854 | 58.0772 | 59.1689 | 60.2607 | 61.3525 | 62.4442 | 63.536 | 64.2638 | 64.9915 | 65.7193 | 66.447 | 67.1748 | 67.9025 | 68.6303 | 69.358 | 70.0858 | 70.8136 | 71.5413 | 72.2691 | 72.9968 | 73.7246 | 74.4523 | 75.0477 | 75.643 | 76.2384 | 76.8338 | 77.4291 | 78.0245 | 78.6198 | 79.2152 | 79.8105 | 80.4059 | 81.0012 | 81.5966 | 82.192 | 82.7873 | 83.3827 | 83.548 | 83.7134 | 83.8788 | 84.0441 | 84.2095 | 84.3749 | 84.5402 | 84.7056 | 84.871 | 85.0363 | 85.2017 | 85.3671 | 85.5324 | 85.6978 | 85.8632 | 86.0285 | 86.1939 | 86.3593 | 86.5246 | 86.69 | 86.8554 | 87.0207 | 87.1861 | 87.3515 | 87.5168 | 87.6822 | 87.8476 | 88.0129 | 88.1783 | 88.3437 | 88.4098 | 88.4759 | 88.542 | 88.6081 | 88.6742 | 88.7403 | 88.8064 | 88.8726 | 88.9387 | 89.0048 | 89.0709 | 89.137 | 89.2031 | 89.2692 | 89.3353 | 89.4014 | 89.4676 | 89.5337 | 89.5998 | 89.6659 | 89.732 | 89.7981 | 89.8642 | 89.9303 | 89.9964 | 90.0626 | 90.1287 | 90.1948 | 90.2609 | 90.327 | 90.327 | 90.327 | 90.327 | 90.327 | 90.327 | 90.327 | 90.327 | 90.327 | 90.327 | 90.327 | 90.327 | 90.327 | 90.327 | 90.327 | 90.327 | 90.327 | 90.327 | 90.327 | 90.327 | 90.327 | 90.327 | 90.327 | 90.327 | 90.327 | 90.327 | 90.327 | 90.327 | 90.327 | 90.327 | 90.327 | 90.2278 | 90.1287 | 90.0295 | 89.9303 | 89.8312 | 89.732 | 89.6328 | 89.5337 | 89.4345 | 89.3353 | 89.2362 | 89.137 | 89.0378 | 88.9387 | 88.8395 | 88.7403 | 88.6412 | 88.542 | 88.4428 | 88.3437 | 88.2445 | 88.1453 | 88.0462 | 87.947 | 87.8478 | 87.7487 | 87.6495 | 87.5503 | 87.4512 | 87.352
10 | 0 | 30 | 50 | 53 | 64 | 75 | 84 | 89 | 91 | 91 | 88 | -1.7764e-15 | 3 | 6 | 9 | 12 | 15 | 18 | 21 | 24 | 27 | 30 | 34 | 38 | 42 | 46 | 50 | 50.6 | 51.2 | 51.8 | 52.4 | 53 | 54.1 | 55.2 | 56.3 | 57.4 | 58.5 | 59.6 | 60.7 | 61.8 | 62.9 | 64 | 64.7333 | 65.4667 | 66.2 | 66.9333 | 67.6667 | 68.4 | 69.1333 | 69.8667 | 70.6 | 71.3333 | 72.0667 | 72.8 | 73.5333 | 74.2667 | 75 | 75.6 | 76.2 | 76.8 | 77.4 | 78 | 78.6 | 79.2 | 79.8 | 80.4 | 81 | 81.6 | 82.2 | 82.8 | 83.4 | 84 | 84.1667 | 84.3333 | 84.5 | 84.6667 | 84.8333 | 85 | 85.1667 | 85.3333 | 85.5 | 85.6667 | 85.8333 | 86 | 86.1667 | 86.3333 | 86.5 | 86.6667 | 86.8333 | 87 | 87.1667 | 87.3333 | 87.5 | 87.6667 | 87.8333 | 88 | 88.1667 | 88.3333 | 88.5 | 88.6667 | 88.8333 | 89 | 89.0667 | 89.1333 | 89.2 | 89.2667 | 89.3333 | 89.4 | 89.4667 | 89.5333 | 89.6 | 89.6667 | 89.7333 | 89.8 | 89.8667 | 89.9333 | 90 | 90.0667 | 90.1333 | 90.2 | 90.2667 | 90.3333 | 90.4 | 90.4667 | 90.5333 | 90.6 | 90.6667 | 90.7333 | 90.8 | 90.8667 | 90.9333 | 91 | 91 | 91 | 91 | 91 | 91 | 91 | 91 | 91 | 91 | 91 | 91 | 91 | 91 | 91 | 91 | 91 | 91 | 91 | 91 | 91 | 91 | 91 | 91 | 91 | 91 | 91 | 91 | 91 | 91 | 91 | 90.9 | 90.8 | 90.7 | 90.6 | 90.5 | 90.4 | 90.3 | 90.2 | 90.1 | 90 | 89.9 | 89.8 | 89.7 | 89.6 | 89.5 | 89.4 | 89.3 | 89.2 | 89.1 | 89 | 88.9 | 88.8 | 88.7 | 88.6 | 88.5 | 88.4 | 88.3 | 88.2 | 88.1 | 88
10.05 | 0 | 30.39 | 50.7353 | 53.689 | 64.8533 | 76.0177 | 85.1773 | 90.285 | 92.3323 | 92.3323 | 89.3573 | -1.7764e-15 | 3.039 | 6.078 | 9.117 | 12.156 | 15.195 | 18.234 | 21.273 | 24.312 | 27.351 | 30.39 | 34.4591 | 38.5281 | 42.5972 | 46.6663 | 50.7353 | 51.3261 | 51.9168 | 52.5075 | 53.0983 | 53.689 | 54.8054 | 55.9219 | 57.0383 | 58.1547 | 59.2712 | 60.3876 | 61.504 | 62.6205 | 63.7369 | 64.8533 | 65.5976 | 66.3419 | 67.0862 | 67.8305 | 68.5748 | 69.3191 | 70.0634 | 70.8076 | 71.5519 | 72.2962 | 73.0405 | 73.7848 | 74.5291 | 75.2734 | 76.0177 | 76.6283 | 77.239 | 77.8496 | 78.4602 | 79.0709 | 79.6815 | 80.2922 | 80.9028 | 81.5135 | 82.1241 | 82.7348 | 83.3454 | 83.956 | 84.5667 | 85.1773 | 85.3476 | 85.5178 | 85.6881 | 85.8584 | 86.0286 | 86.1989 | 86.3691 | 86.5394 | 86.7096 | 86.8799 | 87.0501 | 87.2204 | 87.3907 | 87.5609 | 87.7312 | 87.9014 | 88.0717 | 88.2419 | 88.4122 | 88.5824 | 88.7527 | 88.923 | 89.0932 | 89.2635 | 89.4337 | 89.604 | 89.7742 | 89.9445 | 90.1147 | 90.285 | 90.3532 | 90.4215 | 90.4897 | 90.558 | 90.6262 | 90.6945 | 90.7627 | 90.831 | 90.8992 | 90.9674 | 91.0357 | 91.1039 | 91.1722 | 91.2404 | 91.3087 | 91.3769 | 91.4452 | 91.5134 | 91.5816 | 91.6499 | 91.7181 | 91.7864 | 91.8546 | 91.9229 | 91.9911 | 92.0594 | 92.1276 | 92.1958 | 92.2641 | 92.3323 | 92.3323 | 92.3323 | 92.3323 | 92.3323 | 92.3323 | 92.3323 | 92.3323 | 92.3323 | 92.3323 | 92.3323 | 92.3323 | 92.3323 | 92.3323 | 92.3323 | 92.3323 | 92.3323 | 92.3323 | 92.3323 | 92.3323 | 92.3323 | 92.3323 | 92.3323 | 92.3323 | 92.3323 | 92.3323 | 92.3323 | 92.3323 | 92.3323 | 92.3323 | 92.3323 | 92.2332 | 92.134 | 92.0348 | 91.9357 | 91.8365 | 91.7373 | 91.6382 | 91.539 | 91.4398 | 91.3407 | 91.2415 | 91.1423 | 91.0432 | 90.944 | 90.8448 | 90.7457 | 90.6465 | 90.5473 | 90.4482 | 90.349 | 90.2498 | 90.1507 | 90.0515 | 89.9523 | 89.8532 | 89.754 | 89.6548 | 89.5557 | 89.4565 | 89.3573
10.1 | 0 | 30.78 | 51.4707 | 54.378 | 65.7067 | 77.0353 | 86.3547 | 91.57 | 93.6647 | 93.6647 | 90.7147 | 0 | 3.078 | 6.156 | 9.234 | 12.312 | 15.39 | 18.468 | 21.546 | 24.624 | 27.702 | 30.78 | 34.9181 | 39.0563 | 43.1944 | 47.3325 | 51.4707 | 52.0521 | 52.6336 | 53.2151 | 53.7965 | 54.378 | 55.5109 | 56.6437 | 57.7766 | 58.9095 | 60.0423 | 61.1752 | 62.3081 | 63.4409 | 64.5738 | 65.7067 | 66.4619 | 67.2172 | 67.9724 | 68.7276 | 69.4829 | 70.2381 | 70.9934 | 71.7486 | 72.5039 | 73.2591 | 74.0144 | 74.7696 | 75.5248 | 76.2801 | 77.0353 | 77.6566 | 78.2779 | 78.8992 | 79.5205 | 80.1418 | 80.7631 | 81.3844 | 82.0056 | 82.6269 | 83.2482 | 83.8695 | 84.4908 | 85.1121 | 85.7334 | 86.3547 | 86.5285 | 86.7024 | 86.8762 | 87.05 | 87.2239 | 87.3977 | 87.5716 | 87.7454 | 87.9193 | 88.0931 | 88.267 | 88.4408 | 88.6146 | 88.7885 | 88.9623 | 89.1362 | 89.31 | 89.4839 | 89.6577 | 89.8316 | 90.0054 | 90.1792 | 90.3531 | 90.5269 | 90.7008 | 90.8746 | 91.0485 | 91.2223 | 91.3962 | 91.57 | 91.6398 | 91.7096 | 91.7795 | 91.8493 | 91.9191 | 91.9889 | 92.0588 | 92.1286 | 92.1984 | 92.2682 | 92.338 | 92.4079 | 92.4777 | 92.5475 | 92.6173 | 92.6872 | 92.757 | 92.8268 | 92.8966 | 92.9664 | 93.0363 | 93.1061 | 93.1759 | 93.2457 | 93.3156 | 93.3854 | 93.4552 | 93.525 | 93.5948 | 93.6647 | 93.6647 | 93.6647 | 93.6647 | 93.6647 | 93.6647 | 93.6647 | 93.6647 | 93.6647 | 93.6647 | 93.6647 | 93.6647 | 93.6647 | 93.6647 | 93.6647 | 93.6647 | 93.6647 | 93.6647 | 93.6647 | 93.6647 | 93.6647 | 93.6647 | 93.6647 | 93.6647 | 93.6647 | 93.6647 | 93.6647 | 93.6647 | 93.6647 | 93.6647 | 93.6647 | 93.5663 | 93.468 | 93.3697 | 93.2713 | 93.173 | 93.0747 | 92.9763 | 92.878 | 92.7797 | 92.6813 | 92.583 | 92.4847 | 92.3863 | 92.288 | 92.1897 | 92.0913 | 91.993 | 91.8947 | 91.7963 | 91.698 | 91.5997 | 91.5013 | 91.403 | 91.3047 | 91.2063 | 91.108 | 91.0097 | 90.9113 | 90.813 | 90.7147
10.15 | 0 | 31.17 | 52.206 | 55.067 | 66.56 | 78.053 | 87.532 | 92.855 | 94.997 | 94.997 | 92.072 | 1.7764e-15 | 3.117 | 6.234 | 9.351 | 12.468 | 15.585 | 18.702 | 21.819 | 24.936 | 28.053 | 31.17 | 35.3772 | 39.5844 | 43.7916 | 47.9988 | 52.206 | 52.7782 | 53.3504 | 53.9226 | 54.4948 | 55.067 | 56.2163 | 57.3656 | 58.5149 | 59.6642 | 60.8135 | 61.9628 | 63.1121 | 64.2614 | 65.4107 | 66.56 | 67.3262 | 68.0924 | 68.8586 | 69.6248 | 70.391 | 71.1572 | 71.9234 | 72.6896 | 73.4558 | 74.222 | 74.9882 | 75.7544 | 76.5206 | 77.2868 | 78.053 | 78.6849 | 79.3169 | 79.9488 | 80.5807 | 81.2127 | 81.8446 | 82.4765 | 83.1085 | 83.7404 | 84.3723 | 85.0043 | 85.6362 | 86.2681 | 86.9001 | 87.532 | 87.7094 | 87.8869 | 88.0643 | 88.2417 | 88.4192 | 88.5966 | 88.774 | 88.9515 | 89.1289 | 89.3063 | 89.4838 | 89.6612 | 89.8386 | 90.0161 | 90.1935 | 90.3709 | 90.5484 | 90.7258 | 90.9032 | 91.0807 | 91.2581 | 91.4355 | 91.613 | 91.7904 | 91.9678 | 92.1453 | 92.3227 | 92.5001 | 92.6776 | 92.855 | 92.9264 | 92.9978 | 93.0692 | 93.1406 | 93.212 | 93.2834 | 93.3548 | 93.4262 | 93.4976 | 93.569 | 93.6404 | 93.7118 | 93.7832 | 93.8546 | 93.926 | 93.9974 | 94.0688 | 94.1402 | 94.2116 | 94.283 | 94.3544 | 94.4258 | 94.4972 | 94.5686 | 94.64 | 94.7114 | 94.7828 | 94.8542 | 94.9256 | 94.997 | 94.997 | 94.997 | 94.997 | 94.997 | 94.997 | 94.997 | 94.997 | 94.997 | 94.997 | 94.997 | 94.997 | 94.997 | 94.997 | 94.997 | 94.997 | 94.997 | 94.997 | 94.997 | 94.997 | 94.997 | 94.997 | 94.997 | 94.997 | 94.997 | 94.997 | 94.997 | 94.997 | 94.997 | 94.997 | 94.997 | 94.8995 | 94.802 | 94.7045 | 94.607 | 94.5095 | 94.412 | 94.3145 | 94.217 | 94.1195 | 94.022 | 93.9245 | 93.827 | 93.7295 | 93.632 | 93.5345 | 93.437 | 93.3395 | 93.242 | 93.1445 | 93.047 | 92.9495 | 92.852 | 92.7545 | 92.657 | 92.5595 | 92.462 | 92.3645 | 92.267 | 92.1695 | 92.072
10.2 | 0 | 31.56 | 52.9413 | 55.756 | 67.4133 | 79.0707 | 88.7093 | 94.14 | 96.3293 | 96.3293 | 93.4293 | 0 | 3.156 | 6.312 | 9.468 | 12.624 | 15.78 | 18.936 | 22.092 | 25.248 | 28.404 | 31.56 | 35.8363 | 40.1125 | 44.3888 | 48.6651 | 52.9413 | 53.5043 | 54.0672 | 54.6301 | 55.1931 | 55.756 | 56.9217 | 58.0875 | 59.2532 | 60.4189 | 61.5847 | 62.7504 | 63.9161 | 65.0819 | 66.2476 | 67.4133 | 68.1905 | 68.9676 | 69.7448 | 70.522 | 71.2991 | 72.0763 | 72.8534 | 73.6306 | 74.4077 | 75.1849 | 75.962 | 76.7392 | 77.5164 | 78.2935 | 79.0707 | 79.7132 | 80.3558 | 80.9984 | 81.641 | 82.2836 | 82.9261 | 83.5687 | 84.2113 | 84.8539 | 85.4964 | 86.139 | 86.7816 | 87.4242 | 88.0668 | 88.7093 | 88.8904 | 89.0714 | 89.2524 | 89.4334 | 89.6144 | 89.7955 | 89.9765 | 90.1575 | 90.3385 | 90.5196 | 90.7006 | 90.8816 | 91.0626 | 91.2436 | 91.4247 | 91.6057 | 91.7867 | 91.9677 | 92.1488 | 92.3298 | 92.5108 | 92.6918 | 92.8728 | 93.0539 | 93.2349 | 93.4159 | 93.5969 | 93.778 | 93.959 | 94.14 | 94.213 | 94.286 | 94.3589 | 94.4319 | 94.5049 | 94.5779 | 94.6508 | 94.7238 | 94.7968 | 94.8698 | 94.9428 | 95.0157 | 95.0887 | 95.1617 | 95.2347 | 95.3076 | 95.3806 | 95.4536 | 95.5266 | 95.5996 | 95.6725 | 95.7455 | 95.8185 | 95.8915 | 95.9644 | 96.0374 | 96.1104 | 96.1834 | 96.2564 | 96.3293 | 96.3293 | 96.3293 | 96.3293 | 96.3293 | 96.3293 | 96.3293 | 96.3293 | 96.3293 | 96.3293 | 96.3293 | 96.3293 | 96.3293 | 96.3293 | 96.3293 | 96.3293 | 96.3293 | 96.3293 | 96.3293 | 96.3293 | 96.3293 | 96.3293 | 96.3293 | 96.3293 | 96.3293 | 96.3293 | 96.3293 | 96.3293 | 96.3293 | 96.3293 | 96.3293 | 96.2327 | 96.136 | 96.0393 | 95.9427 | 95.846 | 95.7493 | 95.6527 | 95.556 | 95.4593 | 95.3627 | 95.266 | 95.1693 | 95.0727 | 94.976 | 94.8793 | 94.7827 | 94.686 | 94.5893 | 94.4927 | 94.396 | 94.2993 | 94.2027 | 94.106 | 94.0093 | 93.9127 | 93.816 | 93.7193 | 93.6227 | 93.526 | 93.4293
10.25 | 0 | 31.95 | 53.6767 | 56.445 | 68.2667 | 80.0883 | 89.8867 | 95.425 | 97.6617 | 97.6617 | 94.7867 | 0 | 3.195 | 6.39 | 9.585 | 12.78 | 15.975 | 19.17 | 22.365 | 25.56 | 28.755 | 31.95 | 36.2953 | 40.6407 | 44.986 | 49.3313 | 53.6767 | 54.2303 | 54.784 | 55.3377 | 55.8913 | 56.445 | 57.6272 | 58.8093 | 59.9915 | 61.1737 | 62.3558 | 63.538 | 64.7202 | 65.9023 | 67.0845 | 68.2667 | 69.0548 | 69.8429 | 70.631 | 71.4191 | 72.2072 | 72.9953 | 73.7834 | 74.5716 | 75.3597 | 76.1478 | 76.9359 | 77.724 | 78.5121 | 79.3002 | 80.0883 | 80.7416 | 81.3948 | 82.048 | 82.7012 | 83.3544 | 84.0077 | 84.6609 | 85.3141 | 85.9673 | 86.6206 | 87.2738 | 87.927 | 88.5802 | 89.2334 | 89.8867 | 90.0713 | 90.2559 | 90.4405 | 90.6251 | 90.8097 | 90.9943 | 91.1789 | 91.3636 | 91.5482 | 91.7328 | 91.9174 | 92.102 | 92.2866 | 92.4712 | 92.6558 | 92.8404 | 93.0251 | 93.2097 | 93.3943 | 93.5789 | 93.7635 | 93.9481 | 94.1327 | 94.3173 | 94.5019 | 94.6866 | 94.8712 | 95.0558 | 95.2404 | 95.425 | 95.4996 | 95.5741 | 95.6487 | 95.7232 | 95.7978 | 95.8723 | 95.9469 | 96.0214 | 96.096 | 96.1706 | 96.2451 | 96.3197 | 96.3942 | 96.4688 | 96.5433 | 96.6179 | 96.6924 | 96.767 | 96.8416 | 96.9161 | 96.9907 | 97.0652 | 97.1398 | 97.2143 | 97.2889 | 97.3634 | 97.438 | 97.5126 | 97.5871 | 97.6617 | 97.6617 | 97.6617 | 97.6617 | 97.6617 | 97.6617 | 97.6617 | 97.6617 | 97.6617 | 97.6617 | 97.6617 | 97.6617 | 97.6617 | 97.6617 | 97.6617 | 97.6617 | 97.6617 | 97.6617 | 97.6617 | 97.6617 | 97.6617 | 97.6617 | 97.6617 | 97.6617 | 97.6617 | 97.6617 | 97.6617 | 97.6617 | 97.6617 | 97.6617 | 97.6617 | 97.5658 | 97.47 | 97.3742 | 97.2783 | 97.1825 | 97.0867 | 96.9908 | 96.895 | 96.7992 | 96.7033 | 96.6075 | 96.5117 | 96.4158 | 96.32 | 96.2242 | 96.1283 | 96.0325 | 95.9367 | 95.8408 | 95.745 | 95.6492 | 95.5533 | 95.4575 | 95.3617 | 95.2658 | 95.17 | 95.0742 | 94.9783 | 94.8825 | 94.7867
10.3 | 0 | 32.34 | 54.412 | 57.134 | 69.12 | 81.106 | 91.064 | 96.71 | 98.994 | 98.994 | 96.144 | -3.5527e-15 | 3.234 | 6.468 | 9.702 | 12.936 | 16.17 | 19.404 | 22.638 | 25.872 | 29.106 | 32.34 | 36.7544 | 41.1688 | 45.5832 | 49.9976 | 54.412 | 54.9564 | 55.5008 | 56.0452 | 56.5896 | 57.134 | 58.3326 | 59.5312 | 60.7298 | 61.9284 | 63.127 | 64.3256 | 65.5242 | 66.7228 | 67.9214 | 69.12 | 69.9191 | 70.7181 | 71.5172 | 72.3163 | 73.1153 | 73.9144 | 74.7135 | 75.5125 | 76.3116 | 77.1107 | 77.9097 | 78.7088 | 79.5079 | 80.3069 | 81.106 | 81.7699 | 82.4337 | 83.0976 | 83.7615 | 84.4253 | 85.0892 | 85.7531 | 86.4169 | 87.0808 | 87.7447 | 88.4085 | 89.0724 | 89.7363 | 90.4001 | 91.064 | 91.2522 | 91.4404 | 91.6286 | 91.8168 | 92.005 | 92.1932 | 92.3814 | 92.5696 | 92.7578 | 92.946 | 93.1342 | 93.3224 | 93.5106 | 93.6988 | 93.887 | 94.0752 | 94.2634 | 94.4516 | 94.6398 | 94.828 | 95.0162 | 95.2044 | 95.3926 | 95.5808 | 95.769 | 95.9572 | 96.1454 | 96.3336 | 96.5218 | 96.71 | 96.7861 | 96.8623 | 96.9384 | 97.0145 | 97.0907 | 97.1668 | 97.2429 | 97.3191 | 97.3952 | 97.4713 | 97.5475 | 97.6236 | 97.6997 | 97.7759 | 97.852 | 97.9281 | 98.0043 | 98.0804 | 98.1565 | 98.2327 | 98.3088 | 98.3849 | 98.4611 | 98.5372 | 98.6133 | 98.6895 | 98.7656 | 98.8417 | 98.9179 | 98.994 | 98.994 | 98.994 | 98.994 | 98.994 | 98.994 | 98.994 | 98.994 | 98.994 | 98.994 | 98.994 | 98.994 | 98.994 | 98.994 | 98.994 | 98.994 | 98.994 | 98.994 | 98.994 | 98.994 | 98.994 | 98.994 | 98.994 | 98.994 | 98.994 | 98.994 | 98.994 | 98.994 | 98.994 | 98.994 | 98.994 | 98.899 | 98.804 | 98.709 | 98.614 | 98.519 | 98.424 | 98.329 | 98.234 | 98.139 | 98.044 | 97.949 | 97.854 | 97.759 | 97.664 | 97.569 | 97.474 | 97.379 | 97.284 | 97.189 | 97.094 | 96.999 | 96.904 | 96.809 | 96.714 | 96.619 | 96.524 | 96.429 | 96.334 | 96.239 | 96.144
10.35 | 0 | 32.73 | 55.1473 | 57.823 | 69.9733 | 82.1237 | 92.2413 | 97.995 | 100.3263 | 100.3263 | 97.5013 | 0 | 3.273 | 6.546 | 9.819 | 13.092 | 16.365 | 19.638 | 22.911 | 26.184 | 29.457 | 32.73 | 37.2135 | 41.6969 | 46.1804 | 50.6639 | 55.1473 | 55.6825 | 56.2176 | 56.7527 | 57.2879 | 57.823 | 59.038 | 60.2531 | 61.4681 | 62.6831 | 63.8982 | 65.1132 | 66.3282 | 67.5433 | 68.7583 | 69.9733 | 70.7834 | 71.5934 | 72.4034 | 73.2134 | 74.0234 | 74.8335 | 75.6435 | 76.4535 | 77.2635 | 78.0736 | 78.8836 | 79.6936 | 80.5036 | 81.3136 | 82.1237 | 82.7982 | 83.4727 | 84.1472 | 84.8217 | 85.4962 | 86.1707 | 86.8452 | 87.5198 | 88.1943 | 88.8688 | 89.5433 | 90.2178 | 90.8923 | 91.5668 | 92.2413 | 92.4331 | 92.6249 | 92.8167 | 93.0085 | 93.2003 | 93.3921 | 93.5839 | 93.7756 | 93.9674 | 94.1592 | 94.351 | 94.5428 | 94.7346 | 94.9264 | 95.1182 | 95.31 | 95.5017 | 95.6935 | 95.8853 | 96.0771 | 96.2689 | 96.4607 | 96.6525 | 96.8443 | 97.0361 | 97.2278 | 97.4196 | 97.6114 | 97.8032 | 97.995 | 98.0727 | 98.1504 | 98.2281 | 98.3058 | 98.3836 | 98.4613 | 98.539 | 98.6167 | 98.6944 | 98.7721 | 98.8498 | 98.9275 | 99.0052 | 99.083 | 99.1607 | 99.2384 | 99.3161 | 99.3938 | 99.4715 | 99.5492 | 99.6269 | 99.7046 | 99.7824 | 99.8601 | 99.9378 | 100.0155 | 100.0932 | 100.1709 | 100.2486 | 100.3263 | 100.3263 | 100.3263 | 100.3263 | 100.3263 | 100.3263 | 100.3263 | 100.3263 | 100.3263 | 100.3263 | 100.3263 | 100.3263 | 100.3263 | 100.3263 | 100.3263 | 100.3263 | 100.3263 | 100.3263 | 100.3263 | 100.3263 | 100.3263 | 100.3263 | 100.3263 | 100.3263 | 100.3263 | 100.3263 | 100.3263 | 100.3263 | 100.3263 | 100.3263 | 100.3263 | 100.2322 | 100.138 | 100.0438 | 99.9497 | 99.8555 | 99.7613 | 99.6672 | 99.573 | 99.4788 | 99.3847 | 99.2905 | 99.1963 | 99.1022 | 99.008 | 98.9138 | 98.8197 | 98.7255 | 98.6313 | 98.5372 | 98.443 | 98.3488 | 98.2547 | 98.1605 | 98.0663 | 97.9722 | 97.878 | 97.7838 | 97.6897 | 97.5955 | 97.5013
10.4 | 0 | 33.12 | 55.8827 | 58.512 | 70.8267 | 83.1413 | 93.4187 | 99.28 | 101.6587 | 101.6587 | 98.8587 | 0 | 3.312 | 6.624 | 9.936 | 13.248 | 16.56 | 19.872 | 23.184 | 26.496 | 29.808 | 33.12 | 37.6725 | 42.2251 | 46.7776 | 51.3301 | 55.8827 | 56.4085 | 56.9344 | 57.4603 | 57.9861 | 58.512 | 59.7435 | 60.9749 | 62.2064 | 63.4379 | 64.6693 | 65.9008 | 67.1323 | 68.3637 | 69.5952 | 70.8267 | 71.6476 | 72.4686 | 73.2896 | 74.1106 | 74.9316 | 75.7525 | 76.5735 | 77.3945 | 78.2155 | 79.0364 | 79.8574 | 80.6784 | 81.4994 | 82.3204 | 83.1413 | 83.8265 | 84.5116 | 85.1968 | 85.882 | 86.5671 | 87.2523 | 87.9374 | 88.6226 | 89.3077 | 89.9929 | 90.678 | 91.3632 | 92.0484 | 92.7335 | 93.4187 | 93.614 | 93.8094 | 94.0048 | 94.2002 | 94.3956 | 94.5909 | 94.7863 | 94.9817 | 95.1771 | 95.3724 | 95.5678 | 95.7632 | 95.9586 | 96.154 | 96.3493 | 96.5447 | 96.7401 | 96.9355 | 97.1308 | 97.3262 | 97.5216 | 97.717 | 97.9124 | 98.1077 | 98.3031 | 98.4985 | 98.6939 | 98.8892 | 99.0846 | 99.28 | 99.3593 | 99.4386 | 99.5179 | 99.5972 | 99.6764 | 99.7557 | 99.835 | 99.9143 | 99.9936 | 100.0729 | 100.1522 | 100.2315 | 100.3108 | 100.39 | 100.4693 | 100.5486 | 100.6279 | 100.7072 | 100.7865 | 100.8658 | 100.9451 | 101.0244 | 101.1036 | 101.1829 | 101.2622 | 101.3415 | 101.4208 | 101.5001 | 101.5794 | 101.6587 | 101.6587 | 101.6587 | 101.6587 | 101.6587 | 101.6587 | 101.6587 | 101.6587 | 101.6587 | 101.6587 | 101.6587 | 101.6587 | 101.6587 | 101.6587 | 101.6587 | 101.6587 | 101.6587 | 101.6587 | 101.6587 | 101.6587 | 101.6587 | 101.6587 | 101.6587 | 101.6587 | 101.6587 | 101.6587 | 101.6587 | 101.6587 | 101.6587 | 101.6587 | 101.6587 | 101.5653 | 101.472 | 101.3787 | 101.2853 | 101.192 | 101.0987 | 101.0053 | 100.912 | 100.8187 | 100.7253 | 100.632 | 100.5387 | 100.4453 | 100.352 | 100.2587 | 100.1653 | 100.072 | 99.9787 | 99.8853 | 99.792 | 99.6987 | 99.6053 | 99.512 | 99.4187 | 99.3253 | 99.232 | 99.1387 | 99.0453 | 98.952 | 98.8587
10.45 | 0 | 33.51 | 56.618 | 59.201 | 71.68 | 84.159 | 94.596 | 100.565 | 102.991 | 102.991 | 100.216 | 0 | 3.351 | 6.702 | 10.053 | 13.404 | 16.755 | 20.106 | 23.457 | 26.808 | 30.159 | 33.51 | 38.1316 | 42.7532 | 47.3748 | 51.9964 | 56.618 | 57.1346 | 57.6512 | 58.1678 | 58.6844 | 59.201 | 60.4489 | 61.6968 | 62.9447 | 64.1926 | 65.4405 | 66.6884 | 67.9363 | 69.1842 | 70.4321 | 71.68 | 72.5119 | 73.3439 | 74.1758 | 75.0077 | 75.8397 | 76.6716 | 77.5035 | 78.3355 | 79.1674 | 79.9993 | 80.8313 | 81.6632 | 82.4951 | 83.3271 | 84.159 | 84.8548 | 85.5506 | 86.2464 | 86.9422 | 87.638 | 88.3338 | 89.0296 | 89.7254 | 90.4212 | 91.117 | 91.8128 | 92.5086 | 93.2044 | 93.9002 | 94.596 | 94.795 | 94.9939 | 95.1929 | 95.3919 | 95.5908 | 95.7898 | 95.9888 | 96.1877 | 96.3867 | 96.5857 | 96.7846 | 96.9836 | 97.1826 | 97.3815 | 97.5805 | 97.7795 | 97.9784 | 98.1774 | 98.3764 | 98.5753 | 98.7743 | 98.9733 | 99.1722 | 99.3712 | 99.5702 | 99.7691 | 99.9681 | 100.1671 | 100.366 | 100.565 | 100.6459 | 100.7267 | 100.8076 | 100.8885 | 100.9693 | 101.0502 | 101.1311 | 101.2119 | 101.2928 | 101.3737 | 101.4545 | 101.5354 | 101.6163 | 101.6971 | 101.778 | 101.8589 | 101.9397 | 102.0206 | 102.1015 | 102.1823 | 102.2632 | 102.3441 | 102.4249 | 102.5058 | 102.5867 | 102.6675 | 102.7484 | 102.8293 | 102.9101 | 102.991 | 102.991 | 102.991 | 102.991 | 102.991 | 102.991 | 102.991 | 102.991 | 102.991 | 102.991 | 102.991 | 102.991 | 102.991 | 102.991 | 102.991 | 102.991 | 102.991 | 102.991 | 102.991 | 102.991 | 102.991 | 102.991 | 102.991 | 102.991 | 102.991 | 102.991 | 102.991 | 102.991 | 102.991 | 102.991 | 102.991 | 102.8985 | 102.806 | 102.7135 | 102.621 | 102.5285 | 102.436 | 102.3435 | 102.251 | 102.1585 | 102.066 | 101.9735 | 101.881 | 101.7885 | 101.696 | 101.6035 | 101.511 | 101.4185 | 101.326 | 101.2335 | 101.141 | 101.0485 | 100.956 | 100.8635 | 100.771 | 100.6785 | 100.586 | 100.4935 | 100.401 | 100.3085 | 100.216
10.5 | 0 | 33.9 | 57.3533 | 59.89 | 72.5333 | 85.1767 | 95.7733 | 101.85 | 104.3233 | 104.3233 | 101.5733 | 0 | 3.39 | 6.78 | 10.17 | 13.56 | 16.95 | 20.34 | 23.73 | 27.12 | 30.51 | 33.9 | 38.5907 | 43.2813 | 47.972 | 52.6627 | 57.3533 | 57.8607 | 58.368 | 58.8753 | 59.3827 | 59.89 | 61.1543 | 62.4187 | 63.683 | 64.9473 | 66.2117 | 67.476 | 68.7403 | 70.0047 | 71.269 | 72.5333 | 73.3762 | 74.2191 | 75.062 | 75.9049 | 76.7478 | 77.5907 | 78.4336 | 79.2764 | 80.1193 | 80.9622 | 81.8051 | 82.648 | 83.4909 | 84.3338 | 85.1767 | 85.8831 | 86.5896 | 87.296 | 88.0024 | 88.7089 | 89.4153 | 90.1218 | 90.8282 | 91.5347 | 92.2411 | 92.9476 | 93.654 | 94.3604 | 95.0669 | 95.7733 | 95.9759 | 96.1784 | 96.381 | 96.5836 | 96.7861 | 96.9887 | 97.1912 | 97.3938 | 97.5963 | 97.7989 | 98.0014 | 98.204 | 98.4066 | 98.6091 | 98.8117 | 99.0142 | 99.2168 | 99.4193 | 99.6219 | 99.8244 | 100.027 | 100.2296 | 100.4321 | 100.6347 | 100.8372 | 101.0398 | 101.2423 | 101.4449 | 101.6474 | 101.85 | 101.9324 | 102.0149 | 102.0973 | 102.1798 | 102.2622 | 102.3447 | 102.4271 | 102.5096 | 102.592 | 102.6744 | 102.7569 | 102.8393 | 102.9218 | 103.0042 | 103.0867 | 103.1691 | 103.2516 | 103.334 | 103.4164 | 103.4989 | 103.5813 | 103.6638 | 103.7462 | 103.8287 | 103.9111 | 103.9936 | 104.076 | 104.1584 | 104.2409 | 104.3233 | 104.3233 | 104.3233 | 104.3233 | 104.3233 | 104.3233 | 104.3233 | 104.3233 | 104.3233 | 104.3233 | 104.3233 | 104.3233 | 104.3233 | 104.3233 | 104.3233 | 104.3233 | 104.3233 | 104.3233 | 104.3233 | 104.3233 | 104.3233 | 104.3233 | 104.3233 | 104.3233 | 104.3233 | 104.3233 | 104.3233 | 104.3233 | 104.3233 | 104.3233 | 104.3233 | 104.2317 | 104.14 | 104.0483 | 103.9567 | 103.865 | 103.7733 | 103.6817 | 103.59 | 103.4983 | 103.4067 | 103.315 | 103.2233 | 103.1317 | 103.04 | 102.9483 | 102.8567 | 102.765 | 102.6733 | 102.5817 | 102.49 | 102.3983 | 102.3067 | 102.215 | 102.1233 | 102.0317 | 101.94 | 101.8483 | 101.7567 | 101.665 | 101.5733
10.55 | 0 | 34.29 | 58.0887 | 60.579 | 73.3867 | 86.1943 | 96.9507 | 103.135 | 105.6557 | 105.6557 | 102.9307 | 0 | 3.429 | 6.858 | 10.287 | 13.716 | 17.145 | 20.574 | 24.003 | 27.432 | 30.861 | 34.29 | 39.0497 | 43.8095 | 48.5692 | 53.3289 | 58.0887 | 58.5867 | 59.0848 | 59.5829 | 60.0809 | 60.579 | 61.8598 | 63.1405 | 64.4213 | 65.7021 | 66.9828 | 68.2636 | 69.5444 | 70.8251 | 72.1059 | 73.3867 | 74.2405 | 75.0944 | 75.9482 | 76.802 | 77.6559 | 78.5097 | 79.3636 | 80.2174 | 81.0713 | 81.9251 | 82.779 | 83.6328 | 84.4866 | 85.3405 | 86.1943 | 86.9114 | 87.6285 | 88.3456 | 89.0627 | 89.7798 | 90.4969 | 91.214 | 91.931 | 92.6481 | 93.3652 | 94.0823 | 94.7994 | 95.5165 | 96.2336 | 96.9507 | 97.1568 | 97.363 | 97.5691 | 97.7752 | 97.9814 | 98.1875 | 98.3937 | 98.5998 | 98.806 | 99.0121 | 99.2183 | 99.4244 | 99.6305 | 99.8367 | 100.0428 | 100.249 | 100.4551 | 100.6613 | 100.8674 | 101.0736 | 101.2797 | 101.4858 | 101.692 | 101.8981 | 102.1043 | 102.3104 | 102.5166 | 102.7227 | 102.9289 | 103.135 | 103.219 | 103.303 | 103.3871 | 103.4711 | 103.5551 | 103.6391 | 103.7232 | 103.8072 | 103.8912 | 103.9752 | 104.0592 | 104.1433 | 104.2273 | 104.3113 | 104.3953 | 104.4794 | 104.5634 | 104.6474 | 104.7314 | 104.8154 | 104.8995 | 104.9835 | 105.0675 | 105.1515 | 105.2356 | 105.3196 | 105.4036 | 105.4876 | 105.5716 | 105.6557 | 105.6557 | 105.6557 | 105.6557 | 105.6557 | 105.6557 | 105.6557 | 105.6557 | 105.6557 | 105.6557 | 105.6557 | 105.6557 | 105.6557 | 105.6557 | 105.6557 | 105.6557 | 105.6557 | 105.6557 | 105.6557 | 105.6557 | 105.6557 | 105.6557 | 105.6557 | 105.6557 | 105.6557 | 105.6557 | 105.6557 | 105.6557 | 105.6557 | 105.6557 | 105.6557 | 105.5648 | 105.474 | 105.3832 | 105.2923 | 105.2015 | 105.1107 | 105.0198 | 104.929 | 104.8382 | 104.7473 | 104.6565 | 104.5657 | 104.4748 | 104.384 | 104.2932 | 104.2023 | 104.1115 | 104.0207 | 103.9298 | 103.839 | 103.7482 | 103.6573 | 103.5665 | 103.4757 | 103.3848 | 103.294 | 103.2032 | 103.1123 | 103.0215 | 102.9307
10.6 | 0 | 34.68 | 58.824 | 61.268 | 74.24 | 87.212 | 98.128 | 104.42 | 106.988 | 106.988 | 104.288 | 0 | 3.468 | 6.936 | 10.404 | 13.872 | 17.34 | 20.808 | 24.276 | 27.744 | 31.212 | 34.68 | 39.5088 | 44.3376 | 49.1664 | 53.9952 | 58.824 | 59.3128 | 59.8016 | 60.2904 | 60.7792 | 61.268 | 62.5652 | 63.8624 | 65.1596 | 66.4568 | 67.754 | 69.0512 | 70.3484 | 71.6456 | 72.9428 | 74.24 | 75.1048 | 75.9696 | 76.8344 | 77.6992 | 78.564 | 79.4288 | 80.2936 | 81.1584 | 82.0232 | 82.888 | 83.7528 | 84.6176 | 85.4824 | 86.3472 | 87.212 | 87.9397 | 88.6675 | 89.3952 | 90.1229 | 90.8507 | 91.5784 | 92.3061 | 93.0339 | 93.7616 | 94.4893 | 95.2171 | 95.9448 | 96.6725 | 97.4003 | 98.128 | 98.3377 | 98.5475 | 98.7572 | 98.9669 | 99.1767 | 99.3864 | 99.5961 | 99.8059 | 100.0156 | 100.2253 | 100.4351 | 100.6448 | 100.8545 | 101.0643 | 101.274 | 101.4837 | 101.6935 | 101.9032 | 102.1129 | 102.3227 | 102.5324 | 102.7421 | 102.9519 | 103.1616 | 103.3713 | 103.5811 | 103.7908 | 104.0005 | 104.2103 | 104.42 | 104.5056 | 104.5912 | 104.6768 | 104.7624 | 104.848 | 104.9336 | 105.0192 | 105.1048 | 105.1904 | 105.276 | 105.3616 | 105.4472 | 105.5328 | 105.6184 | 105.704 | 105.7896 | 105.8752 | 105.9608 | 106.0464 | 106.132 | 106.2176 | 106.3032 | 106.3888 | 106.4744 | 106.56 | 106.6456 | 106.7312 | 106.8168 | 106.9024 | 106.988 | 106.988 | 106.988 | 106.988 | 106.988 | 106.988 | 106.988 | 106.988 | 106.988 | 106.988 | 106.988 | 106.988 | 106.988 | 106.988 | 106.988 | 106.988 | 106.988 | 106.988 | 106.988 | 106.988 | 106.988 | 106.988 | 106.988 | 106.988 | 106.988 | 106.988 | 106.988 | 106.988 | 106.988 | 106.988 | 106.988 | 106.898 | 106.808 | 106.718 | 106.628 | 106.538 | 106.448 | 106.358 | 106.268 | 106.178 | 106.088 | 105.998 | 105.908 | 105.818 | 105.728 | 105.638 | 105.548 | 105.458 | 105.368 | 105.278 | 105.188 | 105.098 | 105.008 | 104.918 | 104.828 | 104.738 | 104.648 | 104.558 | 104.468 | 104.378 | 104.288
10.65 | 0 | 35.07 | 59.5593 | 61.957 | 75.0933 | 88.2297 | 99.3053 | 105.705 | 108.3203 | 108.3203 | 105.6453 | 3.5527e-15 | 3.507 | 7.014 | 10.521 | 14.028 | 17.535 | 21.042 | 24.549 | 28.056 | 31.563 | 35.07 | 39.9679 | 44.8657 | 49.7636 | 54.6615 | 59.5593 | 60.0389 | 60.5184 | 60.9979 | 61.4775 | 61.957 | 63.2706 | 64.5843 | 65.8979 | 67.2115 | 68.5252 | 69.8388 | 71.1524 | 72.4661 | 73.7797 | 75.0933 | 75.9691 | 76.8448 | 77.7206 | 78.5964 | 79.4721 | 80.3479 | 81.2236 | 82.0994 | 82.9751 | 83.8509 | 84.7266 | 85.6024 | 86.4782 | 87.3539 | 88.2297 | 88.968 | 89.7064 | 90.4448 | 91.1832 | 91.9216 | 92.6599 | 93.3983 | 94.1367 | 94.8751 | 95.6134 | 96.3518 | 97.0902 | 97.8286 | 98.567 | 99.3053 | 99.5187 | 99.732 | 99.9453 | 100.1586 | 100.3719 | 100.5853 | 100.7986 | 101.0119 | 101.2252 | 101.4386 | 101.6519 | 101.8652 | 102.0785 | 102.2918 | 102.5052 | 102.7185 | 102.9318 | 103.1451 | 103.3585 | 103.5718 | 103.7851 | 103.9984 | 104.2117 | 104.4251 | 104.6384 | 104.8517 | 105.065 | 105.2784 | 105.4917 | 105.705 | 105.7922 | 105.8794 | 105.9665 | 106.0537 | 106.1409 | 106.2281 | 106.3152 | 106.4024 | 106.4896 | 106.5768 | 106.664 | 106.7511 | 106.8383 | 106.9255 | 107.0127 | 107.0998 | 107.187 | 107.2742 | 107.3614 | 107.4486 | 107.5357 | 107.6229 | 107.7101 | 107.7973 | 107.8844 | 107.9716 | 108.0588 | 108.146 | 108.2332 | 108.3203 | 108.3203 | 108.3203 | 108.3203 | 108.3203 | 108.3203 | 108.3203 | 108.3203 | 108.3203 | 108.3203 | 108.3203 | 108.3203 | 108.3203 | 108.3203 | 108.3203 | 108.3203 | 108.3203 | 108.3203 | 108.3203 | 108.3203 | 108.3203 | 108.3203 | 108.3203 | 108.3203 | 108.3203 | 108.3203 | 108.3203 | 108.3203 | 108.3203 | 108.3203 | 108.3203 | 108.2312 | 108.142 | 108.0528 | 107.9637 | 107.8745 | 107.7853 | 107.6962 | 107.607 | 107.5178 | 107.4287 | 107.3395 | 107.2503 | 107.1612 | 107.072 | 106.9828 | 106.8937 | 106.8045 | 106.7153 | 106.6262 | 106.537 | 106.4478 | 106.3587 | 106.2695 | 106.1803 | 106.0912 | 106.002 | 105.9128 | 105.8237 | 105.7345 | 105.6453
10.7 | 0 | 35.46 | 60.2947 | 62.646 | 75.9467 | 89.2473 | 100.4827 | 106.99 | 109.6527 | 109.6527 | 107.0027 | 0 | 3.546 | 7.092 | 10.638 | 14.184 | 17.73 | 21.276 | 24.822 | 28.368 | 31.914 | 35.46 | 40.4269 | 45.3939 | 50.3608 | 55.3277 | 60.2947 | 60.7649 | 61.2352 | 61.7055 | 62.1757 | 62.646 | 63.9761 | 65.3061 | 66.6362 | 67.9663 | 69.2963 | 70.6264 | 71.9565 | 73.2865 | 74.6166 | 75.9467 | 76.8334 | 77.7201 | 78.6068 | 79.4935 | 80.3802 | 81.2669 | 82.1536 | 83.0404 | 83.9271 | 84.8138 | 85.7005 | 86.5872 | 87.4739 | 88.3606 | 89.2473 | 89.9964 | 90.7454 | 91.4944 | 92.2434 | 92.9924 | 93.7415 | 94.4905 | 95.2395 | 95.9885 | 96.7376 | 97.4866 | 98.2356 | 98.9846 | 99.7336 | 100.4827 | 100.6996 | 100.9165 | 101.1334 | 101.3503 | 101.5672 | 101.7841 | 102.001 | 102.218 | 102.4349 | 102.6518 | 102.8687 | 103.0856 | 103.3025 | 103.5194 | 103.7363 | 103.9532 | 104.1702 | 104.3871 | 104.604 | 104.8209 | 105.0378 | 105.2547 | 105.4716 | 105.6885 | 105.9054 | 106.1224 | 106.3393 | 106.5562 | 106.7731 | 106.99 | 107.0788 | 107.1675 | 107.2563 | 107.345 | 107.4338 | 107.5225 | 107.6113 | 107.7 | 107.7888 | 107.8776 | 107.9663 | 108.0551 | 108.1438 | 108.2326 | 108.3213 | 108.4101 | 108.4988 | 108.5876 | 108.6764 | 108.7651 | 108.8539 | 108.9426 | 109.0314 | 109.1201 | 109.2089 | 109.2976 | 109.3864 | 109.4752 | 109.5639 | 109.6527 | 109.6527 | 109.6527 | 109.6527 | 109.6527 | 109.6527 | 109.6527 | 109.6527 | 109.6527 | 109.6527 | 109.6527 | 109.6527 | 109.6527 | 109.6527 | 109.6527 | 109.6527 | 109.6527 | 109.6527 | 109.6527 | 109.6527 | 109.6527 | 109.6527 | 109.6527 | 109.6527 | 109.6527 | 109.6527 | 109.6527 | 109.6527 | 109.6527 | 109.6527 | 109.6527 | 109.5643 | 109.476 | 109.3877 | 109.2993 | 109.211 | 109.1227 | 109.0343 | 108.946 | 108.8577 | 108.7693 | 108.681 | 108.5927 | 108.5043 | 108.416 | 108.3277 | 108.2393 | 108.151 | 108.0627 | 107.9743 | 107.886 | 107.7977 | 107.7093 | 107.621 | 107.5327 | 107.4443 | 107.356 | 107.2677 | 107.1793 | 107.091 | 107.0027
10.75 | 0 | 35.85 | 61.03 | 63.335 | 76.8 | 90.265 | 101.66 | 108.275 | 110.985 | 110.985 | 108.36 | 0 | 3.585 | 7.17 | 10.755 | 14.34 | 17.925 | 21.51 | 25.095 | 28.68 | 32.265 | 35.85 | 40.886 | 45.922 | 50.958 | 55.994 | 61.03 | 61.491 | 61.952 | 62.413 | 62.874 | 63.335 | 64.6815 | 66.028 | 67.3745 | 68.721 | 70.0675 | 71.414 | 72.7605 | 74.107 | 75.4535 | 76.8 | 77.6977 | 78.5953 | 79.493 | 80.3907 | 81.2883 | 82.186 | 83.0837 | 83.9813 | 84.879 | 85.7767 | 86.6743 | 87.572 | 88.4697 | 89.3673 | 90.265 | 91.0247 | 91.7843 | 92.544 | 93.3037 | 94.0633 | 94.823 | 95.5827 | 96.3423 | 97.102 | 97.8617 | 98.6213 | 99.381 | 100.1407 | 100.9003 | 101.66 | 101.8805 | 102.101 | 102.3215 | 102.542 | 102.7625 | 102.983 | 103.2035 | 103.424 | 103.6445 | 103.865 | 104.0855 | 104.306 | 104.5265 | 104.747 | 104.9675 | 105.188 | 105.4085 | 105.629 | 105.8495 | 106.07 | 106.2905 | 106.511 | 106.7315 | 106.952 | 107.1725 | 107.393 | 107.6135 | 107.834 | 108.0545 | 108.275 | 108.3653 | 108.4557 | 108.546 | 108.6363 | 108.7267 | 108.817 | 108.9073 | 108.9977 | 109.088 | 109.1783 | 109.2687 | 109.359 | 109.4493 | 109.5397 | 109.63 | 109.7203 | 109.8107 | 109.901 | 109.9913 | 110.0817 | 110.172 | 110.2623 | 110.3527 | 110.443 | 110.5333 | 110.6237 | 110.714 | 110.8043 | 110.8947 | 110.985 | 110.985 | 110.985 | 110.985 | 110.985 | 110.985 | 110.985 | 110.985 | 110.985 | 110.985 | 110.985 | 110.985 | 110.985 | 110.985 | 110.985 | 110.985 | 110.985 | 110.985 | 110.985 | 110.985 | 110.985 | 110.985 | 110.985 | 110.985 | 110.985 | 110.985 | 110.985 | 110.985 | 110.985 | 110.985 | 110.985 | 110.8975 | 110.81 | 110.7225 | 110.635 | 110.5475 | 110.46 | 110.3725 | 110.285 | 110.1975 | 110.11 | 110.0225 | 109.935 | 109.8475 | 109.76 | 109.6725 | 109.585 | 109.4975 | 109.41 | 109.3225 | 109.235 | 109.1475 | 109.06 | 108.9725 | 108.885 | 108.7975 | 108.71 | 108.6225 | 108.535 | 108.4475 | 108.36
10.8 | 0 | 36.24 | 61.7653 | 64.024 | 77.6533 | 91.2827 | 102.8373 | 109.56 | 112.3173 | 112.3173 | 109.7173 | -3.5527e-15 | 3.624 | 7.248 | 10.872 | 14.496 | 18.12 | 21.744 | 25.368 | 28.992 | 32.616 | 36.24 | 41.3451 | 46.4501 | 51.5552 | 56.6603 | 61.7653 | 62.2171 | 62.6688 | 63.1205 | 63.5723 | 64.024 | 65.3869 | 66.7499 | 68.1128 | 69.4757 | 70.8387 | 72.2016 | 73.5645 | 74.9275 | 76.2904 | 77.6533 | 78.562 | 79.4706 | 80.3792 | 81.2878 | 82.1964 | 83.1051 | 84.0137 | 84.9223 | 85.8309 | 86.7396 | 87.6482 | 88.5568 | 89.4654 | 90.374 | 91.2827 | 92.053 | 92.8233 | 93.5936 | 94.3639 | 95.1342 | 95.9045 | 96.6748 | 97.4452 | 98.2155 | 98.9858 | 99.7561 | 100.5264 | 101.2967 | 102.067 | 102.8373 | 103.0614 | 103.2855 | 103.5096 | 103.7337 | 103.9578 | 104.1819 | 104.406 | 104.63 | 104.8541 | 105.0782 | 105.3023 | 105.5264 | 105.7505 | 105.9746 | 106.1987 | 106.4228 | 106.6468 | 106.8709 | 107.095 | 107.3191 | 107.5432 | 107.7673 | 107.9914 | 108.2155 | 108.4396 | 108.6636 | 108.8877 | 109.1118 | 109.3359 | 109.56 | 109.6519 | 109.7438 | 109.8357 | 109.9276 | 110.0196 | 110.1115 | 110.2034 | 110.2953 | 110.3872 | 110.4791 | 110.571 | 110.6629 | 110.7548 | 110.8468 | 110.9387 | 111.0306 | 111.1225 | 111.2144 | 111.3063 | 111.3982 | 111.4901 | 111.582 | 111.674 | 111.7659 | 111.8578 | 111.9497 | 112.0416 | 112.1335 | 112.2254 | 112.3173 | 112.3173 | 112.3173 | 112.3173 | 112.3173 | 112.3173 | 112.3173 | 112.3173 | 112.3173 | 112.3173 | 112.3173 | 112.3173 | 112.3173 | 112.3173 | 112.3173 | 112.3173 | 112.3173 | 112.3173 | 112.3173 | 112.3173 | 112.3173 | 112.3173 | 112.3173 | 112.3173 | 112.3173 | 112.3173 | 112.3173 | 112.3173 | 112.3173 | 112.3173 | 112.3173 | 112.2307 | 112.144 | 112.0573 | 111.9707 | 111.884 | 111.7973 | 111.7107 | 111.624 | 111.5373 | 111.4507 | 111.364 | 111.2773 | 111.1907 | 111.104 | 111.0173 | 110.9307 | 110.844 | 110.7573 | 110.6707 | 110.584 | 110.4973 | 110.4107 | 110.324 | 110.2373 | 110.1507 | 110.064 | 109.9773 | 109.8907 | 109.804 | 109.7173
10.85 | 0 | 36.63 | 62.5007 | 64.713 | 78.5067 | 92.3003 | 104.0147 | 110.845 | 113.6497 | 113.6497 | 111.0747 | 0 | 3.663 | 7.326 | 10.989 | 14.652 | 18.315 | 21.978 | 25.641 | 29.304 | 32.967 | 36.63 | 41.8041 | 46.9783 | 52.1524 | 57.3265 | 62.5007 | 62.9431 | 63.3856 | 63.8281 | 64.2705 | 64.713 | 66.0924 | 67.4717 | 68.8511 | 70.2305 | 71.6098 | 72.9892 | 74.3686 | 75.7479 | 77.1273 | 78.5067 | 79.4262 | 80.3458 | 81.2654 | 82.185 | 83.1046 | 84.0241 | 84.9437 | 85.8633 | 86.7829 | 87.7024 | 88.622 | 89.5416 | 90.4612 | 91.3808 | 92.3003 | 93.0813 | 93.8622 | 94.6432 | 95.4242 | 96.2051 | 96.9861 | 97.767 | 98.548 | 99.3289 | 100.1099 | 100.8908 | 101.6718 | 102.4528 | 103.2337 | 104.0147 | 104.2423 | 104.47 | 104.6977 | 104.9254 | 105.1531 | 105.3807 | 105.6084 | 105.8361 | 106.0638 | 106.2914 | 106.5191 | 106.7468 | 106.9745 | 107.2022 | 107.4298 | 107.6575 | 107.8852 | 108.1129 | 108.3405 | 108.5682 | 108.7959 | 109.0236 | 109.2513 | 109.4789 | 109.7066 | 109.9343 | 110.162 | 110.3896 | 110.6173 | 110.845 | 110.9385 | 111.032 | 111.1255 | 111.219 | 111.3124 | 111.4059 | 111.4994 | 111.5929 | 111.6864 | 111.7799 | 111.8734 | 111.9669 | 112.0604 | 112.1538 | 112.2473 | 112.3408 | 112.4343 | 112.5278 | 112.6213 | 112.7148 | 112.8083 | 112.9018 | 112.9952 | 113.0887 | 113.1822 | 113.2757 | 113.3692 | 113.4627 | 113.5562 | 113.6497 | 113.6497 | 113.6497 | 113.6497 | 113.6497 | 113.6497 | 113.6497 | 113.6497 | 113.6497 | 113.6497 | 113.6497 | 113.6497 | 113.6497 | 113.6497 | 113.6497 | 113.6497 | 113.6497 | 113.6497 | 113.6497 | 113.6497 | 113.6497 | 113.6497 | 113.6497 | 113.6497 | 113.6497 | 113.6497 | 113.6497 | 113.6497 | 113.6497 | 113.6497 | 113.6497 | 113.5638 | 113.478 | 113.3922 | 113.3063 | 113.2205 | 113.1347 | 113.0488 | 112.963 | 112.8772 | 112.7913 | 112.7055 | 112.6197 | 112.5338 | 112.448 | 112.3622 | 112.2763 | 112.1905 | 112.1047 | 112.0188 | 111.933 | 111.8472 | 111.7613 | 111.6755 | 111.5897 | 111.5038 | 111.418 | 111.3322 | 111.2463 | 111.1605 | 111.0747
10.9 | 0 | 37.02 | 63.236 | 65.402 | 79.36 | 93.318 | 105.192 | 112.13 | 114.982 | 114.982 | 112.432 | 0 | 3.702 | 7.404 | 11.106 | 14.808 | 18.51 | 22.212 | 25.914 | 29.616 | 33.318 | 37.02 | 42.2632 | 47.5064 | 52.7496 | 57.9928 | 63.236 | 63.6692 | 64.1024 | 64.5356 | 64.9688 | 65.402 | 66.7978 | 68.1936 | 69.5894 | 70.9852 | 72.381 | 73.7768 | 75.1726 | 76.5684 | 77.9642 | 79.36 | 80.2905 | 81.2211 | 82.1516 | 83.0821 | 84.0127 | 84.9432 | 85.8737 | 86.8043 | 87.7348 | 88.6653 | 89.5959 | 90.5264 | 91.4569 | 92.3875 | 93.318 | 94.1096 | 94.9012 | 95.6928 | 96.4844 | 97.276 | 98.0676 | 98.8592 | 99.6508 | 100.4424 | 101.234 | 102.0256 | 102.8172 | 103.6088 | 104.4004 | 105.192 | 105.4233 | 105.6545 | 105.8858 | 106.1171 | 106.3483 | 106.5796 | 106.8109 | 107.0421 | 107.2734 | 107.5047 | 107.7359 | 107.9672 | 108.1985 | 108.4297 | 108.661 | 108.8923 | 109.1235 | 109.3548 | 109.5861 | 109.8173 | 110.0486 | 110.2799 | 110.5111 | 110.7424 | 110.9737 | 111.2049 | 111.4362 | 111.6675 | 111.8987 | 112.13 | 112.2251 | 112.3201 | 112.4152 | 112.5103 | 112.6053 | 112.7004 | 112.7955 | 112.8905 | 112.9856 | 113.0807 | 113.1757 | 113.2708 | 113.3659 | 113.4609 | 113.556 | 113.6511 | 113.7461 | 113.8412 | 113.9363 | 114.0313 | 114.1264 | 114.2215 | 114.3165 | 114.4116 | 114.5067 | 114.6017 | 114.6968 | 114.7919 | 114.8869 | 114.982 | 114.982 | 114.982 | 114.982 | 114.982 | 114.982 | 114.982 | 114.982 | 114.982 | 114.982 | 114.982 | 114.982 | 114.982 | 114.982 | 114.982 | 114.982 | 114.982 | 114.982 | 114.982 | 114.982 | 114.982 | 114.982 | 114.982 | 114.982 | 114.982 | 114.982 | 114.982 | 114.982 | 114.982 | 114.982 | 114.982 | 114.897 | 114.812 | 114.727 | 114.642 | 114.557 | 114.472 | 114.387 | 114.302 | 114.217 | 114.132 | 114.047 | 113.962 | 113.877 | 113.792 | 113.707 | 113.622 | 113.537 | 113.452 | 113.367 | 113.282 | 113.197 | 113.112 | 113.027 | 112.942 | 112.857 | 112.772 | 112.687 | 112.602 | 112.517 | 112.432
10.95 | 0 | 37.41 | 63.9713 | 66.091 | 80.2133 | 94.3357 | 106.3693 | 113.415 | 116.3143 | 116.3143 | 113.7893 | 0 | 3.741 | 7.482 | 11.223 | 14.964 | 18.705 | 22.446 | 26.187 | 29.928 | 33.669 | 37.41 | 42.7223 | 48.0345 | 53.3468 | 58.6591 | 63.9713 | 64.3953 | 64.8192 | 65.2431 | 65.6671 | 66.091 | 67.5032 | 68.9155 | 70.3277 | 71.7399 | 73.1522 | 74.5644 | 75.9766 | 77.3889 | 78.8011 | 80.2133 | 81.1548 | 82.0963 | 83.0378 | 83.9793 | 84.9208 | 85.8623 | 86.8038 | 87.7452 | 88.6867 | 89.6282 | 90.5697 | 91.5112 | 92.4527 | 93.3942 | 94.3357 | 95.1379 | 95.9402 | 96.7424 | 97.5446 | 98.3469 | 99.1491 | 99.9514 | 100.7536 | 101.5559 | 102.3581 | 103.1604 | 103.9626 | 104.7648 | 105.5671 | 106.3693 | 106.6042 | 106.839 | 107.0739 | 107.3088 | 107.5436 | 107.7785 | 108.0133 | 108.2482 | 108.483 | 108.7179 | 108.9527 | 109.1876 | 109.4225 | 109.6573 | 109.8922 | 110.127 | 110.3619 | 110.5967 | 110.8316 | 111.0664 | 111.3013 | 111.5362 | 111.771 | 112.0059 | 112.2407 | 112.4756 | 112.7104 | 112.9453 | 113.1801 | 113.415 | 113.5116 | 113.6083 | 113.7049 | 113.8016 | 113.8982 | 113.9949 | 114.0915 | 114.1882 | 114.2848 | 114.3814 | 114.4781 | 114.5747 | 114.6714 | 114.768 | 114.8647 | 114.9613 | 115.058 | 115.1546 | 115.2512 | 115.3479 | 115.4445 | 115.5412 | 115.6378 | 115.7345 | 115.8311 | 115.9278 | 116.0244 | 116.121 | 116.2177 | 116.3143 | 116.3143 | 116.3143 | 116.3143 | 116.3143 | 116.3143 | 116.3143 | 116.3143 | 116.3143 | 116.3143 | 116.3143 | 116.3143 | 116.3143 | 116.3143 | 116.3143 | 116.3143 | 116.3143 | 116.3143 | 116.3143 | 116.3143 | 116.3143 | 116.3143 | 116.3143 | 116.3143 | 116.3143 | 116.3143 | 116.3143 | 116.3143 | 116.3143 | 116.3143 | 116.3143 | 116.2302 | 116.146 | 116.0618 | 115.9777 | 115.8935 | 115.8093 | 115.7252 | 115.641 | 115.5568 | 115.4727 | 115.3885 | 115.3043 | 115.2202 | 115.136 | 115.0518 | 114.9677 | 114.8835 | 114.7993 | 114.7152 | 114.631 | 114.5468 | 114.4627 | 114.3785 | 114.2943 | 114.2102 | 114.126 | 114.0418 | 113.9577 | 113.8735 | 113.7893
11 | 0 | 37.8 | 64.7067 | 66.78 | 81.0667 | 95.3533 | 107.5467 | 114.7 | 117.6467 | 117.6467 | 115.1467 | 0 | 3.78 | 7.56 | 11.34 | 15.12 | 18.9 | 22.68 | 26.46 | 30.24 | 34.02 | 37.8 | 43.1813 | 48.5627 | 53.944 | 59.3253 | 64.7067 | 65.1213 | 65.536 | 65.9507 | 66.3653 | 66.78 | 68.2087 | 69.6373 | 71.066 | 72.4947 | 73.9233 | 75.352 | 76.7807 | 78.2093 | 79.638 | 81.0667 | 82.0191 | 82.9716 | 83.924 | 84.8764 | 85.8289 | 86.7813 | 87.7338 | 88.6862 | 89.6387 | 90.5911 | 91.5436 | 92.496 | 93.4484 | 94.4009 | 95.3533 | 96.1662 | 96.9791 | 97.792 | 98.6049 | 99.4178 | 100.2307 | 101.0436 | 101.8564 | 102.6693 | 103.4822 | 104.2951 | 105.108 | 105.9209 | 106.7338 | 107.5467 | 107.7851 | 108.0236 | 108.262 | 108.5004 | 108.7389 | 108.9773 | 109.2158 | 109.4542 | 109.6927 | 109.9311 | 110.1696 | 110.408 | 110.6464 | 110.8849 | 111.1233 | 111.3618 | 111.6002 | 111.8387 | 112.0771 | 112.3156 | 112.554 | 112.7924 | 113.0309 | 113.2693 | 113.5078 | 113.7462 | 113.9847 | 114.2231 | 114.4616 | 114.7 | 114.7982 | 114.8964 | 114.9947 | 115.0929 | 115.1911 | 115.2893 | 115.3876 | 115.4858 | 115.584 | 115.6822 | 115.7804 | 115.8787 | 115.9769 | 116.0751 | 116.1733 | 116.2716 | 116.3698 | 116.468 | 116.5662 | 116.6644 | 116.7627 | 116.8609 | 116.9591 | 117.0573 | 117.1556 | 117.2538 | 117.352 | 117.4502 | 117.5484 | 117.6467 | 117.6467 | 117.6467 | 117.6467 | 117.6467 | 117.6467 | 117.6467 | 117.6467 | 117.6467 | 117.6467 | 117.6467 | 117.6467 | 117.6467 | 117.6467 | 117.6467 | 117.6467 | 117.6467 | 117.6467 | 117.6467 | 117.6467 | 117.6467 | 117.6467 | 117.6467 | 117.6467 | 117.6467 | 117.6467 | 117.6467 | 117.6467 | 117.6467 | 117.6467 | 117.6467 | 117.5633 | 117.48 | 117.3967 | 117.3133 | 117.23 | 117.1467 | 117.0633 | 116.98 | 116.8967 | 116.8133 | 116.73 | 116.6467 | 116.5633 | 116.48 | 116.3967 | 116.3133 | 116.23 | 116.1467 | 116.0633 | 115.98 | 115.8967 | 115.8133 | 115.73 | 115.6467 | 115.5633 | 115.48 | 115.3967 | 115.3133 | 115.23 | 115.1467
11.05 | 0 | 38.19 | 65.442 | 67.469 | 81.92 | 96.371 | 108.724 | 115.985 | 118.979 | 118.979 | 116.504 | 0 | 3.819 | 7.638 | 11.457 | 15.276 | 19.095 | 22.914 | 26.733 | 30.552 | 34.371 | 38.19 | 43.6404 | 49.0908 | 54.5412 | 59.9916 | 65.442 | 65.8474 | 66.2528 | 66.6582 | 67.0636 | 67.469 | 68.9141 | 70.3592 | 71.8043 | 73.2494 | 74.6945 | 76.1396 | 77.5847 | 79.0298 | 80.4749 | 81.92 | 82.8834 | 83.8468 | 84.8102 | 85.7736 | 86.737 | 87.7004 | 88.6638 | 89.6272 | 90.5906 | 91.554 | 92.5174 | 93.4808 | 94.4442 | 95.4076 | 96.371 | 97.1945 | 98.0181 | 98.8416 | 99.6651 | 100.4887 | 101.3122 | 102.1357 | 102.9593 | 103.7828 | 104.6063 | 105.4299 | 106.2534 | 107.0769 | 107.9005 | 108.724 | 108.966 | 109.2081 | 109.4501 | 109.6921 | 109.9342 | 110.1762 | 110.4182 | 110.6603 | 110.9023 | 111.1443 | 111.3864 | 111.6284 | 111.8704 | 112.1125 | 112.3545 | 112.5965 | 112.8386 | 113.0806 | 113.3226 | 113.5647 | 113.8067 | 114.0487 | 114.2908 | 114.5328 | 114.7748 | 115.0169 | 115.2589 | 115.5009 | 115.743 | 115.985 | 116.0848 | 116.1846 | 116.2844 | 116.3842 | 116.484 | 116.5838 | 116.6836 | 116.7834 | 116.8832 | 116.983 | 117.0828 | 117.1826 | 117.2824 | 117.3822 | 117.482 | 117.5818 | 117.6816 | 117.7814 | 117.8812 | 117.981 | 118.0808 | 118.1806 | 118.2804 | 118.3802 | 118.48 | 118.5798 | 118.6796 | 118.7794 | 118.8792 | 118.979 | 118.979 | 118.979 | 118.979 | 118.979 | 118.979 | 118.979 | 118.979 | 118.979 | 118.979 | 118.979 | 118.979 | 118.979 | 118.979 | 118.979 | 118.979 | 118.979 | 118.979 | 118.979 | 118.979 | 118.979 | 118.979 | 118.979 | 118.979 | 118.979 | 118.979 | 118.979 | 118.979 | 118.979 | 118.979 | 118.979 | 118.8965 | 118.814 | 118.7315 | 118.649 | 118.5665 | 118.484 | 118.4015 | 118.319 | 118.2365 | 118.154 | 118.0715 | 117.989 | 117.9065 | 117.824 | 117.7415 | 117.659 | 117.5765 | 117.494 | 117.4115 | 117.329 | 117.2465 | 117.164 | 117.0815 | 116.999 | 116.9165 | 116.834 | 116.7515 | 116.669 | 116.5865 | 116.504
11.1 | 0 | 38.58 | 66.1773 | 68.158 | 82.7733 | 97.3887 | 109.9013 | 117.27 | 120.3113 | 120.3113 | 117.8613 | 3.5527e-15 | 3.858 | 7.716 | 11.574 | 15.432 | 19.29 | 23.148 | 27.006 | 30.864 | 34.722 | 38.58 | 44.0995 | 49.6189 | 55.1384 | 60.6579 | 66.1773 | 66.5735 | 66.9696 | 67.3657 | 67.7619 | 68.158 | 69.6195 | 71.0811 | 72.5426 | 74.0041 | 75.4657 | 76.9272 | 78.3887 | 79.8503 | 81.3118 | 82.7733 | 83.7477 | 84.722 | 85.6964 | 86.6708 | 87.6451 | 88.6195 | 89.5938 | 90.5682 | 91.5425 | 92.5169 | 93.4912 | 94.4656 | 95.44 | 96.4143 | 97.3887 | 98.2228 | 99.057 | 99.8912 | 100.7254 | 101.5596 | 102.3937 | 103.2279 | 104.0621 | 104.8963 | 105.7304 | 106.5646 | 107.3988 | 108.233 | 109.0672 | 109.9013 | 110.147 | 110.3926 | 110.6382 | 110.8838 | 111.1294 | 111.3751 | 111.6207 | 111.8663 | 112.1119 | 112.3576 | 112.6032 | 112.8488 | 113.0944 | 113.34 | 113.5857 | 113.8313 | 114.0769 | 114.3225 | 114.5682 | 114.8138 | 115.0594 | 115.305 | 115.5506 | 115.7963 | 116.0419 | 116.2875 | 116.5331 | 116.7788 | 117.0244 | 117.27 | 117.3714 | 117.4728 | 117.5741 | 117.6755 | 117.7769 | 117.8783 | 117.9796 | 118.081 | 118.1824 | 118.2838 | 118.3852 | 118.4865 | 118.5879 | 118.6893 | 118.7907 | 118.892 | 118.9934 | 119.0948 | 119.1962 | 119.2976 | 119.3989 | 119.5003 | 119.6017 | 119.7031 | 119.8044 | 119.9058 | 120.0072 | 120.1086 | 120.21 | 120.3113 | 120.3113 | 120.3113 | 120.3113 | 120.3113 | 120.3113 | 120.3113 | 120.3113 | 120.3113 | 120.3113 | 120.3113 | 120.3113 | 120.3113 | 120.3113 | 120.3113 | 120.3113 | 120.3113 | 120.3113 | 120.3113 | 120.3113 | 120.3113 | 120.3113 | 120.3113 | 120.3113 | 120.3113 | 120.3113 | 120.3113 | 120.3113 | 120.3113 | 120.3113 | 120.3113 | 120.2297 | 120.148 | 120.0663 | 119.9847 | 119.903 | 119.8213 | 119.7397 | 119.658 | 119.5763 | 119.4947 | 119.413 | 119.3313 | 119.2497 | 119.168 | 119.0863 | 119.0047 | 118.923 | 118.8413 | 118.7597 | 118.678 | 118.5963 | 118.5147 | 118.433 | 118.3513 | 118.2697 | 118.188 | 118.1063 | 118.0247 | 117.943 | 117.8613
11.15 | 0 | 38.97 | 66.9127 | 68.847 | 83.6267 | 98.4063 | 111.0787 | 118.555 | 121.6437 | 121.6437 | 119.2187 | 0 | 3.897 | 7.794 | 11.691 | 15.588 | 19.485 | 23.382 | 27.279 | 31.176 | 35.073 | 38.97 | 44.5585 | 50.1471 | 55.7356 | 61.3241 | 66.9127 | 67.2995 | 67.6864 | 68.0733 | 68.4601 | 68.847 | 70.325 | 71.8029 | 73.2809 | 74.7589 | 76.2368 | 77.7148 | 79.1928 | 80.6707 | 82.1487 | 83.6267 | 84.612 | 85.5973 | 86.5826 | 87.5679 | 88.5532 | 89.5385 | 90.5238 | 91.5092 | 92.4945 | 93.4798 | 94.4651 | 95.4504 | 96.4357 | 97.421 | 98.4063 | 99.2512 | 100.096 | 100.9408 | 101.7856 | 102.6304 | 103.4753 | 104.3201 | 105.1649 | 106.0097 | 106.8546 | 107.6994 | 108.5442 | 109.389 | 110.2338 | 111.0787 | 111.3279 | 111.5771 | 111.8263 | 112.0755 | 112.3247 | 112.5739 | 112.8231 | 113.0724 | 113.3216 | 113.5708 | 113.82 | 114.0692 | 114.3184 | 114.5676 | 114.8168 | 115.066 | 115.3153 | 115.5645 | 115.8137 | 116.0629 | 116.3121 | 116.5613 | 116.8105 | 117.0597 | 117.3089 | 117.5582 | 117.8074 | 118.0566 | 118.3058 | 118.555 | 118.658 | 118.7609 | 118.8639 | 118.9668 | 119.0698 | 119.1727 | 119.2757 | 119.3786 | 119.4816 | 119.5846 | 119.6875 | 119.7905 | 119.8934 | 119.9964 | 120.0993 | 120.2023 | 120.3052 | 120.4082 | 120.5112 | 120.6141 | 120.7171 | 120.82 | 120.923 | 121.0259 | 121.1289 | 121.2318 | 121.3348 | 121.4378 | 121.5407 | 121.6437 | 121.6437 | 121.6437 | 121.6437 | 121.6437 | 121.6437 | 121.6437 | 121.6437 | 121.6437 | 121.6437 | 121.6437 | 121.6437 | 121.6437 | 121.6437 | 121.6437 | 121.6437 | 121.6437 | 121.6437 | 121.6437 | 121.6437 | 121.6437 | 121.6437 | 121.6437 | 121.6437 | 121.6437 | 121.6437 | 121.6437 | 121.6437 | 121.6437 | 121.6437 | 121.6437 | 121.5628 | 121.482 | 121.4012 | 121.3203 | 121.2395 | 121.1587 | 121.0778 | 120.997 | 120.9162 | 120.8353 | 120.7545 | 120.6737 | 120.5928 | 120.512 | 120.4312 | 120.3503 | 120.2695 | 120.1887 | 120.1078 | 120.027 | 119.9462 | 119.8653 | 119.7845 | 119.7037 | 119.6228 | 119.542 | 119.4612 | 119.3803 | 119.2995 | 119.2187
11.2 | 0 | 39.36 | 67.648 | 69.536 | 84.48 | 99.424 | 112.256 | 119.84 | 122.976 | 122.976 | 120.576 | 0 | 3.936 | 7.872 | 11.808 | 15.744 | 19.68 | 23.616 | 27.552 | 31.488 | 35.424 | 39.36 | 45.0176 | 50.6752 | 56.3328 | 61.9904 | 67.648 | 68.0256 | 68.4032 | 68.7808 | 69.1584 | 69.536 | 71.0304 | 72.5248 | 74.0192 | 75.5136 | 77.008 | 78.5024 | 79.9968 | 81.4912 | 82.9856 | 84.48 | 85.4763 | 86.4725 | 87.4688 | 88.4651 | 89.4613 | 90.4576 | 91.4539 | 92.4501 | 93.4464 | 94.4427 | 95.4389 | 96.4352 | 97.4315 | 98.4277 | 99.424 | 100.2795 | 101.1349 | 101.9904 | 102.8459 | 103.7013 | 104.5568 | 105.4123 | 106.2677 | 107.1232 | 107.9787 | 108.8341 | 109.6896 | 110.5451 | 111.4005 | 112.256 | 112.5088 | 112.7616 | 113.0144 | 113.2672 | 113.52 | 113.7728 | 114.0256 | 114.2784 | 114.5312 | 114.784 | 115.0368 | 115.2896 | 115.5424 | 115.7952 | 116.048 | 116.3008 | 116.5536 | 116.8064 | 117.0592 | 117.312 | 117.5648 | 117.8176 | 118.0704 | 118.3232 | 118.576 | 118.8288 | 119.0816 | 119.3344 | 119.5872 | 119.84 | 119.9445 | 120.0491 | 120.1536 | 120.2581 | 120.3627 | 120.4672 | 120.5717 | 120.6763 | 120.7808 | 120.8853 | 120.9899 | 121.0944 | 121.1989 | 121.3035 | 121.408 | 121.5125 | 121.6171 | 121.7216 | 121.8261 | 121.9307 | 122.0352 | 122.1397 | 122.2443 | 122.3488 | 122.4533 | 122.5579 | 122.6624 | 122.7669 | 122.8715 | 122.976 | 122.976 | 122.976 | 122.976 | 122.976 | 122.976 | 122.976 | 122.976 | 122.976 | 122.976 | 122.976 | 122.976 | 122.976 | 122.976 | 122.976 | 122.976 | 122.976 | 122.976 | 122.976 | 122.976 | 122.976 | 122.976 | 122.976 | 122.976 | 122.976 | 122.976 | 122.976 | 122.976 | 122.976 | 122.976 | 122.976 | 122.896 | 122.816 | 122.736 | 122.656 | 122.576 | 122.496 | 122.416 | 122.336 | 122.256 | 122.176 | 122.096 | 122.016 | 121.936 | 121.856 | 121.776 | 121.696 | 121.616 | 121.536 | 121.456 | 121.376 | 121.296 | 121.216 | 121.136 | 121.056 | 120.976 | 120.896 | 120.816 | 120.736 | 120.656 | 120.576
11.25 | 0 | 39.75 | 68.3833 | 70.225 | 85.3333 | 100.4417 | 113.4333 | 121.125 | 124.3083 | 124.3083 | 121.9333 | -3.5527e-15 | 3.975 | 7.95 | 11.925 | 15.9 | 19.875 | 23.85 | 27.825 | 31.8 | 35.775 | 39.75 | 45.4767 | 51.2033 | 56.93 | 62.6567 | 68.3833 | 68.7517 | 69.12 | 69.4883 | 69.8567 | 70.225 | 71.7358 | 73.2467 | 74.7575 | 76.2683 | 77.7792 | 79.29 | 80.8008 | 82.3117 | 83.8225 | 85.3333 | 86.3406 | 87.3478 | 88.355 | 89.3622 | 90.3694 | 91.3767 | 92.3839 | 93.3911 | 94.3983 | 95.4056 | 96.4128 | 97.42 | 98.4272 | 99.4344 | 100.4417 | 101.3078 | 102.1739 | 103.04 | 103.9061 | 104.7722 | 105.6383 | 106.5044 | 107.3706 | 108.2367 | 109.1028 | 109.9689 | 110.835 | 111.7011 | 112.5672 | 113.4333 | 113.6897 | 113.9461 | 114.2025 | 114.4589 | 114.7153 | 114.9717 | 115.2281 | 115.4844 | 115.7408 | 115.9972 | 116.2536 | 116.51 | 116.7664 | 117.0228 | 117.2792 | 117.5356 | 117.7919 | 118.0483 | 118.3047 | 118.5611 | 118.8175 | 119.0739 | 119.3303 | 119.5867 | 119.8431 | 120.0994 | 120.3558 | 120.6122 | 120.8686 | 121.125 | 121.2311 | 121.3372 | 121.4433 | 121.5494 | 121.6556 | 121.7617 | 121.8678 | 121.9739 | 122.08 | 122.1861 | 122.2922 | 122.3983 | 122.5044 | 122.6106 | 122.7167 | 122.8228 | 122.9289 | 123.035 | 123.1411 | 123.2472 | 123.3533 | 123.4594 | 123.5656 | 123.6717 | 123.7778 | 123.8839 | 123.99 | 124.0961 | 124.2022 | 124.3083 | 124.3083 | 124.3083 | 124.3083 | 124.3083 | 124.3083 | 124.3083 | 124.3083 | 124.3083 | 124.3083 | 124.3083 | 124.3083 | 124.3083 | 124.3083 | 124.3083 | 124.3083 | 124.3083 | 124.3083 | 124.3083 | 124.3083 | 124.3083 | 124.3083 | 124.3083 | 124.3083 | 124.3083 | 124.3083 | 124.3083 | 124.3083 | 124.3083 | 124.3083 | 124.3083 | 124.2292 | 124.15 | 124.0708 | 123.9917 | 123.9125 | 123.8333 | 123.7542 | 123.675 | 123.5958 | 123.5167 | 123.4375 | 123.3583 | 123.2792 | 123.2 | 123.1208 | 123.0417 | 122.9625 | 122.8833 | 122.8042 | 122.725 | 122.6458 | 122.5667 | 122.4875 | 122.4083 | 122.3292 | 122.25 | 122.1708 | 122.0917 | 122.0125 | 121.9333
11.3 | 0 | 40.14 | 69.1187 | 70.914 | 86.1867 | 101.4593 | 114.6107 | 122.41 | 125.6407 | 125.6407 | 123.2907 | -3.5527e-15 | 4.014 | 8.028 | 12.042 | 16.056 | 20.07 | 24.084 | 28.098 | 32.112 | 36.126 | 40.14 | 45.9357 | 51.7315 | 57.5272 | 63.3229 | 69.1187 | 69.4777 | 69.8368 | 70.1959 | 70.5549 | 70.914 | 72.4413 | 73.9685 | 75.4958 | 77.0231 | 78.5503 | 80.0776 | 81.6049 | 83.1321 | 84.6594 | 86.1867 | 87.2048 | 88.223 | 89.2412 | 90.2594 | 91.2776 | 92.2957 | 93.3139 | 94.3321 | 95.3503 | 96.3684 | 97.3866 | 98.4048 | 99.423 | 100.4412 | 101.4593 | 102.3361 | 103.2128 | 104.0896 | 104.9664 | 105.8431 | 106.7199 | 107.5966 | 108.4734 | 109.3501 | 110.2269 | 111.1036 | 111.9804 | 112.8572 | 113.7339 | 114.6107 | 114.8706 | 115.1306 | 115.3906 | 115.6506 | 115.9106 | 116.1705 | 116.4305 | 116.6905 | 116.9505 | 117.2104 | 117.4704 | 117.7304 | 117.9904 | 118.2504 | 118.5103 | 118.7703 | 119.0303 | 119.2903 | 119.5502 | 119.8102 | 120.0702 | 120.3302 | 120.5902 | 120.8501 | 121.1101 | 121.3701 | 121.6301 | 121.89 | 122.15 | 122.41 | 122.5177 | 122.6254 | 122.7331 | 122.8408 | 122.9484 | 123.0561 | 123.1638 | 123.2715 | 123.3792 | 123.4869 | 123.5946 | 123.7023 | 123.81 | 123.9176 | 124.0253 | 124.133 | 124.2407 | 124.3484 | 124.4561 | 124.5638 | 124.6715 | 124.7792 | 124.8868 | 124.9945 | 125.1022 | 125.2099 | 125.3176 | 125.4253 | 125.533 | 125.6407 | 125.6407 | 125.6407 | 125.6407 | 125.6407 | 125.6407 | 125.6407 | 125.6407 | 125.6407 | 125.6407 | 125.6407 | 125.6407 | 125.6407 | 125.6407 | 125.6407 | 125.6407 | 125.6407 | 125.6407 | 125.6407 | 125.6407 | 125.6407 | 125.6407 | 125.6407 | 125.6407 | 125.6407 | 125.6407 | 125.6407 | 125.6407 | 125.6407 | 125.6407 | 125.6407 | 125.5623 | 125.484 | 125.4057 | 125.3273 | 125.249 | 125.1707 | 125.0923 | 125.014 | 124.9357 | 124.8573 | 124.779 | 124.7007 | 124.6223 | 124.544 | 124.4657 | 124.3873 | 124.309 | 124.2307 | 124.1523 | 124.074 | 123.9957 | 123.9173 | 123.839 | 123.7607 | 123.6823 | 123.604 | 123.5257 | 123.4473 | 123.369 | 123.2907
11.35 | 0 | 40.53 | 69.854 | 71.603 | 87.04 | 102.477 | 115.788 | 123.695 | 126.973 | 126.973 | 124.648 | -3.5527e-15 | 4.053 | 8.106 | 12.159 | 16.212 | 20.265 | 24.318 | 28.371 | 32.424 | 36.477 | 40.53 | 46.3948 | 52.2596 | 58.1244 | 63.9892 | 69.854 | 70.2038 | 70.5536 | 70.9034 | 71.2532 | 71.603 | 73.1467 | 74.6904 | 76.2341 | 77.7778 | 79.3215 | 80.8652 | 82.4089 | 83.9526 | 85.4963 | 87.04 | 88.0691 | 89.0983 | 90.1274 | 91.1565 | 92.1857 | 93.2148 | 94.2439 | 95.2731 | 96.3022 | 97.3313 | 98.3605 | 99.3896 | 100.4187 | 101.4479 | 102.477 | 103.3644 | 104.2518 | 105.1392 | 106.0266 | 106.914 | 107.8014 | 108.6888 | 109.5762 | 110.4636 | 111.351 | 112.2384 | 113.1258 | 114.0132 | 114.9006 | 115.788 | 116.0516 | 116.3151 | 116.5787 | 116.8423 | 117.1058 | 117.3694 | 117.633 | 117.8965 | 118.1601 | 118.4237 | 118.6872 | 118.9508 | 119.2144 | 119.4779 | 119.7415 | 120.0051 | 120.2686 | 120.5322 | 120.7958 | 121.0593 | 121.3229 | 121.5865 | 121.85 | 122.1136 | 122.3772 | 122.6407 | 122.9043 | 123.1679 | 123.4314 | 123.695 | 123.8043 | 123.9135 | 124.0228 | 124.1321 | 124.2413 | 124.3506 | 124.4599 | 124.5691 | 124.6784 | 124.7877 | 124.8969 | 125.0062 | 125.1155 | 125.2247 | 125.334 | 125.4433 | 125.5525 | 125.6618 | 125.7711 | 125.8803 | 125.9896 | 126.0989 | 126.2081 | 126.3174 | 126.4267 | 126.5359 | 126.6452 | 126.7545 | 126.8637 | 126.973 | 126.973 | 126.973 | 126.973 | 126.973 | 126.973 | 126.973 | 126.973 | 126.973 | 126.973 | 126.973 | 126.973 | 126.973 | 126.973 | 126.973 | 126.973 | 126.973 | 126.973 | 126.973 | 126.973 | 126.973 | 126.973 | 126.973 | 126.973 | 126.973 | 126.973 | 126.973 | 126.973 | 126.973 | 126.973 | 126.973 | 126.8955 | 126.818 | 126.7405 | 126.663 | 126.5855 | 126.508 | 126.4305 | 126.353 | 126.2755 | 126.198 | 126.1205 | 126.043 | 125.9655 | 125.888 | 125.8105 | 125.733 | 125.6555 | 125.578 | 125.5005 | 125.423 | 125.3455 | 125.268 | 125.1905 | 125.113 | 125.0355 | 124.958 | 124.8805 | 124.803 | 124.7255 | 124.648
11.4 | 0 | 40.92 | 70.5893 | 72.292 | 87.8933 | 103.4947 | 116.9653 | 124.98 | 128.3053 | 128.3053 | 126.0053 | 0 | 4.092 | 8.184 | 12.276 | 16.368 | 20.46 | 24.552 | 28.644 | 32.736 | 36.828 | 40.92 | 46.8539 | 52.7877 | 58.7216 | 64.6555 | 70.5893 | 70.9299 | 71.2704 | 71.6109 | 71.9515 | 72.292 | 73.8521 | 75.4123 | 76.9724 | 78.5325 | 80.0927 | 81.6528 | 83.2129 | 84.7731 | 86.3332 | 87.8933 | 88.9334 | 89.9735 | 91.0136 | 92.0537 | 93.0938 | 94.1339 | 95.174 | 96.214 | 97.2541 | 98.2942 | 99.3343 | 100.3744 | 101.4145 | 102.4546 | 103.4947 | 104.3927 | 105.2908 | 106.1888 | 107.0868 | 107.9849 | 108.8829 | 109.781 | 110.679 | 111.5771 | 112.4751 | 113.3732 | 114.2712 | 115.1692 | 116.0673 | 116.9653 | 117.2325 | 117.4996 | 117.7668 | 118.034 | 118.3011 | 118.5683 | 118.8354 | 119.1026 | 119.3697 | 119.6369 | 119.904 | 120.1712 | 120.4384 | 120.7055 | 120.9727 | 121.2398 | 121.507 | 121.7741 | 122.0413 | 122.3084 | 122.5756 | 122.8428 | 123.1099 | 123.3771 | 123.6442 | 123.9114 | 124.1785 | 124.4457 | 124.7128 | 124.98 | 125.0908 | 125.2017 | 125.3125 | 125.4234 | 125.5342 | 125.6451 | 125.7559 | 125.8668 | 125.9776 | 126.0884 | 126.1993 | 126.3101 | 126.421 | 126.5318 | 126.6427 | 126.7535 | 126.8644 | 126.9752 | 127.086 | 127.1969 | 127.3077 | 127.4186 | 127.5294 | 127.6403 | 127.7511 | 127.862 | 127.9728 | 128.0836 | 128.1945 | 128.3053 | 128.3053 | 128.3053 | 128.3053 | 128.3053 | 128.3053 | 128.3053 | 128.3053 | 128.3053 | 128.3053 | 128.3053 | 128.3053 | 128.3053 | 128.3053 | 128.3053 | 128.3053 | 128.3053 | 128.3053 | 128.3053 | 128.3053 | 128.3053 | 128.3053 | 128.3053 | 128.3053 | 128.3053 | 128.3053 | 128.3053 | 128.3053 | 128.3053 | 128.3053 | 128.3053 | 128.2287 | 128.152 | 128.0753 | 127.9987 | 127.922 | 127.8453 | 127.7687 | 127.692 | 127.6153 | 127.5387 | 127.462 | 127.3853 | 127.3087 | 127.232 | 127.1553 | 127.0787 | 127.002 | 126.9253 | 126.8487 | 126.772 | 126.6953 | 126.6187 | 126.542 | 126.4653 | 126.3887 | 126.312 | 126.2353 | 126.1587 | 126.082 | 126.0053
11.45 | 0 | 41.31 | 71.3247 | 72.981 | 88.7467 | 104.5123 | 118.1427 | 126.265 | 129.6377 | 129.6377 | 127.3627 | 0 | 4.131 | 8.262 | 12.393 | 16.524 | 20.655 | 24.786 | 28.917 | 33.048 | 37.179 | 41.31 | 47.3129 | 53.3159 | 59.3188 | 65.3217 | 71.3247 | 71.6559 | 71.9872 | 72.3185 | 72.6497 | 72.981 | 74.5576 | 76.1341 | 77.7107 | 79.2873 | 80.8638 | 82.4404 | 84.017 | 85.5935 | 87.1701 | 88.7467 | 89.7977 | 90.8488 | 91.8998 | 92.9508 | 94.0019 | 95.0529 | 96.104 | 97.155 | 98.2061 | 99.2571 | 100.3082 | 101.3592 | 102.4102 | 103.4613 | 104.5123 | 105.421 | 106.3297 | 107.2384 | 108.1471 | 109.0558 | 109.9645 | 110.8732 | 111.7818 | 112.6905 | 113.5992 | 114.5079 | 115.4166 | 116.3253 | 117.234 | 118.1427 | 118.4134 | 118.6842 | 118.9549 | 119.2256 | 119.4964 | 119.7671 | 120.0379 | 120.3086 | 120.5794 | 120.8501 | 121.1209 | 121.3916 | 121.6623 | 121.9331 | 122.2038 | 122.4746 | 122.7453 | 123.0161 | 123.2868 | 123.5576 | 123.8283 | 124.099 | 124.3698 | 124.6405 | 124.9113 | 125.182 | 125.4528 | 125.7235 | 125.9943 | 126.265 | 126.3774 | 126.4898 | 126.6023 | 126.7147 | 126.8271 | 126.9395 | 127.052 | 127.1644 | 127.2768 | 127.3892 | 127.5016 | 127.6141 | 127.7265 | 127.8389 | 127.9513 | 128.0638 | 128.1762 | 128.2886 | 128.401 | 128.5134 | 128.6259 | 128.7383 | 128.8507 | 128.9631 | 129.0756 | 129.188 | 129.3004 | 129.4128 | 129.5252 | 129.6377 | 129.6377 | 129.6377 | 129.6377 | 129.6377 | 129.6377 | 129.6377 | 129.6377 | 129.6377 | 129.6377 | 129.6377 | 129.6377 | 129.6377 | 129.6377 | 129.6377 | 129.6377 | 129.6377 | 129.6377 | 129.6377 | 129.6377 | 129.6377 | 129.6377 | 129.6377 | 129.6377 | 129.6377 | 129.6377 | 129.6377 | 129.6377 | 129.6377 | 129.6377 | 129.6377 | 129.5618 | 129.486 | 129.4102 | 129.3343 | 129.2585 | 129.1827 | 129.1068 | 129.031 | 128.9552 | 128.8793 | 128.8035 | 128.7277 | 128.6518 | 128.576 | 128.5002 | 128.4243 | 128.3485 | 128.2727 | 128.1968 | 128.121 | 128.0452 | 127.9693 | 127.8935 | 127.8177 | 127.7418 | 127.666 | 127.5902 | 127.5143 | 127.4385 | 127.3627
11.5 | 0 | 41.7 | 72.06 | 73.67 | 89.6 | 105.53 | 119.32 | 127.55 | 130.97 | 130.97 | 128.72 | 3.5527e-15 | 4.17 | 8.34 | 12.51 | 16.68 | 20.85 | 25.02 | 29.19 | 33.36 | 37.53 | 41.7 | 47.772 | 53.844 | 59.916 | 65.988 | 72.06 | 72.382 | 72.704 | 73.026 | 73.348 | 73.67 | 75.263 | 76.856 | 78.449 | 80.042 | 81.635 | 83.228 | 84.821 | 86.414 | 88.007 | 89.6 | 90.662 | 91.724 | 92.786 | 93.848 | 94.91 | 95.972 | 97.034 | 98.096 | 99.158 | 100.22 | 101.282 | 102.344 | 103.406 | 104.468 | 105.53 | 106.4493 | 107.3687 | 108.288 | 109.2073 | 110.1267 | 111.046 | 111.9653 | 112.8847 | 113.804 | 114.7233 | 115.6427 | 116.562 | 117.4813 | 118.4007 | 119.32 | 119.5943 | 119.8687 | 120.143 | 120.4173 | 120.6917 | 120.966 | 121.2403 | 121.5147 | 121.789 | 122.0633 | 122.3377 | 122.612 | 122.8863 | 123.1607 | 123.435 | 123.7093 | 123.9837 | 124.258 | 124.5323 | 124.8067 | 125.081 | 125.3553 | 125.6297 | 125.904 | 126.1783 | 126.4527 | 126.727 | 127.0013 | 127.2757 | 127.55 | 127.664 | 127.778 | 127.892 | 128.006 | 128.12 | 128.234 | 128.348 | 128.462 | 128.576 | 128.69 | 128.804 | 128.918 | 129.032 | 129.146 | 129.26 | 129.374 | 129.488 | 129.602 | 129.716 | 129.83 | 129.944 | 130.058 | 130.172 | 130.286 | 130.4 | 130.514 | 130.628 | 130.742 | 130.856 | 130.97 | 130.97 | 130.97 | 130.97 | 130.97 | 130.97 | 130.97 | 130.97 | 130.97 | 130.97 | 130.97 | 130.97 | 130.97 | 130.97 | 130.97 | 130.97 | 130.97 | 130.97 | 130.97 | 130.97 | 130.97 | 130.97 | 130.97 | 130.97 | 130.97 | 130.97 | 130.97 | 130.97 | 130.97 | 130.97 | 130.97 | 130.895 | 130.82 | 130.745 | 130.67 | 130.595 | 130.52 | 130.445 | 130.37 | 130.295 | 130.22 | 130.145 | 130.07 | 129.995 | 129.92 | 129.845 | 129.77 | 129.695 | 129.62 | 129.545 | 129.47 | 129.395 | 129.32 | 129.245 | 129.17 | 129.095 | 129.02 | 128.945 | 128.87 | 128.795 | 128.72
11.55 | 0 | 42.09 | 72.7953 | 74.359 | 90.4533 | 106.5477 | 120.4973 | 128.835 | 132.3023 | 132.3023 | 130.0773 | 0 | 4.209 | 8.418 | 12.627 | 16.836 | 21.045 | 25.254 | 29.463 | 33.672 | 37.881 | 42.09 | 48.2311 | 54.3721 | 60.5132 | 66.6543 | 72.7953 | 73.1081 | 73.4208 | 73.7335 | 74.0463 | 74.359 | 75.9684 | 77.5779 | 79.1873 | 80.7967 | 82.4062 | 84.0156 | 85.625 | 87.2345 | 88.8439 | 90.4533 | 91.5263 | 92.5992 | 93.6722 | 94.7452 | 95.8181 | 96.8911 | 97.964 | 99.037 | 100.1099 | 101.1829 | 102.2558 | 103.3288 | 104.4018 | 105.4747 | 106.5477 | 107.4776 | 108.4076 | 109.3376 | 110.2676 | 111.1976 | 112.1275 | 113.0575 | 113.9875 | 114.9175 | 115.8474 | 116.7774 | 117.7074 | 118.6374 | 119.5674 | 120.4973 | 120.7753 | 121.0532 | 121.3311 | 121.609 | 121.8869 | 122.1649 | 122.4428 | 122.7207 | 122.9986 | 123.2766 | 123.5545 | 123.8324 | 124.1103 | 124.3882 | 124.6662 | 124.9441 | 125.222 | 125.4999 | 125.7779 | 126.0558 | 126.3337 | 126.6116 | 126.8895 | 127.1675 | 127.4454 | 127.7233 | 128.0012 | 128.2792 | 128.5571 | 128.835 | 128.9506 | 129.0662 | 129.1817 | 129.2973 | 129.4129 | 129.5285 | 129.644 | 129.7596 | 129.8752 | 129.9908 | 130.1064 | 130.2219 | 130.3375 | 130.4531 | 130.5687 | 130.6842 | 130.7998 | 130.9154 | 131.031 | 131.1466 | 131.2621 | 131.3777 | 131.4933 | 131.6089 | 131.7244 | 131.84 | 131.9556 | 132.0712 | 132.1868 | 132.3023 | 132.3023 | 132.3023 | 132.3023 | 132.3023 | 132.3023 | 132.3023 | 132.3023 | 132.3023 | 132.3023 | 132.3023 | 132.3023 | 132.3023 | 132.3023 | 132.3023 | 132.3023 | 132.3023 | 132.3023 | 132.3023 | 132.3023 | 132.3023 | 132.3023 | 132.3023 | 132.3023 | 132.3023 | 132.3023 | 132.3023 | 132.3023 | 132.3023 | 132.3023 | 132.3023 | 132.2282 | 132.154 | 132.0798 | 132.0057 | 131.9315 | 131.8573 | 131.7832 | 131.709 | 131.6348 | 131.5607 | 131.4865 | 131.4123 | 131.3382 | 131.264 | 131.1898 | 131.1157 | 131.0415 | 130.9673 | 130.8932 | 130.819 | 130.7448 | 130.6707 | 130.5965 | 130.5223 | 130.4482 | 130.374 | 130.2998 | 130.2257 | 130.1515 | 130.0773
11.6 | 0 | 42.48 | 73.5307 | 75.048 | 91.3067 | 107.5653 | 121.6747 | 130.12 | 133.6347 | 133.6347 | 131.4347 | 3.5527e-15 | 4.248 | 8.496 | 12.744 | 16.992 | 21.24 | 25.488 | 29.736 | 33.984 | 38.232 | 42.48 | 48.6901 | 54.9003 | 61.1104 | 67.3205 | 73.5307 | 73.8341 | 74.1376 | 74.4411 | 74.7445 | 75.048 | 76.6739 | 78.2997 | 79.9256 | 81.5515 | 83.1773 | 84.8032 | 86.4291 | 88.0549 | 89.6808 | 91.3067 | 92.3906 | 93.4745 | 94.5584 | 95.6423 | 96.7262 | 97.8101 | 98.894 | 99.978 | 101.0619 | 102.1458 | 103.2297 | 104.3136 | 105.3975 | 106.4814 | 107.5653 | 108.506 | 109.4466 | 110.3872 | 111.3278 | 112.2684 | 113.2091 | 114.1497 | 115.0903 | 116.0309 | 116.9716 | 117.9122 | 118.8528 | 119.7934 | 120.734 | 121.6747 | 121.9562 | 122.2377 | 122.5192 | 122.8007 | 123.0822 | 123.3637 | 123.6452 | 123.9268 | 124.2083 | 124.4898 | 124.7713 | 125.0528 | 125.3343 | 125.6158 | 125.8973 | 126.1788 | 126.4604 | 126.7419 | 127.0234 | 127.3049 | 127.5864 | 127.8679 | 128.1494 | 128.4309 | 128.7124 | 128.994 | 129.2755 | 129.557 | 129.8385 | 130.12 | 130.2372 | 130.3543 | 130.4715 | 130.5886 | 130.7058 | 130.8229 | 130.9401 | 131.0572 | 131.1744 | 131.2916 | 131.4087 | 131.5259 | 131.643 | 131.7602 | 131.8773 | 131.9945 | 132.1116 | 132.2288 | 132.346 | 132.4631 | 132.5803 | 132.6974 | 132.8146 | 132.9317 | 133.0489 | 133.166 | 133.2832 | 133.4004 | 133.5175 | 133.6347 | 133.6347 | 133.6347 | 133.6347 | 133.6347 | 133.6347 | 133.6347 | 133.6347 | 133.6347 | 133.6347 | 133.6347 | 133.6347 | 133.6347 | 133.6347 | 133.6347 | 133.6347 | 133.6347 | 133.6347 | 133.6347 | 133.6347 | 133.6347 | 133.6347 | 133.6347 | 133.6347 | 133.6347 | 133.6347 | 133.6347 | 133.6347 | 133.6347 | 133.6347 | 133.6347 | 133.5613 | 133.488 | 133.4147 | 133.3413 | 133.268 | 133.1947 | 133.1213 | 133.048 | 132.9747 | 132.9013 | 132.828 | 132.7547 | 132.6813 | 132.608 | 132.5347 | 132.4613 | 132.388 | 132.3147 | 132.2413 | 132.168 | 132.0947 | 132.0213 | 131.948 | 131.8747 | 131.8013 | 131.728 | 131.6547 | 131.5813 | 131.508 | 131.4347
11.65 | 0 | 42.87 | 74.266 | 75.737 | 92.16 | 108.583 | 122.852 | 131.405 | 134.967 | 134.967 | 132.792 | 0 | 4.287 | 8.574 | 12.861 | 17.148 | 21.435 | 25.722 | 30.009 | 34.296 | 38.583 | 42.87 | 49.1492 | 55.4284 | 61.7076 | 67.9868 | 74.266 | 74.5602 | 74.8544 | 75.1486 | 75.4428 | 75.737 | 77.3793 | 79.0216 | 80.6639 | 82.3062 | 83.9485 | 85.5908 | 87.2331 | 88.8754 | 90.5177 | 92.16 | 93.2549 | 94.3497 | 95.4446 | 96.5395 | 97.6343 | 98.7292 | 99.8241 | 100.9189 | 102.0138 | 103.1087 | 104.2035 | 105.2984 | 106.3933 | 107.4881 | 108.583 | 109.5343 | 110.4855 | 111.4368 | 112.3881 | 113.3393 | 114.2906 | 115.2419 | 116.1931 | 117.1444 | 118.0957 | 119.0469 | 119.9982 | 120.9495 | 121.9007 | 122.852 | 123.1371 | 123.4222 | 123.7073 | 123.9924 | 124.2775 | 124.5626 | 124.8477 | 125.1328 | 125.4179 | 125.703 | 125.9881 | 126.2732 | 126.5583 | 126.8434 | 127.1285 | 127.4136 | 127.6987 | 127.9838 | 128.2689 | 128.554 | 128.8391 | 129.1242 | 129.4093 | 129.6944 | 129.9795 | 130.2646 | 130.5497 | 130.8348 | 131.1199 | 131.405 | 131.5237 | 131.6425 | 131.7612 | 131.8799 | 131.9987 | 132.1174 | 132.2361 | 132.3549 | 132.4736 | 132.5923 | 132.7111 | 132.8298 | 132.9485 | 133.0673 | 133.186 | 133.3047 | 133.4235 | 133.5422 | 133.6609 | 133.7797 | 133.8984 | 134.0171 | 134.1359 | 134.2546 | 134.3733 | 134.4921 | 134.6108 | 134.7295 | 134.8483 | 134.967 | 134.967 | 134.967 | 134.967 | 134.967 | 134.967 | 134.967 | 134.967 | 134.967 | 134.967 | 134.967 | 134.967 | 134.967 | 134.967 | 134.967 | 134.967 | 134.967 | 134.967 | 134.967 | 134.967 | 134.967 | 134.967 | 134.967 | 134.967 | 134.967 | 134.967 | 134.967 | 134.967 | 134.967 | 134.967 | 134.967 | 134.8945 | 134.822 | 134.7495 | 134.677 | 134.6045 | 134.532 | 134.4595 | 134.387 | 134.3145 | 134.242 | 134.1695 | 134.097 | 134.0245 | 133.952 | 133.8795 | 133.807 | 133.7345 | 133.662 | 133.5895 | 133.517 | 133.4445 | 133.372 | 133.2995 | 133.227 | 133.1545 | 133.082 | 133.0095 | 132.937 | 132.8645 | 132.792
11.7 | 0 | 43.26 | 75.0013 | 76.426 | 93.0133 | 109.6007 | 124.0293 | 132.69 | 136.2993 | 136.2993 | 134.1493 | -3.5527e-15 | 4.326 | 8.652 | 12.978 | 17.304 | 21.63 | 25.956 | 30.282 | 34.608 | 38.934 | 43.26 | 49.6083 | 55.9565 | 62.3048 | 68.6531 | 75.0013 | 75.2863 | 75.5712 | 75.8561 | 76.1411 | 76.426 | 78.0847 | 79.7435 | 81.4022 | 83.0609 | 84.7197 | 86.3784 | 88.0371 | 89.6959 | 91.3546 | 93.0133 | 94.1192 | 95.225 | 96.3308 | 97.4366 | 98.5424 | 99.6483 | 100.7541 | 101.8599 | 102.9657 | 104.0716 | 105.1774 | 106.2832 | 107.389 | 108.4948 | 109.6007 | 110.5626 | 111.5245 | 112.4864 | 113.4483 | 114.4102 | 115.3721 | 116.334 | 117.296 | 118.2579 | 119.2198 | 120.1817 | 121.1436 | 122.1055 | 123.0674 | 124.0293 | 124.318 | 124.6067 | 124.8954 | 125.1841 | 125.4728 | 125.7615 | 126.0502 | 126.3388 | 126.6275 | 126.9162 | 127.2049 | 127.4936 | 127.7823 | 128.071 | 128.3597 | 128.6484 | 128.937 | 129.2257 | 129.5144 | 129.8031 | 130.0918 | 130.3805 | 130.6692 | 130.9579 | 131.2466 | 131.5352 | 131.8239 | 132.1126 | 132.4013 | 132.69 | 132.8103 | 132.9306 | 133.0509 | 133.1712 | 133.2916 | 133.4119 | 133.5322 | 133.6525 | 133.7728 | 133.8931 | 134.0134 | 134.1337 | 134.254 | 134.3744 | 134.4947 | 134.615 | 134.7353 | 134.8556 | 134.9759 | 135.0962 | 135.2165 | 135.3368 | 135.4572 | 135.5775 | 135.6978 | 135.8181 | 135.9384 | 136.0587 | 136.179 | 136.2993 | 136.2993 | 136.2993 | 136.2993 | 136.2993 | 136.2993 | 136.2993 | 136.2993 | 136.2993 | 136.2993 | 136.2993 | 136.2993 | 136.2993 | 136.2993 | 136.2993 | 136.2993 | 136.2993 | 136.2993 | 136.2993 | 136.2993 | 136.2993 | 136.2993 | 136.2993 | 136.2993 | 136.2993 | 136.2993 | 136.2993 | 136.2993 | 136.2993 | 136.2993 | 136.2993 | 136.2277 | 136.156 | 136.0843 | 136.0127 | 135.941 | 135.8693 | 135.7977 | 135.726 | 135.6543 | 135.5827 | 135.511 | 135.4393 | 135.3677 | 135.296 | 135.2243 | 135.1527 | 135.081 | 135.0093 | 134.9377 | 134.866 | 134.7943 | 134.7227 | 134.651 | 134.5793 | 134.5077 | 134.436 | 134.3643 | 134.2927 | 134.221 | 134.1493
11.75 | 0 | 43.65 | 75.7367 | 77.115 | 93.8667 | 110.6183 | 125.2067 | 133.975 | 137.6317 | 137.6317 | 135.5067 | -3.5527e-15 | 4.365 | 8.73 | 13.095 | 17.46 | 21.825 | 26.19 | 30.555 | 34.92 | 39.285 | 43.65 | 50.0673 | 56.4847 | 62.902 | 69.3193 | 75.7367 | 76.0123 | 76.288 | 76.5637 | 76.8393 | 77.115 | 78.7902 | 80.4653 | 82.1405 | 83.8157 | 85.4908 | 87.166 | 88.8412 | 90.5163 | 92.1915 | 93.8667 | 94.9834 | 96.1002 | 97.217 | 98.3338 | 99.4506 | 100.5673 | 101.6841 | 102.8009 | 103.9177 | 105.0344 | 106.1512 | 107.268 | 108.3848 | 109.5016 | 110.6183 | 111.5909 | 112.5634 | 113.536 | 114.5086 | 115.4811 | 116.4537 | 117.4262 | 118.3988 | 119.3713 | 120.3439 | 121.3164 | 122.289 | 123.2616 | 124.2341 | 125.2067 | 125.4989 | 125.7912 | 126.0835 | 126.3758 | 126.6681 | 126.9603 | 127.2526 | 127.5449 | 127.8372 | 128.1294 | 128.4217 | 128.714 | 129.0063 | 129.2986 | 129.5908 | 129.8831 | 130.1754 | 130.4677 | 130.7599 | 131.0522 | 131.3445 | 131.6368 | 131.9291 | 132.2213 | 132.5136 | 132.8059 | 133.0982 | 133.3904 | 133.6827 | 133.975 | 134.0969 | 134.2188 | 134.3407 | 134.4626 | 134.5844 | 134.7063 | 134.8282 | 134.9501 | 135.072 | 135.1939 | 135.3158 | 135.4377 | 135.5596 | 135.6814 | 135.8033 | 135.9252 | 136.0471 | 136.169 | 136.2909 | 136.4128 | 136.5347 | 136.6566 | 136.7784 | 136.9003 | 137.0222 | 137.1441 | 137.266 | 137.3879 | 137.5098 | 137.6317 | 137.6317 | 137.6317 | 137.6317 | 137.6317 | 137.6317 | 137.6317 | 137.6317 | 137.6317 | 137.6317 | 137.6317 | 137.6317 | 137.6317 | 137.6317 | 137.6317 | 137.6317 | 137.6317 | 137.6317 | 137.6317 | 137.6317 | 137.6317 | 137.6317 | 137.6317 | 137.6317 | 137.6317 | 137.6317 | 137.6317 | 137.6317 | 137.6317 | 137.6317 | 137.6317 | 137.5608 | 137.49 | 137.4192 | 137.3483 | 137.2775 | 137.2067 | 137.1358 | 137.065 | 136.9942 | 136.9233 | 136.8525 | 136.7817 | 136.7108 | 136.64 | 136.5692 | 136.4983 | 136.4275 | 136.3567 | 136.2858 | 136.215 | 136.1442 | 136.0733 | 136.0025 | 135.9317 | 135.8608 | 135.79 | 135.7192 | 135.6483 | 135.5775 | 135.5067
11.8 | 0 | 44.04 | 76.472 | 77.804 | 94.72 | 111.636 | 126.384 | 135.26 | 138.964 | 138.964 | 136.864 | 0 | 4.404 | 8.808 | 13.212 | 17.616 | 22.02 | 26.424 | 30.828 | 35.232 | 39.636 | 44.04 | 50.5264 | 57.0128 | 63.4992 | 69.9856 | 76.472 | 76.7384 | 77.0048 | 77.2712 | 77.5376 | 77.804 | 79.4956 | 81.1872 | 82.8788 | 84.5704 | 86.262 | 87.9536 | 89.6452 | 91.3368 | 93.0284 | 94.72 | 95.8477 | 96.9755 | 98.1032 | 99.2309 | 100.3587 | 101.4864 | 102.6141 | 103.7419 | 104.8696 | 105.9973 | 107.1251 | 108.2528 | 109.3805 | 110.5083 | 111.636 | 112.6192 | 113.6024 | 114.5856 | 115.5688 | 116.552 | 117.5352 | 118.5184 | 119.5016 | 120.4848 | 121.468 | 122.4512 | 123.4344 | 124.4176 | 125.4008 | 126.384 | 126.6799 | 126.9757 | 127.2716 | 127.5675 | 127.8633 | 128.1592 | 128.4551 | 128.7509 | 129.0468 | 129.3427 | 129.6385 | 129.9344 | 130.2303 | 130.5261 | 130.822 | 131.1179 | 131.4137 | 131.7096 | 132.0055 | 132.3013 | 132.5972 | 132.8931 | 133.1889 | 133.4848 | 133.7807 | 134.0765 | 134.3724 | 134.6683 | 134.9641 | 135.26 | 135.3835 | 135.5069 | 135.6304 | 135.7539 | 135.8773 | 136.0008 | 136.1243 | 136.2477 | 136.3712 | 136.4947 | 136.6181 | 136.7416 | 136.8651 | 136.9885 | 137.112 | 137.2355 | 137.3589 | 137.4824 | 137.6059 | 137.7293 | 137.8528 | 137.9763 | 138.0997 | 138.2232 | 138.3467 | 138.4701 | 138.5936 | 138.7171 | 138.8405 | 138.964 | 138.964 | 138.964 | 138.964 | 138.964 | 138.964 | 138.964 | 138.964 | 138.964 | 138.964 | 138.964 | 138.964 | 138.964 | 138.964 | 138.964 | 138.964 | 138.964 | 138.964 | 138.964 | 138.964 | 138.964 | 138.964 | 138.964 | 138.964 | 138.964 | 138.964 | 138.964 | 138.964 | 138.964 | 138.964 | 138.964 | 138.894 | 138.824 | 138.754 | 138.684 | 138.614 | 138.544 | 138.474 | 138.404 | 138.334 | 138.264 | 138.194 | 138.124 | 138.054 | 137.984 | 137.914 | 137.844 | 137.774 | 137.704 | 137.634 | 137.564 | 137.494 | 137.424 | 137.354 | 137.284 | 137.214 | 137.144 | 137.074 | 137.004 | 136.934 | 136.864
11.85 | 0 | 44.43 | 77.2073 | 78.493 | 95.5733 | 112.6537 | 127.5613 | 136.545 | 140.2963 | 140.2963 | 138.2213 | 0 | 4.443 | 8.886 | 13.329 | 17.772 | 22.215 | 26.658 | 31.101 | 35.544 | 39.987 | 44.43 | 50.9855 | 57.5409 | 64.0964 | 70.6519 | 77.2073 | 77.4645 | 77.7216 | 77.9787 | 78.2359 | 78.493 | 80.201 | 81.9091 | 83.6171 | 85.3251 | 87.0332 | 88.7412 | 90.4492 | 92.1573 | 93.8653 | 95.5733 | 96.712 | 97.8507 | 98.9894 | 100.1281 | 101.2668 | 102.4055 | 103.5442 | 104.6828 | 105.8215 | 106.9602 | 108.0989 | 109.2376 | 110.3763 | 111.515 | 112.6537 | 113.6475 | 114.6414 | 115.6352 | 116.629 | 117.6229 | 118.6167 | 119.6106 | 120.6044 | 121.5983 | 122.5921 | 123.586 | 124.5798 | 125.5736 | 126.5675 | 127.5613 | 127.8608 | 128.1602 | 128.4597 | 128.7592 | 129.0586 | 129.3581 | 129.6575 | 129.957 | 130.2564 | 130.5559 | 130.8553 | 131.1548 | 131.4543 | 131.7537 | 132.0532 | 132.3526 | 132.6521 | 132.9515 | 133.251 | 133.5504 | 133.8499 | 134.1494 | 134.4488 | 134.7483 | 135.0477 | 135.3472 | 135.6466 | 135.9461 | 136.2455 | 136.545 | 136.67 | 136.7951 | 136.9201 | 137.0452 | 137.1702 | 137.2953 | 137.4203 | 137.5454 | 137.6704 | 137.7954 | 137.9205 | 138.0455 | 138.1706 | 138.2956 | 138.4207 | 138.5457 | 138.6708 | 138.7958 | 138.9208 | 139.0459 | 139.1709 | 139.296 | 139.421 | 139.5461 | 139.6711 | 139.7962 | 139.9212 | 140.0462 | 140.1713 | 140.2963 | 140.2963 | 140.2963 | 140.2963 | 140.2963 | 140.2963 | 140.2963 | 140.2963 | 140.2963 | 140.2963 | 140.2963 | 140.2963 | 140.2963 | 140.2963 | 140.2963 | 140.2963 | 140.2963 | 140.2963 | 140.2963 | 140.2963 | 140.2963 | 140.2963 | 140.2963 | 140.2963 | 140.2963 | 140.2963 | 140.2963 | 140.2963 | 140.2963 | 140.2963 | 140.2963 | 140.2272 | 140.158 | 140.0888 | 140.0197 | 139.9505 | 139.8813 | 139.8122 | 139.743 | 139.6738 | 139.6047 | 139.5355 | 139.4663 | 139.3972 | 139.328 | 139.2588 | 139.1897 | 139.1205 | 139.0513 | 138.9822 | 138.913 | 138.8438 | 138.7747 | 138.7055 | 138.6363 | 138.5672 | 138.498 | 138.4288 | 138.3597 | 138.2905 | 138.2213
11.9 | 0 | 44.82 | 77.9427 | 79.182 | 96.4267 | 113.6713 | 128.7387 | 137.83 | 141.6287 | 141.6287 | 139.5787 | 0 | 4.482 | 8.964 | 13.446 | 17.928 | 22.41 | 26.892 | 31.374 | 35.856 | 40.338 | 44.82 | 51.4445 | 58.0691 | 64.6936 | 71.3181 | 77.9427 | 78.1905 | 78.4384 | 78.6863 | 78.9341 | 79.182 | 80.9065 | 82.6309 | 84.3554 | 86.0799 | 87.8043 | 89.5288 | 91.2533 | 92.9777 | 94.7022 | 96.4267 | 97.5763 | 98.726 | 99.8756 | 101.0252 | 102.1749 | 103.3245 | 104.4742 | 105.6238 | 106.7735 | 107.9231 | 109.0728 | 110.2224 | 111.372 | 112.5217 | 113.6713 | 114.6758 | 115.6803 | 116.6848 | 117.6893 | 118.6938 | 119.6983 | 120.7028 | 121.7072 | 122.7117 | 123.7162 | 124.7207 | 125.7252 | 126.7297 | 127.7342 | 128.7387 | 129.0417 | 129.3448 | 129.6478 | 129.9508 | 130.2539 | 130.5569 | 130.86 | 131.163 | 131.4661 | 131.7691 | 132.0722 | 132.3752 | 132.6782 | 132.9813 | 133.2843 | 133.5874 | 133.8904 | 134.1935 | 134.4965 | 134.7996 | 135.1026 | 135.4056 | 135.7087 | 136.0117 | 136.3148 | 136.6178 | 136.9209 | 137.2239 | 137.527 | 137.83 | 137.9566 | 138.0832 | 138.2099 | 138.3365 | 138.4631 | 138.5897 | 138.7164 | 138.843 | 138.9696 | 139.0962 | 139.2228 | 139.3495 | 139.4761 | 139.6027 | 139.7293 | 139.856 | 139.9826 | 140.1092 | 140.2358 | 140.3624 | 140.4891 | 140.6157 | 140.7423 | 140.8689 | 140.9956 | 141.1222 | 141.2488 | 141.3754 | 141.502 | 141.6287 | 141.6287 | 141.6287 | 141.6287 | 141.6287 | 141.6287 | 141.6287 | 141.6287 | 141.6287 | 141.6287 | 141.6287 | 141.6287 | 141.6287 | 141.6287 | 141.6287 | 141.6287 | 141.6287 | 141.6287 | 141.6287 | 141.6287 | 141.6287 | 141.6287 | 141.6287 | 141.6287 | 141.6287 | 141.6287 | 141.6287 | 141.6287 | 141.6287 | 141.6287 | 141.6287 | 141.5603 | 141.492 | 141.4237 | 141.3553 | 141.287 | 141.2187 | 141.1503 | 141.082 | 141.0137 | 140.9453 | 140.877 | 140.8087 | 140.7403 | 140.672 | 140.6037 | 140.5353 | 140.467 | 140.3987 | 140.3303 | 140.262 | 140.1937 | 140.1253 | 140.057 | 139.9887 | 139.9203 | 139.852 | 139.7837 | 139.7153 | 139.647 | 139.5787
11.95 | 0 | 45.21 | 78.678 | 79.871 | 97.28 | 114.689 | 129.916 | 139.115 | 142.961 | 142.961 | 140.936 | 3.5527e-15 | 4.521 | 9.042 | 13.563 | 18.084 | 22.605 | 27.126 | 31.647 | 36.168 | 40.689 | 45.21 | 51.9036 | 58.5972 | 65.2908 | 71.9844 | 78.678 | 78.9166 | 79.1552 | 79.3938 | 79.6324 | 79.871 | 81.6119 | 83.3528 | 85.0937 | 86.8346 | 88.5755 | 90.3164 | 92.0573 | 93.7982 | 95.5391 | 97.28 | 98.4406 | 99.6012 | 100.7618 | 101.9224 | 103.083 | 104.2436 | 105.4042 | 106.5648 | 107.7254 | 108.886 | 110.0466 | 111.2072 | 112.3678 | 113.5284 | 114.689 | 115.7041 | 116.7193 | 117.7344 | 118.7495 | 119.7647 | 120.7798 | 121.7949 | 122.8101 | 123.8252 | 124.8403 | 125.8555 | 126.8706 | 127.8857 | 128.9009 | 129.916 | 130.2226 | 130.5293 | 130.8359 | 131.1425 | 131.4492 | 131.7558 | 132.0624 | 132.3691 | 132.6757 | 132.9823 | 133.289 | 133.5956 | 133.9022 | 134.2089 | 134.5155 | 134.8221 | 135.1288 | 135.4354 | 135.742 | 136.0487 | 136.3553 | 136.6619 | 136.9686 | 137.2752 | 137.5818 | 137.8885 | 138.1951 | 138.5017 | 138.8084 | 139.115 | 139.2432 | 139.3714 | 139.4996 | 139.6278 | 139.756 | 139.8842 | 140.0124 | 140.1406 | 140.2688 | 140.397 | 140.5252 | 140.6534 | 140.7816 | 140.9098 | 141.038 | 141.1662 | 141.2944 | 141.4226 | 141.5508 | 141.679 | 141.8072 | 141.9354 | 142.0636 | 142.1918 | 142.32 | 142.4482 | 142.5764 | 142.7046 | 142.8328 | 142.961 | 142.961 | 142.961 | 142.961 | 142.961 | 142.961 | 142.961 | 142.961 | 142.961 | 142.961 | 142.961 | 142.961 | 142.961 | 142.961 | 142.961 | 142.961 | 142.961 | 142.961 | 142.961 | 142.961 | 142.961 | 142.961 | 142.961 | 142.961 | 142.961 | 142.961 | 142.961 | 142.961 | 142.961 | 142.961 | 142.961 | 142.8935 | 142.826 | 142.7585 | 142.691 | 142.6235 | 142.556 | 142.4885 | 142.421 | 142.3535 | 142.286 | 142.2185 | 142.151 | 142.0835 | 142.016 | 141.9485 | 141.881 | 141.8135 | 141.746 | 141.6785 | 141.611 | 141.5435 | 141.476 | 141.4085 | 141.341 | 141.2735 | 141.206 | 141.1385 | 141.071 | 141.0035 | 140.936
12 | 0 | 45.6 | 79.4133 | 80.56 | 98.1333 | 115.7067 | 131.0933 | 140.4 | 144.2933 | 144.2933 | 142.2933 | 3.5527e-15 | 4.56 | 9.12 | 13.68 | 18.24 | 22.8 | 27.36 | 31.92 | 36.48 | 41.04 | 45.6 | 52.3627 | 59.1253 | 65.888 | 72.6507 | 79.4133 | 79.6427 | 79.872 | 80.1013 | 80.3307 | 80.56 | 82.3173 | 84.0747 | 85.832 | 87.5893 | 89.3467 | 91.104 | 92.8613 | 94.6187 | 96.376 | 98.1333 | 99.3049 | 100.4764 | 101.648 | 102.8196 | 103.9911 | 105.1627 | 106.3342 | 107.5058 | 108.6773 | 109.8489 | 111.0204 | 112.192 | 113.3636 | 114.5351 | 115.7067 | 116.7324 | 117.7582 | 118.784 | 119.8098 | 120.8356 | 121.8613 | 122.8871 | 123.9129 | 124.9387 | 125.9644 | 126.9902 | 128.016 | 129.0418 | 130.0676 | 131.0933 | 131.4036 | 131.7138 | 132.024 | 132.3342 | 132.6444 | 132.9547 | 133.2649 | 133.5751 | 133.8853 | 134.1956 | 134.5058 | 134.816 | 135.1262 | 135.4364 | 135.7467 | 136.0569 | 136.3671 | 136.6773 | 136.9876 | 137.2978 | 137.608 | 137.9182 | 138.2284 | 138.5387 | 138.8489 | 139.1591 | 139.4693 | 139.7796 | 140.0898 | 140.4 | 140.5298 | 140.6596 | 140.7893 | 140.9191 | 141.0489 | 141.1787 | 141.3084 | 141.4382 | 141.568 | 141.6978 | 141.8276 | 141.9573 | 142.0871 | 142.2169 | 142.3467 | 142.4764 | 142.6062 | 142.736 | 142.8658 | 142.9956 | 143.1253 | 143.2551 | 143.3849 | 143.5147 | 143.6444 | 143.7742 | 143.904 | 144.0338 | 144.1636 | 144.2933 | 144.2933 | 144.2933 | 144.2933 | 144.2933 | 144.2933 | 144.2933 | 144.2933 | 144.2933 | 144.2933 | 144.2933 | 144.2933 | 144.2933 | 144.2933 | 144.2933 | 144.2933 | 144.2933 | 144.2933 | 144.2933 | 144.2933 | 144.2933 | 144.2933 | 144.2933 | 144.2933 | 144.2933 | 144.2933 | 144.2933 | 144.2933 | 144.2933 | 144.2933 | 144.2933 | 144.2267 | 144.16 | 144.0933 | 144.0267 | 143.96 | 143.8933 | 143.8267 | 143.76 | 143.6933 | 143.6267 | 143.56 | 143.4933 | 143.4267 | 143.36 | 143.2933 | 143.2267 | 143.16 | 143.0933 | 143.0267 | 142.96 | 142.8933 | 142.8267 | 142.76 | 142.6933 | 142.6267 | 142.56 | 142.4933 | 142.4267 | 142.36 | 142.2933
12.05 | 0 | 45.99 | 80.1487 | 81.249 | 98.9867 | 116.7243 | 132.2707 | 141.685 | 145.6257 | 145.6257 | 143.6507 | 0 | 4.599 | 9.198 | 13.797 | 18.396 | 22.995 | 27.594 | 32.193 | 36.792 | 41.391 | 45.99 | 52.8217 | 59.6535 | 66.4852 | 73.3169 | 80.1487 | 80.3687 | 80.5888 | 80.8089 | 81.0289 | 81.249 | 83.0228 | 84.7965 | 86.5703 | 88.3441 | 90.1178 | 91.8916 | 93.6654 | 95.4391 | 97.2129 | 98.9867 | 100.1692 | 101.3517 | 102.5342 | 103.7167 | 104.8992 | 106.0817 | 107.2642 | 108.4468 | 109.6293 | 110.8118 | 111.9943 | 113.1768 | 114.3593 | 115.5418 | 116.7243 | 117.7608 | 118.7972 | 119.8336 | 120.87 | 121.9064 | 122.9429 | 123.9793 | 125.0157 | 126.0521 | 127.0886 | 128.125 | 129.1614 | 130.1978 | 131.2342 | 132.2707 | 132.5845 | 132.8983 | 133.2121 | 133.5259 | 133.8397 | 134.1535 | 134.4673 | 134.7812 | 135.095 | 135.4088 | 135.7226 | 136.0364 | 136.3502 | 136.664 | 136.9778 | 137.2916 | 137.6055 | 137.9193 | 138.2331 | 138.5469 | 138.8607 | 139.1745 | 139.4883 | 139.8021 | 140.1159 | 140.4298 | 140.7436 | 141.0574 | 141.3712 | 141.685 | 141.8164 | 141.9477 | 142.0791 | 142.2104 | 142.3418 | 142.4731 | 142.6045 | 142.7358 | 142.8672 | 142.9986 | 143.1299 | 143.2613 | 143.3926 | 143.524 | 143.6553 | 143.7867 | 143.918 | 144.0494 | 144.1808 | 144.3121 | 144.4435 | 144.5748 | 144.7062 | 144.8375 | 144.9689 | 145.1002 | 145.2316 | 145.363 | 145.4943 | 145.6257 | 145.6257 | 145.6257 | 145.6257 | 145.6257 | 145.6257 | 145.6257 | 145.6257 | 145.6257 | 145.6257 | 145.6257 | 145.6257 | 145.6257 | 145.6257 | 145.6257 | 145.6257 | 145.6257 | 145.6257 | 145.6257 | 145.6257 | 145.6257 | 145.6257 | 145.6257 | 145.6257 | 145.6257 | 145.6257 | 145.6257 | 145.6257 | 145.6257 | 145.6257 | 145.6257 | 145.5598 | 145.494 | 145.4282 | 145.3623 | 145.2965 | 145.2307 | 145.1648 | 145.099 | 145.0332 | 144.9673 | 144.9015 | 144.8357 | 144.7698 | 144.704 | 144.6382 | 144.5723 | 144.5065 | 144.4407 | 144.3748 | 144.309 | 144.2432 | 144.1773 | 144.1115 | 144.0457 | 143.9798 | 143.914 | 143.8482 | 143.7823 | 143.7165 | 143.6507
12.1 | 0 | 46.38 | 80.884 | 81.938 | 99.84 | 117.742 | 133.448 | 142.97 | 146.958 | 146.958 | 145.008 | 0 | 4.638 | 9.276 | 13.914 | 18.552 | 23.19 | 27.828 | 32.466 | 37.104 | 41.742 | 46.38 | 53.2808 | 60.1816 | 67.0824 | 73.9832 | 80.884 | 81.0948 | 81.3056 | 81.5164 | 81.7272 | 81.938 | 83.7282 | 85.5184 | 87.3086 | 89.0988 | 90.889 | 92.6792 | 94.4694 | 96.2596 | 98.0498 | 99.84 | 101.0335 | 102.2269 | 103.4204 | 104.6139 | 105.8073 | 107.0008 | 108.1943 | 109.3877 | 110.5812 | 111.7747 | 112.9681 | 114.1616 | 115.3551 | 116.5485 | 117.742 | 118.7891 | 119.8361 | 120.8832 | 121.9303 | 122.9773 | 124.0244 | 125.0715 | 126.1185 | 127.1656 | 128.2127 | 129.2597 | 130.3068 | 131.3539 | 132.4009 | 133.448 | 133.7654 | 134.0828 | 134.4002 | 134.7176 | 135.035 | 135.3524 | 135.6698 | 135.9872 | 136.3046 | 136.622 | 136.9394 | 137.2568 | 137.5742 | 137.8916 | 138.209 | 138.5264 | 138.8438 | 139.1612 | 139.4786 | 139.796 | 140.1134 | 140.4308 | 140.7482 | 141.0656 | 141.383 | 141.7004 | 142.0178 | 142.3352 | 142.6526 | 142.97 | 143.1029 | 143.2359 | 143.3688 | 143.5017 | 143.6347 | 143.7676 | 143.9005 | 144.0335 | 144.1664 | 144.2993 | 144.4323 | 144.5652 | 144.6981 | 144.8311 | 144.964 | 145.0969 | 145.2299 | 145.3628 | 145.4957 | 145.6287 | 145.7616 | 145.8945 | 146.0275 | 146.1604 | 146.2933 | 146.4263 | 146.5592 | 146.6921 | 146.8251 | 146.958 | 146.958 | 146.958 | 146.958 | 146.958 | 146.958 | 146.958 | 146.958 | 146.958 | 146.958 | 146.958 | 146.958 | 146.958 | 146.958 | 146.958 | 146.958 | 146.958 | 146.958 | 146.958 | 146.958 | 146.958 | 146.958 | 146.958 | 146.958 | 146.958 | 146.958 | 146.958 | 146.958 | 146.958 | 146.958 | 146.958 | 146.893 | 146.828 | 146.763 | 146.698 | 146.633 | 146.568 | 146.503 | 146.438 | 146.373 | 146.308 | 146.243 | 146.178 | 146.113 | 146.048 | 145.983 | 145.918 | 145.853 | 145.788 | 145.723 | 145.658 | 145.593 | 145.528 | 145.463 | 145.398 | 145.333 | 145.268 | 145.203 | 145.138 | 145.073 | 145.008
12.15 | 0 | 46.77 | 81.6193 | 82.627 | 100.6933 | 118.7597 | 134.6253 | 144.255 | 148.2903 | 148.2903 | 146.3653 | 0 | 4.677 | 9.354 | 14.031 | 18.708 | 23.385 | 28.062 | 32.739 | 37.416 | 42.093 | 46.77 | 53.7399 | 60.7097 | 67.6796 | 74.6495 | 81.6193 | 81.8209 | 82.0224 | 82.2239 | 82.4255 | 82.627 | 84.4336 | 86.2403 | 88.0469 | 89.8535 | 91.6602 | 93.4668 | 95.2734 | 97.0801 | 98.8867 | 100.6933 | 101.8978 | 103.1022 | 104.3066 | 105.511 | 106.7154 | 107.9199 | 109.1243 | 110.3287 | 111.5331 | 112.7376 | 113.942 | 115.1464 | 116.3508 | 117.5552 | 118.7597 | 119.8174 | 120.8751 | 121.9328 | 122.9905 | 124.0482 | 125.1059 | 126.1636 | 127.2214 | 128.2791 | 129.3368 | 130.3945 | 131.4522 | 132.5099 | 133.5676 | 134.6253 | 134.9463 | 135.2673 | 135.5883 | 135.9093 | 136.2303 | 136.5513 | 136.8723 | 137.1932 | 137.5142 | 137.8352 | 138.1562 | 138.4772 | 138.7982 | 139.1192 | 139.4402 | 139.7612 | 140.0821 | 140.4031 | 140.7241 | 141.0451 | 141.3661 | 141.6871 | 142.0081 | 142.3291 | 142.6501 | 142.971 | 143.292 | 143.613 | 143.934 | 144.255 | 144.3895 | 144.524 | 144.6585 | 144.793 | 144.9276 | 145.0621 | 145.1966 | 145.3311 | 145.4656 | 145.6001 | 145.7346 | 145.8691 | 146.0036 | 146.1382 | 146.2727 | 146.4072 | 146.5417 | 146.6762 | 146.8107 | 146.9452 | 147.0797 | 147.2142 | 147.3488 | 147.4833 | 147.6178 | 147.7523 | 147.8868 | 148.0213 | 148.1558 | 148.2903 | 148.2903 | 148.2903 | 148.2903 | 148.2903 | 148.2903 | 148.2903 | 148.2903 | 148.2903 | 148.2903 | 148.2903 | 148.2903 | 148.2903 | 148.2903 | 148.2903 | 148.2903 | 148.2903 | 148.2903 | 148.2903 | 148.2903 | 148.2903 | 148.2903 | 148.2903 | 148.2903 | 148.2903 | 148.2903 | 148.2903 | 148.2903 | 148.2903 | 148.2903 | 148.2903 | 148.2262 | 148.162 | 148.0978 | 148.0337 | 147.9695 | 147.9053 | 147.8412 | 147.777 | 147.7128 | 147.6487 | 147.5845 | 147.5203 | 147.4562 | 147.392 | 147.3278 | 147.2637 | 147.1995 | 147.1353 | 147.0712 | 147.007 | 146.9428 | 146.8787 | 146.8145 | 146.7503 | 146.6862 | 146.622 | 146.5578 | 146.4937 | 146.4295 | 146.3653
12.2 | 0 | 47.16 | 82.3547 | 83.316 | 101.5467 | 119.7773 | 135.8027 | 145.54 | 149.6227 | 149.6227 | 147.7227 | -3.5527e-15 | 4.716 | 9.432 | 14.148 | 18.864 | 23.58 | 28.296 | 33.012 | 37.728 | 42.444 | 47.16 | 54.1989 | 61.2379 | 68.2768 | 75.3157 | 82.3547 | 82.5469 | 82.7392 | 82.9315 | 83.1237 | 83.316 | 85.1391 | 86.9621 | 88.7852 | 90.6083 | 92.4313 | 94.2544 | 96.0775 | 97.9005 | 99.7236 | 101.5467 | 102.762 | 103.9774 | 105.1928 | 106.4082 | 107.6236 | 108.8389 | 110.0543 | 111.2697 | 112.4851 | 113.7004 | 114.9158 | 116.1312 | 117.3466 | 118.562 | 119.7773 | 120.8457 | 121.914 | 122.9824 | 124.0508 | 125.1191 | 126.1875 | 127.2558 | 128.3242 | 129.3925 | 130.4609 | 131.5292 | 132.5976 | 133.666 | 134.7343 | 135.8027 | 136.1272 | 136.4518 | 136.7764 | 137.101 | 137.4256 | 137.7501 | 138.0747 | 138.3993 | 138.7239 | 139.0484 | 139.373 | 139.6976 | 140.0222 | 140.3468 | 140.6713 | 140.9959 | 141.3205 | 141.6451 | 141.9696 | 142.2942 | 142.6188 | 142.9434 | 143.268 | 143.5925 | 143.9171 | 144.2417 | 144.5663 | 144.8908 | 145.2154 | 145.54 | 145.6761 | 145.8122 | 145.9483 | 146.0844 | 146.2204 | 146.3565 | 146.4926 | 146.6287 | 146.7648 | 146.9009 | 147.037 | 147.1731 | 147.3092 | 147.4452 | 147.5813 | 147.7174 | 147.8535 | 147.9896 | 148.1257 | 148.2618 | 148.3979 | 148.534 | 148.67 | 148.8061 | 148.9422 | 149.0783 | 149.2144 | 149.3505 | 149.4866 | 149.6227 | 149.6227 | 149.6227 | 149.6227 | 149.6227 | 149.6227 | 149.6227 | 149.6227 | 149.6227 | 149.6227 | 149.6227 | 149.6227 | 149.6227 | 149.6227 | 149.6227 | 149.6227 | 149.6227 | 149.6227 | 149.6227 | 149.6227 | 149.6227 | 149.6227 | 149.6227 | 149.6227 | 149.6227 | 149.6227 | 149.6227 | 149.6227 | 149.6227 | 149.6227 | 149.6227 | 149.5593 | 149.496 | 149.4327 | 149.3693 | 149.306 | 149.2427 | 149.1793 | 149.116 | 149.0527 | 148.9893 | 148.926 | 148.8627 | 148.7993 | 148.736 | 148.6727 | 148.6093 | 148.546 | 148.4827 | 148.4193 | 148.356 | 148.2927 | 148.2293 | 148.166 | 148.1027 | 148.0393 | 147.976 | 147.9127 | 147.8493 | 147.786 | 147.7227
12.25 | 0 | 47.55 | 83.09 | 84.005 | 102.4 | 120.795 | 136.98 | 146.825 | 150.955 | 150.955 | 149.08 | 0 | 4.755 | 9.51 | 14.265 | 19.02 | 23.775 | 28.53 | 33.285 | 38.04 | 42.795 | 47.55 | 54.658 | 61.766 | 68.874 | 75.982 | 83.09 | 83.273 | 83.456 | 83.639 | 83.822 | 84.005 | 85.8445 | 87.684 | 89.5235 | 91.363 | 93.2025 | 95.042 | 96.8815 | 98.721 | 100.5605 | 102.4 | 103.6263 | 104.8527 | 106.079 | 107.3053 | 108.5317 | 109.758 | 110.9843 | 112.2107 | 113.437 | 114.6633 | 115.8897 | 117.116 | 118.3423 | 119.5687 | 120.795 | 121.874 | 122.953 | 124.032 | 125.111 | 126.19 | 127.269 | 128.348 | 129.427 | 130.506 | 131.585 | 132.664 | 133.743 | 134.822 | 135.901 | 136.98 | 137.3082 | 137.6363 | 137.9645 | 138.2927 | 138.6208 | 138.949 | 139.2772 | 139.6053 | 139.9335 | 140.2617 | 140.5898 | 140.918 | 141.2462 | 141.5743 | 141.9025 | 142.2307 | 142.5588 | 142.887 | 143.2152 | 143.5433 | 143.8715 | 144.1997 | 144.5278 | 144.856 | 145.1842 | 145.5123 | 145.8405 | 146.1687 | 146.4968 | 146.825 | 146.9627 | 147.1003 | 147.238 | 147.3757 | 147.5133 | 147.651 | 147.7887 | 147.9263 | 148.064 | 148.2017 | 148.3393 | 148.477 | 148.6147 | 148.7523 | 148.89 | 149.0277 | 149.1653 | 149.303 | 149.4407 | 149.5783 | 149.716 | 149.8537 | 149.9913 | 150.129 | 150.2667 | 150.4043 | 150.542 | 150.6797 | 150.8173 | 150.955 | 150.955 | 150.955 | 150.955 | 150.955 | 150.955 | 150.955 | 150.955 | 150.955 | 150.955 | 150.955 | 150.955 | 150.955 | 150.955 | 150.955 | 150.955 | 150.955 | 150.955 | 150.955 | 150.955 | 150.955 | 150.955 | 150.955 | 150.955 | 150.955 | 150.955 | 150.955 | 150.955 | 150.955 | 150.955 | 150.955 | 150.8925 | 150.83 | 150.7675 | 150.705 | 150.6425 | 150.58 | 150.5175 | 150.455 | 150.3925 | 150.33 | 150.2675 | 150.205 | 150.1425 | 150.08 | 150.0175 | 149.955 | 149.8925 | 149.83 | 149.7675 | 149.705 | 149.6425 | 149.58 | 149.5175 | 149.455 | 149.3925 | 149.33 | 149.2675 | 149.205 | 149.1425 | 149.08
12.3 | 0 | 47.94 | 83.8253 | 84.694 | 103.2533 | 121.8127 | 138.1573 | 148.11 | 152.2873 | 152.2873 | 150.4373 | 0 | 4.794 | 9.588 | 14.382 | 19.176 | 23.97 | 28.764 | 33.558 | 38.352 | 43.146 | 47.94 | 55.1171 | 62.2941 | 69.4712 | 76.6483 | 83.8253 | 83.9991 | 84.1728 | 84.3465 | 84.5203 | 84.694 | 86.5499 | 88.4059 | 90.2618 | 92.1177 | 93.9737 | 95.8296 | 97.6855 | 99.5415 | 101.3974 | 103.2533 | 104.4906 | 105.7279 | 106.9652 | 108.2025 | 109.4398 | 110.6771 | 111.9144 | 113.1516 | 114.3889 | 115.6262 | 116.8635 | 118.1008 | 119.3381 | 120.5754 | 121.8127 | 122.9023 | 123.992 | 125.0816 | 126.1712 | 127.2609 | 128.3505 | 129.4402 | 130.5298 | 131.6195 | 132.7091 | 133.7988 | 134.8884 | 135.978 | 137.0677 | 138.1573 | 138.4891 | 138.8208 | 139.1526 | 139.4844 | 139.8161 | 140.1479 | 140.4796 | 140.8114 | 141.1431 | 141.4749 | 141.8066 | 142.1384 | 142.4702 | 142.8019 | 143.1337 | 143.4654 | 143.7972 | 144.1289 | 144.4607 | 144.7924 | 145.1242 | 145.456 | 145.7877 | 146.1195 | 146.4512 | 146.783 | 147.1147 | 147.4465 | 147.7782 | 148.11 | 148.2492 | 148.3885 | 148.5277 | 148.667 | 148.8062 | 148.9455 | 149.0847 | 149.224 | 149.3632 | 149.5024 | 149.6417 | 149.7809 | 149.9202 | 150.0594 | 150.1987 | 150.3379 | 150.4772 | 150.6164 | 150.7556 | 150.8949 | 151.0341 | 151.1734 | 151.3126 | 151.4519 | 151.5911 | 151.7304 | 151.8696 | 152.0088 | 152.1481 | 152.2873 | 152.2873 | 152.2873 | 152.2873 | 152.2873 | 152.2873 | 152.2873 | 152.2873 | 152.2873 | 152.2873 | 152.2873 | 152.2873 | 152.2873 | 152.2873 | 152.2873 | 152.2873 | 152.2873 | 152.2873 | 152.2873 | 152.2873 | 152.2873 | 152.2873 | 152.2873 | 152.2873 | 152.2873 | 152.2873 | 152.2873 | 152.2873 | 152.2873 | 152.2873 | 152.2873 | 152.2257 | 152.164 | 152.1023 | 152.0407 | 151.979 | 151.9173 | 151.8557 | 151.794 | 151.7323 | 151.6707 | 151.609 | 151.5473 | 151.4857 | 151.424 | 151.3623 | 151.3007 | 151.239 | 151.1773 | 151.1157 | 151.054 | 150.9923 | 150.9307 | 150.869 | 150.8073 | 150.7457 | 150.684 | 150.6223 | 150.5607 | 150.499 | 150.4373
12.35 | 0 | 48.33 | 84.5607 | 85.383 | 104.1067 | 122.8303 | 139.3347 | 149.395 | 153.6197 | 153.6197 | 151.7947 | 0 | 4.833 | 9.666 | 14.499 | 19.332 | 24.165 | 28.998 | 33.831 | 38.664 | 43.497 | 48.33 | 55.5761 | 62.8223 | 70.0684 | 77.3145 | 84.5607 | 84.7251 | 84.8896 | 85.0541 | 85.2185 | 85.383 | 87.2554 | 89.1277 | 91.0001 | 92.8725 | 94.7448 | 96.6172 | 98.4896 | 100.3619 | 102.2343 | 104.1067 | 105.3549 | 106.6032 | 107.8514 | 109.0996 | 110.3479 | 111.5961 | 112.8444 | 114.0926 | 115.3409 | 116.5891 | 117.8374 | 119.0856 | 120.3338 | 121.5821 | 122.8303 | 123.9306 | 125.0309 | 126.1312 | 127.2315 | 128.3318 | 129.4321 | 130.5324 | 131.6326 | 132.7329 | 133.8332 | 134.9335 | 136.0338 | 137.1341 | 138.2344 | 139.3347 | 139.67 | 140.0054 | 140.3407 | 140.676 | 141.0114 | 141.3467 | 141.6821 | 142.0174 | 142.3528 | 142.6881 | 143.0235 | 143.3588 | 143.6941 | 144.0295 | 144.3648 | 144.7002 | 145.0355 | 145.3709 | 145.7062 | 146.0416 | 146.3769 | 146.7122 | 147.0476 | 147.3829 | 147.7183 | 148.0536 | 148.389 | 148.7243 | 149.0597 | 149.395 | 149.5358 | 149.6766 | 149.8175 | 149.9583 | 150.0991 | 150.2399 | 150.3808 | 150.5216 | 150.6624 | 150.8032 | 150.944 | 151.0849 | 151.2257 | 151.3665 | 151.5073 | 151.6482 | 151.789 | 151.9298 | 152.0706 | 152.2114 | 152.3523 | 152.4931 | 152.6339 | 152.7747 | 152.9156 | 153.0564 | 153.1972 | 153.338 | 153.4788 | 153.6197 | 153.6197 | 153.6197 | 153.6197 | 153.6197 | 153.6197 | 153.6197 | 153.6197 | 153.6197 | 153.6197 | 153.6197 | 153.6197 | 153.6197 | 153.6197 | 153.6197 | 153.6197 | 153.6197 | 153.6197 | 153.6197 | 153.6197 | 153.6197 | 153.6197 | 153.6197 | 153.6197 | 153.6197 | 153.6197 | 153.6197 | 153.6197 | 153.6197 | 153.6197 | 153.6197 | 153.5588 | 153.498 | 153.4372 | 153.3763 | 153.3155 | 153.2547 | 153.1938 | 153.133 | 153.0722 | 153.0113 | 152.9505 | 152.8897 | 152.8288 | 152.768 | 152.7072 | 152.6463 | 152.5855 | 152.5247 | 152.4638 | 152.403 | 152.3422 | 152.2813 | 152.2205 | 152.1597 | 152.0988 | 152.038 | 151.9772 | 151.9163 | 151.8555 | 151.7947
12.4 | 0 | 48.72 | 85.296 | 86.072 | 104.96 | 123.848 | 140.512 | 150.68 | 154.952 | 154.952 | 153.152 | 0 | 4.872 | 9.744 | 14.616 | 19.488 | 24.36 | 29.232 | 34.104 | 38.976 | 43.848 | 48.72 | 56.0352 | 63.3504 | 70.6656 | 77.9808 | 85.296 | 85.4512 | 85.6064 | 85.7616 | 85.9168 | 86.072 | 87.9608 | 89.8496 | 91.7384 | 93.6272 | 95.516 | 97.4048 | 99.2936 | 101.1824 | 103.0712 | 104.96 | 106.2192 | 107.4784 | 108.7376 | 109.9968 | 111.256 | 112.5152 | 113.7744 | 115.0336 | 116.2928 | 117.552 | 118.8112 | 120.0704 | 121.3296 | 122.5888 | 123.848 | 124.9589 | 126.0699 | 127.1808 | 128.2917 | 129.4027 | 130.5136 | 131.6245 | 132.7355 | 133.8464 | 134.9573 | 136.0683 | 137.1792 | 138.2901 | 139.4011 | 140.512 | 140.8509 | 141.1899 | 141.5288 | 141.8677 | 142.2067 | 142.5456 | 142.8845 | 143.2235 | 143.5624 | 143.9013 | 144.2403 | 144.5792 | 144.9181 | 145.2571 | 145.596 | 145.9349 | 146.2739 | 146.6128 | 146.9517 | 147.2907 | 147.6296 | 147.9685 | 148.3075 | 148.6464 | 148.9853 | 149.3243 | 149.6632 | 150.0021 | 150.3411 | 150.68 | 150.8224 | 150.9648 | 151.1072 | 151.2496 | 151.392 | 151.5344 | 151.6768 | 151.8192 | 151.9616 | 152.104 | 152.2464 | 152.3888 | 152.5312 | 152.6736 | 152.816 | 152.9584 | 153.1008 | 153.2432 | 153.3856 | 153.528 | 153.6704 | 153.8128 | 153.9552 | 154.0976 | 154.24 | 154.3824 | 154.5248 | 154.6672 | 154.8096 | 154.952 | 154.952 | 154.952 | 154.952 | 154.952 | 154.952 | 154.952 | 154.952 | 154.952 | 154.952 | 154.952 | 154.952 | 154.952 | 154.952 | 154.952 | 154.952 | 154.952 | 154.952 | 154.952 | 154.952 | 154.952 | 154.952 | 154.952 | 154.952 | 154.952 | 154.952 | 154.952 | 154.952 | 154.952 | 154.952 | 154.952 | 154.892 | 154.832 | 154.772 | 154.712 | 154.652 | 154.592 | 154.532 | 154.472 | 154.412 | 154.352 | 154.292 | 154.232 | 154.172 | 154.112 | 154.052 | 153.992 | 153.932 | 153.872 | 153.812 | 153.752 | 153.692 | 153.632 | 153.572 | 153.512 | 153.452 | 153.392 | 153.332 | 153.272 | 153.212 | 153.152
12.45 | 0 | 49.11 | 86.0313 | 86.761 | 105.8133 | 124.8657 | 141.6893 | 151.965 | 156.2843 | 156.2843 | 154.5093 | 3.5527e-15 | 4.911 | 9.822 | 14.733 | 19.644 | 24.555 | 29.466 | 34.377 | 39.288 | 44.199 | 49.11 | 56.4943 | 63.8785 | 71.2628 | 78.6471 | 86.0313 | 86.1773 | 86.3232 | 86.4691 | 86.6151 | 86.761 | 88.6662 | 90.5715 | 92.4767 | 94.3819 | 96.2872 | 98.1924 | 100.0976 | 102.0029 | 103.9081 | 105.8133 | 107.0835 | 108.3536 | 109.6238 | 110.894 | 112.1641 | 113.4343 | 114.7044 | 115.9746 | 117.2447 | 118.5149 | 119.785 | 121.0552 | 122.3254 | 123.5955 | 124.8657 | 125.9872 | 127.1088 | 128.2304 | 129.352 | 130.4736 | 131.5951 | 132.7167 | 133.8383 | 134.9599 | 136.0814 | 137.203 | 138.3246 | 139.4462 | 140.5678 | 141.6893 | 142.0319 | 142.3744 | 142.7169 | 143.0594 | 143.4019 | 143.7445 | 144.087 | 144.4295 | 144.772 | 145.1146 | 145.4571 | 145.7996 | 146.1421 | 146.4846 | 146.8272 | 147.1697 | 147.5122 | 147.8547 | 148.1973 | 148.5398 | 148.8823 | 149.2248 | 149.5673 | 149.9099 | 150.2524 | 150.5949 | 150.9374 | 151.28 | 151.6225 | 151.965 | 152.109 | 152.253 | 152.3969 | 152.5409 | 152.6849 | 152.8289 | 152.9728 | 153.1168 | 153.2608 | 153.4048 | 153.5488 | 153.6927 | 153.8367 | 153.9807 | 154.1247 | 154.2686 | 154.4126 | 154.5566 | 154.7006 | 154.8446 | 154.9885 | 155.1325 | 155.2765 | 155.4205 | 155.5644 | 155.7084 | 155.8524 | 155.9964 | 156.1404 | 156.2843 | 156.2843 | 156.2843 | 156.2843 | 156.2843 | 156.2843 | 156.2843 | 156.2843 | 156.2843 | 156.2843 | 156.2843 | 156.2843 | 156.2843 | 156.2843 | 156.2843 | 156.2843 | 156.2843 | 156.2843 | 156.2843 | 156.2843 | 156.2843 | 156.2843 | 156.2843 | 156.2843 | 156.2843 | 156.2843 | 156.2843 | 156.2843 | 156.2843 | 156.2843 | 156.2843 | 156.2252 | 156.166 | 156.1068 | 156.0477 | 155.9885 | 155.9293 | 155.8702 | 155.811 | 155.7518 | 155.6927 | 155.6335 | 155.5743 | 155.5152 | 155.456 | 155.3968 | 155.3377 | 155.2785 | 155.2193 | 155.1602 | 155.101 | 155.0418 | 154.9827 | 154.9235 | 154.8643 | 154.8052 | 154.746 | 154.6868 | 154.6277 | 154.5685 | 154.5093
12.5 | 0 | 49.5 | 86.7667 | 87.45 | 106.6667 | 125.8833 | 142.8667 | 153.25 | 157.6167 | 157.6167 | 155.8667 | 0 | 4.95 | 9.9 | 14.85 | 19.8 | 24.75 | 29.7 | 34.65 | 39.6 | 44.55 | 49.5 | 56.9533 | 64.4067 | 71.86 | 79.3133 | 86.7667 | 86.9033 | 87.04 | 87.1767 | 87.3133 | 87.45 | 89.3717 | 91.2933 | 93.215 | 95.1367 | 97.0583 | 98.98 | 100.9017 | 102.8233 | 104.745 | 106.6667 | 107.9478 | 109.2289 | 110.51 | 111.7911 | 113.0722 | 114.3533 | 115.6344 | 116.9156 | 118.1967 | 119.4778 | 120.7589 | 122.04 | 123.3211 | 124.6022 | 125.8833 | 127.0156 | 128.1478 | 129.28 | 130.4122 | 131.5444 | 132.6767 | 133.8089 | 134.9411 | 136.0733 | 137.2056 | 138.3378 | 139.47 | 140.6022 | 141.7344 | 142.8667 | 143.2128 | 143.5589 | 143.905 | 144.2511 | 144.5972 | 144.9433 | 145.2894 | 145.6356 | 145.9817 | 146.3278 | 146.6739 | 147.02 | 147.3661 | 147.7122 | 148.0583 | 148.4044 | 148.7506 | 149.0967 | 149.4428 | 149.7889 | 150.135 | 150.4811 | 150.8272 | 151.1733 | 151.5194 | 151.8656 | 152.2117 | 152.5578 | 152.9039 | 153.25 | 153.3956 | 153.5411 | 153.6867 | 153.8322 | 153.9778 | 154.1233 | 154.2689 | 154.4144 | 154.56 | 154.7056 | 154.8511 | 154.9967 | 155.1422 | 155.2878 | 155.4333 | 155.5789 | 155.7244 | 155.87 | 156.0156 | 156.1611 | 156.3067 | 156.4522 | 156.5978 | 156.7433 | 156.8889 | 157.0344 | 157.18 | 157.3256 | 157.4711 | 157.6167 | 157.6167 | 157.6167 | 157.6167 | 157.6167 | 157.6167 | 157.6167 | 157.6167 | 157.6167 | 157.6167 | 157.6167 | 157.6167 | 157.6167 | 157.6167 | 157.6167 | 157.6167 | 157.6167 | 157.6167 | 157.6167 | 157.6167 | 157.6167 | 157.6167 | 157.6167 | 157.6167 | 157.6167 | 157.6167 | 157.6167 | 157.6167 | 157.6167 | 157.6167 | 157.6167 | 157.5583 | 157.5 | 157.4417 | 157.3833 | 157.325 | 157.2667 | 157.2083 | 157.15 | 157.0917 | 157.0333 | 156.975 | 156.9167 | 156.8583 | 156.8 | 156.7417 | 156.6833 | 156.625 | 156.5667 | 156.5083 | 156.45 | 156.3917 | 156.3333 | 156.275 | 156.2167 | 156.1583 | 156.1 | 156.0417 | 155.9833 | 155.925 | 155.8667
12.55 | 0 | 49.89 | 87.502 | 88.139 | 107.52 | 126.901 | 144.044 | 154.535 | 158.949 | 158.949 | 157.224 | 3.5527e-15 | 4.989 | 9.978 | 14.967 | 19.956 | 24.945 | 29.934 | 34.923 | 39.912 | 44.901 | 49.89 | 57.4124 | 64.9348 | 72.4572 | 79.9796 | 87.502 | 87.6294 | 87.7568 | 87.8842 | 88.0116 | 88.139 | 90.0771 | 92.0152 | 93.9533 | 95.8914 | 97.8295 | 99.7676 | 101.7057 | 103.6438 | 105.5819 | 107.52 | 108.8121 | 110.1041 | 111.3962 | 112.6883 | 113.9803 | 115.2724 | 116.5645 | 117.8565 | 119.1486 | 120.4407 | 121.7327 | 123.0248 | 124.3169 | 125.6089 | 126.901 | 128.0439 | 129.1867 | 130.3296 | 131.4725 | 132.6153 | 133.7582 | 134.9011 | 136.0439 | 137.1868 | 138.3297 | 139.4725 | 140.6154 | 141.7583 | 142.9011 | 144.044 | 144.3937 | 144.7434 | 145.0931 | 145.4428 | 145.7925 | 146.1422 | 146.4919 | 146.8416 | 147.1913 | 147.541 | 147.8907 | 148.2404 | 148.5901 | 148.9398 | 149.2895 | 149.6392 | 149.9889 | 150.3386 | 150.6883 | 151.038 | 151.3877 | 151.7374 | 152.0871 | 152.4368 | 152.7865 | 153.1362 | 153.4859 | 153.8356 | 154.1853 | 154.535 | 154.6821 | 154.8293 | 154.9764 | 155.1235 | 155.2707 | 155.4178 | 155.5649 | 155.7121 | 155.8592 | 156.0063 | 156.1535 | 156.3006 | 156.4477 | 156.5949 | 156.742 | 156.8891 | 157.0363 | 157.1834 | 157.3305 | 157.4777 | 157.6248 | 157.7719 | 157.9191 | 158.0662 | 158.2133 | 158.3605 | 158.5076 | 158.6547 | 158.8019 | 158.949 | 158.949 | 158.949 | 158.949 | 158.949 | 158.949 | 158.949 | 158.949 | 158.949 | 158.949 | 158.949 | 158.949 | 158.949 | 158.949 | 158.949 | 158.949 | 158.949 | 158.949 | 158.949 | 158.949 | 158.949 | 158.949 | 158.949 | 158.949 | 158.949 | 158.949 | 158.949 | 158.949 | 158.949 | 158.949 | 158.949 | 158.8915 | 158.834 | 158.7765 | 158.719 | 158.6615 | 158.604 | 158.5465 | 158.489 | 158.4315 | 158.374 | 158.3165 | 158.259 | 158.2015 | 158.144 | 158.0865 | 158.029 | 157.9715 | 157.914 | 157.8565 | 157.799 | 157.7415 | 157.684 | 157.6265 | 157.569 | 157.5115 | 157.454 | 157.3965 | 157.339 | 157.2815 | 157.224
12.6 | 0 | 50.28 | 88.2373 | 88.828 | 108.3733 | 127.9187 | 145.2213 | 155.82 | 160.2813 | 160.2813 | 158.5813 | 0 | 5.028 | 10.056 | 15.084 | 20.112 | 25.14 | 30.168 | 35.196 | 40.224 | 45.252 | 50.28 | 57.8715 | 65.4629 | 73.0544 | 80.6459 | 88.2373 | 88.3555 | 88.4736 | 88.5917 | 88.7099 | 88.828 | 90.7825 | 92.7371 | 94.6916 | 96.6461 | 98.6007 | 100.5552 | 102.5097 | 104.4643 | 106.4188 | 108.3733 | 109.6764 | 110.9794 | 112.2824 | 113.5854 | 114.8884 | 116.1915 | 117.4945 | 118.7975 | 120.1005 | 121.4036 | 122.7066 | 124.0096 | 125.3126 | 126.6156 | 127.9187 | 129.0722 | 130.2257 | 131.3792 | 132.5327 | 133.6862 | 134.8397 | 135.9932 | 137.1468 | 138.3003 | 139.4538 | 140.6073 | 141.7608 | 142.9143 | 144.0678 | 145.2213 | 145.5746 | 145.9279 | 146.2812 | 146.6345 | 146.9878 | 147.3411 | 147.6944 | 148.0476 | 148.4009 | 148.7542 | 149.1075 | 149.4608 | 149.8141 | 150.1674 | 150.5207 | 150.874 | 151.2272 | 151.5805 | 151.9338 | 152.2871 | 152.6404 | 152.9937 | 153.347 | 153.7003 | 154.0536 | 154.4068 | 154.7601 | 155.1134 | 155.4667 | 155.82 | 155.9687 | 156.1174 | 156.2661 | 156.4148 | 156.5636 | 156.7123 | 156.861 | 157.0097 | 157.1584 | 157.3071 | 157.4558 | 157.6045 | 157.7532 | 157.902 | 158.0507 | 158.1994 | 158.3481 | 158.4968 | 158.6455 | 158.7942 | 158.9429 | 159.0916 | 159.2404 | 159.3891 | 159.5378 | 159.6865 | 159.8352 | 159.9839 | 160.1326 | 160.2813 | 160.2813 | 160.2813 | 160.2813 | 160.2813 | 160.2813 | 160.2813 | 160.2813 | 160.2813 | 160.2813 | 160.2813 | 160.2813 | 160.2813 | 160.2813 | 160.2813 | 160.2813 | 160.2813 | 160.2813 | 160.2813 | 160.2813 | 160.2813 | 160.2813 | 160.2813 | 160.2813 | 160.2813 | 160.2813 | 160.2813 | 160.2813 | 160.2813 | 160.2813 | 160.2813 | 160.2247 | 160.168 | 160.1113 | 160.0547 | 159.998 | 159.9413 | 159.8847 | 159.828 | 159.7713 | 159.7147 | 159.658 | 159.6013 | 159.5447 | 159.488 | 159.4313 | 159.3747 | 159.318 | 159.2613 | 159.2047 | 159.148 | 159.0913 | 159.0347 | 158.978 | 158.9213 | 158.8647 | 158.808 | 158.7513 | 158.6947 | 158.638 | 158.5813
12.65 | 0 | 50.67 | 88.9727 | 89.517 | 109.2267 | 128.9363 | 146.3987 | 157.105 | 161.6137 | 161.6137 | 159.9387 | 0 | 5.067 | 10.134 | 15.201 | 20.268 | 25.335 | 30.402 | 35.469 | 40.536 | 45.603 | 50.67 | 58.3305 | 65.9911 | 73.6516 | 81.3121 | 88.9727 | 89.0815 | 89.1904 | 89.2993 | 89.4081 | 89.517 | 91.488 | 93.4589 | 95.4299 | 97.4009 | 99.3718 | 101.3428 | 103.3138 | 105.2847 | 107.2557 | 109.2267 | 110.5406 | 111.8546 | 113.1686 | 114.4826 | 115.7966 | 117.1105 | 118.4245 | 119.7385 | 121.0525 | 122.3664 | 123.6804 | 124.9944 | 126.3084 | 127.6224 | 128.9363 | 130.1005 | 131.2646 | 132.4288 | 133.593 | 134.7571 | 135.9213 | 137.0854 | 138.2496 | 139.4137 | 140.5779 | 141.742 | 142.9062 | 144.0704 | 145.2345 | 146.3987 | 146.7555 | 147.1124 | 147.4693 | 147.8262 | 148.1831 | 148.5399 | 148.8968 | 149.2537 | 149.6106 | 149.9674 | 150.3243 | 150.6812 | 151.0381 | 151.395 | 151.7518 | 152.1087 | 152.4656 | 152.8225 | 153.1793 | 153.5362 | 153.8931 | 154.25 | 154.6069 | 154.9637 | 155.3206 | 155.6775 | 156.0344 | 156.3912 | 156.7481 | 157.105 | 157.2553 | 157.4056 | 157.5559 | 157.7062 | 157.8564 | 158.0067 | 158.157 | 158.3073 | 158.4576 | 158.6079 | 158.7582 | 158.9085 | 159.0588 | 159.209 | 159.3593 | 159.5096 | 159.6599 | 159.8102 | 159.9605 | 160.1108 | 160.2611 | 160.4114 | 160.5616 | 160.7119 | 160.8622 | 161.0125 | 161.1628 | 161.3131 | 161.4634 | 161.6137 | 161.6137 | 161.6137 | 161.6137 | 161.6137 | 161.6137 | 161.6137 | 161.6137 | 161.6137 | 161.6137 | 161.6137 | 161.6137 | 161.6137 | 161.6137 | 161.6137 | 161.6137 | 161.6137 | 161.6137 | 161.6137 | 161.6137 | 161.6137 | 161.6137 | 161.6137 | 161.6137 | 161.6137 | 161.6137 | 161.6137 | 161.6137 | 161.6137 | 161.6137 | 161.6137 | 161.5578 | 161.502 | 161.4462 | 161.3903 | 161.3345 | 161.2787 | 161.2228 | 161.167 | 161.1112 | 161.0553 | 160.9995 | 160.9437 | 160.8878 | 160.832 | 160.7762 | 160.7203 | 160.6645 | 160.6087 | 160.5528 | 160.497 | 160.4412 | 160.3853 | 160.3295 | 160.2737 | 160.2178 | 160.162 | 160.1062 | 160.0503 | 159.9945 | 159.9387
12.7 | 0 | 51.06 | 89.708 | 90.206 | 110.08 | 129.954 | 147.576 | 158.39 | 162.946 | 162.946 | 161.296 | 0 | 5.106 | 10.212 | 15.318 | 20.424 | 25.53 | 30.636 | 35.742 | 40.848 | 45.954 | 51.06 | 58.7896 | 66.5192 | 74.2488 | 81.9784 | 89.708 | 89.8076 | 89.9072 | 90.0068 | 90.1064 | 90.206 | 92.1934 | 94.1808 | 96.1682 | 98.1556 | 100.143 | 102.1304 | 104.1178 | 106.1052 | 108.0926 | 110.08 | 111.4049 | 112.7299 | 114.0548 | 115.3797 | 116.7047 | 118.0296 | 119.3545 | 120.6795 | 122.0044 | 123.3293 | 124.6543 | 125.9792 | 127.3041 | 128.6291 | 129.954 | 131.1288 | 132.3036 | 133.4784 | 134.6532 | 135.828 | 137.0028 | 138.1776 | 139.3524 | 140.5272 | 141.702 | 142.8768 | 144.0516 | 145.2264 | 146.4012 | 147.576 | 147.9365 | 148.2969 | 148.6574 | 149.0179 | 149.3783 | 149.7388 | 150.0993 | 150.4597 | 150.8202 | 151.1807 | 151.5411 | 151.9016 | 152.2621 | 152.6225 | 152.983 | 153.3435 | 153.7039 | 154.0644 | 154.4249 | 154.7853 | 155.1458 | 155.5063 | 155.8667 | 156.2272 | 156.5877 | 156.9481 | 157.3086 | 157.6691 | 158.0295 | 158.39 | 158.5419 | 158.6937 | 158.8456 | 158.9975 | 159.1493 | 159.3012 | 159.4531 | 159.6049 | 159.7568 | 159.9087 | 160.0605 | 160.2124 | 160.3643 | 160.5161 | 160.668 | 160.8199 | 160.9717 | 161.1236 | 161.2755 | 161.4273 | 161.5792 | 161.7311 | 161.8829 | 162.0348 | 162.1867 | 162.3385 | 162.4904 | 162.6423 | 162.7941 | 162.946 | 162.946 | 162.946 | 162.946 | 162.946 | 162.946 | 162.946 | 162.946 | 162.946 | 162.946 | 162.946 | 162.946 | 162.946 | 162.946 | 162.946 | 162.946 | 162.946 | 162.946 | 162.946 | 162.946 | 162.946 | 162.946 | 162.946 | 162.946 | 162.946 | 162.946 | 162.946 | 162.946 | 162.946 | 162.946 | 162.946 | 162.891 | 162.836 | 162.781 | 162.726 | 162.671 | 162.616 | 162.561 | 162.506 | 162.451 | 162.396 | 162.341 | 162.286 | 162.231 | 162.176 | 162.121 | 162.066 | 162.011 | 161.956 | 161.901 | 161.846 | 161.791 | 161.736 | 161.681 | 161.626 | 161.571 | 161.516 | 161.461 | 161.406 | 161.351 | 161.296
12.75 | 0 | 51.45 | 90.4433 | 90.895 | 110.9333 | 130.9717 | 148.7533 | 159.675 | 164.2783 | 164.2783 | 162.6533 | 0 | 5.145 | 10.29 | 15.435 | 20.58 | 25.725 | 30.87 | 36.015 | 41.16 | 46.305 | 51.45 | 59.2487 | 67.0473 | 74.846 | 82.6447 | 90.4433 | 90.5337 | 90.624 | 90.7143 | 90.8047 | 90.895 | 92.8988 | 94.9027 | 96.9065 | 98.9103 | 100.9142 | 102.918 | 104.9218 | 106.9257 | 108.9295 | 110.9333 | 112.2692 | 113.6051 | 114.941 | 116.2769 | 117.6128 | 118.9487 | 120.2846 | 121.6204 | 122.9563 | 124.2922 | 125.6281 | 126.964 | 128.2999 | 129.6358 | 130.9717 | 132.1571 | 133.3426 | 134.528 | 135.7134 | 136.8989 | 138.0843 | 139.2698 | 140.4552 | 141.6407 | 142.8261 | 144.0116 | 145.197 | 146.3824 | 147.5679 | 148.7533 | 149.1174 | 149.4814 | 149.8455 | 150.2096 | 150.5736 | 150.9377 | 151.3017 | 151.6658 | 152.0298 | 152.3939 | 152.7579 | 153.122 | 153.4861 | 153.8501 | 154.2142 | 154.5782 | 154.9423 | 155.3063 | 155.6704 | 156.0344 | 156.3985 | 156.7626 | 157.1266 | 157.4907 | 157.8547 | 158.2188 | 158.5828 | 158.9469 | 159.3109 | 159.675 | 159.8284 | 159.9819 | 160.1353 | 160.2888 | 160.4422 | 160.5957 | 160.7491 | 160.9026 | 161.056 | 161.2094 | 161.3629 | 161.5163 | 161.6698 | 161.8232 | 161.9767 | 162.1301 | 162.2836 | 162.437 | 162.5904 | 162.7439 | 162.8973 | 163.0508 | 163.2042 | 163.3577 | 163.5111 | 163.6646 | 163.818 | 163.9714 | 164.1249 | 164.2783 | 164.2783 | 164.2783 | 164.2783 | 164.2783 | 164.2783 | 164.2783 | 164.2783 | 164.2783 | 164.2783 | 164.2783 | 164.2783 | 164.2783 | 164.2783 | 164.2783 | 164.2783 | 164.2783 | 164.2783 | 164.2783 | 164.2783 | 164.2783 | 164.2783 | 164.2783 | 164.2783 | 164.2783 | 164.2783 | 164.2783 | 164.2783 | 164.2783 | 164.2783 | 164.2783 | 164.2242 | 164.17 | 164.1158 | 164.0617 | 164.0075 | 163.9533 | 163.8992 | 163.845 | 163.7908 | 163.7367 | 163.6825 | 163.6283 | 163.5742 | 163.52 | 163.4658 | 163.4117 | 163.3575 | 163.3033 | 163.2492 | 163.195 | 163.1408 | 163.0867 | 163.0325 | 162.9783 | 162.9242 | 162.87 | 162.8158 | 162.7617 | 162.7075 | 162.6533
12.8 | 0 | 51.84 | 91.1787 | 91.584 | 111.7867 | 131.9893 | 149.9307 | 160.96 | 165.6107 | 165.6107 | 164.0107 | -3.5527e-15 | 5.184 | 10.368 | 15.552 | 20.736 | 25.92 | 31.104 | 36.288 | 41.472 | 46.656 | 51.84 | 59.7077 | 67.5755 | 75.4432 | 83.3109 | 91.1787 | 91.2597 | 91.3408 | 91.4219 | 91.5029 | 91.584 | 93.6043 | 95.6245 | 97.6448 | 99.6651 | 101.6853 | 103.7056 | 105.7259 | 107.7461 | 109.7664 | 111.7867 | 113.1335 | 114.4804 | 115.8272 | 117.174 | 118.5209 | 119.8677 | 121.2146 | 122.5614 | 123.9083 | 125.2551 | 126.602 | 127.9488 | 129.2956 | 130.6425 | 131.9893 | 133.1854 | 134.3815 | 135.5776 | 136.7737 | 137.9698 | 139.1659 | 140.362 | 141.558 | 142.7541 | 143.9502 | 145.1463 | 146.3424 | 147.5385 | 148.7346 | 149.9307 | 150.2983 | 150.666 | 151.0336 | 151.4012 | 151.7689 | 152.1365 | 152.5042 | 152.8718 | 153.2395 | 153.6071 | 153.9748 | 154.3424 | 154.71 | 155.0777 | 155.4453 | 155.813 | 156.1806 | 156.5483 | 156.9159 | 157.2836 | 157.6512 | 158.0188 | 158.3865 | 158.7541 | 159.1218 | 159.4894 | 159.8571 | 160.2247 | 160.5924 | 160.96 | 161.115 | 161.27 | 161.4251 | 161.5801 | 161.7351 | 161.8901 | 162.0452 | 162.2002 | 162.3552 | 162.5102 | 162.6652 | 162.8203 | 162.9753 | 163.1303 | 163.2853 | 163.4404 | 163.5954 | 163.7504 | 163.9054 | 164.0604 | 164.2155 | 164.3705 | 164.5255 | 164.6805 | 164.8356 | 164.9906 | 165.1456 | 165.3006 | 165.4556 | 165.6107 | 165.6107 | 165.6107 | 165.6107 | 165.6107 | 165.6107 | 165.6107 | 165.6107 | 165.6107 | 165.6107 | 165.6107 | 165.6107 | 165.6107 | 165.6107 | 165.6107 | 165.6107 | 165.6107 | 165.6107 | 165.6107 | 165.6107 | 165.6107 | 165.6107 | 165.6107 | 165.6107 | 165.6107 | 165.6107 | 165.6107 | 165.6107 | 165.6107 | 165.6107 | 165.6107 | 165.5573 | 165.504 | 165.4507 | 165.3973 | 165.344 | 165.2907 | 165.2373 | 165.184 | 165.1307 | 165.0773 | 165.024 | 164.9707 | 164.9173 | 164.864 | 164.8107 | 164.7573 | 164.704 | 164.6507 | 164.5973 | 164.544 | 164.4907 | 164.4373 | 164.384 | 164.3307 | 164.2773 | 164.224 | 164.1707 | 164.1173 | 164.064 | 164.0107
12.85 | 0 | 52.23 | 91.914 | 92.273 | 112.64 | 133.007 | 151.108 | 162.245 | 166.943 | 166.943 | 165.368 | 0 | 5.223 | 10.446 | 15.669 | 20.892 | 26.115 | 31.338 | 36.561 | 41.784 | 47.007 | 52.23 | 60.1668 | 68.1036 | 76.0404 | 83.9772 | 91.914 | 91.9858 | 92.0576 | 92.1294 | 92.2012 | 92.273 | 94.3097 | 96.3464 | 98.3831 | 100.4198 | 102.4565 | 104.4932 | 106.5299 | 108.5666 | 110.6033 | 112.64 | 113.9978 | 115.3556 | 116.7134 | 118.0712 | 119.429 | 120.7868 | 122.1446 | 123.5024 | 124.8602 | 126.218 | 127.5758 | 128.9336 | 130.2914 | 131.6492 | 133.007 | 134.2137 | 135.4205 | 136.6272 | 137.8339 | 139.0407 | 140.2474 | 141.4541 | 142.6609 | 143.8676 | 145.0743 | 146.2811 | 147.4878 | 148.6945 | 149.9013 | 151.108 | 151.4792 | 151.8505 | 152.2217 | 152.5929 | 152.9642 | 153.3354 | 153.7066 | 154.0779 | 154.4491 | 154.8203 | 155.1916 | 155.5628 | 155.934 | 156.3053 | 156.6765 | 157.0477 | 157.419 | 157.7902 | 158.1614 | 158.5327 | 158.9039 | 159.2751 | 159.6464 | 160.0176 | 160.3888 | 160.7601 | 161.1313 | 161.5025 | 161.8738 | 162.245 | 162.4016 | 162.5582 | 162.7148 | 162.8714 | 163.028 | 163.1846 | 163.3412 | 163.4978 | 163.6544 | 163.811 | 163.9676 | 164.1242 | 164.2808 | 164.4374 | 164.594 | 164.7506 | 164.9072 | 165.0638 | 165.2204 | 165.377 | 165.5336 | 165.6902 | 165.8468 | 166.0034 | 166.16 | 166.3166 | 166.4732 | 166.6298 | 166.7864 | 166.943 | 166.943 | 166.943 | 166.943 | 166.943 | 166.943 | 166.943 | 166.943 | 166.943 | 166.943 | 166.943 | 166.943 | 166.943 | 166.943 | 166.943 | 166.943 | 166.943 | 166.943 | 166.943 | 166.943 | 166.943 | 166.943 | 166.943 | 166.943 | 166.943 | 166.943 | 166.943 | 166.943 | 166.943 | 166.943 | 166.943 | 166.8905 | 166.838 | 166.7855 | 166.733 | 166.6805 | 166.628 | 166.5755 | 166.523 | 166.4705 | 166.418 | 166.3655 | 166.313 | 166.2605 | 166.208 | 166.1555 | 166.103 | 166.0505 | 165.998 | 165.9455 | 165.893 | 165.8405 | 165.788 | 165.7355 | 165.683 | 165.6305 | 165.578 | 165.5255 | 165.473 | 165.4205 | 165.368
12.9 | 0 | 52.62 | 92.6493 | 92.962 | 113.4933 | 134.0247 | 152.2853 | 163.53 | 168.2753 | 168.2753 | 166.7253 | 0 | 5.262 | 10.524 | 15.786 | 21.048 | 26.31 | 31.572 | 36.834 | 42.096 | 47.358 | 52.62 | 60.6259 | 68.6317 | 76.6376 | 84.6435 | 92.6493 | 92.7119 | 92.7744 | 92.8369 | 92.8995 | 92.962 | 95.0151 | 97.0683 | 99.1214 | 101.1745 | 103.2277 | 105.2808 | 107.3339 | 109.3871 | 111.4402 | 113.4933 | 114.8621 | 116.2308 | 117.5996 | 118.9684 | 120.3371 | 121.7059 | 123.0746 | 124.4434 | 125.8121 | 127.1809 | 128.5496 | 129.9184 | 131.2872 | 132.6559 | 134.0247 | 135.242 | 136.4594 | 137.6768 | 138.8942 | 140.1116 | 141.3289 | 142.5463 | 143.7637 | 144.9811 | 146.1984 | 147.4158 | 148.6332 | 149.8506 | 151.068 | 152.2853 | 152.6602 | 153.035 | 153.4098 | 153.7846 | 154.1594 | 154.5343 | 154.9091 | 155.2839 | 155.6587 | 156.0336 | 156.4084 | 156.7832 | 157.158 | 157.5328 | 157.9077 | 158.2825 | 158.6573 | 159.0321 | 159.407 | 159.7818 | 160.1566 | 160.5314 | 160.9062 | 161.2811 | 161.6559 | 162.0307 | 162.4055 | 162.7804 | 163.1552 | 163.53 | 163.6882 | 163.8464 | 164.0045 | 164.1627 | 164.3209 | 164.4791 | 164.6372 | 164.7954 | 164.9536 | 165.1118 | 165.27 | 165.4281 | 165.5863 | 165.7445 | 165.9027 | 166.0608 | 166.219 | 166.3772 | 166.5354 | 166.6936 | 166.8517 | 167.0099 | 167.1681 | 167.3263 | 167.4844 | 167.6426 | 167.8008 | 167.959 | 168.1172 | 168.2753 | 168.2753 | 168.2753 | 168.2753 | 168.2753 | 168.2753 | 168.2753 | 168.2753 | 168.2753 | 168.2753 | 168.2753 | 168.2753 | 168.2753 | 168.2753 | 168.2753 | 168.2753 | 168.2753 | 168.2753 | 168.2753 | 168.2753 | 168.2753 | 168.2753 | 168.2753 | 168.2753 | 168.2753 | 168.2753 | 168.2753 | 168.2753 | 168.2753 | 168.2753 | 168.2753 | 168.2237 | 168.172 | 168.1203 | 168.0687 | 168.017 | 167.9653 | 167.9137 | 167.862 | 167.8103 | 167.7587 | 167.707 | 167.6553 | 167.6037 | 167.552 | 167.5003 | 167.4487 | 167.397 | 167.3453 | 167.2937 | 167.242 | 167.1903 | 167.1387 | 167.087 | 167.0353 | 166.9837 | 166.932 | 166.8803 | 166.8287 | 166.777 | 166.7253
12.95 | 0 | 53.01 | 93.3847 | 93.651 | 114.3467 | 135.0423 | 153.4627 | 164.815 | 169.6077 | 169.6077 | 168.0827 | 0 | 5.301 | 10.602 | 15.903 | 21.204 | 26.505 | 31.806 | 37.107 | 42.408 | 47.709 | 53.01 | 61.0849 | 69.1599 | 77.2348 | 85.3097 | 93.3847 | 93.4379 | 93.4912 | 93.5445 | 93.5977 | 93.651 | 95.7206 | 97.7901 | 99.8597 | 101.9293 | 103.9988 | 106.0684 | 108.138 | 110.2075 | 112.2771 | 114.3467 | 115.7264 | 117.1061 | 118.4858 | 119.8655 | 121.2452 | 122.6249 | 124.0046 | 125.3844 | 126.7641 | 128.1438 | 129.5235 | 130.9032 | 132.2829 | 133.6626 | 135.0423 | 136.2704 | 137.4984 | 138.7264 | 139.9544 | 141.1824 | 142.4105 | 143.6385 | 144.8665 | 146.0945 | 147.3226 | 148.5506 | 149.7786 | 151.0066 | 152.2346 | 153.4627 | 153.8411 | 154.2195 | 154.5979 | 154.9763 | 155.3547 | 155.7331 | 156.1115 | 156.49 | 156.8684 | 157.2468 | 157.6252 | 158.0036 | 158.382 | 158.7604 | 159.1388 | 159.5172 | 159.8957 | 160.2741 | 160.6525 | 161.0309 | 161.4093 | 161.7877 | 162.1661 | 162.5445 | 162.9229 | 163.3014 | 163.6798 | 164.0582 | 164.4366 | 164.815 | 164.9748 | 165.1345 | 165.2943 | 165.454 | 165.6138 | 165.7735 | 165.9333 | 166.093 | 166.2528 | 166.4126 | 166.5723 | 166.7321 | 166.8918 | 167.0516 | 167.2113 | 167.3711 | 167.5308 | 167.6906 | 167.8504 | 168.0101 | 168.1699 | 168.3296 | 168.4894 | 168.6491 | 168.8089 | 168.9686 | 169.1284 | 169.2882 | 169.4479 | 169.6077 | 169.6077 | 169.6077 | 169.6077 | 169.6077 | 169.6077 | 169.6077 | 169.6077 | 169.6077 | 169.6077 | 169.6077 | 169.6077 | 169.6077 | 169.6077 | 169.6077 | 169.6077 | 169.6077 | 169.6077 | 169.6077 | 169.6077 | 169.6077 | 169.6077 | 169.6077 | 169.6077 | 169.6077 | 169.6077 | 169.6077 | 169.6077 | 169.6077 | 169.6077 | 169.6077 | 169.5568 | 169.506 | 169.4552 | 169.4043 | 169.3535 | 169.3027 | 169.2518 | 169.201 | 169.1502 | 169.0993 | 169.0485 | 168.9977 | 168.9468 | 168.896 | 168.8452 | 168.7943 | 168.7435 | 168.6927 | 168.6418 | 168.591 | 168.5402 | 168.4893 | 168.4385 | 168.3877 | 168.3368 | 168.286 | 168.2352 | 168.1843 | 168.1335 | 168.0827
13 | 0 | 53.4 | 94.12 | 94.34 | 115.2 | 136.06 | 154.64 | 166.1 | 170.94 | 170.94 | 169.44 | 0 | 5.34 | 10.68 | 16.02 | 21.36 | 26.7 | 32.04 | 37.38 | 42.72 | 48.06 | 53.4 | 61.544 | 69.688 | 77.832 | 85.976 | 94.12 | 94.164 | 94.208 | 94.252 | 94.296 | 94.34 | 96.426 | 98.512 | 100.598 | 102.684 | 104.77 | 106.856 | 108.942 | 111.028 | 113.114 | 115.2 | 116.5907 | 117.9813 | 119.372 | 120.7627 | 122.1533 | 123.544 | 124.9347 | 126.3253 | 127.716 | 129.1067 | 130.4973 | 131.888 | 133.2787 | 134.6693 | 136.06 | 137.2987 | 138.5373 | 139.776 | 141.0147 | 142.2533 | 143.492 | 144.7307 | 145.9693 | 147.208 | 148.4467 | 149.6853 | 150.924 | 152.1627 | 153.4013 | 154.64 | 155.022 | 155.404 | 155.786 | 156.168 | 156.55 | 156.932 | 157.314 | 157.696 | 158.078 | 158.46 | 158.842 | 159.224 | 159.606 | 159.988 | 160.37 | 160.752 | 161.134 | 161.516 | 161.898 | 162.28 | 162.662 | 163.044 | 163.426 | 163.808 | 164.19 | 164.572 | 164.954 | 165.336 | 165.718 | 166.1 | 166.2613 | 166.4227 | 166.584 | 166.7453 | 166.9067 | 167.068 | 167.2293 | 167.3907 | 167.552 | 167.7133 | 167.8747 | 168.036 | 168.1973 | 168.3587 | 168.52 | 168.6813 | 168.8427 | 169.004 | 169.1653 | 169.3267 | 169.488 | 169.6493 | 169.8107 | 169.972 | 170.1333 | 170.2947 | 170.456 | 170.6173 | 170.7787 | 170.94 | 170.94 | 170.94 | 170.94 | 170.94 | 170.94 | 170.94 | 170.94 | 170.94 | 170.94 | 170.94 | 170.94 | 170.94 | 170.94 | 170.94 | 170.94 | 170.94 | 170.94 | 170.94 | 170.94 | 170.94 | 170.94 | 170.94 | 170.94 | 170.94 | 170.94 | 170.94 | 170.94 | 170.94 | 170.94 | 170.94 | 170.89 | 170.84 | 170.79 | 170.74 | 170.69 | 170.64 | 170.59 | 170.54 | 170.49 | 170.44 | 170.39 | 170.34 | 170.29 | 170.24 | 170.19 | 170.14 | 170.09 | 170.04 | 169.99 | 169.94 | 169.89 | 169.84 | 169.79 | 169.74 | 169.69 | 169.64 | 169.59 | 169.54 | 169.49 | 169.44
13.05 | 0 | 53.79 | 94.8553 | 95.029 | 116.0533 | 137.0777 | 155.8173 | 167.385 | 172.2723 | 172.2723 | 170.7973 | 3.5527e-15 | 5.379 | 10.758 | 16.137 | 21.516 | 26.895 | 32.274 | 37.653 | 43.032 | 48.411 | 53.79 | 62.0031 | 70.2161 | 78.4292 | 86.6423 | 94.8553 | 94.8901 | 94.9248 | 94.9595 | 94.9943 | 95.029 | 97.1314 | 99.2339 | 101.3363 | 103.4387 | 105.5412 | 107.6436 | 109.746 | 111.8485 | 113.9509 | 116.0533 | 117.455 | 118.8566 | 120.2582 | 121.6598 | 123.0614 | 124.4631 | 125.8647 | 127.2663 | 128.6679 | 130.0696 | 131.4712 | 132.8728 | 134.2744 | 135.676 | 137.0777 | 138.327 | 139.5763 | 140.8256 | 142.0749 | 143.3242 | 144.5735 | 145.8228 | 147.0722 | 148.3215 | 149.5708 | 150.8201 | 152.0694 | 153.3187 | 154.568 | 155.8173 | 156.2029 | 156.5885 | 156.9741 | 157.3597 | 157.7453 | 158.1309 | 158.5165 | 158.902 | 159.2876 | 159.6732 | 160.0588 | 160.4444 | 160.83 | 161.2156 | 161.6012 | 161.9868 | 162.3723 | 162.7579 | 163.1435 | 163.5291 | 163.9147 | 164.3003 | 164.6859 | 165.0715 | 165.4571 | 165.8426 | 166.2282 | 166.6138 | 166.9994 | 167.385 | 167.5479 | 167.7108 | 167.8737 | 168.0366 | 168.1996 | 168.3625 | 168.5254 | 168.6883 | 168.8512 | 169.0141 | 169.177 | 169.3399 | 169.5028 | 169.6658 | 169.8287 | 169.9916 | 170.1545 | 170.3174 | 170.4803 | 170.6432 | 170.8061 | 170.969 | 171.132 | 171.2949 | 171.4578 | 171.6207 | 171.7836 | 171.9465 | 172.1094 | 172.2723 | 172.2723 | 172.2723 | 172.2723 | 172.2723 | 172.2723 | 172.2723 | 172.2723 | 172.2723 | 172.2723 | 172.2723 | 172.2723 | 172.2723 | 172.2723 | 172.2723 | 172.2723 | 172.2723 | 172.2723 | 172.2723 | 172.2723 | 172.2723 | 172.2723 | 172.2723 | 172.2723 | 172.2723 | 172.2723 | 172.2723 | 172.2723 | 172.2723 | 172.2723 | 172.2723 | 172.2232 | 172.174 | 172.1248 | 172.0757 | 172.0265 | 171.9773 | 171.9282 | 171.879 | 171.8298 | 171.7807 | 171.7315 | 171.6823 | 171.6332 | 171.584 | 171.5348 | 171.4857 | 171.4365 | 171.3873 | 171.3382 | 171.289 | 171.2398 | 171.1907 | 171.1415 | 171.0923 | 171.0432 | 170.994 | 170.9448 | 170.8957 | 170.8465 | 170.7973
13.1 | 0 | 54.18 | 95.5907 | 95.718 | 116.9067 | 138.0953 | 156.9947 | 168.67 | 173.6047 | 173.6047 | 172.1547 | 0 | 5.418 | 10.836 | 16.254 | 21.672 | 27.09 | 32.508 | 37.926 | 43.344 | 48.762 | 54.18 | 62.4621 | 70.7443 | 79.0264 | 87.3085 | 95.5907 | 95.6161 | 95.6416 | 95.6671 | 95.6925 | 95.718 | 97.8369 | 99.9557 | 102.0746 | 104.1935 | 106.3123 | 108.4312 | 110.5501 | 112.6689 | 114.7878 | 116.9067 | 118.3192 | 119.7318 | 121.1444 | 122.557 | 123.9696 | 125.3821 | 126.7947 | 128.2073 | 129.6199 | 131.0324 | 132.445 | 133.8576 | 135.2702 | 136.6828 | 138.0953 | 139.3553 | 140.6152 | 141.8752 | 143.1352 | 144.3951 | 145.6551 | 146.915 | 148.175 | 149.4349 | 150.6949 | 151.9548 | 153.2148 | 154.4748 | 155.7347 | 156.9947 | 157.3838 | 157.773 | 158.1622 | 158.5514 | 158.9406 | 159.3297 | 159.7189 | 160.1081 | 160.4973 | 160.8864 | 161.2756 | 161.6648 | 162.054 | 162.4432 | 162.8323 | 163.2215 | 163.6107 | 163.9999 | 164.389 | 164.7782 | 165.1674 | 165.5566 | 165.9458 | 166.3349 | 166.7241 | 167.1133 | 167.5025 | 167.8916 | 168.2808 | 168.67 | 168.8345 | 168.999 | 169.1635 | 169.328 | 169.4924 | 169.6569 | 169.8214 | 169.9859 | 170.1504 | 170.3149 | 170.4794 | 170.6439 | 170.8084 | 170.9728 | 171.1373 | 171.3018 | 171.4663 | 171.6308 | 171.7953 | 171.9598 | 172.1243 | 172.2888 | 172.4532 | 172.6177 | 172.7822 | 172.9467 | 173.1112 | 173.2757 | 173.4402 | 173.6047 | 173.6047 | 173.6047 | 173.6047 | 173.6047 | 173.6047 | 173.6047 | 173.6047 | 173.6047 | 173.6047 | 173.6047 | 173.6047 | 173.6047 | 173.6047 | 173.6047 | 173.6047 | 173.6047 | 173.6047 | 173.6047 | 173.6047 | 173.6047 | 173.6047 | 173.6047 | 173.6047 | 173.6047 | 173.6047 | 173.6047 | 173.6047 | 173.6047 | 173.6047 | 173.6047 | 173.5563 | 173.508 | 173.4597 | 173.4113 | 173.363 | 173.3147 | 173.2663 | 173.218 | 173.1697 | 173.1213 | 173.073 | 173.0247 | 172.9763 | 172.928 | 172.8797 | 172.8313 | 172.783 | 172.7347 | 172.6863 | 172.638 | 172.5897 | 172.5413 | 172.493 | 172.4447 | 172.3963 | 172.348 | 172.2997 | 172.2513 | 172.203 | 172.1547
13.15 | 0 | 54.57 | 96.326 | 96.407 | 117.76 | 139.113 | 158.172 | 169.955 | 174.937 | 174.937 | 173.512 | -3.5527e-15 | 5.457 | 10.914 | 16.371 | 21.828 | 27.285 | 32.742 | 38.199 | 43.656 | 49.113 | 54.57 | 62.9212 | 71.2724 | 79.6236 | 87.9748 | 96.326 | 96.3422 | 96.3584 | 96.3746 | 96.3908 | 96.407 | 98.5423 | 100.6776 | 102.8129 | 104.9482 | 107.0835 | 109.2188 | 111.3541 | 113.4894 | 115.6247 | 117.76 | 119.1835 | 120.6071 | 122.0306 | 123.4541 | 124.8777 | 126.3012 | 127.7247 | 129.1483 | 130.5718 | 131.9953 | 133.4189 | 134.8424 | 136.2659 | 137.6895 | 139.113 | 140.3836 | 141.6542 | 142.9248 | 144.1954 | 145.466 | 146.7366 | 148.0072 | 149.2778 | 150.5484 | 151.819 | 153.0896 | 154.3602 | 155.6308 | 156.9014 | 158.172 | 158.5648 | 158.9575 | 159.3503 | 159.7431 | 160.1358 | 160.5286 | 160.9214 | 161.3141 | 161.7069 | 162.0997 | 162.4924 | 162.8852 | 163.278 | 163.6707 | 164.0635 | 164.4563 | 164.849 | 165.2418 | 165.6346 | 166.0273 | 166.4201 | 166.8129 | 167.2056 | 167.5984 | 167.9912 | 168.3839 | 168.7767 | 169.1695 | 169.5622 | 169.955 | 170.1211 | 170.2871 | 170.4532 | 170.6193 | 170.7853 | 170.9514 | 171.1175 | 171.2835 | 171.4496 | 171.6157 | 171.7817 | 171.9478 | 172.1139 | 172.2799 | 172.446 | 172.6121 | 172.7781 | 172.9442 | 173.1103 | 173.2763 | 173.4424 | 173.6085 | 173.7745 | 173.9406 | 174.1067 | 174.2727 | 174.4388 | 174.6049 | 174.7709 | 174.937 | 174.937 | 174.937 | 174.937 | 174.937 | 174.937 | 174.937 | 174.937 | 174.937 | 174.937 | 174.937 | 174.937 | 174.937 | 174.937 | 174.937 | 174.937 | 174.937 | 174.937 | 174.937 | 174.937 | 174.937 | 174.937 | 174.937 | 174.937 | 174.937 | 174.937 | 174.937 | 174.937 | 174.937 | 174.937 | 174.937 | 174.8895 | 174.842 | 174.7945 | 174.747 | 174.6995 | 174.652 | 174.6045 | 174.557 | 174.5095 | 174.462 | 174.4145 | 174.367 | 174.3195 | 174.272 | 174.2245 | 174.177 | 174.1295 | 174.082 | 174.0345 | 173.987 | 173.9395 | 173.892 | 173.8445 | 173.797 | 173.7495 | 173.702 | 173.6545 | 173.607 | 173.5595 | 173.512
13.2 | 0 | 54.96 | 97.0613 | 97.096 | 118.6133 | 140.1307 | 159.3493 | 171.24 | 176.2693 | 176.2693 | 174.8693 | 0 | 5.496 | 10.992 | 16.488 | 21.984 | 27.48 | 32.976 | 38.472 | 43.968 | 49.464 | 54.96 | 63.3803 | 71.8005 | 80.2208 | 88.6411 | 97.0613 | 97.0683 | 97.0752 | 97.0821 | 97.0891 | 97.096 | 99.2477 | 101.3995 | 103.5512 | 105.7029 | 107.8547 | 110.0064 | 112.1581 | 114.3099 | 116.4616 | 118.6133 | 120.0478 | 121.4823 | 122.9168 | 124.3513 | 125.7858 | 127.2203 | 128.6548 | 130.0892 | 131.5237 | 132.9582 | 134.3927 | 135.8272 | 137.2617 | 138.6962 | 140.1307 | 141.4119 | 142.6932 | 143.9744 | 145.2556 | 146.5369 | 147.8181 | 149.0994 | 150.3806 | 151.6619 | 152.9431 | 154.2244 | 155.5056 | 156.7868 | 158.0681 | 159.3493 | 159.7457 | 160.142 | 160.5384 | 160.9348 | 161.3311 | 161.7275 | 162.1238 | 162.5202 | 162.9165 | 163.3129 | 163.7092 | 164.1056 | 164.502 | 164.8983 | 165.2947 | 165.691 | 166.0874 | 166.4837 | 166.8801 | 167.2764 | 167.6728 | 168.0692 | 168.4655 | 168.8619 | 169.2582 | 169.6546 | 170.0509 | 170.4473 | 170.8436 | 171.24 | 171.4076 | 171.5753 | 171.7429 | 171.9106 | 172.0782 | 172.2459 | 172.4135 | 172.5812 | 172.7488 | 172.9164 | 173.0841 | 173.2517 | 173.4194 | 173.587 | 173.7547 | 173.9223 | 174.09 | 174.2576 | 174.4252 | 174.5929 | 174.7605 | 174.9282 | 175.0958 | 175.2635 | 175.4311 | 175.5988 | 175.7664 | 175.934 | 176.1017 | 176.2693 | 176.2693 | 176.2693 | 176.2693 | 176.2693 | 176.2693 | 176.2693 | 176.2693 | 176.2693 | 176.2693 | 176.2693 | 176.2693 | 176.2693 | 176.2693 | 176.2693 | 176.2693 | 176.2693 | 176.2693 | 176.2693 | 176.2693 | 176.2693 | 176.2693 | 176.2693 | 176.2693 | 176.2693 | 176.2693 | 176.2693 | 176.2693 | 176.2693 | 176.2693 | 176.2693 | 176.2227 | 176.176 | 176.1293 | 176.0827 | 176.036 | 175.9893 | 175.9427 | 175.896 | 175.8493 | 175.8027 | 175.756 | 175.7093 | 175.6627 | 175.616 | 175.5693 | 175.5227 | 175.476 | 175.4293 | 175.3827 | 175.336 | 175.2893 | 175.2427 | 175.196 | 175.1493 | 175.1027 | 175.056 | 175.0093 | 174.9627 | 174.916 | 174.8693
13.25 | 0 | 55.35 | 97.7967 | 97.785 | 119.4667 | 141.1483 | 160.5267 | 172.525 | 177.6017 | 177.6017 | 176.2267 | -3.5527e-15 | 5.535 | 11.07 | 16.605 | 22.14 | 27.675 | 33.21 | 38.745 | 44.28 | 49.815 | 55.35 | 63.8393 | 72.3287 | 80.818 | 89.3073 | 97.7967 | 97.7943 | 97.792 | 97.7897 | 97.7873 | 97.785 | 99.9532 | 102.1213 | 104.2895 | 106.4577 | 108.6258 | 110.794 | 112.9622 | 115.1303 | 117.2985 | 119.4667 | 120.9121 | 122.3576 | 123.803 | 125.2484 | 126.6939 | 128.1393 | 129.5848 | 131.0302 | 132.4757 | 133.9211 | 135.3666 | 136.812 | 138.2574 | 139.7029 | 141.1483 | 142.4402 | 143.7321 | 145.024 | 146.3159 | 147.6078 | 148.8997 | 150.1916 | 151.4834 | 152.7753 | 154.0672 | 155.3591 | 156.651 | 157.9429 | 159.2348 | 160.5267 | 160.9266 | 161.3266 | 161.7265 | 162.1264 | 162.5264 | 162.9263 | 163.3263 | 163.7262 | 164.1262 | 164.5261 | 164.9261 | 165.326 | 165.7259 | 166.1259 | 166.5258 | 166.9258 | 167.3257 | 167.7257 | 168.1256 | 168.5256 | 168.9255 | 169.3254 | 169.7254 | 170.1253 | 170.5253 | 170.9252 | 171.3252 | 171.7251 | 172.1251 | 172.525 | 172.6942 | 172.8634 | 173.0327 | 173.2019 | 173.3711 | 173.5403 | 173.7096 | 173.8788 | 174.048 | 174.2172 | 174.3864 | 174.5557 | 174.7249 | 174.8941 | 175.0633 | 175.2326 | 175.4018 | 175.571 | 175.7402 | 175.9094 | 176.0787 | 176.2479 | 176.4171 | 176.5863 | 176.7556 | 176.9248 | 177.094 | 177.2632 | 177.4324 | 177.6017 | 177.6017 | 177.6017 | 177.6017 | 177.6017 | 177.6017 | 177.6017 | 177.6017 | 177.6017 | 177.6017 | 177.6017 | 177.6017 | 177.6017 | 177.6017 | 177.6017 | 177.6017 | 177.6017 | 177.6017 | 177.6017 | 177.6017 | 177.6017 | 177.6017 | 177.6017 | 177.6017 | 177.6017 | 177.6017 | 177.6017 | 177.6017 | 177.6017 | 177.6017 | 177.6017 | 177.5558 | 177.51 | 177.4642 | 177.4183 | 177.3725 | 177.3267 | 177.2808 | 177.235 | 177.1892 | 177.1433 | 177.0975 | 177.0517 | 177.0058 | 176.96 | 176.9142 | 176.8683 | 176.8225 | 176.7767 | 176.7308 | 176.685 | 176.6392 | 176.5933 | 176.5475 | 176.5017 | 176.4558 | 176.41 | 176.3642 | 176.3183 | 176.2725 | 176.2267
13.3 | 0 | 55.74 | 98.532 | 98.474 | 120.32 | 142.166 | 161.704 | 173.81 | 178.934 | 178.934 | 177.584 | 3.5527e-15 | 5.574 | 11.148 | 16.722 | 22.296 | 27.87 | 33.444 | 39.018 | 44.592 | 50.166 | 55.74 | 64.2984 | 72.8568 | 81.4152 | 89.9736 | 98.532 | 98.5204 | 98.5088 | 98.4972 | 98.4856 | 98.474 | 100.6586 | 102.8432 | 105.0278 | 107.2124 | 109.397 | 111.5816 | 113.7662 | 115.9508 | 118.1354 | 120.32 | 121.7764 | 123.2328 | 124.6892 | 126.1456 | 127.602 | 129.0584 | 130.5148 | 131.9712 | 133.4276 | 134.884 | 136.3404 | 137.7968 | 139.2532 | 140.7096 | 142.166 | 143.4685 | 144.7711 | 146.0736 | 147.3761 | 148.6787 | 149.9812 | 151.2837 | 152.5863 | 153.8888 | 155.1913 | 156.4939 | 157.7964 | 159.0989 | 160.4015 | 161.704 | 162.1075 | 162.5111 | 162.9146 | 163.3181 | 163.7217 | 164.1252 | 164.5287 | 164.9323 | 165.3358 | 165.7393 | 166.1429 | 166.5464 | 166.9499 | 167.3535 | 167.757 | 168.1605 | 168.5641 | 168.9676 | 169.3711 | 169.7747 | 170.1782 | 170.5817 | 170.9853 | 171.3888 | 171.7923 | 172.1959 | 172.5994 | 173.0029 | 173.4065 | 173.81 | 173.9808 | 174.1516 | 174.3224 | 174.4932 | 174.664 | 174.8348 | 175.0056 | 175.1764 | 175.3472 | 175.518 | 175.6888 | 175.8596 | 176.0304 | 176.2012 | 176.372 | 176.5428 | 176.7136 | 176.8844 | 177.0552 | 177.226 | 177.3968 | 177.5676 | 177.7384 | 177.9092 | 178.08 | 178.2508 | 178.4216 | 178.5924 | 178.7632 | 178.934 | 178.934 | 178.934 | 178.934 | 178.934 | 178.934 | 178.934 | 178.934 | 178.934 | 178.934 | 178.934 | 178.934 | 178.934 | 178.934 | 178.934 | 178.934 | 178.934 | 178.934 | 178.934 | 178.934 | 178.934 | 178.934 | 178.934 | 178.934 | 178.934 | 178.934 | 178.934 | 178.934 | 178.934 | 178.934 | 178.934 | 178.889 | 178.844 | 178.799 | 178.754 | 178.709 | 178.664 | 178.619 | 178.574 | 178.529 | 178.484 | 178.439 | 178.394 | 178.349 | 178.304 | 178.259 | 178.214 | 178.169 | 178.124 | 178.079 | 178.034 | 177.989 | 177.944 | 177.899 | 177.854 | 177.809 | 177.764 | 177.719 | 177.674 | 177.629 | 177.584
13.35 | 0 | 56.13 | 99.2673 | 99.163 | 121.1733 | 143.1837 | 162.8813 | 175.095 | 180.2663 | 180.2663 | 178.9413 | 0 | 5.613 | 11.226 | 16.839 | 22.452 | 28.065 | 33.678 | 39.291 | 44.904 | 50.517 | 56.13 | 64.7575 | 73.3849 | 82.0124 | 90.6399 | 99.2673 | 99.2465 | 99.2256 | 99.2047 | 99.1839 | 99.163 | 101.364 | 103.5651 | 105.7661 | 107.9671 | 110.1682 | 112.3692 | 114.5702 | 116.7713 | 118.9723 | 121.1733 | 122.6407 | 124.108 | 125.5754 | 127.0428 | 128.5101 | 129.9775 | 131.4448 | 132.9122 | 134.3795 | 135.8469 | 137.3142 | 138.7816 | 140.249 | 141.7163 | 143.1837 | 144.4968 | 145.81 | 147.1232 | 148.4364 | 149.7496 | 151.0627 | 152.3759 | 153.6891 | 155.0023 | 156.3154 | 157.6286 | 158.9418 | 160.255 | 161.5682 | 162.8813 | 163.2885 | 163.6956 | 164.1027 | 164.5098 | 164.9169 | 165.3241 | 165.7312 | 166.1383 | 166.5454 | 166.9526 | 167.3597 | 167.7668 | 168.1739 | 168.581 | 168.9882 | 169.3953 | 169.8024 | 170.2095 | 170.6167 | 171.0238 | 171.4309 | 171.838 | 172.2451 | 172.6523 | 173.0594 | 173.4665 | 173.8736 | 174.2808 | 174.6879 | 175.095 | 175.2674 | 175.4398 | 175.6121 | 175.7845 | 175.9569 | 176.1293 | 176.3016 | 176.474 | 176.6464 | 176.8188 | 176.9912 | 177.1635 | 177.3359 | 177.5083 | 177.6807 | 177.853 | 178.0254 | 178.1978 | 178.3702 | 178.5426 | 178.7149 | 178.8873 | 179.0597 | 179.2321 | 179.4044 | 179.5768 | 179.7492 | 179.9216 | 180.094 | 180.2663 | 180.2663 | 180.2663 | 180.2663 | 180.2663 | 180.2663 | 180.2663 | 180.2663 | 180.2663 | 180.2663 | 180.2663 | 180.2663 | 180.2663 | 180.2663 | 180.2663 | 180.2663 | 180.2663 | 180.2663 | 180.2663 | 180.2663 | 180.2663 | 180.2663 | 180.2663 | 180.2663 | 180.2663 | 180.2663 | 180.2663 | 180.2663 | 180.2663 | 180.2663 | 180.2663 | 180.2222 | 180.178 | 180.1338 | 180.0897 | 180.0455 | 180.0013 | 179.9572 | 179.913 | 179.8688 | 179.8247 | 179.7805 | 179.7363 | 179.6922 | 179.648 | 179.6038 | 179.5597 | 179.5155 | 179.4713 | 179.4272 | 179.383 | 179.3388 | 179.2947 | 179.2505 | 179.2063 | 179.1622 | 179.118 | 179.0738 | 179.0297 | 178.9855 | 178.9413
13.4 | 0 | 56.52 | 100.0027 | 99.852 | 122.0267 | 144.2013 | 164.0587 | 176.38 | 181.5987 | 181.5987 | 180.2987 | -3.5527e-15 | 5.652 | 11.304 | 16.956 | 22.608 | 28.26 | 33.912 | 39.564 | 45.216 | 50.868 | 56.52 | 65.2165 | 73.9131 | 82.6096 | 91.3061 | 100.0027 | 99.9725 | 99.9424 | 99.9123 | 99.8821 | 99.852 | 102.0695 | 104.2869 | 106.5044 | 108.7219 | 110.9393 | 113.1568 | 115.3743 | 117.5917 | 119.8092 | 122.0267 | 123.505 | 124.9833 | 126.4616 | 127.9399 | 129.4182 | 130.8965 | 132.3748 | 133.8532 | 135.3315 | 136.8098 | 138.2881 | 139.7664 | 141.2447 | 142.723 | 144.2013 | 145.5252 | 146.849 | 148.1728 | 149.4966 | 150.8204 | 152.1443 | 153.4681 | 154.7919 | 156.1157 | 157.4396 | 158.7634 | 160.0872 | 161.411 | 162.7348 | 164.0587 | 164.4694 | 164.8801 | 165.2908 | 165.7015 | 166.1122 | 166.5229 | 166.9336 | 167.3444 | 167.7551 | 168.1658 | 168.5765 | 168.9872 | 169.3979 | 169.8086 | 170.2193 | 170.63 | 171.0408 | 171.4515 | 171.8622 | 172.2729 | 172.6836 | 173.0943 | 173.505 | 173.9157 | 174.3264 | 174.7372 | 175.1479 | 175.5586 | 175.9693 | 176.38 | 176.554 | 176.7279 | 176.9019 | 177.0758 | 177.2498 | 177.4237 | 177.5977 | 177.7716 | 177.9456 | 178.1196 | 178.2935 | 178.4675 | 178.6414 | 178.8154 | 178.9893 | 179.1633 | 179.3372 | 179.5112 | 179.6852 | 179.8591 | 180.0331 | 180.207 | 180.381 | 180.5549 | 180.7289 | 180.9028 | 181.0768 | 181.2508 | 181.4247 | 181.5987 | 181.5987 | 181.5987 | 181.5987 | 181.5987 | 181.5987 | 181.5987 | 181.5987 | 181.5987 | 181.5987 | 181.5987 | 181.5987 | 181.5987 | 181.5987 | 181.5987 | 181.5987 | 181.5987 | 181.5987 | 181.5987 | 181.5987 | 181.5987 | 181.5987 | 181.5987 | 181.5987 | 181.5987 | 181.5987 | 181.5987 | 181.5987 | 181.5987 | 181.5987 | 181.5987 | 181.5553 | 181.512 | 181.4687 | 181.4253 | 181.382 | 181.3387 | 181.2953 | 181.252 | 181.2087 | 181.1653 | 181.122 | 181.0787 | 181.0353 | 180.992 | 180.9487 | 180.9053 | 180.862 | 180.8187 | 180.7753 | 180.732 | 180.6887 | 180.6453 | 180.602 | 180.5587 | 180.5153 | 180.472 | 180.4287 | 180.3853 | 180.342 | 180.2987
13.45 | 0 | 56.91 | 100.738 | 100.541 | 122.88 | 145.219 | 165.236 | 177.665 | 182.931 | 182.931 | 181.656 | 0 | 5.691 | 11.382 | 17.073 | 22.764 | 28.455 | 34.146 | 39.837 | 45.528 | 51.219 | 56.91 | 65.6756 | 74.4412 | 83.2068 | 91.9724 | 100.738 | 100.6986 | 100.6592 | 100.6198 | 100.5804 | 100.541 | 102.7749 | 105.0088 | 107.2427 | 109.4766 | 111.7105 | 113.9444 | 116.1783 | 118.4122 | 120.6461 | 122.88 | 124.3693 | 125.8585 | 127.3478 | 128.8371 | 130.3263 | 131.8156 | 133.3049 | 134.7941 | 136.2834 | 137.7727 | 139.2619 | 140.7512 | 142.2405 | 143.7297 | 145.219 | 146.5535 | 147.8879 | 149.2224 | 150.5569 | 151.8913 | 153.2258 | 154.5603 | 155.8947 | 157.2292 | 158.5637 | 159.8981 | 161.2326 | 162.5671 | 163.9015 | 165.236 | 165.6503 | 166.0646 | 166.4789 | 166.8932 | 167.3075 | 167.7218 | 168.1361 | 168.5504 | 168.9647 | 169.379 | 169.7933 | 170.2076 | 170.6219 | 171.0362 | 171.4505 | 171.8648 | 172.2791 | 172.6934 | 173.1077 | 173.522 | 173.9363 | 174.3506 | 174.7649 | 175.1792 | 175.5935 | 176.0078 | 176.4221 | 176.8364 | 177.2507 | 177.665 | 177.8405 | 178.0161 | 178.1916 | 178.3671 | 178.5427 | 178.7182 | 178.8937 | 179.0693 | 179.2448 | 179.4203 | 179.5959 | 179.7714 | 179.9469 | 180.1225 | 180.298 | 180.4735 | 180.6491 | 180.8246 | 181.0001 | 181.1757 | 181.3512 | 181.5267 | 181.7023 | 181.8778 | 182.0533 | 182.2289 | 182.4044 | 182.5799 | 182.7555 | 182.931 | 182.931 | 182.931 | 182.931 | 182.931 | 182.931 | 182.931 | 182.931 | 182.931 | 182.931 | 182.931 | 182.931 | 182.931 | 182.931 | 182.931 | 182.931 | 182.931 | 182.931 | 182.931 | 182.931 | 182.931 | 182.931 | 182.931 | 182.931 | 182.931 | 182.931 | 182.931 | 182.931 | 182.931 | 182.931 | 182.931 | 182.8885 | 182.846 | 182.8035 | 182.761 | 182.7185 | 182.676 | 182.6335 | 182.591 | 182.5485 | 182.506 | 182.4635 | 182.421 | 182.3785 | 182.336 | 182.2935 | 182.251 | 182.2085 | 182.166 | 182.1235 | 182.081 | 182.0385 | 181.996 | 181.9535 | 181.911 | 181.8685 | 181.826 | 181.7835 | 181.741 | 181.6985 | 181.656
13.5 | 0 | 57.3 | 101.4733 | 101.23 | 123.7333 | 146.2367 | 166.4133 | 178.95 | 184.2633 | 184.2633 | 183.0133 | 3.5527e-15 | 5.73 | 11.46 | 17.19 | 22.92 | 28.65 | 34.38 | 40.11 | 45.84 | 51.57 | 57.3 | 66.1347 | 74.9693 | 83.804 | 92.6387 | 101.4733 | 101.4247 | 101.376 | 101.3273 | 101.2787 | 101.23 | 103.4803 | 105.7307 | 107.981 | 110.2313 | 112.4817 | 114.732 | 116.9823 | 119.2327 | 121.483 | 123.7333 | 125.2336 | 126.7338 | 128.234 | 129.7342 | 131.2344 | 132.7347 | 134.2349 | 135.7351 | 137.2353 | 138.7356 | 140.2358 | 141.736 | 143.2362 | 144.7364 | 146.2367 | 147.5818 | 148.9269 | 150.272 | 151.6171 | 152.9622 | 154.3073 | 155.6524 | 156.9976 | 158.3427 | 159.6878 | 161.0329 | 162.378 | 163.7231 | 165.0682 | 166.4133 | 166.8312 | 167.2491 | 167.667 | 168.0849 | 168.5028 | 168.9207 | 169.3386 | 169.7564 | 170.1743 | 170.5922 | 171.0101 | 171.428 | 171.8459 | 172.2638 | 172.6817 | 173.0996 | 173.5174 | 173.9353 | 174.3532 | 174.7711 | 175.189 | 175.6069 | 176.0248 | 176.4427 | 176.8606 | 177.2784 | 177.6963 | 178.1142 | 178.5321 | 178.95 | 179.1271 | 179.3042 | 179.4813 | 179.6584 | 179.8356 | 180.0127 | 180.1898 | 180.3669 | 180.544 | 180.7211 | 180.8982 | 181.0753 | 181.2524 | 181.4296 | 181.6067 | 181.7838 | 181.9609 | 182.138 | 182.3151 | 182.4922 | 182.6693 | 182.8464 | 183.0236 | 183.2007 | 183.3778 | 183.5549 | 183.732 | 183.9091 | 184.0862 | 184.2633 | 184.2633 | 184.2633 | 184.2633 | 184.2633 | 184.2633 | 184.2633 | 184.2633 | 184.2633 | 184.2633 | 184.2633 | 184.2633 | 184.2633 | 184.2633 | 184.2633 | 184.2633 | 184.2633 | 184.2633 | 184.2633 | 184.2633 | 184.2633 | 184.2633 | 184.2633 | 184.2633 | 184.2633 | 184.2633 | 184.2633 | 184.2633 | 184.2633 | 184.2633 | 184.2633 | 184.2217 | 184.18 | 184.1383 | 184.0967 | 184.055 | 184.0133 | 183.9717 | 183.93 | 183.8883 | 183.8467 | 183.805 | 183.7633 | 183.7217 | 183.68 | 183.6383 | 183.5967 | 183.555 | 183.5133 | 183.4717 | 183.43 | 183.3883 | 183.3467 | 183.305 | 183.2633 | 183.2217 | 183.18 | 183.1383 | 183.0967 | 183.055 | 183.0133
13.55 | 0 | 57.69 | 102.2087 | 101.919 | 124.5867 | 147.2543 | 167.5907 | 180.235 | 185.5957 | 185.5957 | 184.3707 | -3.5527e-15 | 5.769 | 11.538 | 17.307 | 23.076 | 28.845 | 34.614 | 40.383 | 46.152 | 51.921 | 57.69 | 66.5937 | 75.4975 | 84.4012 | 93.3049 | 102.2087 | 102.1507 | 102.0928 | 102.0349 | 101.9769 | 101.919 | 104.1858 | 106.4525 | 108.7193 | 110.9861 | 113.2528 | 115.5196 | 117.7864 | 120.0531 | 122.3199 | 124.5867 | 126.0978 | 127.609 | 129.1202 | 130.6314 | 132.1426 | 133.6537 | 135.1649 | 136.6761 | 138.1873 | 139.6984 | 141.2096 | 142.7208 | 144.232 | 145.7432 | 147.2543 | 148.6101 | 149.9658 | 151.3216 | 152.6774 | 154.0331 | 155.3889 | 156.7446 | 158.1004 | 159.4561 | 160.8119 | 162.1676 | 163.5234 | 164.8792 | 166.2349 | 167.5907 | 168.0121 | 168.4336 | 168.8551 | 169.2766 | 169.6981 | 170.1195 | 170.541 | 170.9625 | 171.384 | 171.8054 | 172.2269 | 172.6484 | 173.0699 | 173.4914 | 173.9128 | 174.3343 | 174.7558 | 175.1773 | 175.5987 | 176.0202 | 176.4417 | 176.8632 | 177.2847 | 177.7061 | 178.1276 | 178.5491 | 178.9706 | 179.392 | 179.8135 | 180.235 | 180.4137 | 180.5924 | 180.7711 | 180.9498 | 181.1284 | 181.3071 | 181.4858 | 181.6645 | 181.8432 | 182.0219 | 182.2006 | 182.3793 | 182.558 | 182.7366 | 182.9153 | 183.094 | 183.2727 | 183.4514 | 183.6301 | 183.8088 | 183.9875 | 184.1662 | 184.3448 | 184.5235 | 184.7022 | 184.8809 | 185.0596 | 185.2383 | 185.417 | 185.5957 | 185.5957 | 185.5957 | 185.5957 | 185.5957 | 185.5957 | 185.5957 | 185.5957 | 185.5957 | 185.5957 | 185.5957 | 185.5957 | 185.5957 | 185.5957 | 185.5957 | 185.5957 | 185.5957 | 185.5957 | 185.5957 | 185.5957 | 185.5957 | 185.5957 | 185.5957 | 185.5957 | 185.5957 | 185.5957 | 185.5957 | 185.5957 | 185.5957 | 185.5957 | 185.5957 | 185.5548 | 185.514 | 185.4732 | 185.4323 | 185.3915 | 185.3507 | 185.3098 | 185.269 | 185.2282 | 185.1873 | 185.1465 | 185.1057 | 185.0648 | 185.024 | 184.9832 | 184.9423 | 184.9015 | 184.8607 | 184.8198 | 184.779 | 184.7382 | 184.6973 | 184.6565 | 184.6157 | 184.5748 | 184.534 | 184.4932 | 184.4523 | 184.4115 | 184.3707
13.6 | 0 | 58.08 | 102.944 | 102.608 | 125.44 | 148.272 | 168.768 | 181.52 | 186.928 | 186.928 | 185.728 | -3.5527e-15 | 5.808 | 11.616 | 17.424 | 23.232 | 29.04 | 34.848 | 40.656 | 46.464 | 52.272 | 58.08 | 67.0528 | 76.0256 | 84.9984 | 93.9712 | 102.944 | 102.8768 | 102.8096 | 102.7424 | 102.6752 | 102.608 | 104.8912 | 107.1744 | 109.4576 | 111.7408 | 114.024 | 116.3072 | 118.5904 | 120.8736 | 123.1568 | 125.44 | 126.9621 | 128.4843 | 130.0064 | 131.5285 | 133.0507 | 134.5728 | 136.0949 | 137.6171 | 139.1392 | 140.6613 | 142.1835 | 143.7056 | 145.2277 | 146.7499 | 148.272 | 149.6384 | 151.0048 | 152.3712 | 153.7376 | 155.104 | 156.4704 | 157.8368 | 159.2032 | 160.5696 | 161.936 | 163.3024 | 164.6688 | 166.0352 | 167.4016 | 168.768 | 169.1931 | 169.6181 | 170.0432 | 170.4683 | 170.8933 | 171.3184 | 171.7435 | 172.1685 | 172.5936 | 173.0187 | 173.4437 | 173.8688 | 174.2939 | 174.7189 | 175.144 | 175.5691 | 175.9941 | 176.4192 | 176.8443 | 177.2693 | 177.6944 | 178.1195 | 178.5445 | 178.9696 | 179.3947 | 179.8197 | 180.2448 | 180.6699 | 181.0949 | 181.52 | 181.7003 | 181.8805 | 182.0608 | 182.2411 | 182.4213 | 182.6016 | 182.7819 | 182.9621 | 183.1424 | 183.3227 | 183.5029 | 183.6832 | 183.8635 | 184.0437 | 184.224 | 184.4043 | 184.5845 | 184.7648 | 184.9451 | 185.1253 | 185.3056 | 185.4859 | 185.6661 | 185.8464 | 186.0267 | 186.2069 | 186.3872 | 186.5675 | 186.7477 | 186.928 | 186.928 | 186.928 | 186.928 | 186.928 | 186.928 | 186.928 | 186.928 | 186.928 | 186.928 | 186.928 | 186.928 | 186.928 | 186.928 | 186.928 | 186.928 | 186.928 | 186.928 | 186.928 | 186.928 | 186.928 | 186.928 | 186.928 | 186.928 | 186.928 | 186.928 | 186.928 | 186.928 | 186.928 | 186.928 | 186.928 | 186.888 | 186.848 | 186.808 | 186.768 | 186.728 | 186.688 | 186.648 | 186.608 | 186.568 | 186.528 | 186.488 | 186.448 | 186.408 | 186.368 | 186.328 | 186.288 | 186.248 | 186.208 | 186.168 | 186.128 | 186.088 | 186.048 | 186.008 | 185.968 | 185.928 | 185.888 | 185.848 | 185.808 | 185.768 | 185.728
13.65 | 0 | 58.47 | 103.6793 | 103.297 | 126.2933 | 149.2897 | 169.9453 | 182.805 | 188.2603 | 188.2603 | 187.0853 | -3.5527e-15 | 5.847 | 11.694 | 17.541 | 23.388 | 29.235 | 35.082 | 40.929 | 46.776 | 52.623 | 58.47 | 67.5119 | 76.5537 | 85.5956 | 94.6375 | 103.6793 | 103.6029 | 103.5264 | 103.4499 | 103.3735 | 103.297 | 105.5966 | 107.8963 | 110.1959 | 112.4955 | 114.7952 | 117.0948 | 119.3944 | 121.6941 | 123.9937 | 126.2933 | 127.8264 | 129.3595 | 130.8926 | 132.4257 | 133.9588 | 135.4919 | 137.025 | 138.558 | 140.0911 | 141.6242 | 143.1573 | 144.6904 | 146.2235 | 147.7566 | 149.2897 | 150.6667 | 152.0438 | 153.4208 | 154.7978 | 156.1749 | 157.5519 | 158.929 | 160.306 | 161.6831 | 163.0601 | 164.4372 | 165.8142 | 167.1912 | 168.5683 | 169.9453 | 170.374 | 170.8026 | 171.2313 | 171.66 | 172.0886 | 172.5173 | 172.9459 | 173.3746 | 173.8032 | 174.2319 | 174.6605 | 175.0892 | 175.5179 | 175.9465 | 176.3752 | 176.8038 | 177.2325 | 177.6611 | 178.0898 | 178.5184 | 178.9471 | 179.3758 | 179.8044 | 180.2331 | 180.6617 | 181.0904 | 181.519 | 181.9477 | 182.3763 | 182.805 | 182.9868 | 183.1687 | 183.3505 | 183.5324 | 183.7142 | 183.8961 | 184.0779 | 184.2598 | 184.4416 | 184.6234 | 184.8053 | 184.9871 | 185.169 | 185.3508 | 185.5327 | 185.7145 | 185.8964 | 186.0782 | 186.26 | 186.4419 | 186.6237 | 186.8056 | 186.9874 | 187.1693 | 187.3511 | 187.533 | 187.7148 | 187.8966 | 188.0785 | 188.2603 | 188.2603 | 188.2603 | 188.2603 | 188.2603 | 188.2603 | 188.2603 | 188.2603 | 188.2603 | 188.2603 | 188.2603 | 188.2603 | 188.2603 | 188.2603 | 188.2603 | 188.2603 | 188.2603 | 188.2603 | 188.2603 | 188.2603 | 188.2603 | 188.2603 | 188.2603 | 188.2603 | 188.2603 | 188.2603 | 188.2603 | 188.2603 | 188.2603 | 188.2603 | 188.2603 | 188.2212 | 188.182 | 188.1428 | 188.1037 | 188.0645 | 188.0253 | 187.9862 | 187.947 | 187.9078 | 187.8687 | 187.8295 | 187.7903 | 187.7512 | 187.712 | 187.6728 | 187.6337 | 187.5945 | 187.5553 | 187.5162 | 187.477 | 187.4378 | 187.3987 | 187.3595 | 187.3203 | 187.2812 | 187.242 | 187.2028 | 187.1637 | 187.1245 | 187.0853
13.7 | 0 | 58.86 | 104.4147 | 103.986 | 127.1467 | 150.3073 | 171.1227 | 184.09 | 189.5927 | 189.5927 | 188.4427 | 0 | 5.886 | 11.772 | 17.658 | 23.544 | 29.43 | 35.316 | 41.202 | 47.088 | 52.974 | 58.86 | 67.9709 | 77.0819 | 86.1928 | 95.3037 | 104.4147 | 104.3289 | 104.2432 | 104.1575 | 104.0717 | 103.986 | 106.3021 | 108.6181 | 110.9342 | 113.2503 | 115.5663 | 117.8824 | 120.1985 | 122.5145 | 124.8306 | 127.1467 | 128.6907 | 130.2348 | 131.7788 | 133.3228 | 134.8669 | 136.4109 | 137.955 | 139.499 | 141.0431 | 142.5871 | 144.1312 | 145.6752 | 147.2192 | 148.7633 | 150.3073 | 151.695 | 153.0827 | 154.4704 | 155.8581 | 157.2458 | 158.6335 | 160.0212 | 161.4088 | 162.7965 | 164.1842 | 165.5719 | 166.9596 | 168.3473 | 169.735 | 171.1227 | 171.5549 | 171.9872 | 172.4194 | 172.8516 | 173.2839 | 173.7161 | 174.1484 | 174.5806 | 175.0129 | 175.4451 | 175.8774 | 176.3096 | 176.7418 | 177.1741 | 177.6063 | 178.0386 | 178.4708 | 178.9031 | 179.3353 | 179.7676 | 180.1998 | 180.632 | 181.0643 | 181.4965 | 181.9288 | 182.361 | 182.7933 | 183.2255 | 183.6578 | 184.09 | 184.2734 | 184.4568 | 184.6403 | 184.8237 | 185.0071 | 185.1905 | 185.374 | 185.5574 | 185.7408 | 185.9242 | 186.1076 | 186.2911 | 186.4745 | 186.6579 | 186.8413 | 187.0248 | 187.2082 | 187.3916 | 187.575 | 187.7584 | 187.9419 | 188.1253 | 188.3087 | 188.4921 | 188.6756 | 188.859 | 189.0424 | 189.2258 | 189.4092 | 189.5927 | 189.5927 | 189.5927 | 189.5927 | 189.5927 | 189.5927 | 189.5927 | 189.5927 | 189.5927 | 189.5927 | 189.5927 | 189.5927 | 189.5927 | 189.5927 | 189.5927 | 189.5927 | 189.5927 | 189.5927 | 189.5927 | 189.5927 | 189.5927 | 189.5927 | 189.5927 | 189.5927 | 189.5927 | 189.5927 | 189.5927 | 189.5927 | 189.5927 | 189.5927 | 189.5927 | 189.5543 | 189.516 | 189.4777 | 189.4393 | 189.401 | 189.3627 | 189.3243 | 189.286 | 189.2477 | 189.2093 | 189.171 | 189.1327 | 189.0943 | 189.056 | 189.0177 | 188.9793 | 188.941 | 188.9027 | 188.8643 | 188.826 | 188.7877 | 188.7493 | 188.711 | 188.6727 | 188.6343 | 188.596 | 188.5577 | 188.5193 | 188.481 | 188.4427
13.75 | 0 | 59.25 | 105.15 | 104.675 | 128 | 151.325 | 172.3 | 185.375 | 190.925 | 190.925 | 189.8 | 3.5527e-15 | 5.925 | 11.85 | 17.775 | 23.7 | 29.625 | 35.55 | 41.475 | 47.4 | 53.325 | 59.25 | 68.43 | 77.61 | 86.79 | 95.97 | 105.15 | 105.055 | 104.96 | 104.865 | 104.77 | 104.675 | 107.0075 | 109.34 | 111.6725 | 114.005 | 116.3375 | 118.67 | 121.0025 | 123.335 | 125.6675 | 128 | 129.555 | 131.11 | 132.665 | 134.22 | 135.775 | 137.33 | 138.885 | 140.44 | 141.995 | 143.55 | 145.105 | 146.66 | 148.215 | 149.77 | 151.325 | 152.7233 | 154.1217 | 155.52 | 156.9183 | 158.3167 | 159.715 | 161.1133 | 162.5117 | 163.91 | 165.3083 | 166.7067 | 168.105 | 169.5033 | 170.9017 | 172.3 | 172.7358 | 173.1717 | 173.6075 | 174.0433 | 174.4792 | 174.915 | 175.3508 | 175.7867 | 176.2225 | 176.6583 | 177.0942 | 177.53 | 177.9658 | 178.4017 | 178.8375 | 179.2733 | 179.7092 | 180.145 | 180.5808 | 181.0167 | 181.4525 | 181.8883 | 182.3242 | 182.76 | 183.1958 | 183.6317 | 184.0675 | 184.5033 | 184.9392 | 185.375 | 185.56 | 185.745 | 185.93 | 186.115 | 186.3 | 186.485 | 186.67 | 186.855 | 187.04 | 187.225 | 187.41 | 187.595 | 187.78 | 187.965 | 188.15 | 188.335 | 188.52 | 188.705 | 188.89 | 189.075 | 189.26 | 189.445 | 189.63 | 189.815 | 190 | 190.185 | 190.37 | 190.555 | 190.74 | 190.925 | 190.925 | 190.925 | 190.925 | 190.925 | 190.925 | 190.925 | 190.925 | 190.925 | 190.925 | 190.925 | 190.925 | 190.925 | 190.925 | 190.925 | 190.925 | 190.925 | 190.925 | 190.925 | 190.925 | 190.925 | 190.925 | 190.925 | 190.925 | 190.925 | 190.925 | 190.925 | 190.925 | 190.925 | 190.925 | 190.925 | 190.8875 | 190.85 | 190.8125 | 190.775 | 190.7375 | 190.7 | 190.6625 | 190.625 | 190.5875 | 190.55 | 190.5125 | 190.475 | 190.4375 | 190.4 | 190.3625 | 190.325 | 190.2875 | 190.25 | 190.2125 | 190.175 | 190.1375 | 190.1 | 190.0625 | 190.025 | 189.9875 | 189.95 | 189.9125 | 189.875 | 189.8375 | 189.8
13.8 | 0 | 59.64 | 105.8853 | 105.364 | 128.8533 | 152.3427 | 173.4773 | 186.66 | 192.2573 | 192.2573 | 191.1573 | 0 | 5.964 | 11.928 | 17.892 | 23.856 | 29.82 | 35.784 | 41.748 | 47.712 | 53.676 | 59.64 | 68.8891 | 78.1381 | 87.3872 | 96.6363 | 105.8853 | 105.7811 | 105.6768 | 105.5725 | 105.4683 | 105.364 | 107.7129 | 110.0619 | 112.4108 | 114.7597 | 117.1087 | 119.4576 | 121.8065 | 124.1555 | 126.5044 | 128.8533 | 130.4193 | 131.9852 | 133.5512 | 135.1172 | 136.6831 | 138.2491 | 139.815 | 141.381 | 142.9469 | 144.5129 | 146.0788 | 147.6448 | 149.2108 | 150.7767 | 152.3427 | 153.7516 | 155.1606 | 156.5696 | 157.9786 | 159.3876 | 160.7965 | 162.2055 | 163.6145 | 165.0235 | 166.4324 | 167.8414 | 169.2504 | 170.6594 | 172.0684 | 173.4773 | 173.9168 | 174.3562 | 174.7956 | 175.235 | 175.6744 | 176.1139 | 176.5533 | 176.9927 | 177.4321 | 177.8716 | 178.311 | 178.7504 | 179.1898 | 179.6292 | 180.0687 | 180.5081 | 180.9475 | 181.3869 | 181.8264 | 182.2658 | 182.7052 | 183.1446 | 183.584 | 184.0235 | 184.4629 | 184.9023 | 185.3417 | 185.7812 | 186.2206 | 186.66 | 186.8466 | 187.0332 | 187.2197 | 187.4063 | 187.5929 | 187.7795 | 187.966 | 188.1526 | 188.3392 | 188.5258 | 188.7124 | 188.8989 | 189.0855 | 189.2721 | 189.4587 | 189.6452 | 189.8318 | 190.0184 | 190.205 | 190.3916 | 190.5781 | 190.7647 | 190.9513 | 191.1379 | 191.3244 | 191.511 | 191.6976 | 191.8842 | 192.0708 | 192.2573 | 192.2573 | 192.2573 | 192.2573 | 192.2573 | 192.2573 | 192.2573 | 192.2573 | 192.2573 | 192.2573 | 192.2573 | 192.2573 | 192.2573 | 192.2573 | 192.2573 | 192.2573 | 192.2573 | 192.2573 | 192.2573 | 192.2573 | 192.2573 | 192.2573 | 192.2573 | 192.2573 | 192.2573 | 192.2573 | 192.2573 | 192.2573 | 192.2573 | 192.2573 | 192.2573 | 192.2207 | 192.184 | 192.1473 | 192.1107 | 192.074 | 192.0373 | 192.0007 | 191.964 | 191.9273 | 191.8907 | 191.854 | 191.8173 | 191.7807 | 191.744 | 191.7073 | 191.6707 | 191.634 | 191.5973 | 191.5607 | 191.524 | 191.4873 | 191.4507 | 191.414 | 191.3773 | 191.3407 | 191.304 | 191.2673 | 191.2307 | 191.194 | 191.1573
13.85 | 0 | 60.03 | 106.6207 | 106.053 | 129.7067 | 153.3603 | 174.6547 | 187.945 | 193.5897 | 193.5897 | 192.5147 | 0 | 6.003 | 12.006 | 18.009 | 24.012 | 30.015 | 36.018 | 42.021 | 48.024 | 54.027 | 60.03 | 69.3481 | 78.6663 | 87.9844 | 97.3025 | 106.6207 | 106.5071 | 106.3936 | 106.2801 | 106.1665 | 106.053 | 108.4184 | 110.7837 | 113.1491 | 115.5145 | 117.8798 | 120.2452 | 122.6106 | 124.9759 | 127.3413 | 129.7067 | 131.2836 | 132.8605 | 134.4374 | 136.0143 | 137.5912 | 139.1681 | 140.745 | 142.322 | 143.8989 | 145.4758 | 147.0527 | 148.6296 | 150.2065 | 151.7834 | 153.3603 | 154.78 | 156.1996 | 157.6192 | 159.0388 | 160.4584 | 161.8781 | 163.2977 | 164.7173 | 166.1369 | 167.5566 | 168.9762 | 170.3958 | 171.8154 | 173.235 | 174.6547 | 175.0977 | 175.5407 | 175.9837 | 176.4267 | 176.8697 | 177.3127 | 177.7557 | 178.1988 | 178.6418 | 179.0848 | 179.5278 | 179.9708 | 180.4138 | 180.8568 | 181.2998 | 181.7428 | 182.1859 | 182.6289 | 183.0719 | 183.5149 | 183.9579 | 184.4009 | 184.8439 | 185.2869 | 185.7299 | 186.173 | 186.616 | 187.059 | 187.502 | 187.945 | 188.1332 | 188.3213 | 188.5095 | 188.6976 | 188.8858 | 189.0739 | 189.2621 | 189.4502 | 189.6384 | 189.8266 | 190.0147 | 190.2029 | 190.391 | 190.5792 | 190.7673 | 190.9555 | 191.1436 | 191.3318 | 191.52 | 191.7081 | 191.8963 | 192.0844 | 192.2726 | 192.4607 | 192.6489 | 192.837 | 193.0252 | 193.2134 | 193.4015 | 193.5897 | 193.5897 | 193.5897 | 193.5897 | 193.5897 | 193.5897 | 193.5897 | 193.5897 | 193.5897 | 193.5897 | 193.5897 | 193.5897 | 193.5897 | 193.5897 | 193.5897 | 193.5897 | 193.5897 | 193.5897 | 193.5897 | 193.5897 | 193.5897 | 193.5897 | 193.5897 | 193.5897 | 193.5897 | 193.5897 | 193.5897 | 193.5897 | 193.5897 | 193.5897 | 193.5897 | 193.5538 | 193.518 | 193.4822 | 193.4463 | 193.4105 | 193.3747 | 193.3388 | 193.303 | 193.2672 | 193.2313 | 193.1955 | 193.1597 | 193.1238 | 193.088 | 193.0522 | 193.0163 | 192.9805 | 192.9447 | 192.9088 | 192.873 | 192.8372 | 192.8013 | 192.7655 | 192.7297 | 192.6938 | 192.658 | 192.6222 | 192.5863 | 192.5505 | 192.5147
13.9 | 0 | 60.42 | 107.356 | 106.742 | 130.56 | 154.378 | 175.832 | 189.23 | 194.922 | 194.922 | 193.872 | 3.5527e-15 | 6.042 | 12.084 | 18.126 | 24.168 | 30.21 | 36.252 | 42.294 | 48.336 | 54.378 | 60.42 | 69.8072 | 79.1944 | 88.5816 | 97.9688 | 107.356 | 107.2332 | 107.1104 | 106.9876 | 106.8648 | 106.742 | 109.1238 | 111.5056 | 113.8874 | 116.2692 | 118.651 | 121.0328 | 123.4146 | 125.7964 | 128.1782 | 130.56 | 132.1479 | 133.7357 | 135.3236 | 136.9115 | 138.4993 | 140.0872 | 141.6751 | 143.2629 | 144.8508 | 146.4387 | 148.0265 | 149.6144 | 151.2023 | 152.7901 | 154.378 | 155.8083 | 157.2385 | 158.6688 | 160.0991 | 161.5293 | 162.9596 | 164.3899 | 165.8201 | 167.2504 | 168.6807 | 170.1109 | 171.5412 | 172.9715 | 174.4017 | 175.832 | 176.2786 | 176.7252 | 177.1718 | 177.6184 | 178.065 | 178.5116 | 178.9582 | 179.4048 | 179.8514 | 180.298 | 180.7446 | 181.1912 | 181.6378 | 182.0844 | 182.531 | 182.9776 | 183.4242 | 183.8708 | 184.3174 | 184.764 | 185.2106 | 185.6572 | 186.1038 | 186.5504 | 186.997 | 187.4436 | 187.8902 | 188.3368 | 188.7834 | 189.23 | 189.4197 | 189.6095 | 189.7992 | 189.9889 | 190.1787 | 190.3684 | 190.5581 | 190.7479 | 190.9376 | 191.1273 | 191.3171 | 191.5068 | 191.6965 | 191.8863 | 192.076 | 192.2657 | 192.4555 | 192.6452 | 192.8349 | 193.0247 | 193.2144 | 193.4041 | 193.5939 | 193.7836 | 193.9733 | 194.1631 | 194.3528 | 194.5425 | 194.7323 | 194.922 | 194.922 | 194.922 | 194.922 | 194.922 | 194.922 | 194.922 | 194.922 | 194.922 | 194.922 | 194.922 | 194.922 | 194.922 | 194.922 | 194.922 | 194.922 | 194.922 | 194.922 | 194.922 | 194.922 | 194.922 | 194.922 | 194.922 | 194.922 | 194.922 | 194.922 | 194.922 | 194.922 | 194.922 | 194.922 | 194.922 | 194.887 | 194.852 | 194.817 | 194.782 | 194.747 | 194.712 | 194.677 | 194.642 | 194.607 | 194.572 | 194.537 | 194.502 | 194.467 | 194.432 | 194.397 | 194.362 | 194.327 | 194.292 | 194.257 | 194.222 | 194.187 | 194.152 | 194.117 | 194.082 | 194.047 | 194.012 | 193.977 | 193.942 | 193.907 | 193.872
13.95 | 0 | 60.81 | 108.0913 | 107.431 | 131.4133 | 155.3957 | 177.0093 | 190.515 | 196.2543 | 196.2543 | 195.2293 | 3.5527e-15 | 6.081 | 12.162 | 18.243 | 24.324 | 30.405 | 36.486 | 42.567 | 48.648 | 54.729 | 60.81 | 70.2663 | 79.7225 | 89.1788 | 98.6351 | 108.0913 | 107.9593 | 107.8272 | 107.6951 | 107.5631 | 107.431 | 109.8292 | 112.2275 | 114.6257 | 117.0239 | 119.4222 | 121.8204 | 124.2186 | 126.6169 | 129.0151 | 131.4133 | 133.0122 | 134.611 | 136.2098 | 137.8086 | 139.4074 | 141.0063 | 142.6051 | 144.2039 | 145.8027 | 147.4016 | 149.0004 | 150.5992 | 152.198 | 153.7968 | 155.3957 | 156.8366 | 158.2775 | 159.7184 | 161.1593 | 162.6002 | 164.0411 | 165.482 | 166.923 | 168.3639 | 169.8048 | 171.2457 | 172.6866 | 174.1275 | 175.5684 | 177.0093 | 177.4595 | 177.9097 | 178.3599 | 178.8101 | 179.2603 | 179.7105 | 180.1607 | 180.6108 | 181.061 | 181.5112 | 181.9614 | 182.4116 | 182.8618 | 183.312 | 183.7622 | 184.2124 | 184.6625 | 185.1127 | 185.5629 | 186.0131 | 186.4633 | 186.9135 | 187.3637 | 187.8139 | 188.2641 | 188.7142 | 189.1644 | 189.6146 | 190.0648 | 190.515 | 190.7063 | 190.8976 | 191.0889 | 191.2802 | 191.4716 | 191.6629 | 191.8542 | 192.0455 | 192.2368 | 192.4281 | 192.6194 | 192.8107 | 193.002 | 193.1934 | 193.3847 | 193.576 | 193.7673 | 193.9586 | 194.1499 | 194.3412 | 194.5325 | 194.7238 | 194.9152 | 195.1065 | 195.2978 | 195.4891 | 195.6804 | 195.8717 | 196.063 | 196.2543 | 196.2543 | 196.2543 | 196.2543 | 196.2543 | 196.2543 | 196.2543 | 196.2543 | 196.2543 | 196.2543 | 196.2543 | 196.2543 | 196.2543 | 196.2543 | 196.2543 | 196.2543 | 196.2543 | 196.2543 | 196.2543 | 196.2543 | 196.2543 | 196.2543 | 196.2543 | 196.2543 | 196.2543 | 196.2543 | 196.2543 | 196.2543 | 196.2543 | 196.2543 | 196.2543 | 196.2202 | 196.186 | 196.1518 | 196.1177 | 196.0835 | 196.0493 | 196.0152 | 195.981 | 195.9468 | 195.9127 | 195.8785 | 195.8443 | 195.8102 | 195.776 | 195.7418 | 195.7077 | 195.6735 | 195.6393 | 195.6052 | 195.571 | 195.5368 | 195.5027 | 195.4685 | 195.4343 | 195.4002 | 195.366 | 195.3318 | 195.2977 | 195.2635 | 195.2293
14 | 0 | 61.2 | 108.8267 | 108.12 | 132.2667 | 156.4133 | 178.1867 | 191.8 | 197.5867 | 197.5867 | 196.5867 | -3.5527e-15 | 6.12 | 12.24 | 18.36 | 24.48 | 30.6 | 36.72 | 42.84 | 48.96 | 55.08 | 61.2 | 70.7253 | 80.2507 | 89.776 | 99.3013 | 108.8267 | 108.6853 | 108.544 | 108.4027 | 108.2613 | 108.12 | 110.5347 | 112.9493 | 115.364 | 117.7787 | 120.1933 | 122.608 | 125.0227 | 127.4373 | 129.852 | 132.2667 | 133.8764 | 135.4862 | 137.096 | 138.7058 | 140.3156 | 141.9253 | 143.5351 | 145.1449 | 146.7547 | 148.3644 | 149.9742 | 151.584 | 153.1938 | 154.8036 | 156.4133 | 157.8649 | 159.3164 | 160.768 | 162.2196 | 163.6711 | 165.1227 | 166.5742 | 168.0258 | 169.4773 | 170.9289 | 172.3804 | 173.832 | 175.2836 | 176.7351 | 178.1867 | 178.6404 | 179.0942 | 179.548 | 180.0018 | 180.4556 | 180.9093 | 181.3631 | 181.8169 | 182.2707 | 182.7244 | 183.1782 | 183.632 | 184.0858 | 184.5396 | 184.9933 | 185.4471 | 185.9009 | 186.3547 | 186.8084 | 187.2622 | 187.716 | 188.1698 | 188.6236 | 189.0773 | 189.5311 | 189.9849 | 190.4387 | 190.8924 | 191.3462 | 191.8 | 191.9929 | 192.1858 | 192.3787 | 192.5716 | 192.7644 | 192.9573 | 193.1502 | 193.3431 | 193.536 | 193.7289 | 193.9218 | 194.1147 | 194.3076 | 194.5004 | 194.6933 | 194.8862 | 195.0791 | 195.272 | 195.4649 | 195.6578 | 195.8507 | 196.0436 | 196.2364 | 196.4293 | 196.6222 | 196.8151 | 197.008 | 197.2009 | 197.3938 | 197.5867 | 197.5867 | 197.5867 | 197.5867 | 197.5867 | 197.5867 | 197.5867 | 197.5867 | 197.5867 | 197.5867 | 197.5867 | 197.5867 | 197.5867 | 197.5867 | 197.5867 | 197.5867 | 197.5867 | 197.5867 | 197.5867 | 197.5867 | 197.5867 | 197.5867 | 197.5867 | 197.5867 | 197.5867 | 197.5867 | 197.5867 | 197.5867 | 197.5867 | 197.5867 | 197.5867 | 197.5533 | 197.52 | 197.4867 | 197.4533 | 197.42 | 197.3867 | 197.3533 | 197.32 | 197.2867 | 197.2533 | 197.22 | 197.1867 | 197.1533 | 197.12 | 197.0867 | 197.0533 | 197.02 | 196.9867 | 196.9533 | 196.92 | 196.8867 | 196.8533 | 196.82 | 196.7867 | 196.7533 | 196.72 | 196.6867 | 196.6533 | 196.62 | 196.5867
14.05 | 0 | 61.59 | 109.562 | 108.809 | 133.12 | 157.431 | 179.364 | 193.085 | 198.919 | 198.919 | 197.944 | 0 | 6.159 | 12.318 | 18.477 | 24.636 | 30.795 | 36.954 | 43.113 | 49.272 | 55.431 | 61.59 | 71.1844 | 80.7788 | 90.3732 | 99.9676 | 109.562 | 109.4114 | 109.2608 | 109.1102 | 108.9596 | 108.809 | 111.2401 | 113.6712 | 116.1023 | 118.5334 | 120.9645 | 123.3956 | 125.8267 | 128.2578 | 130.6889 | 133.12 | 134.7407 | 136.3615 | 137.9822 | 139.6029 | 141.2237 | 142.8444 | 144.4651 | 146.0859 | 147.7066 | 149.3273 | 150.9481 | 152.5688 | 154.1895 | 155.8103 | 157.431 | 158.8932 | 160.3554 | 161.8176 | 163.2798 | 164.742 | 166.2042 | 167.6664 | 169.1286 | 170.5908 | 172.053 | 173.5152 | 174.9774 | 176.4396 | 177.9018 | 179.364 | 179.8214 | 180.2787 | 180.7361 | 181.1935 | 181.6508 | 182.1082 | 182.5656 | 183.0229 | 183.4803 | 183.9377 | 184.395 | 184.8524 | 185.3098 | 185.7671 | 186.2245 | 186.6819 | 187.1392 | 187.5966 | 188.054 | 188.5113 | 188.9687 | 189.4261 | 189.8834 | 190.3408 | 190.7982 | 191.2555 | 191.7129 | 192.1703 | 192.6276 | 193.085 | 193.2795 | 193.4739 | 193.6684 | 193.8629 | 194.0573 | 194.2518 | 194.4463 | 194.6407 | 194.8352 | 195.0297 | 195.2241 | 195.4186 | 195.6131 | 195.8075 | 196.002 | 196.1965 | 196.3909 | 196.5854 | 196.7799 | 196.9743 | 197.1688 | 197.3633 | 197.5577 | 197.7522 | 197.9467 | 198.1411 | 198.3356 | 198.5301 | 198.7245 | 198.919 | 198.919 | 198.919 | 198.919 | 198.919 | 198.919 | 198.919 | 198.919 | 198.919 | 198.919 | 198.919 | 198.919 | 198.919 | 198.919 | 198.919 | 198.919 | 198.919 | 198.919 | 198.919 | 198.919 | 198.919 | 198.919 | 198.919 | 198.919 | 198.919 | 198.919 | 198.919 | 198.919 | 198.919 | 198.919 | 198.919 | 198.8865 | 198.854 | 198.8215 | 198.789 | 198.7565 | 198.724 | 198.6915 | 198.659 | 198.6265 | 198.594 | 198.5615 | 198.529 | 198.4965 | 198.464 | 198.4315 | 198.399 | 198.3665 | 198.334 | 198.3015 | 198.269 | 198.2365 | 198.204 | 198.1715 | 198.139 | 198.1065 | 198.074 | 198.0415 | 198.009 | 197.9765 | 197.944
14.1 | 0 | 61.98 | 110.2973 | 109.498 | 133.9733 | 158.4487 | 180.5413 | 194.37 | 200.2513 | 200.2513 | 199.3013 | -3.5527e-15 | 6.198 | 12.396 | 18.594 | 24.792 | 30.99 | 37.188 | 43.386 | 49.584 | 55.782 | 61.98 | 71.6435 | 81.3069 | 90.9704 | 100.6339 | 110.2973 | 110.1375 | 109.9776 | 109.8177 | 109.6579 | 109.498 | 111.9455 | 114.3931 | 116.8406 | 119.2881 | 121.7357 | 124.1832 | 126.6307 | 129.0783 | 131.5258 | 133.9733 | 135.605 | 137.2367 | 138.8684 | 140.5001 | 142.1318 | 143.7635 | 145.3952 | 147.0268 | 148.6585 | 150.2902 | 151.9219 | 153.5536 | 155.1853 | 156.817 | 158.4487 | 159.9215 | 161.3944 | 162.8672 | 164.34 | 165.8129 | 167.2857 | 168.7586 | 170.2314 | 171.7043 | 173.1771 | 174.65 | 176.1228 | 177.5956 | 179.0685 | 180.5413 | 181.0023 | 181.4632 | 181.9242 | 182.3852 | 182.8461 | 183.3071 | 183.768 | 184.229 | 184.6899 | 185.1509 | 185.6118 | 186.0728 | 186.5338 | 186.9947 | 187.4557 | 187.9166 | 188.3776 | 188.8385 | 189.2995 | 189.7604 | 190.2214 | 190.6824 | 191.1433 | 191.6043 | 192.0652 | 192.5262 | 192.9871 | 193.4481 | 193.909 | 194.37 | 194.566 | 194.7621 | 194.9581 | 195.1542 | 195.3502 | 195.5463 | 195.7423 | 195.9384 | 196.1344 | 196.3304 | 196.5265 | 196.7225 | 196.9186 | 197.1146 | 197.3107 | 197.5067 | 197.7028 | 197.8988 | 198.0948 | 198.2909 | 198.4869 | 198.683 | 198.879 | 199.0751 | 199.2711 | 199.4672 | 199.6632 | 199.8592 | 200.0553 | 200.2513 | 200.2513 | 200.2513 | 200.2513 | 200.2513 | 200.2513 | 200.2513 | 200.2513 | 200.2513 | 200.2513 | 200.2513 | 200.2513 | 200.2513 | 200.2513 | 200.2513 | 200.2513 | 200.2513 | 200.2513 | 200.2513 | 200.2513 | 200.2513 | 200.2513 | 200.2513 | 200.2513 | 200.2513 | 200.2513 | 200.2513 | 200.2513 | 200.2513 | 200.2513 | 200.2513 | 200.2197 | 200.188 | 200.1563 | 200.1247 | 200.093 | 200.0613 | 200.0297 | 199.998 | 199.9663 | 199.9347 | 199.903 | 199.8713 | 199.8397 | 199.808 | 199.7763 | 199.7447 | 199.713 | 199.6813 | 199.6497 | 199.618 | 199.5863 | 199.5547 | 199.523 | 199.4913 | 199.4597 | 199.428 | 199.3963 | 199.3647 | 199.333 | 199.3013
14.15 | 0 | 62.37 | 111.0327 | 110.187 | 134.8267 | 159.4663 | 181.7187 | 195.655 | 201.5837 | 201.5837 | 200.6587 | 3.5527e-15 | 6.237 | 12.474 | 18.711 | 24.948 | 31.185 | 37.422 | 43.659 | 49.896 | 56.133 | 62.37 | 72.1025 | 81.8351 | 91.5676 | 101.3001 | 111.0327 | 110.8635 | 110.6944 | 110.5253 | 110.3561 | 110.187 | 112.651 | 115.1149 | 117.5789 | 120.0429 | 122.5068 | 124.9708 | 127.4348 | 129.8987 | 132.3627 | 134.8267 | 136.4693 | 138.112 | 139.7546 | 141.3972 | 143.0399 | 144.6825 | 146.3252 | 147.9678 | 149.6105 | 151.2531 | 152.8958 | 154.5384 | 156.181 | 157.8237 | 159.4663 | 160.9498 | 162.4333 | 163.9168 | 165.4003 | 166.8838 | 168.3673 | 169.8508 | 171.3342 | 172.8177 | 174.3012 | 175.7847 | 177.2682 | 178.7517 | 180.2352 | 181.7187 | 182.1832 | 182.6478 | 183.1123 | 183.5768 | 184.0414 | 184.5059 | 184.9705 | 185.435 | 185.8996 | 186.3641 | 186.8287 | 187.2932 | 187.7577 | 188.2223 | 188.6868 | 189.1514 | 189.6159 | 190.0805 | 190.545 | 191.0096 | 191.4741 | 191.9386 | 192.4032 | 192.8677 | 193.3323 | 193.7968 | 194.2614 | 194.7259 | 195.1905 | 195.655 | 195.8526 | 196.0502 | 196.2479 | 196.4455 | 196.6431 | 196.8407 | 197.0384 | 197.236 | 197.4336 | 197.6312 | 197.8288 | 198.0265 | 198.2241 | 198.4217 | 198.6193 | 198.817 | 199.0146 | 199.2122 | 199.4098 | 199.6074 | 199.8051 | 200.0027 | 200.2003 | 200.3979 | 200.5956 | 200.7932 | 200.9908 | 201.1884 | 201.386 | 201.5837 | 201.5837 | 201.5837 | 201.5837 | 201.5837 | 201.5837 | 201.5837 | 201.5837 | 201.5837 | 201.5837 | 201.5837 | 201.5837 | 201.5837 | 201.5837 | 201.5837 | 201.5837 | 201.5837 | 201.5837 | 201.5837 | 201.5837 | 201.5837 | 201.5837 | 201.5837 | 201.5837 | 201.5837 | 201.5837 | 201.5837 | 201.5837 | 201.5837 | 201.5837 | 201.5837 | 201.5528 | 201.522 | 201.4912 | 201.4603 | 201.4295 | 201.3987 | 201.3678 | 201.337 | 201.3062 | 201.2753 | 201.2445 | 201.2137 | 201.1828 | 201.152 | 201.1212 | 201.0903 | 201.0595 | 201.0287 | 200.9978 | 200.967 | 200.9362 | 200.9053 | 200.8745 | 200.8437 | 200.8128 | 200.782 | 200.7512 | 200.7203 | 200.6895 | 200.6587
14.2 | 0 | 62.76 | 111.768 | 110.876 | 135.68 | 160.484 | 182.896 | 196.94 | 202.916 | 202.916 | 202.016 | 3.5527e-15 | 6.276 | 12.552 | 18.828 | 25.104 | 31.38 | 37.656 | 43.932 | 50.208 | 56.484 | 62.76 | 72.5616 | 82.3632 | 92.1648 | 101.9664 | 111.768 | 111.5896 | 111.4112 | 111.2328 | 111.0544 | 110.876 | 113.3564 | 115.8368 | 118.3172 | 120.7976 | 123.278 | 125.7584 | 128.2388 | 130.7192 | 133.1996 | 135.68 | 137.3336 | 138.9872 | 140.6408 | 142.2944 | 143.948 | 145.6016 | 147.2552 | 148.9088 | 150.5624 | 152.216 | 153.8696 | 155.5232 | 157.1768 | 158.8304 | 160.484 | 161.9781 | 163.4723 | 164.9664 | 166.4605 | 167.9547 | 169.4488 | 170.9429 | 172.4371 | 173.9312 | 175.4253 | 176.9195 | 178.4136 | 179.9077 | 181.4019 | 182.896 | 183.3641 | 183.8323 | 184.3004 | 184.7685 | 185.2367 | 185.7048 | 186.1729 | 186.6411 | 187.1092 | 187.5773 | 188.0455 | 188.5136 | 188.9817 | 189.4499 | 189.918 | 190.3861 | 190.8543 | 191.3224 | 191.7905 | 192.2587 | 192.7268 | 193.1949 | 193.6631 | 194.1312 | 194.5993 | 195.0675 | 195.5356 | 196.0037 | 196.4719 | 196.94 | 197.1392 | 197.3384 | 197.5376 | 197.7368 | 197.936 | 198.1352 | 198.3344 | 198.5336 | 198.7328 | 198.932 | 199.1312 | 199.3304 | 199.5296 | 199.7288 | 199.928 | 200.1272 | 200.3264 | 200.5256 | 200.7248 | 200.924 | 201.1232 | 201.3224 | 201.5216 | 201.7208 | 201.92 | 202.1192 | 202.3184 | 202.5176 | 202.7168 | 202.916 | 202.916 | 202.916 | 202.916 | 202.916 | 202.916 | 202.916 | 202.916 | 202.916 | 202.916 | 202.916 | 202.916 | 202.916 | 202.916 | 202.916 | 202.916 | 202.916 | 202.916 | 202.916 | 202.916 | 202.916 | 202.916 | 202.916 | 202.916 | 202.916 | 202.916 | 202.916 | 202.916 | 202.916 | 202.916 | 202.916 | 202.886 | 202.856 | 202.826 | 202.796 | 202.766 | 202.736 | 202.706 | 202.676 | 202.646 | 202.616 | 202.586 | 202.556 | 202.526 | 202.496 | 202.466 | 202.436 | 202.406 | 202.376 | 202.346 | 202.316 | 202.286 | 202.256 | 202.226 | 202.196 | 202.166 | 202.136 | 202.106 | 202.076 | 202.046 | 202.016
14.25 | 0 | 63.15 | 112.5033 | 111.565 | 136.5333 | 161.5017 | 184.0733 | 198.225 | 204.2483 | 204.2483 | 203.3733 | -3.5527e-15 | 6.315 | 12.63 | 18.945 | 25.26 | 31.575 | 37.89 | 44.205 | 50.52 | 56.835 | 63.15 | 73.0207 | 82.8913 | 92.762 | 102.6327 | 112.5033 | 112.3157 | 112.128 | 111.9403 | 111.7527 | 111.565 | 114.0618 | 116.5587 | 119.0555 | 121.5523 | 124.0492 | 126.546 | 129.0428 | 131.5397 | 134.0365 | 136.5333 | 138.1979 | 139.8624 | 141.527 | 143.1916 | 144.8561 | 146.5207 | 148.1852 | 149.8498 | 151.5143 | 153.1789 | 154.8434 | 156.508 | 158.1726 | 159.8371 | 161.5017 | 163.0064 | 164.5112 | 166.016 | 167.5208 | 169.0256 | 170.5303 | 172.0351 | 173.5399 | 175.0447 | 176.5494 | 178.0542 | 179.559 | 181.0638 | 182.5686 | 184.0733 | 184.5451 | 185.0168 | 185.4885 | 185.9602 | 186.4319 | 186.9037 | 187.3754 | 187.8471 | 188.3188 | 188.7906 | 189.2623 | 189.734 | 190.2057 | 190.6774 | 191.1492 | 191.6209 | 192.0926 | 192.5643 | 193.0361 | 193.5078 | 193.9795 | 194.4512 | 194.9229 | 195.3947 | 195.8664 | 196.3381 | 196.8098 | 197.2816 | 197.7533 | 198.225 | 198.4258 | 198.6266 | 198.8273 | 199.0281 | 199.2289 | 199.4297 | 199.6304 | 199.8312 | 200.032 | 200.2328 | 200.4336 | 200.6343 | 200.8351 | 201.0359 | 201.2367 | 201.4374 | 201.6382 | 201.839 | 202.0398 | 202.2406 | 202.4413 | 202.6421 | 202.8429 | 203.0437 | 203.2444 | 203.4452 | 203.646 | 203.8468 | 204.0476 | 204.2483 | 204.2483 | 204.2483 | 204.2483 | 204.2483 | 204.2483 | 204.2483 | 204.2483 | 204.2483 | 204.2483 | 204.2483 | 204.2483 | 204.2483 | 204.2483 | 204.2483 | 204.2483 | 204.2483 | 204.2483 | 204.2483 | 204.2483 | 204.2483 | 204.2483 | 204.2483 | 204.2483 | 204.2483 | 204.2483 | 204.2483 | 204.2483 | 204.2483 | 204.2483 | 204.2483 | 204.2192 | 204.19 | 204.1608 | 204.1317 | 204.1025 | 204.0733 | 204.0442 | 204.015 | 203.9858 | 203.9567 | 203.9275 | 203.8983 | 203.8692 | 203.84 | 203.8108 | 203.7817 | 203.7525 | 203.7233 | 203.6942 | 203.665 | 203.6358 | 203.6067 | 203.5775 | 203.5483 | 203.5192 | 203.49 | 203.4608 | 203.4317 | 203.4025 | 203.3733
14.3 | 0 | 63.54 | 113.2387 | 112.254 | 137.3867 | 162.5193 | 185.2507 | 199.51 | 205.5807 | 205.5807 | 204.7307 | 0 | 6.354 | 12.708 | 19.062 | 25.416 | 31.77 | 38.124 | 44.478 | 50.832 | 57.186 | 63.54 | 73.4797 | 83.4195 | 93.3592 | 103.2989 | 113.2387 | 113.0417 | 112.8448 | 112.6479 | 112.4509 | 112.254 | 114.7673 | 117.2805 | 119.7938 | 122.3071 | 124.8203 | 127.3336 | 129.8469 | 132.3601 | 134.8734 | 137.3867 | 139.0622 | 140.7377 | 142.4132 | 144.0887 | 145.7642 | 147.4397 | 149.1152 | 150.7908 | 152.4663 | 154.1418 | 155.8173 | 157.4928 | 159.1683 | 160.8438 | 162.5193 | 164.0348 | 165.5502 | 167.0656 | 168.581 | 170.0964 | 171.6119 | 173.1273 | 174.6427 | 176.1581 | 177.6736 | 179.189 | 180.7044 | 182.2198 | 183.7352 | 185.2507 | 185.726 | 186.2013 | 186.6766 | 187.1519 | 187.6272 | 188.1025 | 188.5778 | 189.0532 | 189.5285 | 190.0038 | 190.4791 | 190.9544 | 191.4297 | 191.905 | 192.3803 | 192.8556 | 193.331 | 193.8063 | 194.2816 | 194.7569 | 195.2322 | 195.7075 | 196.1828 | 196.6581 | 197.1334 | 197.6088 | 198.0841 | 198.5594 | 199.0347 | 199.51 | 199.7124 | 199.9147 | 200.1171 | 200.3194 | 200.5218 | 200.7241 | 200.9265 | 201.1288 | 201.3312 | 201.5336 | 201.7359 | 201.9383 | 202.1406 | 202.343 | 202.5453 | 202.7477 | 202.95 | 203.1524 | 203.3548 | 203.5571 | 203.7595 | 203.9618 | 204.1642 | 204.3665 | 204.5689 | 204.7712 | 204.9736 | 205.176 | 205.3783 | 205.5807 | 205.5807 | 205.5807 | 205.5807 | 205.5807 | 205.5807 | 205.5807 | 205.5807 | 205.5807 | 205.5807 | 205.5807 | 205.5807 | 205.5807 | 205.5807 | 205.5807 | 205.5807 | 205.5807 | 205.5807 | 205.5807 | 205.5807 | 205.5807 | 205.5807 | 205.5807 | 205.5807 | 205.5807 | 205.5807 | 205.5807 | 205.5807 | 205.5807 | 205.5807 | 205.5807 | 205.5523 | 205.524 | 205.4957 | 205.4673 | 205.439 | 205.4107 | 205.3823 | 205.354 | 205.3257 | 205.2973 | 205.269 | 205.2407 | 205.2123 | 205.184 | 205.1557 | 205.1273 | 205.099 | 205.0707 | 205.0423 | 205.014 | 204.9857 | 204.9573 | 204.929 | 204.9007 | 204.8723 | 204.844 | 204.8157 | 204.7873 | 204.759 | 204.7307
14.35 | 0 | 63.93 | 113.974 | 112.943 | 138.24 | 163.537 | 186.428 | 200.795 | 206.913 | 206.913 | 206.088 | 3.5527e-15 | 6.393 | 12.786 | 19.179 | 25.572 | 31.965 | 38.358 | 44.751 | 51.144 | 57.537 | 63.93 | 73.9388 | 83.9476 | 93.9564 | 103.9652 | 113.974 | 113.7678 | 113.5616 | 113.3554 | 113.1492 | 112.943 | 115.4727 | 118.0024 | 120.5321 | 123.0618 | 125.5915 | 128.1212 | 130.6509 | 133.1806 | 135.7103 | 138.24 | 139.9265 | 141.6129 | 143.2994 | 144.9859 | 146.6723 | 148.3588 | 150.0453 | 151.7317 | 153.4182 | 155.1047 | 156.7911 | 158.4776 | 160.1641 | 161.8505 | 163.537 | 165.0631 | 166.5891 | 168.1152 | 169.6413 | 171.1673 | 172.6934 | 174.2195 | 175.7455 | 177.2716 | 178.7977 | 180.3237 | 181.8498 | 183.3759 | 184.9019 | 186.428 | 186.9069 | 187.3858 | 187.8647 | 188.3436 | 188.8225 | 189.3014 | 189.7803 | 190.2592 | 190.7381 | 191.217 | 191.6959 | 192.1748 | 192.6537 | 193.1326 | 193.6115 | 194.0904 | 194.5693 | 195.0482 | 195.5271 | 196.006 | 196.4849 | 196.9638 | 197.4427 | 197.9216 | 198.4005 | 198.8794 | 199.3583 | 199.8372 | 200.3161 | 200.795 | 200.9989 | 201.2029 | 201.4068 | 201.6107 | 201.8147 | 202.0186 | 202.2225 | 202.4265 | 202.6304 | 202.8343 | 203.0383 | 203.2422 | 203.4461 | 203.6501 | 203.854 | 204.0579 | 204.2619 | 204.4658 | 204.6697 | 204.8737 | 205.0776 | 205.2815 | 205.4855 | 205.6894 | 205.8933 | 206.0973 | 206.3012 | 206.5051 | 206.7091 | 206.913 | 206.913 | 206.913 | 206.913 | 206.913 | 206.913 | 206.913 | 206.913 | 206.913 | 206.913 | 206.913 | 206.913 | 206.913 | 206.913 | 206.913 | 206.913 | 206.913 | 206.913 | 206.913 | 206.913 | 206.913 | 206.913 | 206.913 | 206.913 | 206.913 | 206.913 | 206.913 | 206.913 | 206.913 | 206.913 | 206.913 | 206.8855 | 206.858 | 206.8305 | 206.803 | 206.7755 | 206.748 | 206.7205 | 206.693 | 206.6655 | 206.638 | 206.6105 | 206.583 | 206.5555 | 206.528 | 206.5005 | 206.473 | 206.4455 | 206.418 | 206.3905 | 206.363 | 206.3355 | 206.308 | 206.2805 | 206.253 | 206.2255 | 206.198 | 206.1705 | 206.143 | 206.1155 | 206.088
14.4 | 0 | 64.32 | 114.7093 | 113.632 | 139.0933 | 164.5547 | 187.6053 | 202.08 | 208.2453 | 208.2453 | 207.4453 | 0 | 6.432 | 12.864 | 19.296 | 25.728 | 32.16 | 38.592 | 45.024 | 51.456 | 57.888 | 64.32 | 74.3979 | 84.4757 | 94.5536 | 104.6315 | 114.7093 | 114.4939 | 114.2784 | 114.0629 | 113.8475 | 113.632 | 116.1781 | 118.7243 | 121.2704 | 123.8165 | 126.3627 | 128.9088 | 131.4549 | 134.0011 | 136.5472 | 139.0933 | 140.7908 | 142.4882 | 144.1856 | 145.883 | 147.5804 | 149.2779 | 150.9753 | 152.6727 | 154.3701 | 156.0676 | 157.765 | 159.4624 | 161.1598 | 162.8572 | 164.5547 | 166.0914 | 167.6281 | 169.1648 | 170.7015 | 172.2382 | 173.7749 | 175.3116 | 176.8484 | 178.3851 | 179.9218 | 181.4585 | 182.9952 | 184.5319 | 186.0686 | 187.6053 | 188.0878 | 188.5703 | 189.0528 | 189.5353 | 190.0178 | 190.5003 | 190.9828 | 191.4652 | 191.9477 | 192.4302 | 192.9127 | 193.3952 | 193.8777 | 194.3602 | 194.8427 | 195.3252 | 195.8076 | 196.2901 | 196.7726 | 197.2551 | 197.7376 | 198.2201 | 198.7026 | 199.1851 | 199.6676 | 200.15 | 200.6325 | 201.115 | 201.5975 | 202.08 | 202.2855 | 202.491 | 202.6965 | 202.902 | 203.1076 | 203.3131 | 203.5186 | 203.7241 | 203.9296 | 204.1351 | 204.3406 | 204.5461 | 204.7516 | 204.9572 | 205.1627 | 205.3682 | 205.5737 | 205.7792 | 205.9847 | 206.1902 | 206.3957 | 206.6012 | 206.8068 | 207.0123 | 207.2178 | 207.4233 | 207.6288 | 207.8343 | 208.0398 | 208.2453 | 208.2453 | 208.2453 | 208.2453 | 208.2453 | 208.2453 | 208.2453 | 208.2453 | 208.2453 | 208.2453 | 208.2453 | 208.2453 | 208.2453 | 208.2453 | 208.2453 | 208.2453 | 208.2453 | 208.2453 | 208.2453 | 208.2453 | 208.2453 | 208.2453 | 208.2453 | 208.2453 | 208.2453 | 208.2453 | 208.2453 | 208.2453 | 208.2453 | 208.2453 | 208.2453 | 208.2187 | 208.192 | 208.1653 | 208.1387 | 208.112 | 208.0853 | 208.0587 | 208.032 | 208.0053 | 207.9787 | 207.952 | 207.9253 | 207.8987 | 207.872 | 207.8453 | 207.8187 | 207.792 | 207.7653 | 207.7387 | 207.712 | 207.6853 | 207.6587 | 207.632 | 207.6053 | 207.5787 | 207.552 | 207.5253 | 207.4987 | 207.472 | 207.4453
14.45 | 0 | 64.71 | 115.4447 | 114.321 | 139.9467 | 165.5723 | 188.7827 | 203.365 | 209.5777 | 209.5777 | 208.8027 | 0 | 6.471 | 12.942 | 19.413 | 25.884 | 32.355 | 38.826 | 45.297 | 51.768 | 58.239 | 64.71 | 74.8569 | 85.0039 | 95.1508 | 105.2977 | 115.4447 | 115.2199 | 114.9952 | 114.7705 | 114.5457 | 114.321 | 116.8836 | 119.4461 | 122.0087 | 124.5713 | 127.1338 | 129.6964 | 132.259 | 134.8215 | 137.3841 | 139.9467 | 141.655 | 143.3634 | 145.0718 | 146.7802 | 148.4886 | 150.1969 | 151.9053 | 153.6137 | 155.3221 | 157.0304 | 158.7388 | 160.4472 | 162.1556 | 163.864 | 165.5723 | 167.1197 | 168.667 | 170.2144 | 171.7618 | 173.3091 | 174.8565 | 176.4038 | 177.9512 | 179.4985 | 181.0459 | 182.5932 | 184.1406 | 185.688 | 187.2353 | 188.7827 | 189.2687 | 189.7548 | 190.2409 | 190.727 | 191.2131 | 191.6991 | 192.1852 | 192.6713 | 193.1574 | 193.6434 | 194.1295 | 194.6156 | 195.1017 | 195.5878 | 196.0738 | 196.5599 | 197.046 | 197.5321 | 198.0181 | 198.5042 | 198.9903 | 199.4764 | 199.9625 | 200.4485 | 200.9346 | 201.4207 | 201.9068 | 202.3928 | 202.8789 | 203.365 | 203.5721 | 203.7792 | 203.9863 | 204.1934 | 204.4004 | 204.6075 | 204.8146 | 205.0217 | 205.2288 | 205.4359 | 205.643 | 205.8501 | 206.0572 | 206.2642 | 206.4713 | 206.6784 | 206.8855 | 207.0926 | 207.2997 | 207.5068 | 207.7139 | 207.921 | 208.128 | 208.3351 | 208.5422 | 208.7493 | 208.9564 | 209.1635 | 209.3706 | 209.5777 | 209.5777 | 209.5777 | 209.5777 | 209.5777 | 209.5777 | 209.5777 | 209.5777 | 209.5777 | 209.5777 | 209.5777 | 209.5777 | 209.5777 | 209.5777 | 209.5777 | 209.5777 | 209.5777 | 209.5777 | 209.5777 | 209.5777 | 209.5777 | 209.5777 | 209.5777 | 209.5777 | 209.5777 | 209.5777 | 209.5777 | 209.5777 | 209.5777 | 209.5777 | 209.5777 | 209.5518 | 209.526 | 209.5002 | 209.4743 | 209.4485 | 209.4227 | 209.3968 | 209.371 | 209.3452 | 209.3193 | 209.2935 | 209.2677 | 209.2418 | 209.216 | 209.1902 | 209.1643 | 209.1385 | 209.1127 | 209.0868 | 209.061 | 209.0352 | 209.0093 | 208.9835 | 208.9577 | 208.9318 | 208.906 | 208.8802 | 208.8543 | 208.8285 | 208.8027
14.5 | 0 | 65.1 | 116.18 | 115.01 | 140.8 | 166.59 | 189.96 | 204.65 | 210.91 | 210.91 | 210.16 | 0 | 6.51 | 13.02 | 19.53 | 26.04 | 32.55 | 39.06 | 45.57 | 52.08 | 58.59 | 65.1 | 75.316 | 85.532 | 95.748 | 105.964 | 116.18 | 115.946 | 115.712 | 115.478 | 115.244 | 115.01 | 117.589 | 120.168 | 122.747 | 125.326 | 127.905 | 130.484 | 133.063 | 135.642 | 138.221 | 140.8 | 142.5193 | 144.2387 | 145.958 | 147.6773 | 149.3967 | 151.116 | 152.8353 | 154.5547 | 156.274 | 157.9933 | 159.7127 | 161.432 | 163.1513 | 164.8707 | 166.59 | 168.148 | 169.706 | 171.264 | 172.822 | 174.38 | 175.938 | 177.496 | 179.054 | 180.612 | 182.17 | 183.728 | 185.286 | 186.844 | 188.402 | 189.96 | 190.4497 | 190.9393 | 191.429 | 191.9187 | 192.4083 | 192.898 | 193.3877 | 193.8773 | 194.367 | 194.8567 | 195.3463 | 195.836 | 196.3257 | 196.8153 | 197.305 | 197.7947 | 198.2843 | 198.774 | 199.2637 | 199.7533 | 200.243 | 200.7327 | 201.2223 | 201.712 | 202.2017 | 202.6913 | 203.181 | 203.6707 | 204.1603 | 204.65 | 204.8587 | 205.0673 | 205.276 | 205.4847 | 205.6933 | 205.902 | 206.1107 | 206.3193 | 206.528 | 206.7367 | 206.9453 | 207.154 | 207.3627 | 207.5713 | 207.78 | 207.9887 | 208.1973 | 208.406 | 208.6147 | 208.8233 | 209.032 | 209.2407 | 209.4493 | 209.658 | 209.8667 | 210.0753 | 210.284 | 210.4927 | 210.7013 | 210.91 | 210.91 | 210.91 | 210.91 | 210.91 | 210.91 | 210.91 | 210.91 | 210.91 | 210.91 | 210.91 | 210.91 | 210.91 | 210.91 | 210.91 | 210.91 | 210.91 | 210.91 | 210.91 | 210.91 | 210.91 | 210.91 | 210.91 | 210.91 | 210.91 | 210.91 | 210.91 | 210.91 | 210.91 | 210.91 | 210.91 | 210.885 | 210.86 | 210.835 | 210.81 | 210.785 | 210.76 | 210.735 | 210.71 | 210.685 | 210.66 | 210.635 | 210.61 | 210.585 | 210.56 | 210.535 | 210.51 | 210.485 | 210.46 | 210.435 | 210.41 | 210.385 | 210.36 | 210.335 | 210.31 | 210.285 | 210.26 | 210.235 | 210.21 | 210.185 | 210.16
14.55 | 0 | 65.49 | 116.9153 | 115.699 | 141.6533 | 167.6077 | 191.1373 | 205.935 | 212.2423 | 212.2423 | 211.5173 | 0 | 6.549 | 13.098 | 19.647 | 26.196 | 32.745 | 39.294 | 45.843 | 52.392 | 58.941 | 65.49 | 75.7751 | 86.0601 | 96.3452 | 106.6303 | 116.9153 | 116.6721 | 116.4288 | 116.1855 | 115.9423 | 115.699 | 118.2944 | 120.8899 | 123.4853 | 126.0807 | 128.6762 | 131.2716 | 133.867 | 136.4625 | 139.0579 | 141.6533 | 143.3836 | 145.1139 | 146.8442 | 148.5745 | 150.3048 | 152.0351 | 153.7654 | 155.4956 | 157.2259 | 158.9562 | 160.6865 | 162.4168 | 164.1471 | 165.8774 | 167.6077 | 169.1763 | 170.745 | 172.3136 | 173.8822 | 175.4509 | 177.0195 | 178.5882 | 180.1568 | 181.7255 | 183.2941 | 184.8628 | 186.4314 | 188 | 189.5687 | 191.1373 | 191.6306 | 192.1238 | 192.6171 | 193.1104 | 193.6036 | 194.0969 | 194.5901 | 195.0834 | 195.5766 | 196.0699 | 196.5631 | 197.0564 | 197.5497 | 198.0429 | 198.5362 | 199.0294 | 199.5227 | 200.0159 | 200.5092 | 201.0024 | 201.4957 | 201.989 | 202.4822 | 202.9755 | 203.4687 | 203.962 | 204.4552 | 204.9485 | 205.4417 | 205.935 | 206.1452 | 206.3555 | 206.5657 | 206.776 | 206.9862 | 207.1965 | 207.4067 | 207.617 | 207.8272 | 208.0374 | 208.2477 | 208.4579 | 208.6682 | 208.8784 | 209.0887 | 209.2989 | 209.5092 | 209.7194 | 209.9296 | 210.1399 | 210.3501 | 210.5604 | 210.7706 | 210.9809 | 211.1911 | 211.4014 | 211.6116 | 211.8218 | 212.0321 | 212.2423 | 212.2423 | 212.2423 | 212.2423 | 212.2423 | 212.2423 | 212.2423 | 212.2423 | 212.2423 | 212.2423 | 212.2423 | 212.2423 | 212.2423 | 212.2423 | 212.2423 | 212.2423 | 212.2423 | 212.2423 | 212.2423 | 212.2423 | 212.2423 | 212.2423 | 212.2423 | 212.2423 | 212.2423 | 212.2423 | 212.2423 | 212.2423 | 212.2423 | 212.2423 | 212.2423 | 212.2182 | 212.194 | 212.1698 | 212.1457 | 212.1215 | 212.0973 | 212.0732 | 212.049 | 212.0248 | 212.0007 | 211.9765 | 211.9523 | 211.9282 | 211.904 | 211.8798 | 211.8557 | 211.8315 | 211.8073 | 211.7832 | 211.759 | 211.7348 | 211.7107 | 211.6865 | 211.6623 | 211.6382 | 211.614 | 211.5898 | 211.5657 | 211.5415 | 211.5173
14.6 | 0 | 65.88 | 117.6507 | 116.388 | 142.5067 | 168.6253 | 192.3147 | 207.22 | 213.5747 | 213.5747 | 212.8747 | 0 | 6.588 | 13.176 | 19.764 | 26.352 | 32.94 | 39.528 | 46.116 | 52.704 | 59.292 | 65.88 | 76.2341 | 86.5883 | 96.9424 | 107.2965 | 117.6507 | 117.3981 | 117.1456 | 116.8931 | 116.6405 | 116.388 | 118.9999 | 121.6117 | 124.2236 | 126.8355 | 129.4473 | 132.0592 | 134.6711 | 137.2829 | 139.8948 | 142.5067 | 144.2479 | 145.9892 | 147.7304 | 149.4716 | 151.2129 | 152.9541 | 154.6954 | 156.4366 | 158.1779 | 159.9191 | 161.6604 | 163.4016 | 165.1428 | 166.8841 | 168.6253 | 170.2046 | 171.7839 | 173.3632 | 174.9425 | 176.5218 | 178.1011 | 179.6804 | 181.2596 | 182.8389 | 184.4182 | 185.9975 | 187.5768 | 189.1561 | 190.7354 | 192.3147 | 192.8115 | 193.3084 | 193.8052 | 194.302 | 194.7989 | 195.2957 | 195.7926 | 196.2894 | 196.7863 | 197.2831 | 197.78 | 198.2768 | 198.7736 | 199.2705 | 199.7673 | 200.2642 | 200.761 | 201.2579 | 201.7547 | 202.2516 | 202.7484 | 203.2452 | 203.7421 | 204.2389 | 204.7358 | 205.2326 | 205.7295 | 206.2263 | 206.7232 | 207.22 | 207.4318 | 207.6436 | 207.8555 | 208.0673 | 208.2791 | 208.4909 | 208.7028 | 208.9146 | 209.1264 | 209.3382 | 209.55 | 209.7619 | 209.9737 | 210.1855 | 210.3973 | 210.6092 | 210.821 | 211.0328 | 211.2446 | 211.4564 | 211.6683 | 211.8801 | 212.0919 | 212.3037 | 212.5156 | 212.7274 | 212.9392 | 213.151 | 213.3628 | 213.5747 | 213.5747 | 213.5747 | 213.5747 | 213.5747 | 213.5747 | 213.5747 | 213.5747 | 213.5747 | 213.5747 | 213.5747 | 213.5747 | 213.5747 | 213.5747 | 213.5747 | 213.5747 | 213.5747 | 213.5747 | 213.5747 | 213.5747 | 213.5747 | 213.5747 | 213.5747 | 213.5747 | 213.5747 | 213.5747 | 213.5747 | 213.5747 | 213.5747 | 213.5747 | 213.5747 | 213.5513 | 213.528 | 213.5047 | 213.4813 | 213.458 | 213.4347 | 213.4113 | 213.388 | 213.3647 | 213.3413 | 213.318 | 213.2947 | 213.2713 | 213.248 | 213.2247 | 213.2013 | 213.178 | 213.1547 | 213.1313 | 213.108 | 213.0847 | 213.0613 | 213.038 | 213.0147 | 212.9913 | 212.968 | 212.9447 | 212.9213 | 212.898 | 212.8747
14.65 | 0 | 66.27 | 118.386 | 117.077 | 143.36 | 169.643 | 193.492 | 208.505 | 214.907 | 214.907 | 214.232 | 0 | 6.627 | 13.254 | 19.881 | 26.508 | 33.135 | 39.762 | 46.389 | 53.016 | 59.643 | 66.27 | 76.6932 | 87.1164 | 97.5396 | 107.9628 | 118.386 | 118.1242 | 117.8624 | 117.6006 | 117.3388 | 117.077 | 119.7053 | 122.3336 | 124.9619 | 127.5902 | 130.2185 | 132.8468 | 135.4751 | 138.1034 | 140.7317 | 143.36 | 145.1122 | 146.8644 | 148.6166 | 150.3688 | 152.121 | 153.8732 | 155.6254 | 157.3776 | 159.1298 | 160.882 | 162.6342 | 164.3864 | 166.1386 | 167.8908 | 169.643 | 171.2329 | 172.8229 | 174.4128 | 176.0027 | 177.5927 | 179.1826 | 180.7725 | 182.3625 | 183.9524 | 185.5423 | 187.1323 | 188.7222 | 190.3121 | 191.9021 | 193.492 | 193.9924 | 194.4929 | 194.9933 | 195.4937 | 195.9942 | 196.4946 | 196.995 | 197.4955 | 197.9959 | 198.4963 | 198.9968 | 199.4972 | 199.9976 | 200.4981 | 200.9985 | 201.4989 | 201.9994 | 202.4998 | 203.0002 | 203.5007 | 204.0011 | 204.5015 | 205.002 | 205.5024 | 206.0028 | 206.5033 | 207.0037 | 207.5041 | 208.0046 | 208.505 | 208.7184 | 208.9318 | 209.1452 | 209.3586 | 209.572 | 209.7854 | 209.9988 | 210.2122 | 210.4256 | 210.639 | 210.8524 | 211.0658 | 211.2792 | 211.4926 | 211.706 | 211.9194 | 212.1328 | 212.3462 | 212.5596 | 212.773 | 212.9864 | 213.1998 | 213.4132 | 213.6266 | 213.84 | 214.0534 | 214.2668 | 214.4802 | 214.6936 | 214.907 | 214.907 | 214.907 | 214.907 | 214.907 | 214.907 | 214.907 | 214.907 | 214.907 | 214.907 | 214.907 | 214.907 | 214.907 | 214.907 | 214.907 | 214.907 | 214.907 | 214.907 | 214.907 | 214.907 | 214.907 | 214.907 | 214.907 | 214.907 | 214.907 | 214.907 | 214.907 | 214.907 | 214.907 | 214.907 | 214.907 | 214.8845 | 214.862 | 214.8395 | 214.817 | 214.7945 | 214.772 | 214.7495 | 214.727 | 214.7045 | 214.682 | 214.6595 | 214.637 | 214.6145 | 214.592 | 214.5695 | 214.547 | 214.5245 | 214.502 | 214.4795 | 214.457 | 214.4345 | 214.412 | 214.3895 | 214.367 | 214.3445 | 214.322 | 214.2995 | 214.277 | 214.2545 | 214.232
14.7 | 0 | 66.66 | 119.1213 | 117.766 | 144.2133 | 170.6607 | 194.6693 | 209.79 | 216.2393 | 216.2393 | 215.5893 | 0 | 6.666 | 13.332 | 19.998 | 26.664 | 33.33 | 39.996 | 46.662 | 53.328 | 59.994 | 66.66 | 77.1523 | 87.6445 | 98.1368 | 108.6291 | 119.1213 | 118.8503 | 118.5792 | 118.3081 | 118.0371 | 117.766 | 120.4107 | 123.0555 | 125.7002 | 128.3449 | 130.9897 | 133.6344 | 136.2791 | 138.9239 | 141.5686 | 144.2133 | 145.9765 | 147.7396 | 149.5028 | 151.266 | 153.0291 | 154.7923 | 156.5554 | 158.3186 | 160.0817 | 161.8449 | 163.608 | 165.3712 | 167.1344 | 168.8975 | 170.6607 | 172.2612 | 173.8618 | 175.4624 | 177.063 | 178.6636 | 180.2641 | 181.8647 | 183.4653 | 185.0659 | 186.6664 | 188.267 | 189.8676 | 191.4682 | 193.0688 | 194.6693 | 195.1734 | 195.6774 | 196.1814 | 196.6854 | 197.1894 | 197.6935 | 198.1975 | 198.7015 | 199.2055 | 199.7096 | 200.2136 | 200.7176 | 201.2216 | 201.7256 | 202.2297 | 202.7337 | 203.2377 | 203.7417 | 204.2458 | 204.7498 | 205.2538 | 205.7578 | 206.2618 | 206.7659 | 207.2699 | 207.7739 | 208.2779 | 208.782 | 209.286 | 209.79 | 210.005 | 210.22 | 210.4349 | 210.6499 | 210.8649 | 211.0799 | 211.2948 | 211.5098 | 211.7248 | 211.9398 | 212.1548 | 212.3697 | 212.5847 | 212.7997 | 213.0147 | 213.2296 | 213.4446 | 213.6596 | 213.8746 | 214.0896 | 214.3045 | 214.5195 | 214.7345 | 214.9495 | 215.1644 | 215.3794 | 215.5944 | 215.8094 | 216.0244 | 216.2393 | 216.2393 | 216.2393 | 216.2393 | 216.2393 | 216.2393 | 216.2393 | 216.2393 | 216.2393 | 216.2393 | 216.2393 | 216.2393 | 216.2393 | 216.2393 | 216.2393 | 216.2393 | 216.2393 | 216.2393 | 216.2393 | 216.2393 | 216.2393 | 216.2393 | 216.2393 | 216.2393 | 216.2393 | 216.2393 | 216.2393 | 216.2393 | 216.2393 | 216.2393 | 216.2393 | 216.2177 | 216.196 | 216.1743 | 216.1527 | 216.131 | 216.1093 | 216.0877 | 216.066 | 216.0443 | 216.0227 | 216.001 | 215.9793 | 215.9577 | 215.936 | 215.9143 | 215.8927 | 215.871 | 215.8493 | 215.8277 | 215.806 | 215.7843 | 215.7627 | 215.741 | 215.7193 | 215.6977 | 215.676 | 215.6543 | 215.6327 | 215.611 | 215.5893
14.75 | 0 | 67.05 | 119.8567 | 118.455 | 145.0667 | 171.6783 | 195.8467 | 211.075 | 217.5717 | 217.5717 | 216.9467 | 7.1054e-15 | 6.705 | 13.41 | 20.115 | 26.82 | 33.525 | 40.23 | 46.935 | 53.64 | 60.345 | 67.05 | 77.6113 | 88.1727 | 98.734 | 109.2953 | 119.8567 | 119.5763 | 119.296 | 119.0157 | 118.7353 | 118.455 | 121.1162 | 123.7773 | 126.4385 | 129.0997 | 131.7608 | 134.422 | 137.0832 | 139.7443 | 142.4055 | 145.0667 | 146.8408 | 148.6149 | 150.389 | 152.1631 | 153.9372 | 155.7113 | 157.4854 | 159.2596 | 161.0337 | 162.8078 | 164.5819 | 166.356 | 168.1301 | 169.9042 | 171.6783 | 173.2896 | 174.9008 | 176.512 | 178.1232 | 179.7344 | 181.3457 | 182.9569 | 184.5681 | 186.1793 | 187.7906 | 189.4018 | 191.013 | 192.6242 | 194.2354 | 195.8467 | 196.3543 | 196.8619 | 197.3695 | 197.8771 | 198.3847 | 198.8923 | 199.3999 | 199.9076 | 200.4152 | 200.9228 | 201.4304 | 201.938 | 202.4456 | 202.9532 | 203.4608 | 203.9684 | 204.4761 | 204.9837 | 205.4913 | 205.9989 | 206.5065 | 207.0141 | 207.5217 | 208.0293 | 208.5369 | 209.0446 | 209.5522 | 210.0598 | 210.5674 | 211.075 | 211.2916 | 211.5081 | 211.7247 | 211.9412 | 212.1578 | 212.3743 | 212.5909 | 212.8074 | 213.024 | 213.2406 | 213.4571 | 213.6737 | 213.8902 | 214.1068 | 214.3233 | 214.5399 | 214.7564 | 214.973 | 215.1896 | 215.4061 | 215.6227 | 215.8392 | 216.0558 | 216.2723 | 216.4889 | 216.7054 | 216.922 | 217.1386 | 217.3551 | 217.5717 | 217.5717 | 217.5717 | 217.5717 | 217.5717 | 217.5717 | 217.5717 | 217.5717 | 217.5717 | 217.5717 | 217.5717 | 217.5717 | 217.5717 | 217.5717 | 217.5717 | 217.5717 | 217.5717 | 217.5717 | 217.5717 | 217.5717 | 217.5717 | 217.5717 | 217.5717 | 217.5717 | 217.5717 | 217.5717 | 217.5717 | 217.5717 | 217.5717 | 217.5717 | 217.5717 | 217.5508 | 217.53 | 217.5092 | 217.4883 | 217.4675 | 217.4467 | 217.4258 | 217.405 | 217.3842 | 217.3633 | 217.3425 | 217.3217 | 217.3008 | 217.28 | 217.2592 | 217.2383 | 217.2175 | 217.1967 | 217.1758 | 217.155 | 217.1342 | 217.1133 | 217.0925 | 217.0717 | 217.0508 | 217.03 | 217.0092 | 216.9883 | 216.9675 | 216.9467
14.8 | 0 | 67.44 | 120.592 | 119.144 | 145.92 | 172.696 | 197.024 | 212.36 | 218.904 | 218.904 | 218.304 | 0 | 6.744 | 13.488 | 20.232 | 26.976 | 33.72 | 40.464 | 47.208 | 53.952 | 60.696 | 67.44 | 78.0704 | 88.7008 | 99.3312 | 109.9616 | 120.592 | 120.3024 | 120.0128 | 119.7232 | 119.4336 | 119.144 | 121.8216 | 124.4992 | 127.1768 | 129.8544 | 132.532 | 135.2096 | 137.8872 | 140.5648 | 143.2424 | 145.92 | 147.7051 | 149.4901 | 151.2752 | 153.0603 | 154.8453 | 156.6304 | 158.4155 | 160.2005 | 161.9856 | 163.7707 | 165.5557 | 167.3408 | 169.1259 | 170.9109 | 172.696 | 174.3179 | 175.9397 | 177.5616 | 179.1835 | 180.8053 | 182.4272 | 184.0491 | 185.6709 | 187.2928 | 188.9147 | 190.5365 | 192.1584 | 193.7803 | 195.4021 | 197.024 | 197.5352 | 198.0464 | 198.5576 | 199.0688 | 199.58 | 200.0912 | 200.6024 | 201.1136 | 201.6248 | 202.136 | 202.6472 | 203.1584 | 203.6696 | 204.1808 | 204.692 | 205.2032 | 205.7144 | 206.2256 | 206.7368 | 207.248 | 207.7592 | 208.2704 | 208.7816 | 209.2928 | 209.804 | 210.3152 | 210.8264 | 211.3376 | 211.8488 | 212.36 | 212.5781 | 212.7963 | 213.0144 | 213.2325 | 213.4507 | 213.6688 | 213.8869 | 214.1051 | 214.3232 | 214.5413 | 214.7595 | 214.9776 | 215.1957 | 215.4139 | 215.632 | 215.8501 | 216.0683 | 216.2864 | 216.5045 | 216.7227 | 216.9408 | 217.1589 | 217.3771 | 217.5952 | 217.8133 | 218.0315 | 218.2496 | 218.4677 | 218.6859 | 218.904 | 218.904 | 218.904 | 218.904 | 218.904 | 218.904 | 218.904 | 218.904 | 218.904 | 218.904 | 218.904 | 218.904 | 218.904 | 218.904 | 218.904 | 218.904 | 218.904 | 218.904 | 218.904 | 218.904 | 218.904 | 218.904 | 218.904 | 218.904 | 218.904 | 218.904 | 218.904 | 218.904 | 218.904 | 218.904 | 218.904 | 218.884 | 218.864 | 218.844 | 218.824 | 218.804 | 218.784 | 218.764 | 218.744 | 218.724 | 218.704 | 218.684 | 218.664 | 218.644 | 218.624 | 218.604 | 218.584 | 218.564 | 218.544 | 218.524 | 218.504 | 218.484 | 218.464 | 218.444 | 218.424 | 218.404 | 218.384 | 218.364 | 218.344 | 218.324 | 218.304
14.85 | 0 | 67.83 | 121.3273 | 119.833 | 146.7733 | 173.7137 | 198.2013 | 213.645 | 220.2363 | 220.2363 | 219.6613 | 0 | 6.783 | 13.566 | 20.349 | 27.132 | 33.915 | 40.698 | 47.481 | 54.264 | 61.047 | 67.83 | 78.5295 | 89.2289 | 99.9284 | 110.6279 | 121.3273 | 121.0285 | 120.7296 | 120.4307 | 120.1319 | 119.833 | 122.527 | 125.2211 | 127.9151 | 130.6091 | 133.3032 | 135.9972 | 138.6912 | 141.3853 | 144.0793 | 146.7733 | 148.5694 | 150.3654 | 152.1614 | 153.9574 | 155.7534 | 157.5495 | 159.3455 | 161.1415 | 162.9375 | 164.7336 | 166.5296 | 168.3256 | 170.1216 | 171.9176 | 173.7137 | 175.3462 | 176.9787 | 178.6112 | 180.2437 | 181.8762 | 183.5087 | 185.1412 | 186.7738 | 188.4063 | 190.0388 | 191.6713 | 193.3038 | 194.9363 | 196.5688 | 198.2013 | 198.7161 | 199.2309 | 199.7457 | 200.2605 | 200.7753 | 201.2901 | 201.8049 | 202.3196 | 202.8344 | 203.3492 | 203.864 | 204.3788 | 204.8936 | 205.4084 | 205.9232 | 206.438 | 206.9527 | 207.4675 | 207.9823 | 208.4971 | 209.0119 | 209.5267 | 210.0415 | 210.5563 | 211.0711 | 211.5858 | 212.1006 | 212.6154 | 213.1302 | 213.645 | 213.8647 | 214.0844 | 214.3041 | 214.5238 | 214.7436 | 214.9633 | 215.183 | 215.4027 | 215.6224 | 215.8421 | 216.0618 | 216.2815 | 216.5012 | 216.721 | 216.9407 | 217.1604 | 217.3801 | 217.5998 | 217.8195 | 218.0392 | 218.2589 | 218.4786 | 218.6984 | 218.9181 | 219.1378 | 219.3575 | 219.5772 | 219.7969 | 220.0166 | 220.2363 | 220.2363 | 220.2363 | 220.2363 | 220.2363 | 220.2363 | 220.2363 | 220.2363 | 220.2363 | 220.2363 | 220.2363 | 220.2363 | 220.2363 | 220.2363 | 220.2363 | 220.2363 | 220.2363 | 220.2363 | 220.2363 | 220.2363 | 220.2363 | 220.2363 | 220.2363 | 220.2363 | 220.2363 | 220.2363 | 220.2363 | 220.2363 | 220.2363 | 220.2363 | 220.2363 | 220.2172 | 220.198 | 220.1788 | 220.1597 | 220.1405 | 220.1213 | 220.1022 | 220.083 | 220.0638 | 220.0447 | 220.0255 | 220.0063 | 219.9872 | 219.968 | 219.9488 | 219.9297 | 219.9105 | 219.8913 | 219.8722 | 219.853 | 219.8338 | 219.8147 | 219.7955 | 219.7763 | 219.7572 | 219.738 | 219.7188 | 219.6997 | 219.6805 | 219.6613
14.9 | 0 | 68.22 | 122.0627 | 120.522 | 147.6267 | 174.7313 | 199.3787 | 214.93 | 221.5687 | 221.5687 | 221.0187 | 0 | 6.822 | 13.644 | 20.466 | 27.288 | 34.11 | 40.932 | 47.754 | 54.576 | 61.398 | 68.22 | 78.9885 | 89.7571 | 100.5256 | 111.2941 | 122.0627 | 121.7545 | 121.4464 | 121.1383 | 120.8301 | 120.522 | 123.2325 | 125.9429 | 128.6534 | 131.3639 | 134.0743 | 136.7848 | 139.4953 | 142.2057 | 144.9162 | 147.6267 | 149.4336 | 151.2406 | 153.0476 | 154.8546 | 156.6616 | 158.4685 | 160.2755 | 162.0825 | 163.8895 | 165.6964 | 167.5034 | 169.3104 | 171.1174 | 172.9244 | 174.7313 | 176.3745 | 178.0176 | 179.6608 | 181.304 | 182.9471 | 184.5903 | 186.2334 | 187.8766 | 189.5197 | 191.1629 | 192.806 | 194.4492 | 196.0924 | 197.7355 | 199.3787 | 199.897 | 200.4154 | 200.9338 | 201.4522 | 201.9706 | 202.4889 | 203.0073 | 203.5257 | 204.0441 | 204.5624 | 205.0808 | 205.5992 | 206.1176 | 206.636 | 207.1543 | 207.6727 | 208.1911 | 208.7095 | 209.2278 | 209.7462 | 210.2646 | 210.783 | 211.3014 | 211.8197 | 212.3381 | 212.8565 | 213.3749 | 213.8932 | 214.4116 | 214.93 | 215.1513 | 215.3726 | 215.5939 | 215.8152 | 216.0364 | 216.2577 | 216.479 | 216.7003 | 216.9216 | 217.1429 | 217.3642 | 217.5855 | 217.8068 | 218.028 | 218.2493 | 218.4706 | 218.6919 | 218.9132 | 219.1345 | 219.3558 | 219.5771 | 219.7984 | 220.0196 | 220.2409 | 220.4622 | 220.6835 | 220.9048 | 221.1261 | 221.3474 | 221.5687 | 221.5687 | 221.5687 | 221.5687 | 221.5687 | 221.5687 | 221.5687 | 221.5687 | 221.5687 | 221.5687 | 221.5687 | 221.5687 | 221.5687 | 221.5687 | 221.5687 | 221.5687 | 221.5687 | 221.5687 | 221.5687 | 221.5687 | 221.5687 | 221.5687 | 221.5687 | 221.5687 | 221.5687 | 221.5687 | 221.5687 | 221.5687 | 221.5687 | 221.5687 | 221.5687 | 221.5503 | 221.532 | 221.5137 | 221.4953 | 221.477 | 221.4587 | 221.4403 | 221.422 | 221.4037 | 221.3853 | 221.367 | 221.3487 | 221.3303 | 221.312 | 221.2937 | 221.2753 | 221.257 | 221.2387 | 221.2203 | 221.202 | 221.1837 | 221.1653 | 221.147 | 221.1287 | 221.1103 | 221.092 | 221.0737 | 221.0553 | 221.037 | 221.0187
14.95 | 0 | 68.61 | 122.798 | 121.211 | 148.48 | 175.749 | 200.556 | 216.215 | 222.901 | 222.901 | 222.376 | 0 | 6.861 | 13.722 | 20.583 | 27.444 | 34.305 | 41.166 | 48.027 | 54.888 | 61.749 | 68.61 | 79.4476 | 90.2852 | 101.1228 | 111.9604 | 122.798 | 122.4806 | 122.1632 | 121.8458 | 121.5284 | 121.211 | 123.9379 | 126.6648 | 129.3917 | 132.1186 | 134.8455 | 137.5724 | 140.2993 | 143.0262 | 145.7531 | 148.48 | 150.2979 | 152.1159 | 153.9338 | 155.7517 | 157.5697 | 159.3876 | 161.2055 | 163.0235 | 164.8414 | 166.6593 | 168.4773 | 170.2952 | 172.1131 | 173.9311 | 175.749 | 177.4028 | 179.0566 | 180.7104 | 182.3642 | 184.018 | 185.6718 | 187.3256 | 188.9794 | 190.6332 | 192.287 | 193.9408 | 195.5946 | 197.2484 | 198.9022 | 200.556 | 201.078 | 201.5999 | 202.1219 | 202.6439 | 203.1658 | 203.6878 | 204.2098 | 204.7317 | 205.2537 | 205.7757 | 206.2976 | 206.8196 | 207.3416 | 207.8635 | 208.3855 | 208.9075 | 209.4294 | 209.9514 | 210.4734 | 210.9953 | 211.5173 | 212.0393 | 212.5612 | 213.0832 | 213.6052 | 214.1271 | 214.6491 | 215.1711 | 215.693 | 216.215 | 216.4379 | 216.6607 | 216.8836 | 217.1065 | 217.3293 | 217.5522 | 217.7751 | 217.9979 | 218.2208 | 218.4437 | 218.6665 | 218.8894 | 219.1123 | 219.3351 | 219.558 | 219.7809 | 220.0037 | 220.2266 | 220.4495 | 220.6723 | 220.8952 | 221.1181 | 221.3409 | 221.5638 | 221.7867 | 222.0095 | 222.2324 | 222.4553 | 222.6781 | 222.901 | 222.901 | 222.901 | 222.901 | 222.901 | 222.901 | 222.901 | 222.901 | 222.901 | 222.901 | 222.901 | 222.901 | 222.901 | 222.901 | 222.901 | 222.901 | 222.901 | 222.901 | 222.901 | 222.901 | 222.901 | 222.901 | 222.901 | 222.901 | 222.901 | 222.901 | 222.901 | 222.901 | 222.901 | 222.901 | 222.901 | 222.8835 | 222.866 | 222.8485 | 222.831 | 222.8135 | 222.796 | 222.7785 | 222.761 | 222.7435 | 222.726 | 222.7085 | 222.691 | 222.6735 | 222.656 | 222.6385 | 222.621 | 222.6035 | 222.586 | 222.5685 | 222.551 | 222.5335 | 222.516 | 222.4985 | 222.481 | 222.4635 | 222.446 | 222.4285 | 222.411 | 222.3935 | 222.376
15 | 0 | 69 | 123.5333 | 121.9 | 149.3333 | 176.7667 | 201.7333 | 217.5 | 224.2333 | 224.2333 | 223.7333 | 0 | 6.9 | 13.8 | 20.7 | 27.6 | 34.5 | 41.4 | 48.3 | 55.2 | 62.1 | 69 | 79.9067 | 90.8133 | 101.72 | 112.6267 | 123.5333 | 123.2067 | 122.88 | 122.5533 | 122.2267 | 121.9 | 124.6433 | 127.3867 | 130.13 | 132.8733 | 135.6167 | 138.36 | 141.1033 | 143.8467 | 146.59 | 149.3333 | 151.1622 | 152.9911 | 154.82 | 156.6489 | 158.4778 | 160.3067 | 162.1356 | 163.9644 | 165.7933 | 167.6222 | 169.4511 | 171.28 | 173.1089 | 174.9378 | 176.7667 | 178.4311 | 180.0956 | 181.76 | 183.4244 | 185.0889 | 186.7533 | 188.4178 | 190.0822 | 191.7467 | 193.4111 | 195.0756 | 196.74 | 198.4044 | 200.0689 | 201.7333 | 202.2589 | 202.7844 | 203.31 | 203.8356 | 204.3611 | 204.8867 | 205.4122 | 205.9378 | 206.4633 | 206.9889 | 207.5144 | 208.04 | 208.5656 | 209.0911 | 209.6167 | 210.1422 | 210.6678 | 211.1933 | 211.7189 | 212.2444 | 212.77 | 213.2956 | 213.8211 | 214.3467 | 214.8722 | 215.3978 | 215.9233 | 216.4489 | 216.9744 | 217.5 | 217.7244 | 217.9489 | 218.1733 | 218.3978 | 218.6222 | 218.8467 | 219.0711 | 219.2956 | 219.52 | 219.7444 | 219.9689 | 220.1933 | 220.4178 | 220.6422 | 220.8667 | 221.0911 | 221.3156 | 221.54 | 221.7644 | 221.9889 | 222.2133 | 222.4378 | 222.6622 | 222.8867 | 223.1111 | 223.3356 | 223.56 | 223.7844 | 224.0089 | 224.2333 | 224.2333 | 224.2333 | 224.2333 | 224.2333 | 224.2333 | 224.2333 | 224.2333 | 224.2333 | 224.2333 | 224.2333 | 224.2333 | 224.2333 | 224.2333 | 224.2333 | 224.2333 | 224.2333 | 224.2333 | 224.2333 | 224.2333 | 224.2333 | 224.2333 | 224.2333 | 224.2333 | 224.2333 | 224.2333 | 224.2333 | 224.2333 | 224.2333 | 224.2333 | 224.2333 | 224.2167 | 224.2 | 224.1833 | 224.1667 | 224.15 | 224.1333 | 224.1167 | 224.1 | 224.0833 | 224.0667 | 224.05 | 224.0333 | 224.0167 | 224 | 223.9833 | 223.9667 | 223.95 | 223.9333 | 223.9167 | 223.9 | 223.8833 | 223.8667 | 223.85 | 223.8333 | 223.8167 | 223.8 | 223.7833 | 223.7667 | 223.75 | 223.7333
15.05 | 0 | 69.39 | 124.2687 | 122.589 | 150.1867 | 177.7843 | 202.9107 | 218.785 | 225.5657 | 225.5657 | 225.0907 | 0 | 6.939 | 13.878 | 20.817 | 27.756 | 34.695 | 41.634 | 48.573 | 55.512 | 62.451 | 69.39 | 80.3657 | 91.3415 | 102.3172 | 113.2929 | 124.2687 | 123.9327 | 123.5968 | 123.2609 | 122.9249 | 122.589 | 125.3488 | 128.1085 | 130.8683 | 133.6281 | 136.3878 | 139.1476 | 141.9074 | 144.6671 | 147.4269 | 150.1867 | 152.0265 | 153.8664 | 155.7062 | 157.546 | 159.3859 | 161.2257 | 163.0656 | 164.9054 | 166.7453 | 168.5851 | 170.425 | 172.2648 | 174.1046 | 175.9445 | 177.7843 | 179.4594 | 181.1345 | 182.8096 | 184.4847 | 186.1598 | 187.8349 | 189.51 | 191.185 | 192.8601 | 194.5352 | 196.2103 | 197.8854 | 199.5605 | 201.2356 | 202.9107 | 203.4398 | 203.969 | 204.4981 | 205.0272 | 205.5564 | 206.0855 | 206.6147 | 207.1438 | 207.673 | 208.2021 | 208.7313 | 209.2604 | 209.7895 | 210.3187 | 210.8478 | 211.377 | 211.9061 | 212.4353 | 212.9644 | 213.4936 | 214.0227 | 214.5518 | 215.081 | 215.6101 | 216.1393 | 216.6684 | 217.1976 | 217.7267 | 218.2559 | 218.785 | 219.011 | 219.237 | 219.4631 | 219.6891 | 219.9151 | 220.1411 | 220.3672 | 220.5932 | 220.8192 | 221.0452 | 221.2712 | 221.4973 | 221.7233 | 221.9493 | 222.1753 | 222.4014 | 222.6274 | 222.8534 | 223.0794 | 223.3054 | 223.5315 | 223.7575 | 223.9835 | 224.2095 | 224.4356 | 224.6616 | 224.8876 | 225.1136 | 225.3396 | 225.5657 | 225.5657 | 225.5657 | 225.5657 | 225.5657 | 225.5657 | 225.5657 | 225.5657 | 225.5657 | 225.5657 | 225.5657 | 225.5657 | 225.5657 | 225.5657 | 225.5657 | 225.5657 | 225.5657 | 225.5657 | 225.5657 | 225.5657 | 225.5657 | 225.5657 | 225.5657 | 225.5657 | 225.5657 | 225.5657 | 225.5657 | 225.5657 | 225.5657 | 225.5657 | 225.5657 | 225.5498 | 225.534 | 225.5182 | 225.5023 | 225.4865 | 225.4707 | 225.4548 | 225.439 | 225.4232 | 225.4073 | 225.3915 | 225.3757 | 225.3598 | 225.344 | 225.3282 | 225.3123 | 225.2965 | 225.2807 | 225.2648 | 225.249 | 225.2332 | 225.2173 | 225.2015 | 225.1857 | 225.1698 | 225.154 | 225.1382 | 225.1223 | 225.1065 | 225.0907
15.1 | 0 | 69.78 | 125.004 | 123.278 | 151.04 | 178.802 | 204.088 | 220.07 | 226.898 | 226.898 | 226.448 | 0 | 6.978 | 13.956 | 20.934 | 27.912 | 34.89 | 41.868 | 48.846 | 55.824 | 62.802 | 69.78 | 80.8248 | 91.8696 | 102.9144 | 113.9592 | 125.004 | 124.6588 | 124.3136 | 123.9684 | 123.6232 | 123.278 | 126.0542 | 128.8304 | 131.6066 | 134.3828 | 137.159 | 139.9352 | 142.7114 | 145.4876 | 148.2638 | 151.04 | 152.8908 | 154.7416 | 156.5924 | 158.4432 | 160.294 | 162.1448 | 163.9956 | 165.8464 | 167.6972 | 169.548 | 171.3988 | 173.2496 | 175.1004 | 176.9512 | 178.802 | 180.4877 | 182.1735 | 183.8592 | 185.5449 | 187.2307 | 188.9164 | 190.6021 | 192.2879 | 193.9736 | 195.6593 | 197.3451 | 199.0308 | 200.7165 | 202.4023 | 204.088 | 204.6207 | 205.1535 | 205.6862 | 206.2189 | 206.7517 | 207.2844 | 207.8171 | 208.3499 | 208.8826 | 209.4153 | 209.9481 | 210.4808 | 211.0135 | 211.5463 | 212.079 | 212.6117 | 213.1445 | 213.6772 | 214.2099 | 214.7427 | 215.2754 | 215.8081 | 216.3409 | 216.8736 | 217.4063 | 217.9391 | 218.4718 | 219.0045 | 219.5373 | 220.07 | 220.2976 | 220.5252 | 220.7528 | 220.9804 | 221.208 | 221.4356 | 221.6632 | 221.8908 | 222.1184 | 222.346 | 222.5736 | 222.8012 | 223.0288 | 223.2564 | 223.484 | 223.7116 | 223.9392 | 224.1668 | 224.3944 | 224.622 | 224.8496 | 225.0772 | 225.3048 | 225.5324 | 225.76 | 225.9876 | 226.2152 | 226.4428 | 226.6704 | 226.898 | 226.898 | 226.898 | 226.898 | 226.898 | 226.898 | 226.898 | 226.898 | 226.898 | 226.898 | 226.898 | 226.898 | 226.898 | 226.898 | 226.898 | 226.898 | 226.898 | 226.898 | 226.898 | 226.898 | 226.898 | 226.898 | 226.898 | 226.898 | 226.898 | 226.898 | 226.898 | 226.898 | 226.898 | 226.898 | 226.898 | 226.883 | 226.868 | 226.853 | 226.838 | 226.823 | 226.808 | 226.793 | 226.778 | 226.763 | 226.748 | 226.733 | 226.718 | 226.703 | 226.688 | 226.673 | 226.658 | 226.643 | 226.628 | 226.613 | 226.598 | 226.583 | 226.568 | 226.553 | 226.538 | 226.523 | 226.508 | 226.493 | 226.478 | 226.463 | 226.448
15.15 | 0 | 70.17 | 125.7393 | 123.967 | 151.8933 | 179.8197 | 205.2653 | 221.355 | 228.2303 | 228.2303 | 227.8053 | 0 | 7.017 | 14.034 | 21.051 | 28.068 | 35.085 | 42.102 | 49.119 | 56.136 | 63.153 | 70.17 | 81.2839 | 92.3977 | 103.5116 | 114.6255 | 125.7393 | 125.3849 | 125.0304 | 124.6759 | 124.3215 | 123.967 | 126.7596 | 129.5523 | 132.3449 | 135.1375 | 137.9302 | 140.7228 | 143.5154 | 146.3081 | 149.1007 | 151.8933 | 153.7551 | 155.6168 | 157.4786 | 159.3404 | 161.2021 | 163.0639 | 164.9256 | 166.7874 | 168.6491 | 170.5109 | 172.3726 | 174.2344 | 176.0962 | 177.9579 | 179.8197 | 181.516 | 183.2124 | 184.9088 | 186.6052 | 188.3016 | 189.9979 | 191.6943 | 193.3907 | 195.0871 | 196.7834 | 198.4798 | 200.1762 | 201.8726 | 203.569 | 205.2653 | 205.8017 | 206.338 | 206.8743 | 207.4106 | 207.9469 | 208.4833 | 209.0196 | 209.5559 | 210.0922 | 210.6286 | 211.1649 | 211.7012 | 212.2375 | 212.7738 | 213.3102 | 213.8465 | 214.3828 | 214.9191 | 215.4555 | 215.9918 | 216.5281 | 217.0644 | 217.6007 | 218.1371 | 218.6734 | 219.2097 | 219.746 | 220.2824 | 220.8187 | 221.355 | 221.5842 | 221.8134 | 222.0425 | 222.2717 | 222.5009 | 222.7301 | 222.9592 | 223.1884 | 223.4176 | 223.6468 | 223.876 | 224.1051 | 224.3343 | 224.5635 | 224.7927 | 225.0218 | 225.251 | 225.4802 | 225.7094 | 225.9386 | 226.1677 | 226.3969 | 226.6261 | 226.8553 | 227.0844 | 227.3136 | 227.5428 | 227.772 | 228.0012 | 228.2303 | 228.2303 | 228.2303 | 228.2303 | 228.2303 | 228.2303 | 228.2303 | 228.2303 | 228.2303 | 228.2303 | 228.2303 | 228.2303 | 228.2303 | 228.2303 | 228.2303 | 228.2303 | 228.2303 | 228.2303 | 228.2303 | 228.2303 | 228.2303 | 228.2303 | 228.2303 | 228.2303 | 228.2303 | 228.2303 | 228.2303 | 228.2303 | 228.2303 | 228.2303 | 228.2303 | 228.2162 | 228.202 | 228.1878 | 228.1737 | 228.1595 | 228.1453 | 228.1312 | 228.117 | 228.1028 | 228.0887 | 228.0745 | 228.0603 | 228.0462 | 228.032 | 228.0178 | 228.0037 | 227.9895 | 227.9753 | 227.9612 | 227.947 | 227.9328 | 227.9187 | 227.9045 | 227.8903 | 227.8762 | 227.862 | 227.8478 | 227.8337 | 227.8195 | 227.8053
15.2 | 0 | 70.56 | 126.4747 | 124.656 | 152.7467 | 180.8373 | 206.4427 | 222.64 | 229.5627 | 229.5627 | 229.1627 | 7.1054e-15 | 7.056 | 14.112 | 21.168 | 28.224 | 35.28 | 42.336 | 49.392 | 56.448 | 63.504 | 70.56 | 81.7429 | 92.9259 | 104.1088 | 115.2917 | 126.4747 | 126.1109 | 125.7472 | 125.3835 | 125.0197 | 124.656 | 127.4651 | 130.2741 | 133.0832 | 135.8923 | 138.7013 | 141.5104 | 144.3195 | 147.1285 | 149.9376 | 152.7467 | 154.6194 | 156.4921 | 158.3648 | 160.2375 | 162.1102 | 163.9829 | 165.8556 | 167.7284 | 169.6011 | 171.4738 | 173.3465 | 175.2192 | 177.0919 | 178.9646 | 180.8373 | 182.5444 | 184.2514 | 185.9584 | 187.6654 | 189.3724 | 191.0795 | 192.7865 | 194.4935 | 196.2005 | 197.9076 | 199.6146 | 201.3216 | 203.0286 | 204.7356 | 206.4427 | 206.9826 | 207.5225 | 208.0624 | 208.6023 | 209.1422 | 209.6821 | 210.222 | 210.762 | 211.3019 | 211.8418 | 212.3817 | 212.9216 | 213.4615 | 214.0014 | 214.5413 | 215.0812 | 215.6212 | 216.1611 | 216.701 | 217.2409 | 217.7808 | 218.3207 | 218.8606 | 219.4005 | 219.9404 | 220.4804 | 221.0203 | 221.5602 | 222.1001 | 222.64 | 222.8708 | 223.1015 | 223.3323 | 223.563 | 223.7938 | 224.0245 | 224.2553 | 224.486 | 224.7168 | 224.9476 | 225.1783 | 225.4091 | 225.6398 | 225.8706 | 226.1013 | 226.3321 | 226.5628 | 226.7936 | 227.0244 | 227.2551 | 227.4859 | 227.7166 | 227.9474 | 228.1781 | 228.4089 | 228.6396 | 228.8704 | 229.1012 | 229.3319 | 229.5627 | 229.5627 | 229.5627 | 229.5627 | 229.5627 | 229.5627 | 229.5627 | 229.5627 | 229.5627 | 229.5627 | 229.5627 | 229.5627 | 229.5627 | 229.5627 | 229.5627 | 229.5627 | 229.5627 | 229.5627 | 229.5627 | 229.5627 | 229.5627 | 229.5627 | 229.5627 | 229.5627 | 229.5627 | 229.5627 | 229.5627 | 229.5627 | 229.5627 | 229.5627 | 229.5627 | 229.5493 | 229.536 | 229.5227 | 229.5093 | 229.496 | 229.4827 | 229.4693 | 229.456 | 229.4427 | 229.4293 | 229.416 | 229.4027 | 229.3893 | 229.376 | 229.3627 | 229.3493 | 229.336 | 229.3227 | 229.3093 | 229.296 | 229.2827 | 229.2693 | 229.256 | 229.2427 | 229.2293 | 229.216 | 229.2027 | 229.1893 | 229.176 | 229.1627
15.25 | 0 | 70.95 | 127.21 | 125.345 | 153.6 | 181.855 | 207.62 | 223.925 | 230.895 | 230.895 | 230.52 | 0 | 7.095 | 14.19 | 21.285 | 28.38 | 35.475 | 42.57 | 49.665 | 56.76 | 63.855 | 70.95 | 82.202 | 93.454 | 104.706 | 115.958 | 127.21 | 126.837 | 126.464 | 126.091 | 125.718 | 125.345 | 128.1705 | 130.996 | 133.8215 | 136.647 | 139.4725 | 142.298 | 145.1235 | 147.949 | 150.7745 | 153.6 | 155.4837 | 157.3673 | 159.251 | 161.1347 | 163.0183 | 164.902 | 166.7857 | 168.6693 | 170.553 | 172.4367 | 174.3203 | 176.204 | 178.0877 | 179.9713 | 181.855 | 183.5727 | 185.2903 | 187.008 | 188.7257 | 190.4433 | 192.161 | 193.8787 | 195.5963 | 197.314 | 199.0317 | 200.7493 | 202.467 | 204.1847 | 205.9023 | 207.62 | 208.1635 | 208.707 | 209.2505 | 209.794 | 210.3375 | 210.881 | 211.4245 | 211.968 | 212.5115 | 213.055 | 213.5985 | 214.142 | 214.6855 | 215.229 | 215.7725 | 216.316 | 216.8595 | 217.403 | 217.9465 | 218.49 | 219.0335 | 219.577 | 220.1205 | 220.664 | 221.2075 | 221.751 | 222.2945 | 222.838 | 223.3815 | 223.925 | 224.1573 | 224.3897 | 224.622 | 224.8543 | 225.0867 | 225.319 | 225.5513 | 225.7837 | 226.016 | 226.2483 | 226.4807 | 226.713 | 226.9453 | 227.1777 | 227.41 | 227.6423 | 227.8747 | 228.107 | 228.3393 | 228.5717 | 228.804 | 229.0363 | 229.2687 | 229.501 | 229.7333 | 229.9657 | 230.198 | 230.4303 | 230.6627 | 230.895 | 230.895 | 230.895 | 230.895 | 230.895 | 230.895 | 230.895 | 230.895 | 230.895 | 230.895 | 230.895 | 230.895 | 230.895 | 230.895 | 230.895 | 230.895 | 230.895 | 230.895 | 230.895 | 230.895 | 230.895 | 230.895 | 230.895 | 230.895 | 230.895 | 230.895 | 230.895 | 230.895 | 230.895 | 230.895 | 230.895 | 230.8825 | 230.87 | 230.8575 | 230.845 | 230.8325 | 230.82 | 230.8075 | 230.795 | 230.7825 | 230.77 | 230.7575 | 230.745 | 230.7325 | 230.72 | 230.7075 | 230.695 | 230.6825 | 230.67 | 230.6575 | 230.645 | 230.6325 | 230.62 | 230.6075 | 230.595 | 230.5825 | 230.57 | 230.5575 | 230.545 | 230.5325 | 230.52
15.3 | 0 | 71.34 | 127.9453 | 126.034 | 154.4533 | 182.8727 | 208.7973 | 225.21 | 232.2273 | 232.2273 | 231.8773 | -7.1054e-15 | 7.134 | 14.268 | 21.402 | 28.536 | 35.67 | 42.804 | 49.938 | 57.072 | 64.206 | 71.34 | 82.6611 | 93.9821 | 105.3032 | 116.6243 | 127.9453 | 127.5631 | 127.1808 | 126.7985 | 126.4163 | 126.034 | 128.8759 | 131.7179 | 134.5598 | 137.4017 | 140.2437 | 143.0856 | 145.9275 | 148.7695 | 151.6114 | 154.4533 | 156.348 | 158.2426 | 160.1372 | 162.0318 | 163.9264 | 165.8211 | 167.7157 | 169.6103 | 171.5049 | 173.3996 | 175.2942 | 177.1888 | 179.0834 | 180.978 | 182.8727 | 184.601 | 186.3293 | 188.0576 | 189.7859 | 191.5142 | 193.2425 | 194.9708 | 196.6992 | 198.4275 | 200.1558 | 201.8841 | 203.6124 | 205.3407 | 207.069 | 208.7973 | 209.3444 | 209.8915 | 210.4386 | 210.9857 | 211.5328 | 212.0799 | 212.627 | 213.174 | 213.7211 | 214.2682 | 214.8153 | 215.3624 | 215.9095 | 216.4566 | 217.0037 | 217.5508 | 218.0978 | 218.6449 | 219.192 | 219.7391 | 220.2862 | 220.8333 | 221.3804 | 221.9275 | 222.4746 | 223.0216 | 223.5687 | 224.1158 | 224.6629 | 225.21 | 225.4439 | 225.6778 | 225.9117 | 226.1456 | 226.3796 | 226.6135 | 226.8474 | 227.0813 | 227.3152 | 227.5491 | 227.783 | 228.0169 | 228.2508 | 228.4848 | 228.7187 | 228.9526 | 229.1865 | 229.4204 | 229.6543 | 229.8882 | 230.1221 | 230.356 | 230.59 | 230.8239 | 231.0578 | 231.2917 | 231.5256 | 231.7595 | 231.9934 | 232.2273 | 232.2273 | 232.2273 | 232.2273 | 232.2273 | 232.2273 | 232.2273 | 232.2273 | 232.2273 | 232.2273 | 232.2273 | 232.2273 | 232.2273 | 232.2273 | 232.2273 | 232.2273 | 232.2273 | 232.2273 | 232.2273 | 232.2273 | 232.2273 | 232.2273 | 232.2273 | 232.2273 | 232.2273 | 232.2273 | 232.2273 | 232.2273 | 232.2273 | 232.2273 | 232.2273 | 232.2157 | 232.204 | 232.1923 | 232.1807 | 232.169 | 232.1573 | 232.1457 | 232.134 | 232.1223 | 232.1107 | 232.099 | 232.0873 | 232.0757 | 232.064 | 232.0523 | 232.0407 | 232.029 | 232.0173 | 232.0057 | 231.994 | 231.9823 | 231.9707 | 231.959 | 231.9473 | 231.9357 | 231.924 | 231.9123 | 231.9007 | 231.889 | 231.8773
15.35 | 0 | 71.73 | 128.6807 | 126.723 | 155.3067 | 183.8903 | 209.9747 | 226.495 | 233.5597 | 233.5597 | 233.2347 | 0 | 7.173 | 14.346 | 21.519 | 28.692 | 35.865 | 43.038 | 50.211 | 57.384 | 64.557 | 71.73 | 83.1201 | 94.5103 | 105.9004 | 117.2905 | 128.6807 | 128.2891 | 127.8976 | 127.5061 | 127.1145 | 126.723 | 129.5814 | 132.4397 | 135.2981 | 138.1565 | 141.0148 | 143.8732 | 146.7316 | 149.5899 | 152.4483 | 155.3067 | 157.2122 | 159.1178 | 161.0234 | 162.929 | 164.8346 | 166.7401 | 168.6457 | 170.5513 | 172.4569 | 174.3624 | 176.268 | 178.1736 | 180.0792 | 181.9848 | 183.8903 | 185.6293 | 187.3682 | 189.1072 | 190.8462 | 192.5851 | 194.3241 | 196.063 | 197.802 | 199.5409 | 201.2799 | 203.0188 | 204.7578 | 206.4968 | 208.2357 | 209.9747 | 210.5253 | 211.076 | 211.6267 | 212.1774 | 212.7281 | 213.2787 | 213.8294 | 214.3801 | 214.9308 | 215.4814 | 216.0321 | 216.5828 | 217.1335 | 217.6842 | 218.2348 | 218.7855 | 219.3362 | 219.8869 | 220.4375 | 220.9882 | 221.5389 | 222.0896 | 222.6403 | 223.1909 | 223.7416 | 224.2923 | 224.843 | 225.3936 | 225.9443 | 226.495 | 226.7305 | 226.966 | 227.2015 | 227.437 | 227.6724 | 227.9079 | 228.1434 | 228.3789 | 228.6144 | 228.8499 | 229.0854 | 229.3209 | 229.5564 | 229.7918 | 230.0273 | 230.2628 | 230.4983 | 230.7338 | 230.9693 | 231.2048 | 231.4403 | 231.6758 | 231.9112 | 232.1467 | 232.3822 | 232.6177 | 232.8532 | 233.0887 | 233.3242 | 233.5597 | 233.5597 | 233.5597 | 233.5597 | 233.5597 | 233.5597 | 233.5597 | 233.5597 | 233.5597 | 233.5597 | 233.5597 | 233.5597 | 233.5597 | 233.5597 | 233.5597 | 233.5597 | 233.5597 | 233.5597 | 233.5597 | 233.5597 | 233.5597 | 233.5597 | 233.5597 | 233.5597 | 233.5597 | 233.5597 | 233.5597 | 233.5597 | 233.5597 | 233.5597 | 233.5597 | 233.5488 | 233.538 | 233.5272 | 233.5163 | 233.5055 | 233.4947 | 233.4838 | 233.473 | 233.4622 | 233.4513 | 233.4405 | 233.4297 | 233.4188 | 233.408 | 233.3972 | 233.3863 | 233.3755 | 233.3647 | 233.3538 | 233.343 | 233.3322 | 233.3213 | 233.3105 | 233.2997 | 233.2888 | 233.278 | 233.2672 | 233.2563 | 233.2455 | 233.2347
15.4 | 0 | 72.12 | 129.416 | 127.412 | 156.16 | 184.908 | 211.152 | 227.78 | 234.892 | 234.892 | 234.592 | 0 | 7.212 | 14.424 | 21.636 | 28.848 | 36.06 | 43.272 | 50.484 | 57.696 | 64.908 | 72.12 | 83.5792 | 95.0384 | 106.4976 | 117.9568 | 129.416 | 129.0152 | 128.6144 | 128.2136 | 127.8128 | 127.412 | 130.2868 | 133.1616 | 136.0364 | 138.9112 | 141.786 | 144.6608 | 147.5356 | 150.4104 | 153.2852 | 156.16 | 158.0765 | 159.9931 | 161.9096 | 163.8261 | 165.7427 | 167.6592 | 169.5757 | 171.4923 | 173.4088 | 175.3253 | 177.2419 | 179.1584 | 181.0749 | 182.9915 | 184.908 | 186.6576 | 188.4072 | 190.1568 | 191.9064 | 193.656 | 195.4056 | 197.1552 | 198.9048 | 200.6544 | 202.404 | 204.1536 | 205.9032 | 207.6528 | 209.4024 | 211.152 | 211.7063 | 212.2605 | 212.8148 | 213.3691 | 213.9233 | 214.4776 | 215.0319 | 215.5861 | 216.1404 | 216.6947 | 217.2489 | 217.8032 | 218.3575 | 218.9117 | 219.466 | 220.0203 | 220.5745 | 221.1288 | 221.6831 | 222.2373 | 222.7916 | 223.3459 | 223.9001 | 224.4544 | 225.0087 | 225.5629 | 226.1172 | 226.6715 | 227.2257 | 227.78 | 228.0171 | 228.2541 | 228.4912 | 228.7283 | 228.9653 | 229.2024 | 229.4395 | 229.6765 | 229.9136 | 230.1507 | 230.3877 | 230.6248 | 230.8619 | 231.0989 | 231.336 | 231.5731 | 231.8101 | 232.0472 | 232.2843 | 232.5213 | 232.7584 | 232.9955 | 233.2325 | 233.4696 | 233.7067 | 233.9437 | 234.1808 | 234.4179 | 234.6549 | 234.892 | 234.892 | 234.892 | 234.892 | 234.892 | 234.892 | 234.892 | 234.892 | 234.892 | 234.892 | 234.892 | 234.892 | 234.892 | 234.892 | 234.892 | 234.892 | 234.892 | 234.892 | 234.892 | 234.892 | 234.892 | 234.892 | 234.892 | 234.892 | 234.892 | 234.892 | 234.892 | 234.892 | 234.892 | 234.892 | 234.892 | 234.882 | 234.872 | 234.862 | 234.852 | 234.842 | 234.832 | 234.822 | 234.812 | 234.802 | 234.792 | 234.782 | 234.772 | 234.762 | 234.752 | 234.742 | 234.732 | 234.722 | 234.712 | 234.702 | 234.692 | 234.682 | 234.672 | 234.662 | 234.652 | 234.642 | 234.632 | 234.622 | 234.612 | 234.602 | 234.592
15.45 | 0 | 72.51 | 130.1513 | 128.101 | 157.0133 | 185.9257 | 212.3293 | 229.065 | 236.2243 | 236.2243 | 235.9493 | 0 | 7.251 | 14.502 | 21.753 | 29.004 | 36.255 | 43.506 | 50.757 | 58.008 | 65.259 | 72.51 | 84.0383 | 95.5665 | 107.0948 | 118.6231 | 130.1513 | 129.7413 | 129.3312 | 128.9211 | 128.5111 | 128.101 | 130.9922 | 133.8835 | 136.7747 | 139.6659 | 142.5572 | 145.4484 | 148.3396 | 151.2309 | 154.1221 | 157.0133 | 158.9408 | 160.8683 | 162.7958 | 164.7233 | 166.6508 | 168.5783 | 170.5058 | 172.4332 | 174.3607 | 176.2882 | 178.2157 | 180.1432 | 182.0707 | 183.9982 | 185.9257 | 187.6859 | 189.4462 | 191.2064 | 192.9666 | 194.7269 | 196.4871 | 198.2474 | 200.0076 | 201.7679 | 203.5281 | 205.2884 | 207.0486 | 208.8088 | 210.5691 | 212.3293 | 212.8872 | 213.445 | 214.0029 | 214.5608 | 215.1186 | 215.6765 | 216.2343 | 216.7922 | 217.35 | 217.9079 | 218.4657 | 219.0236 | 219.5815 | 220.1393 | 220.6972 | 221.255 | 221.8129 | 222.3707 | 222.9286 | 223.4864 | 224.0443 | 224.6022 | 225.16 | 225.7179 | 226.2757 | 226.8336 | 227.3914 | 227.9493 | 228.5071 | 229.065 | 229.3036 | 229.5423 | 229.7809 | 230.0196 | 230.2582 | 230.4969 | 230.7355 | 230.9742 | 231.2128 | 231.4514 | 231.6901 | 231.9287 | 232.1674 | 232.406 | 232.6447 | 232.8833 | 233.122 | 233.3606 | 233.5992 | 233.8379 | 234.0765 | 234.3152 | 234.5538 | 234.7925 | 235.0311 | 235.2698 | 235.5084 | 235.747 | 235.9857 | 236.2243 | 236.2243 | 236.2243 | 236.2243 | 236.2243 | 236.2243 | 236.2243 | 236.2243 | 236.2243 | 236.2243 | 236.2243 | 236.2243 | 236.2243 | 236.2243 | 236.2243 | 236.2243 | 236.2243 | 236.2243 | 236.2243 | 236.2243 | 236.2243 | 236.2243 | 236.2243 | 236.2243 | 236.2243 | 236.2243 | 236.2243 | 236.2243 | 236.2243 | 236.2243 | 236.2243 | 236.2152 | 236.206 | 236.1968 | 236.1877 | 236.1785 | 236.1693 | 236.1602 | 236.151 | 236.1418 | 236.1327 | 236.1235 | 236.1143 | 236.1052 | 236.096 | 236.0868 | 236.0777 | 236.0685 | 236.0593 | 236.0502 | 236.041 | 236.0318 | 236.0227 | 236.0135 | 236.0043 | 235.9952 | 235.986 | 235.9768 | 235.9677 | 235.9585 | 235.9493
15.5 | 0 | 72.9 | 130.8867 | 128.79 | 157.8667 | 186.9433 | 213.5067 | 230.35 | 237.5567 | 237.5567 | 237.3067 | 0 | 7.29 | 14.58 | 21.87 | 29.16 | 36.45 | 43.74 | 51.03 | 58.32 | 65.61 | 72.9 | 84.4973 | 96.0947 | 107.692 | 119.2893 | 130.8867 | 130.4673 | 130.048 | 129.6287 | 129.2093 | 128.79 | 131.6977 | 134.6053 | 137.513 | 140.4207 | 143.3283 | 146.236 | 149.1437 | 152.0513 | 154.959 | 157.8667 | 159.8051 | 161.7436 | 163.682 | 165.6204 | 167.5589 | 169.4973 | 171.4358 | 173.3742 | 175.3127 | 177.2511 | 179.1896 | 181.128 | 183.0664 | 185.0049 | 186.9433 | 188.7142 | 190.4851 | 192.256 | 194.0269 | 195.7978 | 197.5687 | 199.3396 | 201.1104 | 202.8813 | 204.6522 | 206.4231 | 208.194 | 209.9649 | 211.7358 | 213.5067 | 214.0681 | 214.6296 | 215.191 | 215.7524 | 216.3139 | 216.8753 | 217.4368 | 217.9982 | 218.5597 | 219.1211 | 219.6826 | 220.244 | 220.8054 | 221.3669 | 221.9283 | 222.4898 | 223.0512 | 223.6127 | 224.1741 | 224.7356 | 225.297 | 225.8584 | 226.4199 | 226.9813 | 227.5428 | 228.1042 | 228.6657 | 229.2271 | 229.7886 | 230.35 | 230.5902 | 230.8304 | 231.0707 | 231.3109 | 231.5511 | 231.7913 | 232.0316 | 232.2718 | 232.512 | 232.7522 | 232.9924 | 233.2327 | 233.4729 | 233.7131 | 233.9533 | 234.1936 | 234.4338 | 234.674 | 234.9142 | 235.1544 | 235.3947 | 235.6349 | 235.8751 | 236.1153 | 236.3556 | 236.5958 | 236.836 | 237.0762 | 237.3164 | 237.5567 | 237.5567 | 237.5567 | 237.5567 | 237.5567 | 237.5567 | 237.5567 | 237.5567 | 237.5567 | 237.5567 | 237.5567 | 237.5567 | 237.5567 | 237.5567 | 237.5567 | 237.5567 | 237.5567 | 237.5567 | 237.5567 | 237.5567 | 237.5567 | 237.5567 | 237.5567 | 237.5567 | 237.5567 | 237.5567 | 237.5567 | 237.5567 | 237.5567 | 237.5567 | 237.5567 | 237.5483 | 237.54 | 237.5317 | 237.5233 | 237.515 | 237.5067 | 237.4983 | 237.49 | 237.4817 | 237.4733 | 237.465 | 237.4567 | 237.4483 | 237.44 | 237.4317 | 237.4233 | 237.415 | 237.4067 | 237.3983 | 237.39 | 237.3817 | 237.3733 | 237.365 | 237.3567 | 237.3483 | 237.34 | 237.3317 | 237.3233 | 237.315 | 237.3067
15.55 | 0 | 73.29 | 131.622 | 129.479 | 158.72 | 187.961 | 214.684 | 231.635 | 238.889 | 238.889 | 238.664 | 0 | 7.329 | 14.658 | 21.987 | 29.316 | 36.645 | 43.974 | 51.303 | 58.632 | 65.961 | 73.29 | 84.9564 | 96.6228 | 108.2892 | 119.9556 | 131.622 | 131.1934 | 130.7648 | 130.3362 | 129.9076 | 129.479 | 132.4031 | 135.3272 | 138.2513 | 141.1754 | 144.0995 | 147.0236 | 149.9477 | 152.8718 | 155.7959 | 158.72 | 160.6694 | 162.6188 | 164.5682 | 166.5176 | 168.467 | 170.4164 | 172.3658 | 174.3152 | 176.2646 | 178.214 | 180.1634 | 182.1128 | 184.0622 | 186.0116 | 187.961 | 189.7425 | 191.5241 | 193.3056 | 195.0871 | 196.8687 | 198.6502 | 200.4317 | 202.2133 | 203.9948 | 205.7763 | 207.5579 | 209.3394 | 211.1209 | 212.9025 | 214.684 | 215.249 | 215.8141 | 216.3791 | 216.9441 | 217.5092 | 218.0742 | 218.6392 | 219.2043 | 219.7693 | 220.3343 | 220.8994 | 221.4644 | 222.0294 | 222.5945 | 223.1595 | 223.7245 | 224.2896 | 224.8546 | 225.4196 | 225.9847 | 226.5497 | 227.1147 | 227.6798 | 228.2448 | 228.8098 | 229.3749 | 229.9399 | 230.5049 | 231.07 | 231.635 | 231.8768 | 232.1186 | 232.3604 | 232.6022 | 232.844 | 233.0858 | 233.3276 | 233.5694 | 233.8112 | 234.053 | 234.2948 | 234.5366 | 234.7784 | 235.0202 | 235.262 | 235.5038 | 235.7456 | 235.9874 | 236.2292 | 236.471 | 236.7128 | 236.9546 | 237.1964 | 237.4382 | 237.68 | 237.9218 | 238.1636 | 238.4054 | 238.6472 | 238.889 | 238.889 | 238.889 | 238.889 | 238.889 | 238.889 | 238.889 | 238.889 | 238.889 | 238.889 | 238.889 | 238.889 | 238.889 | 238.889 | 238.889 | 238.889 | 238.889 | 238.889 | 238.889 | 238.889 | 238.889 | 238.889 | 238.889 | 238.889 | 238.889 | 238.889 | 238.889 | 238.889 | 238.889 | 238.889 | 238.889 | 238.8815 | 238.874 | 238.8665 | 238.859 | 238.8515 | 238.844 | 238.8365 | 238.829 | 238.8215 | 238.814 | 238.8065 | 238.799 | 238.7915 | 238.784 | 238.7765 | 238.769 | 238.7615 | 238.754 | 238.7465 | 238.739 | 238.7315 | 238.724 | 238.7165 | 238.709 | 238.7015 | 238.694 | 238.6865 | 238.679 | 238.6715 | 238.664
15.6 | 0 | 73.68 | 132.3573 | 130.168 | 159.5733 | 188.9787 | 215.8613 | 232.92 | 240.2213 | 240.2213 | 240.0213 | 0 | 7.368 | 14.736 | 22.104 | 29.472 | 36.84 | 44.208 | 51.576 | 58.944 | 66.312 | 73.68 | 85.4155 | 97.1509 | 108.8864 | 120.6219 | 132.3573 | 131.9195 | 131.4816 | 131.0437 | 130.6059 | 130.168 | 133.1085 | 136.0491 | 138.9896 | 141.9301 | 144.8707 | 147.8112 | 150.7517 | 153.6923 | 156.6328 | 159.5733 | 161.5337 | 163.494 | 165.4544 | 167.4148 | 169.3751 | 171.3355 | 173.2958 | 175.2562 | 177.2165 | 179.1769 | 181.1372 | 183.0976 | 185.058 | 187.0183 | 188.9787 | 190.7708 | 192.563 | 194.3552 | 196.1474 | 197.9396 | 199.7317 | 201.5239 | 203.3161 | 205.1083 | 206.9004 | 208.6926 | 210.4848 | 212.277 | 214.0692 | 215.8613 | 216.43 | 216.9986 | 217.5672 | 218.1358 | 218.7044 | 219.2731 | 219.8417 | 220.4103 | 220.9789 | 221.5476 | 222.1162 | 222.6848 | 223.2534 | 223.822 | 224.3907 | 224.9593 | 225.5279 | 226.0965 | 226.6652 | 227.2338 | 227.8024 | 228.371 | 228.9396 | 229.5083 | 230.0769 | 230.6455 | 231.2141 | 231.7828 | 232.3514 | 232.92 | 233.1634 | 233.4068 | 233.6501 | 233.8935 | 234.1369 | 234.3803 | 234.6236 | 234.867 | 235.1104 | 235.3538 | 235.5972 | 235.8405 | 236.0839 | 236.3273 | 236.5707 | 236.814 | 237.0574 | 237.3008 | 237.5442 | 237.7876 | 238.0309 | 238.2743 | 238.5177 | 238.7611 | 239.0044 | 239.2478 | 239.4912 | 239.7346 | 239.978 | 240.2213 | 240.2213 | 240.2213 | 240.2213 | 240.2213 | 240.2213 | 240.2213 | 240.2213 | 240.2213 | 240.2213 | 240.2213 | 240.2213 | 240.2213 | 240.2213 | 240.2213 | 240.2213 | 240.2213 | 240.2213 | 240.2213 | 240.2213 | 240.2213 | 240.2213 | 240.2213 | 240.2213 | 240.2213 | 240.2213 | 240.2213 | 240.2213 | 240.2213 | 240.2213 | 240.2213 | 240.2147 | 240.208 | 240.2013 | 240.1947 | 240.188 | 240.1813 | 240.1747 | 240.168 | 240.1613 | 240.1547 | 240.148 | 240.1413 | 240.1347 | 240.128 | 240.1213 | 240.1147 | 240.108 | 240.1013 | 240.0947 | 240.088 | 240.0813 | 240.0747 | 240.068 | 240.0613 | 240.0547 | 240.048 | 240.0413 | 240.0347 | 240.028 | 240.0213
15.65 | 0 | 74.07 | 133.0927 | 130.857 | 160.4267 | 189.9963 | 217.0387 | 234.205 | 241.5537 | 241.5537 | 241.3787 | 0 | 7.407 | 14.814 | 22.221 | 29.628 | 37.035 | 44.442 | 51.849 | 59.256 | 66.663 | 74.07 | 85.8745 | 97.6791 | 109.4836 | 121.2881 | 133.0927 | 132.6455 | 132.1984 | 131.7513 | 131.3041 | 130.857 | 133.814 | 136.7709 | 139.7279 | 142.6849 | 145.6418 | 148.5988 | 151.5558 | 154.5127 | 157.4697 | 160.4267 | 162.398 | 164.3693 | 166.3406 | 168.3119 | 170.2832 | 172.2545 | 174.2258 | 176.1972 | 178.1685 | 180.1398 | 182.1111 | 184.0824 | 186.0537 | 188.025 | 189.9963 | 191.7992 | 193.602 | 195.4048 | 197.2076 | 199.0104 | 200.8133 | 202.6161 | 204.4189 | 206.2217 | 208.0246 | 209.8274 | 211.6302 | 213.433 | 215.2358 | 217.0387 | 217.6109 | 218.1831 | 218.7553 | 219.3275 | 219.8997 | 220.4719 | 221.0441 | 221.6164 | 222.1886 | 222.7608 | 223.333 | 223.9052 | 224.4774 | 225.0496 | 225.6218 | 226.194 | 226.7663 | 227.3385 | 227.9107 | 228.4829 | 229.0551 | 229.6273 | 230.1995 | 230.7717 | 231.3439 | 231.9162 | 232.4884 | 233.0606 | 233.6328 | 234.205 | 234.45 | 234.6949 | 234.9399 | 235.1848 | 235.4298 | 235.6747 | 235.9197 | 236.1646 | 236.4096 | 236.6546 | 236.8995 | 237.1445 | 237.3894 | 237.6344 | 237.8793 | 238.1243 | 238.3692 | 238.6142 | 238.8592 | 239.1041 | 239.3491 | 239.594 | 239.839 | 240.0839 | 240.3289 | 240.5738 | 240.8188 | 241.0638 | 241.3087 | 241.5537 | 241.5537 | 241.5537 | 241.5537 | 241.5537 | 241.5537 | 241.5537 | 241.5537 | 241.5537 | 241.5537 | 241.5537 | 241.5537 | 241.5537 | 241.5537 | 241.5537 | 241.5537 | 241.5537 | 241.5537 | 241.5537 | 241.5537 | 241.5537 | 241.5537 | 241.5537 | 241.5537 | 241.5537 | 241.5537 | 241.5537 | 241.5537 | 241.5537 | 241.5537 | 241.5537 | 241.5478 | 241.542 | 241.5362 | 241.5303 | 241.5245 | 241.5187 | 241.5128 | 241.507 | 241.5012 | 241.4953 | 241.4895 | 241.4837 | 241.4778 | 241.472 | 241.4662 | 241.4603 | 241.4545 | 241.4487 | 241.4428 | 241.437 | 241.4312 | 241.4253 | 241.4195 | 241.4137 | 241.4078 | 241.402 | 241.3962 | 241.3903 | 241.3845 | 241.3787
15.7 | 0 | 74.46 | 133.828 | 131.546 | 161.28 | 191.014 | 218.216 | 235.49 | 242.886 | 242.886 | 242.736 | 0 | 7.446 | 14.892 | 22.338 | 29.784 | 37.23 | 44.676 | 52.122 | 59.568 | 67.014 | 74.46 | 86.3336 | 98.2072 | 110.0808 | 121.9544 | 133.828 | 133.3716 | 132.9152 | 132.4588 | 132.0024 | 131.546 | 134.5194 | 137.4928 | 140.4662 | 143.4396 | 146.413 | 149.3864 | 152.3598 | 155.3332 | 158.3066 | 161.28 | 163.2623 | 165.2445 | 167.2268 | 169.2091 | 171.1913 | 173.1736 | 175.1559 | 177.1381 | 179.1204 | 181.1027 | 183.0849 | 185.0672 | 187.0495 | 189.0317 | 191.014 | 192.8275 | 194.6409 | 196.4544 | 198.2679 | 200.0813 | 201.8948 | 203.7083 | 205.5217 | 207.3352 | 209.1487 | 210.9621 | 212.7756 | 214.5891 | 216.4025 | 218.216 | 218.7918 | 219.3676 | 219.9434 | 220.5192 | 221.095 | 221.6708 | 222.2466 | 222.8224 | 223.3982 | 223.974 | 224.5498 | 225.1256 | 225.7014 | 226.2772 | 226.853 | 227.4288 | 228.0046 | 228.5804 | 229.1562 | 229.732 | 230.3078 | 230.8836 | 231.4594 | 232.0352 | 232.611 | 233.1868 | 233.7626 | 234.3384 | 234.9142 | 235.49 | 235.7365 | 235.9831 | 236.2296 | 236.4761 | 236.7227 | 236.9692 | 237.2157 | 237.4623 | 237.7088 | 237.9553 | 238.2019 | 238.4484 | 238.6949 | 238.9415 | 239.188 | 239.4345 | 239.6811 | 239.9276 | 240.1741 | 240.4207 | 240.6672 | 240.9137 | 241.1603 | 241.4068 | 241.6533 | 241.8999 | 242.1464 | 242.3929 | 242.6395 | 242.886 | 242.886 | 242.886 | 242.886 | 242.886 | 242.886 | 242.886 | 242.886 | 242.886 | 242.886 | 242.886 | 242.886 | 242.886 | 242.886 | 242.886 | 242.886 | 242.886 | 242.886 | 242.886 | 242.886 | 242.886 | 242.886 | 242.886 | 242.886 | 242.886 | 242.886 | 242.886 | 242.886 | 242.886 | 242.886 | 242.886 | 242.881 | 242.876 | 242.871 | 242.866 | 242.861 | 242.856 | 242.851 | 242.846 | 242.841 | 242.836 | 242.831 | 242.826 | 242.821 | 242.816 | 242.811 | 242.806 | 242.801 | 242.796 | 242.791 | 242.786 | 242.781 | 242.776 | 242.771 | 242.766 | 242.761 | 242.756 | 242.751 | 242.746 | 242.741 | 242.736
15.75 | 0 | 74.85 | 134.5633 | 132.235 | 162.1333 | 192.0317 | 219.3933 | 236.775 | 244.2183 | 244.2183 | 244.0933 | -7.1054e-15 | 7.485 | 14.97 | 22.455 | 29.94 | 37.425 | 44.91 | 52.395 | 59.88 | 67.365 | 74.85 | 86.7927 | 98.7353 | 110.678 | 122.6207 | 134.5633 | 134.0977 | 133.632 | 133.1663 | 132.7007 | 132.235 | 135.2248 | 138.2147 | 141.2045 | 144.1943 | 147.1842 | 150.174 | 153.1638 | 156.1537 | 159.1435 | 162.1333 | 164.1266 | 166.1198 | 168.113 | 170.1062 | 172.0994 | 174.0927 | 176.0859 | 178.0791 | 180.0723 | 182.0656 | 184.0588 | 186.052 | 188.0452 | 190.0384 | 192.0317 | 193.8558 | 195.6799 | 197.504 | 199.3281 | 201.1522 | 202.9763 | 204.8004 | 206.6246 | 208.4487 | 210.2728 | 212.0969 | 213.921 | 215.7451 | 217.5692 | 219.3933 | 219.9727 | 220.5521 | 221.1315 | 221.7109 | 222.2903 | 222.8697 | 223.4491 | 224.0284 | 224.6078 | 225.1872 | 225.7666 | 226.346 | 226.9254 | 227.5048 | 228.0842 | 228.6636 | 229.2429 | 229.8223 | 230.4017 | 230.9811 | 231.5605 | 232.1399 | 232.7193 | 233.2987 | 233.8781 | 234.4574 | 235.0368 | 235.6162 | 236.1956 | 236.775 | 237.0231 | 237.2712 | 237.5193 | 237.7674 | 238.0156 | 238.2637 | 238.5118 | 238.7599 | 239.008 | 239.2561 | 239.5042 | 239.7523 | 240.0004 | 240.2486 | 240.4967 | 240.7448 | 240.9929 | 241.241 | 241.4891 | 241.7372 | 241.9853 | 242.2334 | 242.4816 | 242.7297 | 242.9778 | 243.2259 | 243.474 | 243.7221 | 243.9702 | 244.2183 | 244.2183 | 244.2183 | 244.2183 | 244.2183 | 244.2183 | 244.2183 | 244.2183 | 244.2183 | 244.2183 | 244.2183 | 244.2183 | 244.2183 | 244.2183 | 244.2183 | 244.2183 | 244.2183 | 244.2183 | 244.2183 | 244.2183 | 244.2183 | 244.2183 | 244.2183 | 244.2183 | 244.2183 | 244.2183 | 244.2183 | 244.2183 | 244.2183 | 244.2183 | 244.2183 | 244.2142 | 244.21 | 244.2058 | 244.2017 | 244.1975 | 244.1933 | 244.1892 | 244.185 | 244.1808 | 244.1767 | 244.1725 | 244.1683 | 244.1642 | 244.16 | 244.1558 | 244.1517 | 244.1475 | 244.1433 | 244.1392 | 244.135 | 244.1308 | 244.1267 | 244.1225 | 244.1183 | 244.1142 | 244.11 | 244.1058 | 244.1017 | 244.0975 | 244.0933
15.8 | 0 | 75.24 | 135.2987 | 132.924 | 162.9867 | 193.0493 | 220.5707 | 238.06 | 245.5507 | 245.5507 | 245.4507 | 0 | 7.524 | 15.048 | 22.572 | 30.096 | 37.62 | 45.144 | 52.668 | 60.192 | 67.716 | 75.24 | 87.2517 | 99.2635 | 111.2752 | 123.2869 | 135.2987 | 134.8237 | 134.3488 | 133.8739 | 133.3989 | 132.924 | 135.9303 | 138.9365 | 141.9428 | 144.9491 | 147.9553 | 150.9616 | 153.9679 | 156.9741 | 159.9804 | 162.9867 | 164.9908 | 166.995 | 168.9992 | 171.0034 | 173.0076 | 175.0117 | 177.0159 | 179.0201 | 181.0243 | 183.0284 | 185.0326 | 187.0368 | 189.041 | 191.0452 | 193.0493 | 194.8841 | 196.7188 | 198.5536 | 200.3884 | 202.2231 | 204.0579 | 205.8926 | 207.7274 | 209.5621 | 211.3969 | 213.2316 | 215.0664 | 216.9012 | 218.7359 | 220.5707 | 221.1536 | 221.7366 | 222.3196 | 222.9026 | 223.4856 | 224.0685 | 224.6515 | 225.2345 | 225.8175 | 226.4004 | 226.9834 | 227.5664 | 228.1494 | 228.7324 | 229.3153 | 229.8983 | 230.4813 | 231.0643 | 231.6472 | 232.2302 | 232.8132 | 233.3962 | 233.9792 | 234.5621 | 235.1451 | 235.7281 | 236.3111 | 236.894 | 237.477 | 238.06 | 238.3097 | 238.5594 | 238.8091 | 239.0588 | 239.3084 | 239.5581 | 239.8078 | 240.0575 | 240.3072 | 240.5569 | 240.8066 | 241.0563 | 241.306 | 241.5556 | 241.8053 | 242.055 | 242.3047 | 242.5544 | 242.8041 | 243.0538 | 243.3035 | 243.5532 | 243.8028 | 244.0525 | 244.3022 | 244.5519 | 244.8016 | 245.0513 | 245.301 | 245.5507 | 245.5507 | 245.5507 | 245.5507 | 245.5507 | 245.5507 | 245.5507 | 245.5507 | 245.5507 | 245.5507 | 245.5507 | 245.5507 | 245.5507 | 245.5507 | 245.5507 | 245.5507 | 245.5507 | 245.5507 | 245.5507 | 245.5507 | 245.5507 | 245.5507 | 245.5507 | 245.5507 | 245.5507 | 245.5507 | 245.5507 | 245.5507 | 245.5507 | 245.5507 | 245.5507 | 245.5473 | 245.544 | 245.5407 | 245.5373 | 245.534 | 245.5307 | 245.5273 | 245.524 | 245.5207 | 245.5173 | 245.514 | 245.5107 | 245.5073 | 245.504 | 245.5007 | 245.4973 | 245.494 | 245.4907 | 245.4873 | 245.484 | 245.4807 | 245.4773 | 245.474 | 245.4707 | 245.4673 | 245.464 | 245.4607 | 245.4573 | 245.454 | 245.4507
15.85 | 0 | 75.63 | 136.034 | 133.613 | 163.84 | 194.067 | 221.748 | 239.345 | 246.883 | 246.883 | 246.808 | 0 | 7.563 | 15.126 | 22.689 | 30.252 | 37.815 | 45.378 | 52.941 | 60.504 | 68.067 | 75.63 | 87.7108 | 99.7916 | 111.8724 | 123.9532 | 136.034 | 135.5498 | 135.0656 | 134.5814 | 134.0972 | 133.613 | 136.6357 | 139.6584 | 142.6811 | 145.7038 | 148.7265 | 151.7492 | 154.7719 | 157.7946 | 160.8173 | 163.84 | 165.8551 | 167.8703 | 169.8854 | 171.9005 | 173.9157 | 175.9308 | 177.9459 | 179.9611 | 181.9762 | 183.9913 | 186.0065 | 188.0216 | 190.0367 | 192.0519 | 194.067 | 195.9124 | 197.7578 | 199.6032 | 201.4486 | 203.294 | 205.1394 | 206.9848 | 208.8302 | 210.6756 | 212.521 | 214.3664 | 216.2118 | 218.0572 | 219.9026 | 221.748 | 222.3346 | 222.9211 | 223.5077 | 224.0943 | 224.6808 | 225.2674 | 225.854 | 226.4405 | 227.0271 | 227.6137 | 228.2002 | 228.7868 | 229.3734 | 229.9599 | 230.5465 | 231.1331 | 231.7196 | 232.3062 | 232.8928 | 233.4793 | 234.0659 | 234.6525 | 235.239 | 235.8256 | 236.4122 | 236.9987 | 237.5853 | 238.1719 | 238.7584 | 239.345 | 239.5963 | 239.8475 | 240.0988 | 240.3501 | 240.6013 | 240.8526 | 241.1039 | 241.3551 | 241.6064 | 241.8577 | 242.1089 | 242.3602 | 242.6115 | 242.8627 | 243.114 | 243.3653 | 243.6165 | 243.8678 | 244.1191 | 244.3703 | 244.6216 | 244.8729 | 245.1241 | 245.3754 | 245.6267 | 245.8779 | 246.1292 | 246.3805 | 246.6317 | 246.883 | 246.883 | 246.883 | 246.883 | 246.883 | 246.883 | 246.883 | 246.883 | 246.883 | 246.883 | 246.883 | 246.883 | 246.883 | 246.883 | 246.883 | 246.883 | 246.883 | 246.883 | 246.883 | 246.883 | 246.883 | 246.883 | 246.883 | 246.883 | 246.883 | 246.883 | 246.883 | 246.883 | 246.883 | 246.883 | 246.883 | 246.8805 | 246.878 | 246.8755 | 246.873 | 246.8705 | 246.868 | 246.8655 | 246.863 | 246.8605 | 246.858 | 246.8555 | 246.853 | 246.8505 | 246.848 | 246.8455 | 246.843 | 246.8405 | 246.838 | 246.8355 | 246.833 | 246.8305 | 246.828 | 246.8255 | 246.823 | 246.8205 | 246.818 | 246.8155 | 246.813 | 246.8105 | 246.808
15.9 | 0 | 76.02 | 136.7693 | 134.302 | 164.6933 | 195.0847 | 222.9253 | 240.63 | 248.2153 | 248.2153 | 248.1653 | 0 | 7.602 | 15.204 | 22.806 | 30.408 | 38.01 | 45.612 | 53.214 | 60.816 | 68.418 | 76.02 | 88.1699 | 100.3197 | 112.4696 | 124.6195 | 136.7693 | 136.2759 | 135.7824 | 135.2889 | 134.7955 | 134.302 | 137.3411 | 140.3803 | 143.4194 | 146.4585 | 149.4977 | 152.5368 | 155.5759 | 158.6151 | 161.6542 | 164.6933 | 166.7194 | 168.7455 | 170.7716 | 172.7977 | 174.8238 | 176.8499 | 178.876 | 180.902 | 182.9281 | 184.9542 | 186.9803 | 189.0064 | 191.0325 | 193.0586 | 195.0847 | 196.9407 | 198.7968 | 200.6528 | 202.5088 | 204.3649 | 206.2209 | 208.077 | 209.933 | 211.7891 | 213.6451 | 215.5012 | 217.3572 | 219.2132 | 221.0693 | 222.9253 | 223.5155 | 224.1056 | 224.6958 | 225.286 | 225.8761 | 226.4663 | 227.0564 | 227.6466 | 228.2367 | 228.8269 | 229.417 | 230.0072 | 230.5974 | 231.1875 | 231.7777 | 232.3678 | 232.958 | 233.5481 | 234.1383 | 234.7284 | 235.3186 | 235.9088 | 236.4989 | 237.0891 | 237.6792 | 238.2694 | 238.8595 | 239.4497 | 240.0398 | 240.63 | 240.8828 | 241.1357 | 241.3885 | 241.6414 | 241.8942 | 242.1471 | 242.3999 | 242.6528 | 242.9056 | 243.1584 | 243.4113 | 243.6641 | 243.917 | 244.1698 | 244.4227 | 244.6755 | 244.9284 | 245.1812 | 245.434 | 245.6869 | 245.9397 | 246.1926 | 246.4454 | 246.6983 | 246.9511 | 247.204 | 247.4568 | 247.7096 | 247.9625 | 248.2153 | 248.2153 | 248.2153 | 248.2153 | 248.2153 | 248.2153 | 248.2153 | 248.2153 | 248.2153 | 248.2153 | 248.2153 | 248.2153 | 248.2153 | 248.2153 | 248.2153 | 248.2153 | 248.2153 | 248.2153 | 248.2153 | 248.2153 | 248.2153 | 248.2153 | 248.2153 | 248.2153 | 248.2153 | 248.2153 | 248.2153 | 248.2153 | 248.2153 | 248.2153 | 248.2153 | 248.2137 | 248.212 | 248.2103 | 248.2087 | 248.207 | 248.2053 | 248.2037 | 248.202 | 248.2003 | 248.1987 | 248.197 | 248.1953 | 248.1937 | 248.192 | 248.1903 | 248.1887 | 248.187 | 248.1853 | 248.1837 | 248.182 | 248.1803 | 248.1787 | 248.177 | 248.1753 | 248.1737 | 248.172 | 248.1703 | 248.1687 | 248.167 | 248.1653
15.95 | 0 | 76.41 | 137.5047 | 134.991 | 165.5467 | 196.1023 | 224.1027 | 241.915 | 249.5477 | 249.5477 | 249.5227 | 0 | 7.641 | 15.282 | 22.923 | 30.564 | 38.205 | 45.846 | 53.487 | 61.128 | 68.769 | 76.41 | 88.6289 | 100.8479 | 113.0668 | 125.2857 | 137.5047 | 137.0019 | 136.4992 | 135.9965 | 135.4937 | 134.991 | 138.0466 | 141.1021 | 144.1577 | 147.2133 | 150.2688 | 153.3244 | 156.38 | 159.4355 | 162.4911 | 165.5467 | 167.5837 | 169.6208 | 171.6578 | 173.6948 | 175.7319 | 177.7689 | 179.806 | 181.843 | 183.8801 | 185.9171 | 187.9542 | 189.9912 | 192.0282 | 194.0653 | 196.1023 | 197.969 | 199.8357 | 201.7024 | 203.5691 | 205.4358 | 207.3025 | 209.1692 | 211.0358 | 212.9025 | 214.7692 | 216.6359 | 218.5026 | 220.3693 | 222.236 | 224.1027 | 224.6964 | 225.2902 | 225.8839 | 226.4776 | 227.0714 | 227.6651 | 228.2589 | 228.8526 | 229.4464 | 230.0401 | 230.6339 | 231.2276 | 231.8213 | 232.4151 | 233.0088 | 233.6026 | 234.1963 | 234.7901 | 235.3838 | 235.9776 | 236.5713 | 237.165 | 237.7588 | 238.3525 | 238.9463 | 239.54 | 240.1338 | 240.7275 | 241.3213 | 241.915 | 242.1694 | 242.4238 | 242.6783 | 242.9327 | 243.1871 | 243.4415 | 243.696 | 243.9504 | 244.2048 | 244.4592 | 244.7136 | 244.9681 | 245.2225 | 245.4769 | 245.7313 | 245.9858 | 246.2402 | 246.4946 | 246.749 | 247.0034 | 247.2579 | 247.5123 | 247.7667 | 248.0211 | 248.2756 | 248.53 | 248.7844 | 249.0388 | 249.2932 | 249.5477 | 249.5477 | 249.5477 | 249.5477 | 249.5477 | 249.5477 | 249.5477 | 249.5477 | 249.5477 | 249.5477 | 249.5477 | 249.5477 | 249.5477 | 249.5477 | 249.5477 | 249.5477 | 249.5477 | 249.5477 | 249.5477 | 249.5477 | 249.5477 | 249.5477 | 249.5477 | 249.5477 | 249.5477 | 249.5477 | 249.5477 | 249.5477 | 249.5477 | 249.5477 | 249.5477 | 249.5468 | 249.546 | 249.5452 | 249.5443 | 249.5435 | 249.5427 | 249.5418 | 249.541 | 249.5402 | 249.5393 | 249.5385 | 249.5377 | 249.5368 | 249.536 | 249.5352 | 249.5343 | 249.5335 | 249.5327 | 249.5318 | 249.531 | 249.5302 | 249.5293 | 249.5285 | 249.5277 | 249.5268 | 249.526 | 249.5252 | 249.5243 | 249.5235 | 249.5227
16 | 0 | 76.8 | 138.24 | 135.68 | 166.4 | 197.12 | 225.28 | 243.2 | 250.88 | 250.88 | 250.88 | 0 | 7.68 | 15.36 | 23.04 | 30.72 | 38.4 | 46.08 | 53.76 | 61.44 | 69.12 | 76.8 | 89.088 | 101.376 | 113.664 | 125.952 | 138.24 | 137.728 | 137.216 | 136.704 | 136.192 | 135.68 | 138.752 | 141.824 | 144.896 | 147.968 | 151.04 | 154.112 | 157.184 | 160.256 | 163.328 | 166.4 | 168.448 | 170.496 | 172.544 | 174.592 | 176.64 | 178.688 | 180.736 | 182.784 | 184.832 | 186.88 | 188.928 | 190.976 | 193.024 | 195.072 | 197.12 | 198.9973 | 200.8747 | 202.752 | 204.6293 | 206.5067 | 208.384 | 210.2613 | 212.1387 | 214.016 | 215.8933 | 217.7707 | 219.648 | 221.5253 | 223.4027 | 225.28 | 225.8773 | 226.4747 | 227.072 | 227.6693 | 228.2667 | 228.864 | 229.4613 | 230.0587 | 230.656 | 231.2533 | 231.8507 | 232.448 | 233.0453 | 233.6427 | 234.24 | 234.8373 | 235.4347 | 236.032 | 236.6293 | 237.2267 | 237.824 | 238.4213 | 239.0187 | 239.616 | 240.2133 | 240.8107 | 241.408 | 242.0053 | 242.6027 | 243.2 | 243.456 | 243.712 | 243.968 | 244.224 | 244.48 | 244.736 | 244.992 | 245.248 | 245.504 | 245.76 | 246.016 | 246.272 | 246.528 | 246.784 | 247.04 | 247.296 | 247.552 | 247.808 | 248.064 | 248.32 | 248.576 | 248.832 | 249.088 | 249.344 | 249.6 | 249.856 | 250.112 | 250.368 | 250.624 | 250.88 | 250.88 | 250.88 | 250.88 | 250.88 | 250.88 | 250.88 | 250.88 | 250.88 | 250.88 | 250.88 | 250.88 | 250.88 | 250.88 | 250.88 | 250.88 | 250.88 | 250.88 | 250.88 | 250.88 | 250.88 | 250.88 | 250.88 | 250.88 | 250.88 | 250.88 | 250.88 | 250.88 | 250.88 | 250.88 | 250.88 | 250.88 | 250.88 | 250.88 | 250.88 | 250.88 | 250.88 | 250.88 | 250.88 | 250.88 | 250.88 | 250.88 | 250.88 | 250.88 | 250.88 | 250.88 | 250.88 | 250.88 | 250.88 | 250.88 | 250.88 | 250.88 | 250.88 | 250.88 | 250.88 | 250.88 | 250.88 | 250.88 | 250.88 | 250.88 | 250.88

## Sheet2
SR4-2 Transition, Pyramidal, Supply Air Systems
Transition Length, L | 230 | mm
Incoming (Pre-Transition) | (A1)
Duct Width, W (mm) | 400 | mm
Duct Height, H (mm) | 400 | mm
Air Flow, Q (CFM) | 600 | CFM
Air Velocity, VC (FPM) | 348.513 | FPM
Velocity Pressure, VP ("w.g.) | 0.0075724 | "w.g.
Outgoing (Post-Transition) | (A0)
Duct Width, W (mm) | 300 | mm
Duct Height, H (mm) | 300 | mm
Air Flow, Q (CFM) | 600 | CFM
Air Velocity, VC (FPM) | 619.5787 | FPM
Velocity Pressure, VP ("w.g.) | 0.023932 | "w.g.
θ1 (Side) | 24.5264 | °
θ2 (Top) | 24.5264 | °
θ (Max) | 25 | °
A0 /A1 | 0.5625
C | 0.054
Frictional Pressure Loss, ΔP | 0.0012924 | "w.g.
| 0.32309 | Pa
Ashrae SR4-2
A0 /A1 | θ
| 10 | 15 | 20 | 30 | 45 | 60 | 90 | 120 | 150 | 180
0.1 | 0.05 | 0.05 | 0.05 | 0.05 | 0.07 | 0.08 | 0.19 | 0.29 | 0.37 | 0.43
0.17 | 0.05 | 0.05 | 0.05 | 0.04 | 0.06 | 0.07 | 0.18 | 0.28 | 0.36 | 0.42
0.25 | 0.06 | 0.05 | 0.05 | 0.04 | 0.06 | 0.07 | 0.17 | 0.27 | 0.35 | 0.41
0.5 | 0.06 | 0.07 | 0.07 | 0.05 | 0.06 | 0.06 | 0.12 | 0.18 | 0.24 | 0.26
1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 0.6 | 0.84 | 1 | 1.2 | 1.32 | 1.32 | 1.32 | 1.28 | 1.24 | 1.2
4 | 4 | 5.76 | 7.2 | 8.32 | 9.28 | 9.92 | 10.24 | 10.24 | 10.24 | 10.24
10 | 30 | 50 | 53 | 64 | 75 | 84 | 89 | 91 | 91 | 88
16 | 76.8 | 138.24 | 135.68 | 166.4 | 197.12 | 225.28 | 243.2 | 250.88 | 250.88 | 250.88
A0 /A1 θ | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 41 | 42 | 43 | 44 | 45 | 46 | 47 | 48 | 49 | 50 | 51 | 52 | 53 | 54 | 55 | 56 | 57 | 58 | 59 | 60 | 61 | 62 | 63 | 64 | 65 | 66 | 67 | 68 | 69 | 70 | 71 | 72 | 73 | 74 | 75 | 76 | 77 | 78 | 79 | 80 | 81 | 82 | 83 | 84 | 85 | 86 | 87 | 88 | 89 | 90 | 91 | 92 | 93 | 94 | 95 | 96 | 97 | 98 | 99 | 100 | 101 | 102 | 103 | 104 | 105 | 106 | 107 | 108 | 109 | 110 | 111 | 112 | 113 | 114 | 115 | 116 | 117 | 118 | 119 | 120 | 121 | 122 | 123 | 124 | 125 | 126 | 127 | 128 | 129 | 130 | 131 | 132 | 133 | 134 | 135 | 136 | 137 | 138 | 139 | 140 | 141 | 142 | 143 | 144 | 145 | 146 | 147 | 148 | 149 | 150 | 151 | 152 | 153 | 154 | 155 | 156 | 157 | 158 | 159 | 160 | 161 | 162 | 163 | 164 | 165 | 166 | 167 | 168 | 169 | 170 | 171 | 172 | 173 | 174 | 175 | 176 | 177 | 178 | 179 | 180
0.1 | 0 | 0.005 | 0.01 | 0.015 | 0.02 | 0.025 | 0.03 | 0.035 | 0.04 | 0.045 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.051333 | 0.052667 | 0.054 | 0.055333 | 0.056667 | 0.058 | 0.059333 | 0.060667 | 0.062 | 0.063333 | 0.064667 | 0.066 | 0.067333 | 0.068667 | 0.07 | 0.070667 | 0.071333 | 0.072 | 0.072667 | 0.073333 | 0.074 | 0.074667 | 0.075333 | 0.076 | 0.076667 | 0.077333 | 0.078 | 0.078667 | 0.079333 | 0.08 | 0.083667 | 0.087333 | 0.091 | 0.094667 | 0.098333 | 0.102 | 0.10567 | 0.10933 | 0.113 | 0.11667 | 0.12033 | 0.124 | 0.12767 | 0.13133 | 0.135 | 0.13867 | 0.14233 | 0.146 | 0.14967 | 0.15333 | 0.157 | 0.16067 | 0.16433 | 0.168 | 0.17167 | 0.17533 | 0.179 | 0.18267 | 0.18633 | 0.19 | 0.19333 | 0.19667 | 0.2 | 0.20333 | 0.20667 | 0.21 | 0.21333 | 0.21667 | 0.22 | 0.22333 | 0.22667 | 0.23 | 0.23333 | 0.23667 | 0.24 | 0.24333 | 0.24667 | 0.25 | 0.25333 | 0.25667 | 0.26 | 0.26333 | 0.26667 | 0.27 | 0.27333 | 0.27667 | 0.28 | 0.28333 | 0.28667 | 0.29 | 0.29267 | 0.29533 | 0.298 | 0.30067 | 0.30333 | 0.306 | 0.30867 | 0.31133 | 0.314 | 0.31667 | 0.31933 | 0.322 | 0.32467 | 0.32733 | 0.33 | 0.33267 | 0.33533 | 0.338 | 0.34067 | 0.34333 | 0.346 | 0.34867 | 0.35133 | 0.354 | 0.35667 | 0.35933 | 0.362 | 0.36467 | 0.36733 | 0.37 | 0.372 | 0.374 | 0.376 | 0.378 | 0.38 | 0.382 | 0.384 | 0.386 | 0.388 | 0.39 | 0.392 | 0.394 | 0.396 | 0.398 | 0.4 | 0.402 | 0.404 | 0.406 | 0.408 | 0.41 | 0.412 | 0.414 | 0.416 | 0.418 | 0.42 | 0.422 | 0.424 | 0.426 | 0.428 | 0.43
0.15 | 0 | 0.005 | 0.01 | 0.015 | 0.02 | 0.025 | 0.03 | 0.035 | 0.04 | 0.045 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.049286 | 0.048571 | 0.047857 | 0.047143 | 0.046429 | 0.045714 | 0.045 | 0.044286 | 0.043571 | 0.042857 | 0.04419 | 0.045524 | 0.046857 | 0.04819 | 0.049524 | 0.050857 | 0.05219 | 0.053524 | 0.054857 | 0.05619 | 0.057524 | 0.058857 | 0.06019 | 0.061524 | 0.062857 | 0.063524 | 0.06419 | 0.064857 | 0.065524 | 0.06619 | 0.066857 | 0.067524 | 0.06819 | 0.068857 | 0.069524 | 0.07019 | 0.070857 | 0.071524 | 0.07219 | 0.072857 | 0.076524 | 0.08019 | 0.083857 | 0.087524 | 0.09119 | 0.094857 | 0.098524 | 0.10219 | 0.10586 | 0.10952 | 0.11319 | 0.11686 | 0.12052 | 0.12419 | 0.12786 | 0.13152 | 0.13519 | 0.13886 | 0.14252 | 0.14619 | 0.14986 | 0.15352 | 0.15719 | 0.16086 | 0.16452 | 0.16819 | 0.17186 | 0.17552 | 0.17919 | 0.18286 | 0.18619 | 0.18952 | 0.19286 | 0.19619 | 0.19952 | 0.20286 | 0.20619 | 0.20952 | 0.21286 | 0.21619 | 0.21952 | 0.22286 | 0.22619 | 0.22952 | 0.23286 | 0.23619 | 0.23952 | 0.24286 | 0.24619 | 0.24952 | 0.25286 | 0.25619 | 0.25952 | 0.26286 | 0.26619 | 0.26952 | 0.27286 | 0.27619 | 0.27952 | 0.28286 | 0.28552 | 0.28819 | 0.29086 | 0.29352 | 0.29619 | 0.29886 | 0.30152 | 0.30419 | 0.30686 | 0.30952 | 0.31219 | 0.31486 | 0.31752 | 0.32019 | 0.32286 | 0.32552 | 0.32819 | 0.33086 | 0.33352 | 0.33619 | 0.33886 | 0.34152 | 0.34419 | 0.34686 | 0.34952 | 0.35219 | 0.35486 | 0.35752 | 0.36019 | 0.36286 | 0.36486 | 0.36686 | 0.36886 | 0.37086 | 0.37286 | 0.37486 | 0.37686 | 0.37886 | 0.38086 | 0.38286 | 0.38486 | 0.38686 | 0.38886 | 0.39086 | 0.39286 | 0.39486 | 0.39686 | 0.39886 | 0.40086 | 0.40286 | 0.40486 | 0.40686 | 0.40886 | 0.41086 | 0.41286 | 0.41486 | 0.41686 | 0.41886 | 0.42086 | 0.42286
0.17 | 0 | 0.005 | 0.01 | 0.015 | 0.02 | 0.025 | 0.03 | 0.035 | 0.04 | 0.045 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.049 | 0.048 | 0.047 | 0.046 | 0.045 | 0.044 | 0.043 | 0.042 | 0.041 | 0.04 | 0.041333 | 0.042667 | 0.044 | 0.045333 | 0.046667 | 0.048 | 0.049333 | 0.050667 | 0.052 | 0.053333 | 0.054667 | 0.056 | 0.057333 | 0.058667 | 0.06 | 0.060667 | 0.061333 | 0.062 | 0.062667 | 0.063333 | 0.064 | 0.064667 | 0.065333 | 0.066 | 0.066667 | 0.067333 | 0.068 | 0.068667 | 0.069333 | 0.07 | 0.073667 | 0.077333 | 0.081 | 0.084667 | 0.088333 | 0.092 | 0.095667 | 0.099333 | 0.103 | 0.10667 | 0.11033 | 0.114 | 0.11767 | 0.12133 | 0.125 | 0.12867 | 0.13233 | 0.136 | 0.13967 | 0.14333 | 0.147 | 0.15067 | 0.15433 | 0.158 | 0.16167 | 0.16533 | 0.169 | 0.17267 | 0.17633 | 0.18 | 0.18333 | 0.18667 | 0.19 | 0.19333 | 0.19667 | 0.2 | 0.20333 | 0.20667 | 0.21 | 0.21333 | 0.21667 | 0.22 | 0.22333 | 0.22667 | 0.23 | 0.23333 | 0.23667 | 0.24 | 0.24333 | 0.24667 | 0.25 | 0.25333 | 0.25667 | 0.26 | 0.26333 | 0.26667 | 0.27 | 0.27333 | 0.27667 | 0.28 | 0.28267 | 0.28533 | 0.288 | 0.29067 | 0.29333 | 0.296 | 0.29867 | 0.30133 | 0.304 | 0.30667 | 0.30933 | 0.312 | 0.31467 | 0.31733 | 0.32 | 0.32267 | 0.32533 | 0.328 | 0.33067 | 0.33333 | 0.336 | 0.33867 | 0.34133 | 0.344 | 0.34667 | 0.34933 | 0.352 | 0.35467 | 0.35733 | 0.36 | 0.362 | 0.364 | 0.366 | 0.368 | 0.37 | 0.372 | 0.374 | 0.376 | 0.378 | 0.38 | 0.382 | 0.384 | 0.386 | 0.388 | 0.39 | 0.392 | 0.394 | 0.396 | 0.398 | 0.4 | 0.402 | 0.404 | 0.406 | 0.408 | 0.41 | 0.412 | 0.414 | 0.416 | 0.418 | 0.42
0.2 | 0 | 0.005375 | 0.01075 | 0.016125 | 0.0215 | 0.026875 | 0.03225 | 0.037625 | 0.043 | 0.048375 | 0.05375 | 0.053 | 0.05225 | 0.0515 | 0.05075 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.049 | 0.048 | 0.047 | 0.046 | 0.045 | 0.044 | 0.043 | 0.042 | 0.041 | 0.04 | 0.041333 | 0.042667 | 0.044 | 0.045333 | 0.046667 | 0.048 | 0.049333 | 0.050667 | 0.052 | 0.053333 | 0.054667 | 0.056 | 0.057333 | 0.058667 | 0.06 | 0.060667 | 0.061333 | 0.062 | 0.062667 | 0.063333 | 0.064 | 0.064667 | 0.065333 | 0.066 | 0.066667 | 0.067333 | 0.068 | 0.068667 | 0.069333 | 0.07 | 0.073542 | 0.077083 | 0.080625 | 0.084167 | 0.087708 | 0.09125 | 0.094792 | 0.098333 | 0.10187 | 0.10542 | 0.10896 | 0.1125 | 0.11604 | 0.11958 | 0.12312 | 0.12667 | 0.13021 | 0.13375 | 0.13729 | 0.14083 | 0.14438 | 0.14792 | 0.15146 | 0.155 | 0.15854 | 0.16208 | 0.16562 | 0.16917 | 0.17271 | 0.17625 | 0.17958 | 0.18292 | 0.18625 | 0.18958 | 0.19292 | 0.19625 | 0.19958 | 0.20292 | 0.20625 | 0.20958 | 0.21292 | 0.21625 | 0.21958 | 0.22292 | 0.22625 | 0.22958 | 0.23292 | 0.23625 | 0.23958 | 0.24292 | 0.24625 | 0.24958 | 0.25292 | 0.25625 | 0.25958 | 0.26292 | 0.26625 | 0.26958 | 0.27292 | 0.27625 | 0.27892 | 0.28158 | 0.28425 | 0.28692 | 0.28958 | 0.29225 | 0.29492 | 0.29758 | 0.30025 | 0.30292 | 0.30558 | 0.30825 | 0.31092 | 0.31358 | 0.31625 | 0.31892 | 0.32158 | 0.32425 | 0.32692 | 0.32958 | 0.33225 | 0.33492 | 0.33758 | 0.34025 | 0.34292 | 0.34558 | 0.34825 | 0.35092 | 0.35358 | 0.35625 | 0.35825 | 0.36025 | 0.36225 | 0.36425 | 0.36625 | 0.36825 | 0.37025 | 0.37225 | 0.37425 | 0.37625 | 0.37825 | 0.38025 | 0.38225 | 0.38425 | 0.38625 | 0.38825 | 0.39025 | 0.39225 | 0.39425 | 0.39625 | 0.39825 | 0.40025 | 0.40225 | 0.40425 | 0.40625 | 0.40825 | 0.41025 | 0.41225 | 0.41425 | 0.41625
0.25 | 0 | 0.006 | 0.012 | 0.018 | 0.024 | 0.03 | 0.036 | 0.042 | 0.048 | 0.054 | 0.06 | 0.058 | 0.056 | 0.054 | 0.052 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.049 | 0.048 | 0.047 | 0.046 | 0.045 | 0.044 | 0.043 | 0.042 | 0.041 | 0.04 | 0.041333 | 0.042667 | 0.044 | 0.045333 | 0.046667 | 0.048 | 0.049333 | 0.050667 | 0.052 | 0.053333 | 0.054667 | 0.056 | 0.057333 | 0.058667 | 0.06 | 0.060667 | 0.061333 | 0.062 | 0.062667 | 0.063333 | 0.064 | 0.064667 | 0.065333 | 0.066 | 0.066667 | 0.067333 | 0.068 | 0.068667 | 0.069333 | 0.07 | 0.073333 | 0.076667 | 0.08 | 0.083333 | 0.086667 | 0.09 | 0.093333 | 0.096667 | 0.1 | 0.10333 | 0.10667 | 0.11 | 0.11333 | 0.11667 | 0.12 | 0.12333 | 0.12667 | 0.13 | 0.13333 | 0.13667 | 0.14 | 0.14333 | 0.14667 | 0.15 | 0.15333 | 0.15667 | 0.16 | 0.16333 | 0.16667 | 0.17 | 0.17333 | 0.17667 | 0.18 | 0.18333 | 0.18667 | 0.19 | 0.19333 | 0.19667 | 0.2 | 0.20333 | 0.20667 | 0.21 | 0.21333 | 0.21667 | 0.22 | 0.22333 | 0.22667 | 0.23 | 0.23333 | 0.23667 | 0.24 | 0.24333 | 0.24667 | 0.25 | 0.25333 | 0.25667 | 0.26 | 0.26333 | 0.26667 | 0.27 | 0.27267 | 0.27533 | 0.278 | 0.28067 | 0.28333 | 0.286 | 0.28867 | 0.29133 | 0.294 | 0.29667 | 0.29933 | 0.302 | 0.30467 | 0.30733 | 0.31 | 0.31267 | 0.31533 | 0.318 | 0.32067 | 0.32333 | 0.326 | 0.32867 | 0.33133 | 0.334 | 0.33667 | 0.33933 | 0.342 | 0.34467 | 0.34733 | 0.35 | 0.352 | 0.354 | 0.356 | 0.358 | 0.36 | 0.362 | 0.364 | 0.366 | 0.368 | 0.37 | 0.372 | 0.374 | 0.376 | 0.378 | 0.38 | 0.382 | 0.384 | 0.386 | 0.388 | 0.39 | 0.392 | 0.394 | 0.396 | 0.398 | 0.4 | 0.402 | 0.404 | 0.406 | 0.408 | 0.41
0.3 | 0 | 0.006 | 0.012 | 0.018 | 0.024 | 0.03 | 0.036 | 0.042 | 0.048 | 0.054 | 0.06 | 0.0588 | 0.0576 | 0.0564 | 0.0552 | 0.054 | 0.054 | 0.054 | 0.054 | 0.054 | 0.054 | 0.0528 | 0.0516 | 0.0504 | 0.0492 | 0.048 | 0.0468 | 0.0456 | 0.0444 | 0.0432 | 0.042 | 0.0432 | 0.0444 | 0.0456 | 0.0468 | 0.048 | 0.0492 | 0.0504 | 0.0516 | 0.0528 | 0.054 | 0.0552 | 0.0564 | 0.0576 | 0.0588 | 0.06 | 0.060533 | 0.061067 | 0.0616 | 0.062133 | 0.062667 | 0.0632 | 0.063733 | 0.064267 | 0.0648 | 0.065333 | 0.065867 | 0.0664 | 0.066933 | 0.067467 | 0.068 | 0.071067 | 0.074133 | 0.0772 | 0.080267 | 0.083333 | 0.0864 | 0.089467 | 0.092533 | 0.0956 | 0.098667 | 0.10173 | 0.1048 | 0.10787 | 0.11093 | 0.114 | 0.11707 | 0.12013 | 0.1232 | 0.12627 | 0.12933 | 0.1324 | 0.13547 | 0.13853 | 0.1416 | 0.14467 | 0.14773 | 0.1508 | 0.15387 | 0.15693 | 0.16 | 0.16307 | 0.16613 | 0.1692 | 0.17227 | 0.17533 | 0.1784 | 0.18147 | 0.18453 | 0.1876 | 0.19067 | 0.19373 | 0.1968 | 0.19987 | 0.20293 | 0.206 | 0.20907 | 0.21213 | 0.2152 | 0.21827 | 0.22133 | 0.2244 | 0.22747 | 0.23053 | 0.2336 | 0.23667 | 0.23973 | 0.2428 | 0.24587 | 0.24893 | 0.252 | 0.25453 | 0.25707 | 0.2596 | 0.26213 | 0.26467 | 0.2672 | 0.26973 | 0.27227 | 0.2748 | 0.27733 | 0.27987 | 0.2824 | 0.28493 | 0.28747 | 0.29 | 0.29253 | 0.29507 | 0.2976 | 0.30013 | 0.30267 | 0.3052 | 0.30773 | 0.31027 | 0.3128 | 0.31533 | 0.31787 | 0.3204 | 0.32293 | 0.32547 | 0.328 | 0.32973 | 0.33147 | 0.3332 | 0.33493 | 0.33667 | 0.3384 | 0.34013 | 0.34187 | 0.3436 | 0.34533 | 0.34707 | 0.3488 | 0.35053 | 0.35227 | 0.354 | 0.35573 | 0.35747 | 0.3592 | 0.36093 | 0.36267 | 0.3644 | 0.36613 | 0.36787 | 0.3696 | 0.37133 | 0.37307 | 0.3748 | 0.37653 | 0.37827 | 0.38
0.35 | 0 | 0.006 | 0.012 | 0.018 | 0.024 | 0.03 | 0.036 | 0.042 | 0.048 | 0.054 | 0.06 | 0.0596 | 0.0592 | 0.0588 | 0.0584 | 0.058 | 0.058 | 0.058 | 0.058 | 0.058 | 0.058 | 0.0566 | 0.0552 | 0.0538 | 0.0524 | 0.051 | 0.0496 | 0.0482 | 0.0468 | 0.0454 | 0.044 | 0.045067 | 0.046133 | 0.0472 | 0.048267 | 0.049333 | 0.0504 | 0.051467 | 0.052533 | 0.0536 | 0.054667 | 0.055733 | 0.0568 | 0.057867 | 0.058933 | 0.06 | 0.0604 | 0.0608 | 0.0612 | 0.0616 | 0.062 | 0.0624 | 0.0628 | 0.0632 | 0.0636 | 0.064 | 0.0644 | 0.0648 | 0.0652 | 0.0656 | 0.066 | 0.0688 | 0.0716 | 0.0744 | 0.0772 | 0.08 | 0.0828 | 0.0856 | 0.0884 | 0.0912 | 0.094 | 0.0968 | 0.0996 | 0.1024 | 0.1052 | 0.108 | 0.1108 | 0.1136 | 0.1164 | 0.1192 | 0.122 | 0.1248 | 0.1276 | 0.1304 | 0.1332 | 0.136 | 0.1388 | 0.1416 | 0.1444 | 0.1472 | 0.15 | 0.1528 | 0.1556 | 0.1584 | 0.1612 | 0.164 | 0.1668 | 0.1696 | 0.1724 | 0.1752 | 0.178 | 0.1808 | 0.1836 | 0.1864 | 0.1892 | 0.192 | 0.1948 | 0.1976 | 0.2004 | 0.2032 | 0.206 | 0.2088 | 0.2116 | 0.2144 | 0.2172 | 0.22 | 0.2228 | 0.2256 | 0.2284 | 0.2312 | 0.234 | 0.2364 | 0.2388 | 0.2412 | 0.2436 | 0.246 | 0.2484 | 0.2508 | 0.2532 | 0.2556 | 0.258 | 0.2604 | 0.2628 | 0.2652 | 0.2676 | 0.27 | 0.2724 | 0.2748 | 0.2772 | 0.2796 | 0.282 | 0.2844 | 0.2868 | 0.2892 | 0.2916 | 0.294 | 0.2964 | 0.2988 | 0.3012 | 0.3036 | 0.306 | 0.30747 | 0.30893 | 0.3104 | 0.31187 | 0.31333 | 0.3148 | 0.31627 | 0.31773 | 0.3192 | 0.32067 | 0.32213 | 0.3236 | 0.32507 | 0.32653 | 0.328 | 0.32947 | 0.33093 | 0.3324 | 0.33387 | 0.33533 | 0.3368 | 0.33827 | 0.33973 | 0.3412 | 0.34267 | 0.34413 | 0.3456 | 0.34707 | 0.34853 | 0.35
0.4 | 0 | 0.006 | 0.012 | 0.018 | 0.024 | 0.03 | 0.036 | 0.042 | 0.048 | 0.054 | 0.06 | 0.0604 | 0.0608 | 0.0612 | 0.0616 | 0.062 | 0.062 | 0.062 | 0.062 | 0.062 | 0.062 | 0.0604 | 0.0588 | 0.0572 | 0.0556 | 0.054 | 0.0524 | 0.0508 | 0.0492 | 0.0476 | 0.046 | 0.046933 | 0.047867 | 0.0488 | 0.049733 | 0.050667 | 0.0516 | 0.052533 | 0.053467 | 0.0544 | 0.055333 | 0.056267 | 0.0572 | 0.058133 | 0.059067 | 0.06 | 0.060267 | 0.060533 | 0.0608 | 0.061067 | 0.061333 | 0.0616 | 0.061867 | 0.062133 | 0.0624 | 0.062667 | 0.062933 | 0.0632 | 0.063467 | 0.063733 | 0.064 | 0.066533 | 0.069067 | 0.0716 | 0.074133 | 0.076667 | 0.0792 | 0.081733 | 0.084267 | 0.0868 | 0.089333 | 0.091867 | 0.0944 | 0.096933 | 0.099467 | 0.102 | 0.10453 | 0.10707 | 0.1096 | 0.11213 | 0.11467 | 0.1172 | 0.11973 | 0.12227 | 0.1248 | 0.12733 | 0.12987 | 0.1324 | 0.13493 | 0.13747 | 0.14 | 0.14253 | 0.14507 | 0.1476 | 0.15013 | 0.15267 | 0.1552 | 0.15773 | 0.16027 | 0.1628 | 0.16533 | 0.16787 | 0.1704 | 0.17293 | 0.17547 | 0.178 | 0.18053 | 0.18307 | 0.1856 | 0.18813 | 0.19067 | 0.1932 | 0.19573 | 0.19827 | 0.2008 | 0.20333 | 0.20587 | 0.2084 | 0.21093 | 0.21347 | 0.216 | 0.21827 | 0.22053 | 0.2228 | 0.22507 | 0.22733 | 0.2296 | 0.23187 | 0.23413 | 0.2364 | 0.23867 | 0.24093 | 0.2432 | 0.24547 | 0.24773 | 0.25 | 0.25227 | 0.25453 | 0.2568 | 0.25907 | 0.26133 | 0.2636 | 0.26587 | 0.26813 | 0.2704 | 0.27267 | 0.27493 | 0.2772 | 0.27947 | 0.28173 | 0.284 | 0.2852 | 0.2864 | 0.2876 | 0.2888 | 0.29 | 0.2912 | 0.2924 | 0.2936 | 0.2948 | 0.296 | 0.2972 | 0.2984 | 0.2996 | 0.3008 | 0.302 | 0.3032 | 0.3044 | 0.3056 | 0.3068 | 0.308 | 0.3092 | 0.3104 | 0.3116 | 0.3128 | 0.314 | 0.3152 | 0.3164 | 0.3176 | 0.3188 | 0.32
0.45 | 0 | 0.006 | 0.012 | 0.018 | 0.024 | 0.03 | 0.036 | 0.042 | 0.048 | 0.054 | 0.06 | 0.0612 | 0.0624 | 0.0636 | 0.0648 | 0.066 | 0.066 | 0.066 | 0.066 | 0.066 | 0.066 | 0.0642 | 0.0624 | 0.0606 | 0.0588 | 0.057 | 0.0552 | 0.0534 | 0.0516 | 0.0498 | 0.048 | 0.0488 | 0.0496 | 0.0504 | 0.0512 | 0.052 | 0.0528 | 0.0536 | 0.0544 | 0.0552 | 0.056 | 0.0568 | 0.0576 | 0.0584 | 0.0592 | 0.06 | 0.060133 | 0.060267 | 0.0604 | 0.060533 | 0.060667 | 0.0608 | 0.060933 | 0.061067 | 0.0612 | 0.061333 | 0.061467 | 0.0616 | 0.061733 | 0.061867 | 0.062 | 0.064267 | 0.066533 | 0.0688 | 0.071067 | 0.073333 | 0.0756 | 0.077867 | 0.080133 | 0.0824 | 0.084667 | 0.086933 | 0.0892 | 0.091467 | 0.093733 | 0.096 | 0.098267 | 0.10053 | 0.1028 | 0.10507 | 0.10733 | 0.1096 | 0.11187 | 0.11413 | 0.1164 | 0.11867 | 0.12093 | 0.1232 | 0.12547 | 0.12773 | 0.13 | 0.13227 | 0.13453 | 0.1368 | 0.13907 | 0.14133 | 0.1436 | 0.14587 | 0.14813 | 0.1504 | 0.15267 | 0.15493 | 0.1572 | 0.15947 | 0.16173 | 0.164 | 0.16627 | 0.16853 | 0.1708 | 0.17307 | 0.17533 | 0.1776 | 0.17987 | 0.18213 | 0.1844 | 0.18667 | 0.18893 | 0.1912 | 0.19347 | 0.19573 | 0.198 | 0.20013 | 0.20227 | 0.2044 | 0.20653 | 0.20867 | 0.2108 | 0.21293 | 0.21507 | 0.2172 | 0.21933 | 0.22147 | 0.2236 | 0.22573 | 0.22787 | 0.23 | 0.23213 | 0.23427 | 0.2364 | 0.23853 | 0.24067 | 0.2428 | 0.24493 | 0.24707 | 0.2492 | 0.25133 | 0.25347 | 0.2556 | 0.25773 | 0.25987 | 0.262 | 0.26293 | 0.26387 | 0.2648 | 0.26573 | 0.26667 | 0.2676 | 0.26853 | 0.26947 | 0.2704 | 0.27133 | 0.27227 | 0.2732 | 0.27413 | 0.27507 | 0.276 | 0.27693 | 0.27787 | 0.2788 | 0.27973 | 0.28067 | 0.2816 | 0.28253 | 0.28347 | 0.2844 | 0.28533 | 0.28627 | 0.2872 | 0.28813 | 0.28907 | 0.29
0.5 | 0 | 0.006 | 0.012 | 0.018 | 0.024 | 0.03 | 0.036 | 0.042 | 0.048 | 0.054 | 0.06 | 0.062 | 0.064 | 0.066 | 0.068 | 0.07 | 0.07 | 0.07 | 0.07 | 0.07 | 0.07 | 0.068 | 0.066 | 0.064 | 0.062 | 0.06 | 0.058 | 0.056 | 0.054 | 0.052 | 0.05 | 0.050667 | 0.051333 | 0.052 | 0.052667 | 0.053333 | 0.054 | 0.054667 | 0.055333 | 0.056 | 0.056667 | 0.057333 | 0.058 | 0.058667 | 0.059333 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.062 | 0.064 | 0.066 | 0.068 | 0.07 | 0.072 | 0.074 | 0.076 | 0.078 | 0.08 | 0.082 | 0.084 | 0.086 | 0.088 | 0.09 | 0.092 | 0.094 | 0.096 | 0.098 | 0.1 | 0.102 | 0.104 | 0.106 | 0.108 | 0.11 | 0.112 | 0.114 | 0.116 | 0.118 | 0.12 | 0.122 | 0.124 | 0.126 | 0.128 | 0.13 | 0.132 | 0.134 | 0.136 | 0.138 | 0.14 | 0.142 | 0.144 | 0.146 | 0.148 | 0.15 | 0.152 | 0.154 | 0.156 | 0.158 | 0.16 | 0.162 | 0.164 | 0.166 | 0.168 | 0.17 | 0.172 | 0.174 | 0.176 | 0.178 | 0.18 | 0.182 | 0.184 | 0.186 | 0.188 | 0.19 | 0.192 | 0.194 | 0.196 | 0.198 | 0.2 | 0.202 | 0.204 | 0.206 | 0.208 | 0.21 | 0.212 | 0.214 | 0.216 | 0.218 | 0.22 | 0.222 | 0.224 | 0.226 | 0.228 | 0.23 | 0.232 | 0.234 | 0.236 | 0.238 | 0.24 | 0.24067 | 0.24133 | 0.242 | 0.24267 | 0.24333 | 0.244 | 0.24467 | 0.24533 | 0.246 | 0.24667 | 0.24733 | 0.248 | 0.24867 | 0.24933 | 0.25 | 0.25067 | 0.25133 | 0.252 | 0.25267 | 0.25333 | 0.254 | 0.25467 | 0.25533 | 0.256 | 0.25667 | 0.25733 | 0.258 | 0.25867 | 0.25933 | 0.26
0.55 | 0 | 0.0054 | 0.0108 | 0.0162 | 0.0216 | 0.027 | 0.0324 | 0.0378 | 0.0432 | 0.0486 | 0.054 | 0.0558 | 0.0576 | 0.0594 | 0.0612 | 0.063 | 0.063 | 0.063 | 0.063 | 0.063 | 0.063 | 0.0612 | 0.0594 | 0.0576 | 0.0558 | 0.054 | 0.0522 | 0.0504 | 0.0486 | 0.0468 | 0.045 | 0.0456 | 0.0462 | 0.0468 | 0.0474 | 0.048 | 0.0486 | 0.0492 | 0.0498 | 0.0504 | 0.051 | 0.0516 | 0.0522 | 0.0528 | 0.0534 | 0.054 | 0.054 | 0.054 | 0.054 | 0.054 | 0.054 | 0.054 | 0.054 | 0.054 | 0.054 | 0.054 | 0.054 | 0.054 | 0.054 | 0.054 | 0.054 | 0.0558 | 0.0576 | 0.0594 | 0.0612 | 0.063 | 0.0648 | 0.0666 | 0.0684 | 0.0702 | 0.072 | 0.0738 | 0.0756 | 0.0774 | 0.0792 | 0.081 | 0.0828 | 0.0846 | 0.0864 | 0.0882 | 0.09 | 0.0918 | 0.0936 | 0.0954 | 0.0972 | 0.099 | 0.1008 | 0.1026 | 0.1044 | 0.1062 | 0.108 | 0.1098 | 0.1116 | 0.1134 | 0.1152 | 0.117 | 0.1188 | 0.1206 | 0.1224 | 0.1242 | 0.126 | 0.1278 | 0.1296 | 0.1314 | 0.1332 | 0.135 | 0.1368 | 0.1386 | 0.1404 | 0.1422 | 0.144 | 0.1458 | 0.1476 | 0.1494 | 0.1512 | 0.153 | 0.1548 | 0.1566 | 0.1584 | 0.1602 | 0.162 | 0.1638 | 0.1656 | 0.1674 | 0.1692 | 0.171 | 0.1728 | 0.1746 | 0.1764 | 0.1782 | 0.18 | 0.1818 | 0.1836 | 0.1854 | 0.1872 | 0.189 | 0.1908 | 0.1926 | 0.1944 | 0.1962 | 0.198 | 0.1998 | 0.2016 | 0.2034 | 0.2052 | 0.207 | 0.2088 | 0.2106 | 0.2124 | 0.2142 | 0.216 | 0.2166 | 0.2172 | 0.2178 | 0.2184 | 0.219 | 0.2196 | 0.2202 | 0.2208 | 0.2214 | 0.222 | 0.2226 | 0.2232 | 0.2238 | 0.2244 | 0.225 | 0.2256 | 0.2262 | 0.2268 | 0.2274 | 0.228 | 0.2286 | 0.2292 | 0.2298 | 0.2304 | 0.231 | 0.2316 | 0.2322 | 0.2328 | 0.2334 | 0.234
0.6 | 0 | 0.0048 | 0.0096 | 0.0144 | 0.0192 | 0.024 | 0.0288 | 0.0336 | 0.0384 | 0.0432 | 0.048 | 0.0496 | 0.0512 | 0.0528 | 0.0544 | 0.056 | 0.056 | 0.056 | 0.056 | 0.056 | 0.056 | 0.0544 | 0.0528 | 0.0512 | 0.0496 | 0.048 | 0.0464 | 0.0448 | 0.0432 | 0.0416 | 0.04 | 0.040533 | 0.041067 | 0.0416 | 0.042133 | 0.042667 | 0.0432 | 0.043733 | 0.044267 | 0.0448 | 0.045333 | 0.045867 | 0.0464 | 0.046933 | 0.047467 | 0.048 | 0.048 | 0.048 | 0.048 | 0.048 | 0.048 | 0.048 | 0.048 | 0.048 | 0.048 | 0.048 | 0.048 | 0.048 | 0.048 | 0.048 | 0.048 | 0.0496 | 0.0512 | 0.0528 | 0.0544 | 0.056 | 0.0576 | 0.0592 | 0.0608 | 0.0624 | 0.064 | 0.0656 | 0.0672 | 0.0688 | 0.0704 | 0.072 | 0.0736 | 0.0752 | 0.0768 | 0.0784 | 0.08 | 0.0816 | 0.0832 | 0.0848 | 0.0864 | 0.088 | 0.0896 | 0.0912 | 0.0928 | 0.0944 | 0.096 | 0.0976 | 0.0992 | 0.1008 | 0.1024 | 0.104 | 0.1056 | 0.1072 | 0.1088 | 0.1104 | 0.112 | 0.1136 | 0.1152 | 0.1168 | 0.1184 | 0.12 | 0.1216 | 0.1232 | 0.1248 | 0.1264 | 0.128 | 0.1296 | 0.1312 | 0.1328 | 0.1344 | 0.136 | 0.1376 | 0.1392 | 0.1408 | 0.1424 | 0.144 | 0.1456 | 0.1472 | 0.1488 | 0.1504 | 0.152 | 0.1536 | 0.1552 | 0.1568 | 0.1584 | 0.16 | 0.1616 | 0.1632 | 0.1648 | 0.1664 | 0.168 | 0.1696 | 0.1712 | 0.1728 | 0.1744 | 0.176 | 0.1776 | 0.1792 | 0.1808 | 0.1824 | 0.184 | 0.1856 | 0.1872 | 0.1888 | 0.1904 | 0.192 | 0.19253 | 0.19307 | 0.1936 | 0.19413 | 0.19467 | 0.1952 | 0.19573 | 0.19627 | 0.1968 | 0.19733 | 0.19787 | 0.1984 | 0.19893 | 0.19947 | 0.2 | 0.20053 | 0.20107 | 0.2016 | 0.20213 | 0.20267 | 0.2032 | 0.20373 | 0.20427 | 0.2048 | 0.20533 | 0.20587 | 0.2064 | 0.20693 | 0.20747 | 0.208
0.65 | 0 | 0.0042 | 0.0084 | 0.0126 | 0.0168 | 0.021 | 0.0252 | 0.0294 | 0.0336 | 0.0378 | 0.042 | 0.0434 | 0.0448 | 0.0462 | 0.0476 | 0.049 | 0.049 | 0.049 | 0.049 | 0.049 | 0.049 | 0.0476 | 0.0462 | 0.0448 | 0.0434 | 0.042 | 0.0406 | 0.0392 | 0.0378 | 0.0364 | 0.035 | 0.035467 | 0.035933 | 0.0364 | 0.036867 | 0.037333 | 0.0378 | 0.038267 | 0.038733 | 0.0392 | 0.039667 | 0.040133 | 0.0406 | 0.041067 | 0.041533 | 0.042 | 0.042 | 0.042 | 0.042 | 0.042 | 0.042 | 0.042 | 0.042 | 0.042 | 0.042 | 0.042 | 0.042 | 0.042 | 0.042 | 0.042 | 0.042 | 0.0434 | 0.0448 | 0.0462 | 0.0476 | 0.049 | 0.0504 | 0.0518 | 0.0532 | 0.0546 | 0.056 | 0.0574 | 0.0588 | 0.0602 | 0.0616 | 0.063 | 0.0644 | 0.0658 | 0.0672 | 0.0686 | 0.07 | 0.0714 | 0.0728 | 0.0742 | 0.0756 | 0.077 | 0.0784 | 0.0798 | 0.0812 | 0.0826 | 0.084 | 0.0854 | 0.0868 | 0.0882 | 0.0896 | 0.091 | 0.0924 | 0.0938 | 0.0952 | 0.0966 | 0.098 | 0.0994 | 0.1008 | 0.1022 | 0.1036 | 0.105 | 0.1064 | 0.1078 | 0.1092 | 0.1106 | 0.112 | 0.1134 | 0.1148 | 0.1162 | 0.1176 | 0.119 | 0.1204 | 0.1218 | 0.1232 | 0.1246 | 0.126 | 0.1274 | 0.1288 | 0.1302 | 0.1316 | 0.133 | 0.1344 | 0.1358 | 0.1372 | 0.1386 | 0.14 | 0.1414 | 0.1428 | 0.1442 | 0.1456 | 0.147 | 0.1484 | 0.1498 | 0.1512 | 0.1526 | 0.154 | 0.1554 | 0.1568 | 0.1582 | 0.1596 | 0.161 | 0.1624 | 0.1638 | 0.1652 | 0.1666 | 0.168 | 0.16847 | 0.16893 | 0.1694 | 0.16987 | 0.17033 | 0.1708 | 0.17127 | 0.17173 | 0.1722 | 0.17267 | 0.17313 | 0.1736 | 0.17407 | 0.17453 | 0.175 | 0.17547 | 0.17593 | 0.1764 | 0.17687 | 0.17733 | 0.1778 | 0.17827 | 0.17873 | 0.1792 | 0.17967 | 0.18013 | 0.1806 | 0.18107 | 0.18153 | 0.182
0.7 | 0 | 0.0036 | 0.0072 | 0.0108 | 0.0144 | 0.018 | 0.0216 | 0.0252 | 0.0288 | 0.0324 | 0.036 | 0.0372 | 0.0384 | 0.0396 | 0.0408 | 0.042 | 0.042 | 0.042 | 0.042 | 0.042 | 0.042 | 0.0408 | 0.0396 | 0.0384 | 0.0372 | 0.036 | 0.0348 | 0.0336 | 0.0324 | 0.0312 | 0.03 | 0.0304 | 0.0308 | 0.0312 | 0.0316 | 0.032 | 0.0324 | 0.0328 | 0.0332 | 0.0336 | 0.034 | 0.0344 | 0.0348 | 0.0352 | 0.0356 | 0.036 | 0.036 | 0.036 | 0.036 | 0.036 | 0.036 | 0.036 | 0.036 | 0.036 | 0.036 | 0.036 | 0.036 | 0.036 | 0.036 | 0.036 | 0.036 | 0.0372 | 0.0384 | 0.0396 | 0.0408 | 0.042 | 0.0432 | 0.0444 | 0.0456 | 0.0468 | 0.048 | 0.0492 | 0.0504 | 0.0516 | 0.0528 | 0.054 | 0.0552 | 0.0564 | 0.0576 | 0.0588 | 0.06 | 0.0612 | 0.0624 | 0.0636 | 0.0648 | 0.066 | 0.0672 | 0.0684 | 0.0696 | 0.0708 | 0.072 | 0.0732 | 0.0744 | 0.0756 | 0.0768 | 0.078 | 0.0792 | 0.0804 | 0.0816 | 0.0828 | 0.084 | 0.0852 | 0.0864 | 0.0876 | 0.0888 | 0.09 | 0.0912 | 0.0924 | 0.0936 | 0.0948 | 0.096 | 0.0972 | 0.0984 | 0.0996 | 0.1008 | 0.102 | 0.1032 | 0.1044 | 0.1056 | 0.1068 | 0.108 | 0.1092 | 0.1104 | 0.1116 | 0.1128 | 0.114 | 0.1152 | 0.1164 | 0.1176 | 0.1188 | 0.12 | 0.1212 | 0.1224 | 0.1236 | 0.1248 | 0.126 | 0.1272 | 0.1284 | 0.1296 | 0.1308 | 0.132 | 0.1332 | 0.1344 | 0.1356 | 0.1368 | 0.138 | 0.1392 | 0.1404 | 0.1416 | 0.1428 | 0.144 | 0.1444 | 0.1448 | 0.1452 | 0.1456 | 0.146 | 0.1464 | 0.1468 | 0.1472 | 0.1476 | 0.148 | 0.1484 | 0.1488 | 0.1492 | 0.1496 | 0.15 | 0.1504 | 0.1508 | 0.1512 | 0.1516 | 0.152 | 0.1524 | 0.1528 | 0.1532 | 0.1536 | 0.154 | 0.1544 | 0.1548 | 0.1552 | 0.1556 | 0.156
0.75 | 0 | 0.003 | 0.006 | 0.009 | 0.012 | 0.015 | 0.018 | 0.021 | 0.024 | 0.027 | 0.03 | 0.031 | 0.032 | 0.033 | 0.034 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035 | 0.034 | 0.033 | 0.032 | 0.031 | 0.03 | 0.029 | 0.028 | 0.027 | 0.026 | 0.025 | 0.025333 | 0.025667 | 0.026 | 0.026333 | 0.026667 | 0.027 | 0.027333 | 0.027667 | 0.028 | 0.028333 | 0.028667 | 0.029 | 0.029333 | 0.029667 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.031 | 0.032 | 0.033 | 0.034 | 0.035 | 0.036 | 0.037 | 0.038 | 0.039 | 0.04 | 0.041 | 0.042 | 0.043 | 0.044 | 0.045 | 0.046 | 0.047 | 0.048 | 0.049 | 0.05 | 0.051 | 0.052 | 0.053 | 0.054 | 0.055 | 0.056 | 0.057 | 0.058 | 0.059 | 0.06 | 0.061 | 0.062 | 0.063 | 0.064 | 0.065 | 0.066 | 0.067 | 0.068 | 0.069 | 0.07 | 0.071 | 0.072 | 0.073 | 0.074 | 0.075 | 0.076 | 0.077 | 0.078 | 0.079 | 0.08 | 0.081 | 0.082 | 0.083 | 0.084 | 0.085 | 0.086 | 0.087 | 0.088 | 0.089 | 0.09 | 0.091 | 0.092 | 0.093 | 0.094 | 0.095 | 0.096 | 0.097 | 0.098 | 0.099 | 0.1 | 0.101 | 0.102 | 0.103 | 0.104 | 0.105 | 0.106 | 0.107 | 0.108 | 0.109 | 0.11 | 0.111 | 0.112 | 0.113 | 0.114 | 0.115 | 0.116 | 0.117 | 0.118 | 0.119 | 0.12 | 0.12033 | 0.12067 | 0.121 | 0.12133 | 0.12167 | 0.122 | 0.12233 | 0.12267 | 0.123 | 0.12333 | 0.12367 | 0.124 | 0.12433 | 0.12467 | 0.125 | 0.12533 | 0.12567 | 0.126 | 0.12633 | 0.12667 | 0.127 | 0.12733 | 0.12767 | 0.128 | 0.12833 | 0.12867 | 0.129 | 0.12933 | 0.12967 | 0.13
0.8 | 0 | 0.0024 | 0.0048 | 0.0072 | 0.0096 | 0.012 | 0.0144 | 0.0168 | 0.0192 | 0.0216 | 0.024 | 0.0248 | 0.0256 | 0.0264 | 0.0272 | 0.028 | 0.028 | 0.028 | 0.028 | 0.028 | 0.028 | 0.0272 | 0.0264 | 0.0256 | 0.0248 | 0.024 | 0.0232 | 0.0224 | 0.0216 | 0.0208 | 0.02 | 0.020267 | 0.020533 | 0.0208 | 0.021067 | 0.021333 | 0.0216 | 0.021867 | 0.022133 | 0.0224 | 0.022667 | 0.022933 | 0.0232 | 0.023467 | 0.023733 | 0.024 | 0.024 | 0.024 | 0.024 | 0.024 | 0.024 | 0.024 | 0.024 | 0.024 | 0.024 | 0.024 | 0.024 | 0.024 | 0.024 | 0.024 | 0.024 | 0.0248 | 0.0256 | 0.0264 | 0.0272 | 0.028 | 0.0288 | 0.0296 | 0.0304 | 0.0312 | 0.032 | 0.0328 | 0.0336 | 0.0344 | 0.0352 | 0.036 | 0.0368 | 0.0376 | 0.0384 | 0.0392 | 0.04 | 0.0408 | 0.0416 | 0.0424 | 0.0432 | 0.044 | 0.0448 | 0.0456 | 0.0464 | 0.0472 | 0.048 | 0.0488 | 0.0496 | 0.0504 | 0.0512 | 0.052 | 0.0528 | 0.0536 | 0.0544 | 0.0552 | 0.056 | 0.0568 | 0.0576 | 0.0584 | 0.0592 | 0.06 | 0.0608 | 0.0616 | 0.0624 | 0.0632 | 0.064 | 0.0648 | 0.0656 | 0.0664 | 0.0672 | 0.068 | 0.0688 | 0.0696 | 0.0704 | 0.0712 | 0.072 | 0.0728 | 0.0736 | 0.0744 | 0.0752 | 0.076 | 0.0768 | 0.0776 | 0.0784 | 0.0792 | 0.08 | 0.0808 | 0.0816 | 0.0824 | 0.0832 | 0.084 | 0.0848 | 0.0856 | 0.0864 | 0.0872 | 0.088 | 0.0888 | 0.0896 | 0.0904 | 0.0912 | 0.092 | 0.0928 | 0.0936 | 0.0944 | 0.0952 | 0.096 | 0.096267 | 0.096533 | 0.0968 | 0.097067 | 0.097333 | 0.0976 | 0.097867 | 0.098133 | 0.0984 | 0.098667 | 0.098933 | 0.0992 | 0.099467 | 0.099733 | 0.1 | 0.10027 | 0.10053 | 0.1008 | 0.10107 | 0.10133 | 0.1016 | 0.10187 | 0.10213 | 0.1024 | 0.10267 | 0.10293 | 0.1032 | 0.10347 | 0.10373 | 0.104
0.85 | 0 | 0.0018 | 0.0036 | 0.0054 | 0.0072 | 0.009 | 0.0108 | 0.0126 | 0.0144 | 0.0162 | 0.018 | 0.0186 | 0.0192 | 0.0198 | 0.0204 | 0.021 | 0.021 | 0.021 | 0.021 | 0.021 | 0.021 | 0.0204 | 0.0198 | 0.0192 | 0.0186 | 0.018 | 0.0174 | 0.0168 | 0.0162 | 0.0156 | 0.015 | 0.0152 | 0.0154 | 0.0156 | 0.0158 | 0.016 | 0.0162 | 0.0164 | 0.0166 | 0.0168 | 0.017 | 0.0172 | 0.0174 | 0.0176 | 0.0178 | 0.018 | 0.018 | 0.018 | 0.018 | 0.018 | 0.018 | 0.018 | 0.018 | 0.018 | 0.018 | 0.018 | 0.018 | 0.018 | 0.018 | 0.018 | 0.018 | 0.0186 | 0.0192 | 0.0198 | 0.0204 | 0.021 | 0.0216 | 0.0222 | 0.0228 | 0.0234 | 0.024 | 0.0246 | 0.0252 | 0.0258 | 0.0264 | 0.027 | 0.0276 | 0.0282 | 0.0288 | 0.0294 | 0.03 | 0.0306 | 0.0312 | 0.0318 | 0.0324 | 0.033 | 0.0336 | 0.0342 | 0.0348 | 0.0354 | 0.036 | 0.0366 | 0.0372 | 0.0378 | 0.0384 | 0.039 | 0.0396 | 0.0402 | 0.0408 | 0.0414 | 0.042 | 0.0426 | 0.0432 | 0.0438 | 0.0444 | 0.045 | 0.0456 | 0.0462 | 0.0468 | 0.0474 | 0.048 | 0.0486 | 0.0492 | 0.0498 | 0.0504 | 0.051 | 0.0516 | 0.0522 | 0.0528 | 0.0534 | 0.054 | 0.0546 | 0.0552 | 0.0558 | 0.0564 | 0.057 | 0.0576 | 0.0582 | 0.0588 | 0.0594 | 0.06 | 0.0606 | 0.0612 | 0.0618 | 0.0624 | 0.063 | 0.0636 | 0.0642 | 0.0648 | 0.0654 | 0.066 | 0.0666 | 0.0672 | 0.0678 | 0.0684 | 0.069 | 0.0696 | 0.0702 | 0.0708 | 0.0714 | 0.072 | 0.0722 | 0.0724 | 0.0726 | 0.0728 | 0.073 | 0.0732 | 0.0734 | 0.0736 | 0.0738 | 0.074 | 0.0742 | 0.0744 | 0.0746 | 0.0748 | 0.075 | 0.0752 | 0.0754 | 0.0756 | 0.0758 | 0.076 | 0.0762 | 0.0764 | 0.0766 | 0.0768 | 0.077 | 0.0772 | 0.0774 | 0.0776 | 0.0778 | 0.078
0.9 | 0 | 0.0012 | 0.0024 | 0.0036 | 0.0048 | 0.006 | 0.0072 | 0.0084 | 0.0096 | 0.0108 | 0.012 | 0.0124 | 0.0128 | 0.0132 | 0.0136 | 0.014 | 0.014 | 0.014 | 0.014 | 0.014 | 0.014 | 0.0136 | 0.0132 | 0.0128 | 0.0124 | 0.012 | 0.0116 | 0.0112 | 0.0108 | 0.0104 | 0.01 | 0.010133 | 0.010267 | 0.0104 | 0.010533 | 0.010667 | 0.0108 | 0.010933 | 0.011067 | 0.0112 | 0.011333 | 0.011467 | 0.0116 | 0.011733 | 0.011867 | 0.012 | 0.012 | 0.012 | 0.012 | 0.012 | 0.012 | 0.012 | 0.012 | 0.012 | 0.012 | 0.012 | 0.012 | 0.012 | 0.012 | 0.012 | 0.012 | 0.0124 | 0.0128 | 0.0132 | 0.0136 | 0.014 | 0.0144 | 0.0148 | 0.0152 | 0.0156 | 0.016 | 0.0164 | 0.0168 | 0.0172 | 0.0176 | 0.018 | 0.0184 | 0.0188 | 0.0192 | 0.0196 | 0.02 | 0.0204 | 0.0208 | 0.0212 | 0.0216 | 0.022 | 0.0224 | 0.0228 | 0.0232 | 0.0236 | 0.024 | 0.0244 | 0.0248 | 0.0252 | 0.0256 | 0.026 | 0.0264 | 0.0268 | 0.0272 | 0.0276 | 0.028 | 0.0284 | 0.0288 | 0.0292 | 0.0296 | 0.03 | 0.0304 | 0.0308 | 0.0312 | 0.0316 | 0.032 | 0.0324 | 0.0328 | 0.0332 | 0.0336 | 0.034 | 0.0344 | 0.0348 | 0.0352 | 0.0356 | 0.036 | 0.0364 | 0.0368 | 0.0372 | 0.0376 | 0.038 | 0.0384 | 0.0388 | 0.0392 | 0.0396 | 0.04 | 0.0404 | 0.0408 | 0.0412 | 0.0416 | 0.042 | 0.0424 | 0.0428 | 0.0432 | 0.0436 | 0.044 | 0.0444 | 0.0448 | 0.0452 | 0.0456 | 0.046 | 0.0464 | 0.0468 | 0.0472 | 0.0476 | 0.048 | 0.048133 | 0.048267 | 0.0484 | 0.048533 | 0.048667 | 0.0488 | 0.048933 | 0.049067 | 0.0492 | 0.049333 | 0.049467 | 0.0496 | 0.049733 | 0.049867 | 0.05 | 0.050133 | 0.050267 | 0.0504 | 0.050533 | 0.050667 | 0.0508 | 0.050933 | 0.051067 | 0.0512 | 0.051333 | 0.051467 | 0.0516 | 0.051733 | 0.051867 | 0.052
0.95 | 0 | 0.0006 | 0.0012 | 0.0018 | 0.0024 | 0.003 | 0.0036 | 0.0042 | 0.0048 | 0.0054 | 0.006 | 0.0062 | 0.0064 | 0.0066 | 0.0068 | 0.007 | 0.007 | 0.007 | 0.007 | 0.007 | 0.007 | 0.0068 | 0.0066 | 0.0064 | 0.0062 | 0.006 | 0.0058 | 0.0056 | 0.0054 | 0.0052 | 0.005 | 0.0050667 | 0.0051333 | 0.0052 | 0.0052667 | 0.0053333 | 0.0054 | 0.0054667 | 0.0055333 | 0.0056 | 0.0056667 | 0.0057333 | 0.0058 | 0.0058667 | 0.0059333 | 0.006 | 0.006 | 0.006 | 0.006 | 0.006 | 0.006 | 0.006 | 0.006 | 0.006 | 0.006 | 0.006 | 0.006 | 0.006 | 0.006 | 0.006 | 0.006 | 0.0062 | 0.0064 | 0.0066 | 0.0068 | 0.007 | 0.0072 | 0.0074 | 0.0076 | 0.0078 | 0.008 | 0.0082 | 0.0084 | 0.0086 | 0.0088 | 0.009 | 0.0092 | 0.0094 | 0.0096 | 0.0098 | 0.01 | 0.0102 | 0.0104 | 0.0106 | 0.0108 | 0.011 | 0.0112 | 0.0114 | 0.0116 | 0.0118 | 0.012 | 0.0122 | 0.0124 | 0.0126 | 0.0128 | 0.013 | 0.0132 | 0.0134 | 0.0136 | 0.0138 | 0.014 | 0.0142 | 0.0144 | 0.0146 | 0.0148 | 0.015 | 0.0152 | 0.0154 | 0.0156 | 0.0158 | 0.016 | 0.0162 | 0.0164 | 0.0166 | 0.0168 | 0.017 | 0.0172 | 0.0174 | 0.0176 | 0.0178 | 0.018 | 0.0182 | 0.0184 | 0.0186 | 0.0188 | 0.019 | 0.0192 | 0.0194 | 0.0196 | 0.0198 | 0.02 | 0.0202 | 0.0204 | 0.0206 | 0.0208 | 0.021 | 0.0212 | 0.0214 | 0.0216 | 0.0218 | 0.022 | 0.0222 | 0.0224 | 0.0226 | 0.0228 | 0.023 | 0.0232 | 0.0234 | 0.0236 | 0.0238 | 0.024 | 0.024067 | 0.024133 | 0.0242 | 0.024267 | 0.024333 | 0.0244 | 0.024467 | 0.024533 | 0.0246 | 0.024667 | 0.024733 | 0.0248 | 0.024867 | 0.024933 | 0.025 | 0.025067 | 0.025133 | 0.0252 | 0.025267 | 0.025333 | 0.0254 | 0.025467 | 0.025533 | 0.0256 | 0.025667 | 0.025733 | 0.0258 | 0.025867 | 0.025933 | 0.026
1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1.05 | 0 | 0.003 | 0.006 | 0.009 | 0.012 | 0.015 | 0.018 | 0.021 | 0.024 | 0.027 | 0.03 | 0.0324 | 0.0348 | 0.0372 | 0.0396 | 0.042 | 0.0436 | 0.0452 | 0.0468 | 0.0484 | 0.05 | 0.051 | 0.052 | 0.053 | 0.054 | 0.055 | 0.056 | 0.057 | 0.058 | 0.059 | 0.06 | 0.0604 | 0.0608 | 0.0612 | 0.0616 | 0.062 | 0.0624 | 0.0628 | 0.0632 | 0.0636 | 0.064 | 0.0644 | 0.0648 | 0.0652 | 0.0656 | 0.066 | 0.066 | 0.066 | 0.066 | 0.066 | 0.066 | 0.066 | 0.066 | 0.066 | 0.066 | 0.066 | 0.066 | 0.066 | 0.066 | 0.066 | 0.066 | 0.066 | 0.066 | 0.066 | 0.066 | 0.066 | 0.066 | 0.066 | 0.066 | 0.066 | 0.066 | 0.066 | 0.066 | 0.066 | 0.066 | 0.066 | 0.066 | 0.066 | 0.066 | 0.066 | 0.066 | 0.066 | 0.066 | 0.066 | 0.066 | 0.066 | 0.066 | 0.066 | 0.066 | 0.066 | 0.066 | 0.065933 | 0.065867 | 0.0658 | 0.065733 | 0.065667 | 0.0656 | 0.065533 | 0.065467 | 0.0654 | 0.065333 | 0.065267 | 0.0652 | 0.065133 | 0.065067 | 0.065 | 0.064933 | 0.064867 | 0.0648 | 0.064733 | 0.064667 | 0.0646 | 0.064533 | 0.064467 | 0.0644 | 0.064333 | 0.064267 | 0.0642 | 0.064133 | 0.064067 | 0.064 | 0.063933 | 0.063867 | 0.0638 | 0.063733 | 0.063667 | 0.0636 | 0.063533 | 0.063467 | 0.0634 | 0.063333 | 0.063267 | 0.0632 | 0.063133 | 0.063067 | 0.063 | 0.062933 | 0.062867 | 0.0628 | 0.062733 | 0.062667 | 0.0626 | 0.062533 | 0.062467 | 0.0624 | 0.062333 | 0.062267 | 0.0622 | 0.062133 | 0.062067 | 0.062 | 0.061933 | 0.061867 | 0.0618 | 0.061733 | 0.061667 | 0.0616 | 0.061533 | 0.061467 | 0.0614 | 0.061333 | 0.061267 | 0.0612 | 0.061133 | 0.061067 | 0.061 | 0.060933 | 0.060867 | 0.0608 | 0.060733 | 0.060667 | 0.0606 | 0.060533 | 0.060467 | 0.0604 | 0.060333 | 0.060267 | 0.0602 | 0.060133 | 0.060067 | 0.06
1.1 | 0 | 0.006 | 0.012 | 0.018 | 0.024 | 0.03 | 0.036 | 0.042 | 0.048 | 0.054 | 0.06 | 0.0648 | 0.0696 | 0.0744 | 0.0792 | 0.084 | 0.0872 | 0.0904 | 0.0936 | 0.0968 | 0.1 | 0.102 | 0.104 | 0.106 | 0.108 | 0.11 | 0.112 | 0.114 | 0.116 | 0.118 | 0.12 | 0.1208 | 0.1216 | 0.1224 | 0.1232 | 0.124 | 0.1248 | 0.1256 | 0.1264 | 0.1272 | 0.128 | 0.1288 | 0.1296 | 0.1304 | 0.1312 | 0.132 | 0.132 | 0.132 | 0.132 | 0.132 | 0.132 | 0.132 | 0.132 | 0.132 | 0.132 | 0.132 | 0.132 | 0.132 | 0.132 | 0.132 | 0.132 | 0.132 | 0.132 | 0.132 | 0.132 | 0.132 | 0.132 | 0.132 | 0.132 | 0.132 | 0.132 | 0.132 | 0.132 | 0.132 | 0.132 | 0.132 | 0.132 | 0.132 | 0.132 | 0.132 | 0.132 | 0.132 | 0.132 | 0.132 | 0.132 | 0.132 | 0.132 | 0.132 | 0.132 | 0.132 | 0.132 | 0.13187 | 0.13173 | 0.1316 | 0.13147 | 0.13133 | 0.1312 | 0.13107 | 0.13093 | 0.1308 | 0.13067 | 0.13053 | 0.1304 | 0.13027 | 0.13013 | 0.13 | 0.12987 | 0.12973 | 0.1296 | 0.12947 | 0.12933 | 0.1292 | 0.12907 | 0.12893 | 0.1288 | 0.12867 | 0.12853 | 0.1284 | 0.12827 | 0.12813 | 0.128 | 0.12787 | 0.12773 | 0.1276 | 0.12747 | 0.12733 | 0.1272 | 0.12707 | 0.12693 | 0.1268 | 0.12667 | 0.12653 | 0.1264 | 0.12627 | 0.12613 | 0.126 | 0.12587 | 0.12573 | 0.1256 | 0.12547 | 0.12533 | 0.1252 | 0.12507 | 0.12493 | 0.1248 | 0.12467 | 0.12453 | 0.1244 | 0.12427 | 0.12413 | 0.124 | 0.12387 | 0.12373 | 0.1236 | 0.12347 | 0.12333 | 0.1232 | 0.12307 | 0.12293 | 0.1228 | 0.12267 | 0.12253 | 0.1224 | 0.12227 | 0.12213 | 0.122 | 0.12187 | 0.12173 | 0.1216 | 0.12147 | 0.12133 | 0.1212 | 0.12107 | 0.12093 | 0.1208 | 0.12067 | 0.12053 | 0.1204 | 0.12027 | 0.12013 | 0.12
1.15 | 0 | 0.009 | 0.018 | 0.027 | 0.036 | 0.045 | 0.054 | 0.063 | 0.072 | 0.081 | 0.09 | 0.0972 | 0.1044 | 0.1116 | 0.1188 | 0.126 | 0.1308 | 0.1356 | 0.1404 | 0.1452 | 0.15 | 0.153 | 0.156 | 0.159 | 0.162 | 0.165 | 0.168 | 0.171 | 0.174 | 0.177 | 0.18 | 0.1812 | 0.1824 | 0.1836 | 0.1848 | 0.186 | 0.1872 | 0.1884 | 0.1896 | 0.1908 | 0.192 | 0.1932 | 0.1944 | 0.1956 | 0.1968 | 0.198 | 0.198 | 0.198 | 0.198 | 0.198 | 0.198 | 0.198 | 0.198 | 0.198 | 0.198 | 0.198 | 0.198 | 0.198 | 0.198 | 0.198 | 0.198 | 0.198 | 0.198 | 0.198 | 0.198 | 0.198 | 0.198 | 0.198 | 0.198 | 0.198 | 0.198 | 0.198 | 0.198 | 0.198 | 0.198 | 0.198 | 0.198 | 0.198 | 0.198 | 0.198 | 0.198 | 0.198 | 0.198 | 0.198 | 0.198 | 0.198 | 0.198 | 0.198 | 0.198 | 0.198 | 0.198 | 0.1978 | 0.1976 | 0.1974 | 0.1972 | 0.197 | 0.1968 | 0.1966 | 0.1964 | 0.1962 | 0.196 | 0.1958 | 0.1956 | 0.1954 | 0.1952 | 0.195 | 0.1948 | 0.1946 | 0.1944 | 0.1942 | 0.194 | 0.1938 | 0.1936 | 0.1934 | 0.1932 | 0.193 | 0.1928 | 0.1926 | 0.1924 | 0.1922 | 0.192 | 0.1918 | 0.1916 | 0.1914 | 0.1912 | 0.191 | 0.1908 | 0.1906 | 0.1904 | 0.1902 | 0.19 | 0.1898 | 0.1896 | 0.1894 | 0.1892 | 0.189 | 0.1888 | 0.1886 | 0.1884 | 0.1882 | 0.188 | 0.1878 | 0.1876 | 0.1874 | 0.1872 | 0.187 | 0.1868 | 0.1866 | 0.1864 | 0.1862 | 0.186 | 0.1858 | 0.1856 | 0.1854 | 0.1852 | 0.185 | 0.1848 | 0.1846 | 0.1844 | 0.1842 | 0.184 | 0.1838 | 0.1836 | 0.1834 | 0.1832 | 0.183 | 0.1828 | 0.1826 | 0.1824 | 0.1822 | 0.182 | 0.1818 | 0.1816 | 0.1814 | 0.1812 | 0.181 | 0.1808 | 0.1806 | 0.1804 | 0.1802 | 0.18
1.2 | 0 | 0.012 | 0.024 | 0.036 | 0.048 | 0.06 | 0.072 | 0.084 | 0.096 | 0.108 | 0.12 | 0.1296 | 0.1392 | 0.1488 | 0.1584 | 0.168 | 0.1744 | 0.1808 | 0.1872 | 0.1936 | 0.2 | 0.204 | 0.208 | 0.212 | 0.216 | 0.22 | 0.224 | 0.228 | 0.232 | 0.236 | 0.24 | 0.2416 | 0.2432 | 0.2448 | 0.2464 | 0.248 | 0.2496 | 0.2512 | 0.2528 | 0.2544 | 0.256 | 0.2576 | 0.2592 | 0.2608 | 0.2624 | 0.264 | 0.264 | 0.264 | 0.264 | 0.264 | 0.264 | 0.264 | 0.264 | 0.264 | 0.264 | 0.264 | 0.264 | 0.264 | 0.264 | 0.264 | 0.264 | 0.264 | 0.264 | 0.264 | 0.264 | 0.264 | 0.264 | 0.264 | 0.264 | 0.264 | 0.264 | 0.264 | 0.264 | 0.264 | 0.264 | 0.264 | 0.264 | 0.264 | 0.264 | 0.264 | 0.264 | 0.264 | 0.264 | 0.264 | 0.264 | 0.264 | 0.264 | 0.264 | 0.264 | 0.264 | 0.264 | 0.26373 | 0.26347 | 0.2632 | 0.26293 | 0.26267 | 0.2624 | 0.26213 | 0.26187 | 0.2616 | 0.26133 | 0.26107 | 0.2608 | 0.26053 | 0.26027 | 0.26 | 0.25973 | 0.25947 | 0.2592 | 0.25893 | 0.25867 | 0.2584 | 0.25813 | 0.25787 | 0.2576 | 0.25733 | 0.25707 | 0.2568 | 0.25653 | 0.25627 | 0.256 | 0.25573 | 0.25547 | 0.2552 | 0.25493 | 0.25467 | 0.2544 | 0.25413 | 0.25387 | 0.2536 | 0.25333 | 0.25307 | 0.2528 | 0.25253 | 0.25227 | 0.252 | 0.25173 | 0.25147 | 0.2512 | 0.25093 | 0.25067 | 0.2504 | 0.25013 | 0.24987 | 0.2496 | 0.24933 | 0.24907 | 0.2488 | 0.24853 | 0.24827 | 0.248 | 0.24773 | 0.24747 | 0.2472 | 0.24693 | 0.24667 | 0.2464 | 0.24613 | 0.24587 | 0.2456 | 0.24533 | 0.24507 | 0.2448 | 0.24453 | 0.24427 | 0.244 | 0.24373 | 0.24347 | 0.2432 | 0.24293 | 0.24267 | 0.2424 | 0.24213 | 0.24187 | 0.2416 | 0.24133 | 0.24107 | 0.2408 | 0.24053 | 0.24027 | 0.24
1.25 | 0 | 0.015 | 0.03 | 0.045 | 0.06 | 0.075 | 0.09 | 0.105 | 0.12 | 0.135 | 0.15 | 0.162 | 0.174 | 0.186 | 0.198 | 0.21 | 0.218 | 0.226 | 0.234 | 0.242 | 0.25 | 0.255 | 0.26 | 0.265 | 0.27 | 0.275 | 0.28 | 0.285 | 0.29 | 0.295 | 0.3 | 0.302 | 0.304 | 0.306 | 0.308 | 0.31 | 0.312 | 0.314 | 0.316 | 0.318 | 0.32 | 0.322 | 0.324 | 0.326 | 0.328 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.32967 | 0.32933 | 0.329 | 0.32867 | 0.32833 | 0.328 | 0.32767 | 0.32733 | 0.327 | 0.32667 | 0.32633 | 0.326 | 0.32567 | 0.32533 | 0.325 | 0.32467 | 0.32433 | 0.324 | 0.32367 | 0.32333 | 0.323 | 0.32267 | 0.32233 | 0.322 | 0.32167 | 0.32133 | 0.321 | 0.32067 | 0.32033 | 0.32 | 0.31967 | 0.31933 | 0.319 | 0.31867 | 0.31833 | 0.318 | 0.31767 | 0.31733 | 0.317 | 0.31667 | 0.31633 | 0.316 | 0.31567 | 0.31533 | 0.315 | 0.31467 | 0.31433 | 0.314 | 0.31367 | 0.31333 | 0.313 | 0.31267 | 0.31233 | 0.312 | 0.31167 | 0.31133 | 0.311 | 0.31067 | 0.31033 | 0.31 | 0.30967 | 0.30933 | 0.309 | 0.30867 | 0.30833 | 0.308 | 0.30767 | 0.30733 | 0.307 | 0.30667 | 0.30633 | 0.306 | 0.30567 | 0.30533 | 0.305 | 0.30467 | 0.30433 | 0.304 | 0.30367 | 0.30333 | 0.303 | 0.30267 | 0.30233 | 0.302 | 0.30167 | 0.30133 | 0.301 | 0.30067 | 0.30033 | 0.3
1.3 | 0 | 0.018 | 0.036 | 0.054 | 0.072 | 0.09 | 0.108 | 0.126 | 0.144 | 0.162 | 0.18 | 0.1944 | 0.2088 | 0.2232 | 0.2376 | 0.252 | 0.2616 | 0.2712 | 0.2808 | 0.2904 | 0.3 | 0.306 | 0.312 | 0.318 | 0.324 | 0.33 | 0.336 | 0.342 | 0.348 | 0.354 | 0.36 | 0.3624 | 0.3648 | 0.3672 | 0.3696 | 0.372 | 0.3744 | 0.3768 | 0.3792 | 0.3816 | 0.384 | 0.3864 | 0.3888 | 0.3912 | 0.3936 | 0.396 | 0.396 | 0.396 | 0.396 | 0.396 | 0.396 | 0.396 | 0.396 | 0.396 | 0.396 | 0.396 | 0.396 | 0.396 | 0.396 | 0.396 | 0.396 | 0.396 | 0.396 | 0.396 | 0.396 | 0.396 | 0.396 | 0.396 | 0.396 | 0.396 | 0.396 | 0.396 | 0.396 | 0.396 | 0.396 | 0.396 | 0.396 | 0.396 | 0.396 | 0.396 | 0.396 | 0.396 | 0.396 | 0.396 | 0.396 | 0.396 | 0.396 | 0.396 | 0.396 | 0.396 | 0.396 | 0.3956 | 0.3952 | 0.3948 | 0.3944 | 0.394 | 0.3936 | 0.3932 | 0.3928 | 0.3924 | 0.392 | 0.3916 | 0.3912 | 0.3908 | 0.3904 | 0.39 | 0.3896 | 0.3892 | 0.3888 | 0.3884 | 0.388 | 0.3876 | 0.3872 | 0.3868 | 0.3864 | 0.386 | 0.3856 | 0.3852 | 0.3848 | 0.3844 | 0.384 | 0.3836 | 0.3832 | 0.3828 | 0.3824 | 0.382 | 0.3816 | 0.3812 | 0.3808 | 0.3804 | 0.38 | 0.3796 | 0.3792 | 0.3788 | 0.3784 | 0.378 | 0.3776 | 0.3772 | 0.3768 | 0.3764 | 0.376 | 0.3756 | 0.3752 | 0.3748 | 0.3744 | 0.374 | 0.3736 | 0.3732 | 0.3728 | 0.3724 | 0.372 | 0.3716 | 0.3712 | 0.3708 | 0.3704 | 0.37 | 0.3696 | 0.3692 | 0.3688 | 0.3684 | 0.368 | 0.3676 | 0.3672 | 0.3668 | 0.3664 | 0.366 | 0.3656 | 0.3652 | 0.3648 | 0.3644 | 0.364 | 0.3636 | 0.3632 | 0.3628 | 0.3624 | 0.362 | 0.3616 | 0.3612 | 0.3608 | 0.3604 | 0.36
1.35 | 0 | 0.021 | 0.042 | 0.063 | 0.084 | 0.105 | 0.126 | 0.147 | 0.168 | 0.189 | 0.21 | 0.2268 | 0.2436 | 0.2604 | 0.2772 | 0.294 | 0.3052 | 0.3164 | 0.3276 | 0.3388 | 0.35 | 0.357 | 0.364 | 0.371 | 0.378 | 0.385 | 0.392 | 0.399 | 0.406 | 0.413 | 0.42 | 0.4228 | 0.4256 | 0.4284 | 0.4312 | 0.434 | 0.4368 | 0.4396 | 0.4424 | 0.4452 | 0.448 | 0.4508 | 0.4536 | 0.4564 | 0.4592 | 0.462 | 0.462 | 0.462 | 0.462 | 0.462 | 0.462 | 0.462 | 0.462 | 0.462 | 0.462 | 0.462 | 0.462 | 0.462 | 0.462 | 0.462 | 0.462 | 0.462 | 0.462 | 0.462 | 0.462 | 0.462 | 0.462 | 0.462 | 0.462 | 0.462 | 0.462 | 0.462 | 0.462 | 0.462 | 0.462 | 0.462 | 0.462 | 0.462 | 0.462 | 0.462 | 0.462 | 0.462 | 0.462 | 0.462 | 0.462 | 0.462 | 0.462 | 0.462 | 0.462 | 0.462 | 0.462 | 0.46153 | 0.46107 | 0.4606 | 0.46013 | 0.45967 | 0.4592 | 0.45873 | 0.45827 | 0.4578 | 0.45733 | 0.45687 | 0.4564 | 0.45593 | 0.45547 | 0.455 | 0.45453 | 0.45407 | 0.4536 | 0.45313 | 0.45267 | 0.4522 | 0.45173 | 0.45127 | 0.4508 | 0.45033 | 0.44987 | 0.4494 | 0.44893 | 0.44847 | 0.448 | 0.44753 | 0.44707 | 0.4466 | 0.44613 | 0.44567 | 0.4452 | 0.44473 | 0.44427 | 0.4438 | 0.44333 | 0.44287 | 0.4424 | 0.44193 | 0.44147 | 0.441 | 0.44053 | 0.44007 | 0.4396 | 0.43913 | 0.43867 | 0.4382 | 0.43773 | 0.43727 | 0.4368 | 0.43633 | 0.43587 | 0.4354 | 0.43493 | 0.43447 | 0.434 | 0.43353 | 0.43307 | 0.4326 | 0.43213 | 0.43167 | 0.4312 | 0.43073 | 0.43027 | 0.4298 | 0.42933 | 0.42887 | 0.4284 | 0.42793 | 0.42747 | 0.427 | 0.42653 | 0.42607 | 0.4256 | 0.42513 | 0.42467 | 0.4242 | 0.42373 | 0.42327 | 0.4228 | 0.42233 | 0.42187 | 0.4214 | 0.42093 | 0.42047 | 0.42
1.4 | 0 | 0.024 | 0.048 | 0.072 | 0.096 | 0.12 | 0.144 | 0.168 | 0.192 | 0.216 | 0.24 | 0.2592 | 0.2784 | 0.2976 | 0.3168 | 0.336 | 0.3488 | 0.3616 | 0.3744 | 0.3872 | 0.4 | 0.408 | 0.416 | 0.424 | 0.432 | 0.44 | 0.448 | 0.456 | 0.464 | 0.472 | 0.48 | 0.4832 | 0.4864 | 0.4896 | 0.4928 | 0.496 | 0.4992 | 0.5024 | 0.5056 | 0.5088 | 0.512 | 0.5152 | 0.5184 | 0.5216 | 0.5248 | 0.528 | 0.528 | 0.528 | 0.528 | 0.528 | 0.528 | 0.528 | 0.528 | 0.528 | 0.528 | 0.528 | 0.528 | 0.528 | 0.528 | 0.528 | 0.528 | 0.528 | 0.528 | 0.528 | 0.528 | 0.528 | 0.528 | 0.528 | 0.528 | 0.528 | 0.528 | 0.528 | 0.528 | 0.528 | 0.528 | 0.528 | 0.528 | 0.528 | 0.528 | 0.528 | 0.528 | 0.528 | 0.528 | 0.528 | 0.528 | 0.528 | 0.528 | 0.528 | 0.528 | 0.528 | 0.528 | 0.52747 | 0.52693 | 0.5264 | 0.52587 | 0.52533 | 0.5248 | 0.52427 | 0.52373 | 0.5232 | 0.52267 | 0.52213 | 0.5216 | 0.52107 | 0.52053 | 0.52 | 0.51947 | 0.51893 | 0.5184 | 0.51787 | 0.51733 | 0.5168 | 0.51627 | 0.51573 | 0.5152 | 0.51467 | 0.51413 | 0.5136 | 0.51307 | 0.51253 | 0.512 | 0.51147 | 0.51093 | 0.5104 | 0.50987 | 0.50933 | 0.5088 | 0.50827 | 0.50773 | 0.5072 | 0.50667 | 0.50613 | 0.5056 | 0.50507 | 0.50453 | 0.504 | 0.50347 | 0.50293 | 0.5024 | 0.50187 | 0.50133 | 0.5008 | 0.50027 | 0.49973 | 0.4992 | 0.49867 | 0.49813 | 0.4976 | 0.49707 | 0.49653 | 0.496 | 0.49547 | 0.49493 | 0.4944 | 0.49387 | 0.49333 | 0.4928 | 0.49227 | 0.49173 | 0.4912 | 0.49067 | 0.49013 | 0.4896 | 0.48907 | 0.48853 | 0.488 | 0.48747 | 0.48693 | 0.4864 | 0.48587 | 0.48533 | 0.4848 | 0.48427 | 0.48373 | 0.4832 | 0.48267 | 0.48213 | 0.4816 | 0.48107 | 0.48053 | 0.48
1.45 | 0 | 0.027 | 0.054 | 0.081 | 0.108 | 0.135 | 0.162 | 0.189 | 0.216 | 0.243 | 0.27 | 0.2916 | 0.3132 | 0.3348 | 0.3564 | 0.378 | 0.3924 | 0.4068 | 0.4212 | 0.4356 | 0.45 | 0.459 | 0.468 | 0.477 | 0.486 | 0.495 | 0.504 | 0.513 | 0.522 | 0.531 | 0.54 | 0.5436 | 0.5472 | 0.5508 | 0.5544 | 0.558 | 0.5616 | 0.5652 | 0.5688 | 0.5724 | 0.576 | 0.5796 | 0.5832 | 0.5868 | 0.5904 | 0.594 | 0.594 | 0.594 | 0.594 | 0.594 | 0.594 | 0.594 | 0.594 | 0.594 | 0.594 | 0.594 | 0.594 | 0.594 | 0.594 | 0.594 | 0.594 | 0.594 | 0.594 | 0.594 | 0.594 | 0.594 | 0.594 | 0.594 | 0.594 | 0.594 | 0.594 | 0.594 | 0.594 | 0.594 | 0.594 | 0.594 | 0.594 | 0.594 | 0.594 | 0.594 | 0.594 | 0.594 | 0.594 | 0.594 | 0.594 | 0.594 | 0.594 | 0.594 | 0.594 | 0.594 | 0.594 | 0.5934 | 0.5928 | 0.5922 | 0.5916 | 0.591 | 0.5904 | 0.5898 | 0.5892 | 0.5886 | 0.588 | 0.5874 | 0.5868 | 0.5862 | 0.5856 | 0.585 | 0.5844 | 0.5838 | 0.5832 | 0.5826 | 0.582 | 0.5814 | 0.5808 | 0.5802 | 0.5796 | 0.579 | 0.5784 | 0.5778 | 0.5772 | 0.5766 | 0.576 | 0.5754 | 0.5748 | 0.5742 | 0.5736 | 0.573 | 0.5724 | 0.5718 | 0.5712 | 0.5706 | 0.57 | 0.5694 | 0.5688 | 0.5682 | 0.5676 | 0.567 | 0.5664 | 0.5658 | 0.5652 | 0.5646 | 0.564 | 0.5634 | 0.5628 | 0.5622 | 0.5616 | 0.561 | 0.5604 | 0.5598 | 0.5592 | 0.5586 | 0.558 | 0.5574 | 0.5568 | 0.5562 | 0.5556 | 0.555 | 0.5544 | 0.5538 | 0.5532 | 0.5526 | 0.552 | 0.5514 | 0.5508 | 0.5502 | 0.5496 | 0.549 | 0.5484 | 0.5478 | 0.5472 | 0.5466 | 0.546 | 0.5454 | 0.5448 | 0.5442 | 0.5436 | 0.543 | 0.5424 | 0.5418 | 0.5412 | 0.5406 | 0.54
1.5 | 0 | 0.03 | 0.06 | 0.09 | 0.12 | 0.15 | 0.18 | 0.21 | 0.24 | 0.27 | 0.3 | 0.324 | 0.348 | 0.372 | 0.396 | 0.42 | 0.436 | 0.452 | 0.468 | 0.484 | 0.5 | 0.51 | 0.52 | 0.53 | 0.54 | 0.55 | 0.56 | 0.57 | 0.58 | 0.59 | 0.6 | 0.604 | 0.608 | 0.612 | 0.616 | 0.62 | 0.624 | 0.628 | 0.632 | 0.636 | 0.64 | 0.644 | 0.648 | 0.652 | 0.656 | 0.66 | 0.66 | 0.66 | 0.66 | 0.66 | 0.66 | 0.66 | 0.66 | 0.66 | 0.66 | 0.66 | 0.66 | 0.66 | 0.66 | 0.66 | 0.66 | 0.66 | 0.66 | 0.66 | 0.66 | 0.66 | 0.66 | 0.66 | 0.66 | 0.66 | 0.66 | 0.66 | 0.66 | 0.66 | 0.66 | 0.66 | 0.66 | 0.66 | 0.66 | 0.66 | 0.66 | 0.66 | 0.66 | 0.66 | 0.66 | 0.66 | 0.66 | 0.66 | 0.66 | 0.66 | 0.66 | 0.65933 | 0.65867 | 0.658 | 0.65733 | 0.65667 | 0.656 | 0.65533 | 0.65467 | 0.654 | 0.65333 | 0.65267 | 0.652 | 0.65133 | 0.65067 | 0.65 | 0.64933 | 0.64867 | 0.648 | 0.64733 | 0.64667 | 0.646 | 0.64533 | 0.64467 | 0.644 | 0.64333 | 0.64267 | 0.642 | 0.64133 | 0.64067 | 0.64 | 0.63933 | 0.63867 | 0.638 | 0.63733 | 0.63667 | 0.636 | 0.63533 | 0.63467 | 0.634 | 0.63333 | 0.63267 | 0.632 | 0.63133 | 0.63067 | 0.63 | 0.62933 | 0.62867 | 0.628 | 0.62733 | 0.62667 | 0.626 | 0.62533 | 0.62467 | 0.624 | 0.62333 | 0.62267 | 0.622 | 0.62133 | 0.62067 | 0.62 | 0.61933 | 0.61867 | 0.618 | 0.61733 | 0.61667 | 0.616 | 0.61533 | 0.61467 | 0.614 | 0.61333 | 0.61267 | 0.612 | 0.61133 | 0.61067 | 0.61 | 0.60933 | 0.60867 | 0.608 | 0.60733 | 0.60667 | 0.606 | 0.60533 | 0.60467 | 0.604 | 0.60333 | 0.60267 | 0.602 | 0.60133 | 0.60067 | 0.6
1.55 | 0 | 0.033 | 0.066 | 0.099 | 0.132 | 0.165 | 0.198 | 0.231 | 0.264 | 0.297 | 0.33 | 0.3564 | 0.3828 | 0.4092 | 0.4356 | 0.462 | 0.4796 | 0.4972 | 0.5148 | 0.5324 | 0.55 | 0.561 | 0.572 | 0.583 | 0.594 | 0.605 | 0.616 | 0.627 | 0.638 | 0.649 | 0.66 | 0.6644 | 0.6688 | 0.6732 | 0.6776 | 0.682 | 0.6864 | 0.6908 | 0.6952 | 0.6996 | 0.704 | 0.7084 | 0.7128 | 0.7172 | 0.7216 | 0.726 | 0.726 | 0.726 | 0.726 | 0.726 | 0.726 | 0.726 | 0.726 | 0.726 | 0.726 | 0.726 | 0.726 | 0.726 | 0.726 | 0.726 | 0.726 | 0.726 | 0.726 | 0.726 | 0.726 | 0.726 | 0.726 | 0.726 | 0.726 | 0.726 | 0.726 | 0.726 | 0.726 | 0.726 | 0.726 | 0.726 | 0.726 | 0.726 | 0.726 | 0.726 | 0.726 | 0.726 | 0.726 | 0.726 | 0.726 | 0.726 | 0.726 | 0.726 | 0.726 | 0.726 | 0.726 | 0.72527 | 0.72453 | 0.7238 | 0.72307 | 0.72233 | 0.7216 | 0.72087 | 0.72013 | 0.7194 | 0.71867 | 0.71793 | 0.7172 | 0.71647 | 0.71573 | 0.715 | 0.71427 | 0.71353 | 0.7128 | 0.71207 | 0.71133 | 0.7106 | 0.70987 | 0.70913 | 0.7084 | 0.70767 | 0.70693 | 0.7062 | 0.70547 | 0.70473 | 0.704 | 0.70327 | 0.70253 | 0.7018 | 0.70107 | 0.70033 | 0.6996 | 0.69887 | 0.69813 | 0.6974 | 0.69667 | 0.69593 | 0.6952 | 0.69447 | 0.69373 | 0.693 | 0.69227 | 0.69153 | 0.6908 | 0.69007 | 0.68933 | 0.6886 | 0.68787 | 0.68713 | 0.6864 | 0.68567 | 0.68493 | 0.6842 | 0.68347 | 0.68273 | 0.682 | 0.68127 | 0.68053 | 0.6798 | 0.67907 | 0.67833 | 0.6776 | 0.67687 | 0.67613 | 0.6754 | 0.67467 | 0.67393 | 0.6732 | 0.67247 | 0.67173 | 0.671 | 0.67027 | 0.66953 | 0.6688 | 0.66807 | 0.66733 | 0.6666 | 0.66587 | 0.66513 | 0.6644 | 0.66367 | 0.66293 | 0.6622 | 0.66147 | 0.66073 | 0.66
1.6 | 0 | 0.036 | 0.072 | 0.108 | 0.144 | 0.18 | 0.216 | 0.252 | 0.288 | 0.324 | 0.36 | 0.3888 | 0.4176 | 0.4464 | 0.4752 | 0.504 | 0.5232 | 0.5424 | 0.5616 | 0.5808 | 0.6 | 0.612 | 0.624 | 0.636 | 0.648 | 0.66 | 0.672 | 0.684 | 0.696 | 0.708 | 0.72 | 0.7248 | 0.7296 | 0.7344 | 0.7392 | 0.744 | 0.7488 | 0.7536 | 0.7584 | 0.7632 | 0.768 | 0.7728 | 0.7776 | 0.7824 | 0.7872 | 0.792 | 0.792 | 0.792 | 0.792 | 0.792 | 0.792 | 0.792 | 0.792 | 0.792 | 0.792 | 0.792 | 0.792 | 0.792 | 0.792 | 0.792 | 0.792 | 0.792 | 0.792 | 0.792 | 0.792 | 0.792 | 0.792 | 0.792 | 0.792 | 0.792 | 0.792 | 0.792 | 0.792 | 0.792 | 0.792 | 0.792 | 0.792 | 0.792 | 0.792 | 0.792 | 0.792 | 0.792 | 0.792 | 0.792 | 0.792 | 0.792 | 0.792 | 0.792 | 0.792 | 0.792 | 0.792 | 0.7912 | 0.7904 | 0.7896 | 0.7888 | 0.788 | 0.7872 | 0.7864 | 0.7856 | 0.7848 | 0.784 | 0.7832 | 0.7824 | 0.7816 | 0.7808 | 0.78 | 0.7792 | 0.7784 | 0.7776 | 0.7768 | 0.776 | 0.7752 | 0.7744 | 0.7736 | 0.7728 | 0.772 | 0.7712 | 0.7704 | 0.7696 | 0.7688 | 0.768 | 0.7672 | 0.7664 | 0.7656 | 0.7648 | 0.764 | 0.7632 | 0.7624 | 0.7616 | 0.7608 | 0.76 | 0.7592 | 0.7584 | 0.7576 | 0.7568 | 0.756 | 0.7552 | 0.7544 | 0.7536 | 0.7528 | 0.752 | 0.7512 | 0.7504 | 0.7496 | 0.7488 | 0.748 | 0.7472 | 0.7464 | 0.7456 | 0.7448 | 0.744 | 0.7432 | 0.7424 | 0.7416 | 0.7408 | 0.74 | 0.7392 | 0.7384 | 0.7376 | 0.7368 | 0.736 | 0.7352 | 0.7344 | 0.7336 | 0.7328 | 0.732 | 0.7312 | 0.7304 | 0.7296 | 0.7288 | 0.728 | 0.7272 | 0.7264 | 0.7256 | 0.7248 | 0.724 | 0.7232 | 0.7224 | 0.7216 | 0.7208 | 0.72
1.65 | 0 | 0.039 | 0.078 | 0.117 | 0.156 | 0.195 | 0.234 | 0.273 | 0.312 | 0.351 | 0.39 | 0.4212 | 0.4524 | 0.4836 | 0.5148 | 0.546 | 0.5668 | 0.5876 | 0.6084 | 0.6292 | 0.65 | 0.663 | 0.676 | 0.689 | 0.702 | 0.715 | 0.728 | 0.741 | 0.754 | 0.767 | 0.78 | 0.7852 | 0.7904 | 0.7956 | 0.8008 | 0.806 | 0.8112 | 0.8164 | 0.8216 | 0.8268 | 0.832 | 0.8372 | 0.8424 | 0.8476 | 0.8528 | 0.858 | 0.858 | 0.858 | 0.858 | 0.858 | 0.858 | 0.858 | 0.858 | 0.858 | 0.858 | 0.858 | 0.858 | 0.858 | 0.858 | 0.858 | 0.858 | 0.858 | 0.858 | 0.858 | 0.858 | 0.858 | 0.858 | 0.858 | 0.858 | 0.858 | 0.858 | 0.858 | 0.858 | 0.858 | 0.858 | 0.858 | 0.858 | 0.858 | 0.858 | 0.858 | 0.858 | 0.858 | 0.858 | 0.858 | 0.858 | 0.858 | 0.858 | 0.858 | 0.858 | 0.858 | 0.858 | 0.85713 | 0.85627 | 0.8554 | 0.85453 | 0.85367 | 0.8528 | 0.85193 | 0.85107 | 0.8502 | 0.84933 | 0.84847 | 0.8476 | 0.84673 | 0.84587 | 0.845 | 0.84413 | 0.84327 | 0.8424 | 0.84153 | 0.84067 | 0.8398 | 0.83893 | 0.83807 | 0.8372 | 0.83633 | 0.83547 | 0.8346 | 0.83373 | 0.83287 | 0.832 | 0.83113 | 0.83027 | 0.8294 | 0.82853 | 0.82767 | 0.8268 | 0.82593 | 0.82507 | 0.8242 | 0.82333 | 0.82247 | 0.8216 | 0.82073 | 0.81987 | 0.819 | 0.81813 | 0.81727 | 0.8164 | 0.81553 | 0.81467 | 0.8138 | 0.81293 | 0.81207 | 0.8112 | 0.81033 | 0.80947 | 0.8086 | 0.80773 | 0.80687 | 0.806 | 0.80513 | 0.80427 | 0.8034 | 0.80253 | 0.80167 | 0.8008 | 0.79993 | 0.79907 | 0.7982 | 0.79733 | 0.79647 | 0.7956 | 0.79473 | 0.79387 | 0.793 | 0.79213 | 0.79127 | 0.7904 | 0.78953 | 0.78867 | 0.7878 | 0.78693 | 0.78607 | 0.7852 | 0.78433 | 0.78347 | 0.7826 | 0.78173 | 0.78087 | 0.78
1.7 | 0 | 0.042 | 0.084 | 0.126 | 0.168 | 0.21 | 0.252 | 0.294 | 0.336 | 0.378 | 0.42 | 0.4536 | 0.4872 | 0.5208 | 0.5544 | 0.588 | 0.6104 | 0.6328 | 0.6552 | 0.6776 | 0.7 | 0.714 | 0.728 | 0.742 | 0.756 | 0.77 | 0.784 | 0.798 | 0.812 | 0.826 | 0.84 | 0.8456 | 0.8512 | 0.8568 | 0.8624 | 0.868 | 0.8736 | 0.8792 | 0.8848 | 0.8904 | 0.896 | 0.9016 | 0.9072 | 0.9128 | 0.9184 | 0.924 | 0.924 | 0.924 | 0.924 | 0.924 | 0.924 | 0.924 | 0.924 | 0.924 | 0.924 | 0.924 | 0.924 | 0.924 | 0.924 | 0.924 | 0.924 | 0.924 | 0.924 | 0.924 | 0.924 | 0.924 | 0.924 | 0.924 | 0.924 | 0.924 | 0.924 | 0.924 | 0.924 | 0.924 | 0.924 | 0.924 | 0.924 | 0.924 | 0.924 | 0.924 | 0.924 | 0.924 | 0.924 | 0.924 | 0.924 | 0.924 | 0.924 | 0.924 | 0.924 | 0.924 | 0.924 | 0.92307 | 0.92213 | 0.9212 | 0.92027 | 0.91933 | 0.9184 | 0.91747 | 0.91653 | 0.9156 | 0.91467 | 0.91373 | 0.9128 | 0.91187 | 0.91093 | 0.91 | 0.90907 | 0.90813 | 0.9072 | 0.90627 | 0.90533 | 0.9044 | 0.90347 | 0.90253 | 0.9016 | 0.90067 | 0.89973 | 0.8988 | 0.89787 | 0.89693 | 0.896 | 0.89507 | 0.89413 | 0.8932 | 0.89227 | 0.89133 | 0.8904 | 0.88947 | 0.88853 | 0.8876 | 0.88667 | 0.88573 | 0.8848 | 0.88387 | 0.88293 | 0.882 | 0.88107 | 0.88013 | 0.8792 | 0.87827 | 0.87733 | 0.8764 | 0.87547 | 0.87453 | 0.8736 | 0.87267 | 0.87173 | 0.8708 | 0.86987 | 0.86893 | 0.868 | 0.86707 | 0.86613 | 0.8652 | 0.86427 | 0.86333 | 0.8624 | 0.86147 | 0.86053 | 0.8596 | 0.85867 | 0.85773 | 0.8568 | 0.85587 | 0.85493 | 0.854 | 0.85307 | 0.85213 | 0.8512 | 0.85027 | 0.84933 | 0.8484 | 0.84747 | 0.84653 | 0.8456 | 0.84467 | 0.84373 | 0.8428 | 0.84187 | 0.84093 | 0.84
1.75 | 0 | 0.045 | 0.09 | 0.135 | 0.18 | 0.225 | 0.27 | 0.315 | 0.36 | 0.405 | 0.45 | 0.486 | 0.522 | 0.558 | 0.594 | 0.63 | 0.654 | 0.678 | 0.702 | 0.726 | 0.75 | 0.765 | 0.78 | 0.795 | 0.81 | 0.825 | 0.84 | 0.855 | 0.87 | 0.885 | 0.9 | 0.906 | 0.912 | 0.918 | 0.924 | 0.93 | 0.936 | 0.942 | 0.948 | 0.954 | 0.96 | 0.966 | 0.972 | 0.978 | 0.984 | 0.99 | 0.99 | 0.99 | 0.99 | 0.99 | 0.99 | 0.99 | 0.99 | 0.99 | 0.99 | 0.99 | 0.99 | 0.99 | 0.99 | 0.99 | 0.99 | 0.99 | 0.99 | 0.99 | 0.99 | 0.99 | 0.99 | 0.99 | 0.99 | 0.99 | 0.99 | 0.99 | 0.99 | 0.99 | 0.99 | 0.99 | 0.99 | 0.99 | 0.99 | 0.99 | 0.99 | 0.99 | 0.99 | 0.99 | 0.99 | 0.99 | 0.99 | 0.99 | 0.99 | 0.99 | 0.99 | 0.989 | 0.988 | 0.987 | 0.986 | 0.985 | 0.984 | 0.983 | 0.982 | 0.981 | 0.98 | 0.979 | 0.978 | 0.977 | 0.976 | 0.975 | 0.974 | 0.973 | 0.972 | 0.971 | 0.97 | 0.969 | 0.968 | 0.967 | 0.966 | 0.965 | 0.964 | 0.963 | 0.962 | 0.961 | 0.96 | 0.959 | 0.958 | 0.957 | 0.956 | 0.955 | 0.954 | 0.953 | 0.952 | 0.951 | 0.95 | 0.949 | 0.948 | 0.947 | 0.946 | 0.945 | 0.944 | 0.943 | 0.942 | 0.941 | 0.94 | 0.939 | 0.938 | 0.937 | 0.936 | 0.935 | 0.934 | 0.933 | 0.932 | 0.931 | 0.93 | 0.929 | 0.928 | 0.927 | 0.926 | 0.925 | 0.924 | 0.923 | 0.922 | 0.921 | 0.92 | 0.919 | 0.918 | 0.917 | 0.916 | 0.915 | 0.914 | 0.913 | 0.912 | 0.911 | 0.91 | 0.909 | 0.908 | 0.907 | 0.906 | 0.905 | 0.904 | 0.903 | 0.902 | 0.901 | 0.9
1.8 | 0 | 0.048 | 0.096 | 0.144 | 0.192 | 0.24 | 0.288 | 0.336 | 0.384 | 0.432 | 0.48 | 0.5184 | 0.5568 | 0.5952 | 0.6336 | 0.672 | 0.6976 | 0.7232 | 0.7488 | 0.7744 | 0.8 | 0.816 | 0.832 | 0.848 | 0.864 | 0.88 | 0.896 | 0.912 | 0.928 | 0.944 | 0.96 | 0.9664 | 0.9728 | 0.9792 | 0.9856 | 0.992 | 0.9984 | 1.0048 | 1.0112 | 1.0176 | 1.024 | 1.0304 | 1.0368 | 1.0432 | 1.0496 | 1.056 | 1.056 | 1.056 | 1.056 | 1.056 | 1.056 | 1.056 | 1.056 | 1.056 | 1.056 | 1.056 | 1.056 | 1.056 | 1.056 | 1.056 | 1.056 | 1.056 | 1.056 | 1.056 | 1.056 | 1.056 | 1.056 | 1.056 | 1.056 | 1.056 | 1.056 | 1.056 | 1.056 | 1.056 | 1.056 | 1.056 | 1.056 | 1.056 | 1.056 | 1.056 | 1.056 | 1.056 | 1.056 | 1.056 | 1.056 | 1.056 | 1.056 | 1.056 | 1.056 | 1.056 | 1.056 | 1.0549 | 1.0539 | 1.0528 | 1.0517 | 1.0507 | 1.0496 | 1.0485 | 1.0475 | 1.0464 | 1.0453 | 1.0443 | 1.0432 | 1.0421 | 1.0411 | 1.04 | 1.0389 | 1.0379 | 1.0368 | 1.0357 | 1.0347 | 1.0336 | 1.0325 | 1.0315 | 1.0304 | 1.0293 | 1.0283 | 1.0272 | 1.0261 | 1.0251 | 1.024 | 1.0229 | 1.0219 | 1.0208 | 1.0197 | 1.0187 | 1.0176 | 1.0165 | 1.0155 | 1.0144 | 1.0133 | 1.0123 | 1.0112 | 1.0101 | 1.0091 | 1.008 | 1.0069 | 1.0059 | 1.0048 | 1.0037 | 1.0027 | 1.0016 | 1.0005 | 0.99947 | 0.9984 | 0.99733 | 0.99627 | 0.9952 | 0.99413 | 0.99307 | 0.992 | 0.99093 | 0.98987 | 0.9888 | 0.98773 | 0.98667 | 0.9856 | 0.98453 | 0.98347 | 0.9824 | 0.98133 | 0.98027 | 0.9792 | 0.97813 | 0.97707 | 0.976 | 0.97493 | 0.97387 | 0.9728 | 0.97173 | 0.97067 | 0.9696 | 0.96853 | 0.96747 | 0.9664 | 0.96533 | 0.96427 | 0.9632 | 0.96213 | 0.96107 | 0.96
1.85 | 0 | 0.051 | 0.102 | 0.153 | 0.204 | 0.255 | 0.306 | 0.357 | 0.408 | 0.459 | 0.51 | 0.5508 | 0.5916 | 0.6324 | 0.6732 | 0.714 | 0.7412 | 0.7684 | 0.7956 | 0.8228 | 0.85 | 0.867 | 0.884 | 0.901 | 0.918 | 0.935 | 0.952 | 0.969 | 0.986 | 1.003 | 1.02 | 1.0268 | 1.0336 | 1.0404 | 1.0472 | 1.054 | 1.0608 | 1.0676 | 1.0744 | 1.0812 | 1.088 | 1.0948 | 1.1016 | 1.1084 | 1.1152 | 1.122 | 1.122 | 1.122 | 1.122 | 1.122 | 1.122 | 1.122 | 1.122 | 1.122 | 1.122 | 1.122 | 1.122 | 1.122 | 1.122 | 1.122 | 1.122 | 1.122 | 1.122 | 1.122 | 1.122 | 1.122 | 1.122 | 1.122 | 1.122 | 1.122 | 1.122 | 1.122 | 1.122 | 1.122 | 1.122 | 1.122 | 1.122 | 1.122 | 1.122 | 1.122 | 1.122 | 1.122 | 1.122 | 1.122 | 1.122 | 1.122 | 1.122 | 1.122 | 1.122 | 1.122 | 1.122 | 1.1209 | 1.1197 | 1.1186 | 1.1175 | 1.1163 | 1.1152 | 1.1141 | 1.1129 | 1.1118 | 1.1107 | 1.1095 | 1.1084 | 1.1073 | 1.1061 | 1.105 | 1.1039 | 1.1027 | 1.1016 | 1.1005 | 1.0993 | 1.0982 | 1.0971 | 1.0959 | 1.0948 | 1.0937 | 1.0925 | 1.0914 | 1.0903 | 1.0891 | 1.088 | 1.0869 | 1.0857 | 1.0846 | 1.0835 | 1.0823 | 1.0812 | 1.0801 | 1.0789 | 1.0778 | 1.0767 | 1.0755 | 1.0744 | 1.0733 | 1.0721 | 1.071 | 1.0699 | 1.0687 | 1.0676 | 1.0665 | 1.0653 | 1.0642 | 1.0631 | 1.0619 | 1.0608 | 1.0597 | 1.0585 | 1.0574 | 1.0563 | 1.0551 | 1.054 | 1.0529 | 1.0517 | 1.0506 | 1.0495 | 1.0483 | 1.0472 | 1.0461 | 1.0449 | 1.0438 | 1.0427 | 1.0415 | 1.0404 | 1.0393 | 1.0381 | 1.037 | 1.0359 | 1.0347 | 1.0336 | 1.0325 | 1.0313 | 1.0302 | 1.0291 | 1.0279 | 1.0268 | 1.0257 | 1.0245 | 1.0234 | 1.0223 | 1.0211 | 1.02
1.9 | 0 | 0.054 | 0.108 | 0.162 | 0.216 | 0.27 | 0.324 | 0.378 | 0.432 | 0.486 | 0.54 | 0.5832 | 0.6264 | 0.6696 | 0.7128 | 0.756 | 0.7848 | 0.8136 | 0.8424 | 0.8712 | 0.9 | 0.918 | 0.936 | 0.954 | 0.972 | 0.99 | 1.008 | 1.026 | 1.044 | 1.062 | 1.08 | 1.0872 | 1.0944 | 1.1016 | 1.1088 | 1.116 | 1.1232 | 1.1304 | 1.1376 | 1.1448 | 1.152 | 1.1592 | 1.1664 | 1.1736 | 1.1808 | 1.188 | 1.188 | 1.188 | 1.188 | 1.188 | 1.188 | 1.188 | 1.188 | 1.188 | 1.188 | 1.188 | 1.188 | 1.188 | 1.188 | 1.188 | 1.188 | 1.188 | 1.188 | 1.188 | 1.188 | 1.188 | 1.188 | 1.188 | 1.188 | 1.188 | 1.188 | 1.188 | 1.188 | 1.188 | 1.188 | 1.188 | 1.188 | 1.188 | 1.188 | 1.188 | 1.188 | 1.188 | 1.188 | 1.188 | 1.188 | 1.188 | 1.188 | 1.188 | 1.188 | 1.188 | 1.188 | 1.1868 | 1.1856 | 1.1844 | 1.1832 | 1.182 | 1.1808 | 1.1796 | 1.1784 | 1.1772 | 1.176 | 1.1748 | 1.1736 | 1.1724 | 1.1712 | 1.17 | 1.1688 | 1.1676 | 1.1664 | 1.1652 | 1.164 | 1.1628 | 1.1616 | 1.1604 | 1.1592 | 1.158 | 1.1568 | 1.1556 | 1.1544 | 1.1532 | 1.152 | 1.1508 | 1.1496 | 1.1484 | 1.1472 | 1.146 | 1.1448 | 1.1436 | 1.1424 | 1.1412 | 1.14 | 1.1388 | 1.1376 | 1.1364 | 1.1352 | 1.134 | 1.1328 | 1.1316 | 1.1304 | 1.1292 | 1.128 | 1.1268 | 1.1256 | 1.1244 | 1.1232 | 1.122 | 1.1208 | 1.1196 | 1.1184 | 1.1172 | 1.116 | 1.1148 | 1.1136 | 1.1124 | 1.1112 | 1.11 | 1.1088 | 1.1076 | 1.1064 | 1.1052 | 1.104 | 1.1028 | 1.1016 | 1.1004 | 1.0992 | 1.098 | 1.0968 | 1.0956 | 1.0944 | 1.0932 | 1.092 | 1.0908 | 1.0896 | 1.0884 | 1.0872 | 1.086 | 1.0848 | 1.0836 | 1.0824 | 1.0812 | 1.08
1.95 | 0 | 0.057 | 0.114 | 0.171 | 0.228 | 0.285 | 0.342 | 0.399 | 0.456 | 0.513 | 0.57 | 0.6156 | 0.6612 | 0.7068 | 0.7524 | 0.798 | 0.8284 | 0.8588 | 0.8892 | 0.9196 | 0.95 | 0.969 | 0.988 | 1.007 | 1.026 | 1.045 | 1.064 | 1.083 | 1.102 | 1.121 | 1.14 | 1.1476 | 1.1552 | 1.1628 | 1.1704 | 1.178 | 1.1856 | 1.1932 | 1.2008 | 1.2084 | 1.216 | 1.2236 | 1.2312 | 1.2388 | 1.2464 | 1.254 | 1.254 | 1.254 | 1.254 | 1.254 | 1.254 | 1.254 | 1.254 | 1.254 | 1.254 | 1.254 | 1.254 | 1.254 | 1.254 | 1.254 | 1.254 | 1.254 | 1.254 | 1.254 | 1.254 | 1.254 | 1.254 | 1.254 | 1.254 | 1.254 | 1.254 | 1.254 | 1.254 | 1.254 | 1.254 | 1.254 | 1.254 | 1.254 | 1.254 | 1.254 | 1.254 | 1.254 | 1.254 | 1.254 | 1.254 | 1.254 | 1.254 | 1.254 | 1.254 | 1.254 | 1.254 | 1.2527 | 1.2515 | 1.2502 | 1.2489 | 1.2477 | 1.2464 | 1.2451 | 1.2439 | 1.2426 | 1.2413 | 1.2401 | 1.2388 | 1.2375 | 1.2363 | 1.235 | 1.2337 | 1.2325 | 1.2312 | 1.2299 | 1.2287 | 1.2274 | 1.2261 | 1.2249 | 1.2236 | 1.2223 | 1.2211 | 1.2198 | 1.2185 | 1.2173 | 1.216 | 1.2147 | 1.2135 | 1.2122 | 1.2109 | 1.2097 | 1.2084 | 1.2071 | 1.2059 | 1.2046 | 1.2033 | 1.2021 | 1.2008 | 1.1995 | 1.1983 | 1.197 | 1.1957 | 1.1945 | 1.1932 | 1.1919 | 1.1907 | 1.1894 | 1.1881 | 1.1869 | 1.1856 | 1.1843 | 1.1831 | 1.1818 | 1.1805 | 1.1793 | 1.178 | 1.1767 | 1.1755 | 1.1742 | 1.1729 | 1.1717 | 1.1704 | 1.1691 | 1.1679 | 1.1666 | 1.1653 | 1.1641 | 1.1628 | 1.1615 | 1.1603 | 1.159 | 1.1577 | 1.1565 | 1.1552 | 1.1539 | 1.1527 | 1.1514 | 1.1501 | 1.1489 | 1.1476 | 1.1463 | 1.1451 | 1.1438 | 1.1425 | 1.1413 | 1.14
2 | 0 | 0.06 | 0.12 | 0.18 | 0.24 | 0.3 | 0.36 | 0.42 | 0.48 | 0.54 | 0.6 | 0.648 | 0.696 | 0.744 | 0.792 | 0.84 | 0.872 | 0.904 | 0.936 | 0.968 | 1 | 1.02 | 1.04 | 1.06 | 1.08 | 1.1 | 1.12 | 1.14 | 1.16 | 1.18 | 1.2 | 1.208 | 1.216 | 1.224 | 1.232 | 1.24 | 1.248 | 1.256 | 1.264 | 1.272 | 1.28 | 1.288 | 1.296 | 1.304 | 1.312 | 1.32 | 1.32 | 1.32 | 1.32 | 1.32 | 1.32 | 1.32 | 1.32 | 1.32 | 1.32 | 1.32 | 1.32 | 1.32 | 1.32 | 1.32 | 1.32 | 1.32 | 1.32 | 1.32 | 1.32 | 1.32 | 1.32 | 1.32 | 1.32 | 1.32 | 1.32 | 1.32 | 1.32 | 1.32 | 1.32 | 1.32 | 1.32 | 1.32 | 1.32 | 1.32 | 1.32 | 1.32 | 1.32 | 1.32 | 1.32 | 1.32 | 1.32 | 1.32 | 1.32 | 1.32 | 1.32 | 1.3187 | 1.3173 | 1.316 | 1.3147 | 1.3133 | 1.312 | 1.3107 | 1.3093 | 1.308 | 1.3067 | 1.3053 | 1.304 | 1.3027 | 1.3013 | 1.3 | 1.2987 | 1.2973 | 1.296 | 1.2947 | 1.2933 | 1.292 | 1.2907 | 1.2893 | 1.288 | 1.2867 | 1.2853 | 1.284 | 1.2827 | 1.2813 | 1.28 | 1.2787 | 1.2773 | 1.276 | 1.2747 | 1.2733 | 1.272 | 1.2707 | 1.2693 | 1.268 | 1.2667 | 1.2653 | 1.264 | 1.2627 | 1.2613 | 1.26 | 1.2587 | 1.2573 | 1.256 | 1.2547 | 1.2533 | 1.252 | 1.2507 | 1.2493 | 1.248 | 1.2467 | 1.2453 | 1.244 | 1.2427 | 1.2413 | 1.24 | 1.2387 | 1.2373 | 1.236 | 1.2347 | 1.2333 | 1.232 | 1.2307 | 1.2293 | 1.228 | 1.2267 | 1.2253 | 1.224 | 1.2227 | 1.2213 | 1.22 | 1.2187 | 1.2173 | 1.216 | 1.2147 | 1.2133 | 1.212 | 1.2107 | 1.2093 | 1.208 | 1.2067 | 1.2053 | 1.204 | 1.2027 | 1.2013 | 1.2
2.05 | 0 | 0.0685 | 0.137 | 0.2055 | 0.274 | 0.3425 | 0.411 | 0.4795 | 0.548 | 0.6165 | 0.685 | 0.7406 | 0.7962 | 0.8518 | 0.9074 | 0.963 | 1.0014 | 1.0398 | 1.0782 | 1.1166 | 1.155 | 1.1773 | 1.1996 | 1.2219 | 1.2442 | 1.2665 | 1.2888 | 1.3111 | 1.3334 | 1.3557 | 1.378 | 1.3874 | 1.3968 | 1.4062 | 1.4156 | 1.425 | 1.4344 | 1.4438 | 1.4532 | 1.4626 | 1.472 | 1.4814 | 1.4908 | 1.5002 | 1.5096 | 1.519 | 1.5201 | 1.5211 | 1.5222 | 1.5233 | 1.5243 | 1.5254 | 1.5265 | 1.5275 | 1.5286 | 1.5297 | 1.5307 | 1.5318 | 1.5329 | 1.5339 | 1.535 | 1.5353 | 1.5355 | 1.5358 | 1.5361 | 1.5363 | 1.5366 | 1.5369 | 1.5371 | 1.5374 | 1.5377 | 1.5379 | 1.5382 | 1.5385 | 1.5387 | 1.539 | 1.5393 | 1.5395 | 1.5398 | 1.5401 | 1.5403 | 1.5406 | 1.5409 | 1.5411 | 1.5414 | 1.5417 | 1.5419 | 1.5422 | 1.5425 | 1.5427 | 1.543 | 1.5417 | 1.5404 | 1.5391 | 1.5378 | 1.5365 | 1.5352 | 1.5339 | 1.5326 | 1.5313 | 1.53 | 1.5287 | 1.5274 | 1.5261 | 1.5248 | 1.5235 | 1.5222 | 1.5209 | 1.5196 | 1.5183 | 1.517 | 1.5157 | 1.5144 | 1.5131 | 1.5118 | 1.5105 | 1.5092 | 1.5079 | 1.5066 | 1.5053 | 1.504 | 1.5027 | 1.5014 | 1.5001 | 1.4988 | 1.4975 | 1.4962 | 1.4949 | 1.4936 | 1.4923 | 1.491 | 1.4897 | 1.4884 | 1.4871 | 1.4858 | 1.4845 | 1.4832 | 1.4819 | 1.4806 | 1.4793 | 1.478 | 1.4767 | 1.4754 | 1.4741 | 1.4728 | 1.4715 | 1.4702 | 1.4689 | 1.4676 | 1.4663 | 1.465 | 1.4637 | 1.4624 | 1.4611 | 1.4598 | 1.4585 | 1.4572 | 1.4559 | 1.4546 | 1.4533 | 1.452 | 1.4507 | 1.4494 | 1.4481 | 1.4468 | 1.4455 | 1.4442 | 1.4429 | 1.4416 | 1.4403 | 1.439 | 1.4377 | 1.4364 | 1.4351 | 1.4338 | 1.4325 | 1.4312 | 1.4299 | 1.4286 | 1.4273 | 1.426
2.1 | 0 | 0.077 | 0.154 | 0.231 | 0.308 | 0.385 | 0.462 | 0.539 | 0.616 | 0.693 | 0.77 | 0.8332 | 0.8964 | 0.9596 | 1.0228 | 1.086 | 1.1308 | 1.1756 | 1.2204 | 1.2652 | 1.31 | 1.3346 | 1.3592 | 1.3838 | 1.4084 | 1.433 | 1.4576 | 1.4822 | 1.5068 | 1.5314 | 1.556 | 1.5668 | 1.5776 | 1.5884 | 1.5992 | 1.61 | 1.6208 | 1.6316 | 1.6424 | 1.6532 | 1.664 | 1.6748 | 1.6856 | 1.6964 | 1.7072 | 1.718 | 1.7201 | 1.7223 | 1.7244 | 1.7265 | 1.7287 | 1.7308 | 1.7329 | 1.7351 | 1.7372 | 1.7393 | 1.7415 | 1.7436 | 1.7457 | 1.7479 | 1.75 | 1.7505 | 1.7511 | 1.7516 | 1.7521 | 1.7527 | 1.7532 | 1.7537 | 1.7543 | 1.7548 | 1.7553 | 1.7559 | 1.7564 | 1.7569 | 1.7575 | 1.758 | 1.7585 | 1.7591 | 1.7596 | 1.7601 | 1.7607 | 1.7612 | 1.7617 | 1.7623 | 1.7628 | 1.7633 | 1.7639 | 1.7644 | 1.7649 | 1.7655 | 1.766 | 1.7647 | 1.7635 | 1.7622 | 1.7609 | 1.7597 | 1.7584 | 1.7571 | 1.7559 | 1.7546 | 1.7533 | 1.7521 | 1.7508 | 1.7495 | 1.7483 | 1.747 | 1.7457 | 1.7445 | 1.7432 | 1.7419 | 1.7407 | 1.7394 | 1.7381 | 1.7369 | 1.7356 | 1.7343 | 1.7331 | 1.7318 | 1.7305 | 1.7293 | 1.728 | 1.7267 | 1.7255 | 1.7242 | 1.7229 | 1.7217 | 1.7204 | 1.7191 | 1.7179 | 1.7166 | 1.7153 | 1.7141 | 1.7128 | 1.7115 | 1.7103 | 1.709 | 1.7077 | 1.7065 | 1.7052 | 1.7039 | 1.7027 | 1.7014 | 1.7001 | 1.6989 | 1.6976 | 1.6963 | 1.6951 | 1.6938 | 1.6925 | 1.6913 | 1.69 | 1.6887 | 1.6875 | 1.6862 | 1.6849 | 1.6837 | 1.6824 | 1.6811 | 1.6799 | 1.6786 | 1.6773 | 1.6761 | 1.6748 | 1.6735 | 1.6723 | 1.671 | 1.6697 | 1.6685 | 1.6672 | 1.6659 | 1.6647 | 1.6634 | 1.6621 | 1.6609 | 1.6596 | 1.6583 | 1.6571 | 1.6558 | 1.6545 | 1.6533 | 1.652
2.15 | 0 | 0.0855 | 0.171 | 0.2565 | 0.342 | 0.4275 | 0.513 | 0.5985 | 0.684 | 0.7695 | 0.855 | 0.9258 | 0.9966 | 1.0674 | 1.1382 | 1.209 | 1.2602 | 1.3114 | 1.3626 | 1.4138 | 1.465 | 1.4919 | 1.5188 | 1.5457 | 1.5726 | 1.5995 | 1.6264 | 1.6533 | 1.6802 | 1.7071 | 1.734 | 1.7462 | 1.7584 | 1.7706 | 1.7828 | 1.795 | 1.8072 | 1.8194 | 1.8316 | 1.8438 | 1.856 | 1.8682 | 1.8804 | 1.8926 | 1.9048 | 1.917 | 1.9202 | 1.9234 | 1.9266 | 1.9298 | 1.933 | 1.9362 | 1.9394 | 1.9426 | 1.9458 | 1.949 | 1.9522 | 1.9554 | 1.9586 | 1.9618 | 1.965 | 1.9658 | 1.9666 | 1.9674 | 1.9682 | 1.969 | 1.9698 | 1.9706 | 1.9714 | 1.9722 | 1.973 | 1.9738 | 1.9746 | 1.9754 | 1.9762 | 1.977 | 1.9778 | 1.9786 | 1.9794 | 1.9802 | 1.981 | 1.9818 | 1.9826 | 1.9834 | 1.9842 | 1.985 | 1.9858 | 1.9866 | 1.9874 | 1.9882 | 1.989 | 1.9878 | 1.9865 | 1.9853 | 1.9841 | 1.9828 | 1.9816 | 1.9804 | 1.9791 | 1.9779 | 1.9767 | 1.9754 | 1.9742 | 1.973 | 1.9717 | 1.9705 | 1.9693 | 1.968 | 1.9668 | 1.9656 | 1.9643 | 1.9631 | 1.9619 | 1.9606 | 1.9594 | 1.9582 | 1.9569 | 1.9557 | 1.9545 | 1.9532 | 1.952 | 1.9508 | 1.9495 | 1.9483 | 1.9471 | 1.9458 | 1.9446 | 1.9434 | 1.9421 | 1.9409 | 1.9397 | 1.9384 | 1.9372 | 1.936 | 1.9347 | 1.9335 | 1.9323 | 1.931 | 1.9298 | 1.9286 | 1.9273 | 1.9261 | 1.9249 | 1.9236 | 1.9224 | 1.9212 | 1.9199 | 1.9187 | 1.9175 | 1.9162 | 1.915 | 1.9138 | 1.9125 | 1.9113 | 1.9101 | 1.9088 | 1.9076 | 1.9064 | 1.9051 | 1.9039 | 1.9027 | 1.9014 | 1.9002 | 1.899 | 1.8977 | 1.8965 | 1.8953 | 1.894 | 1.8928 | 1.8916 | 1.8903 | 1.8891 | 1.8879 | 1.8866 | 1.8854 | 1.8842 | 1.8829 | 1.8817 | 1.8805 | 1.8792 | 1.878
2.2 | 0 | 0.094 | 0.188 | 0.282 | 0.376 | 0.47 | 0.564 | 0.658 | 0.752 | 0.846 | 0.94 | 1.0184 | 1.0968 | 1.1752 | 1.2536 | 1.332 | 1.3896 | 1.4472 | 1.5048 | 1.5624 | 1.62 | 1.6492 | 1.6784 | 1.7076 | 1.7368 | 1.766 | 1.7952 | 1.8244 | 1.8536 | 1.8828 | 1.912 | 1.9256 | 1.9392 | 1.9528 | 1.9664 | 1.98 | 1.9936 | 2.0072 | 2.0208 | 2.0344 | 2.048 | 2.0616 | 2.0752 | 2.0888 | 2.1024 | 2.116 | 2.1203 | 2.1245 | 2.1288 | 2.1331 | 2.1373 | 2.1416 | 2.1459 | 2.1501 | 2.1544 | 2.1587 | 2.1629 | 2.1672 | 2.1715 | 2.1757 | 2.18 | 2.1811 | 2.1821 | 2.1832 | 2.1843 | 2.1853 | 2.1864 | 2.1875 | 2.1885 | 2.1896 | 2.1907 | 2.1917 | 2.1928 | 2.1939 | 2.1949 | 2.196 | 2.1971 | 2.1981 | 2.1992 | 2.2003 | 2.2013 | 2.2024 | 2.2035 | 2.2045 | 2.2056 | 2.2067 | 2.2077 | 2.2088 | 2.2099 | 2.2109 | 2.212 | 2.2108 | 2.2096 | 2.2084 | 2.2072 | 2.206 | 2.2048 | 2.2036 | 2.2024 | 2.2012 | 2.2 | 2.1988 | 2.1976 | 2.1964 | 2.1952 | 2.194 | 2.1928 | 2.1916 | 2.1904 | 2.1892 | 2.188 | 2.1868 | 2.1856 | 2.1844 | 2.1832 | 2.182 | 2.1808 | 2.1796 | 2.1784 | 2.1772 | 2.176 | 2.1748 | 2.1736 | 2.1724 | 2.1712 | 2.17 | 2.1688 | 2.1676 | 2.1664 | 2.1652 | 2.164 | 2.1628 | 2.1616 | 2.1604 | 2.1592 | 2.158 | 2.1568 | 2.1556 | 2.1544 | 2.1532 | 2.152 | 2.1508 | 2.1496 | 2.1484 | 2.1472 | 2.146 | 2.1448 | 2.1436 | 2.1424 | 2.1412 | 2.14 | 2.1388 | 2.1376 | 2.1364 | 2.1352 | 2.134 | 2.1328 | 2.1316 | 2.1304 | 2.1292 | 2.128 | 2.1268 | 2.1256 | 2.1244 | 2.1232 | 2.122 | 2.1208 | 2.1196 | 2.1184 | 2.1172 | 2.116 | 2.1148 | 2.1136 | 2.1124 | 2.1112 | 2.11 | 2.1088 | 2.1076 | 2.1064 | 2.1052 | 2.104
2.25 | 0 | 0.1025 | 0.205 | 0.3075 | 0.41 | 0.5125 | 0.615 | 0.7175 | 0.82 | 0.9225 | 1.025 | 1.111 | 1.197 | 1.283 | 1.369 | 1.455 | 1.519 | 1.583 | 1.647 | 1.711 | 1.775 | 1.8065 | 1.838 | 1.8695 | 1.901 | 1.9325 | 1.964 | 1.9955 | 2.027 | 2.0585 | 2.09 | 2.105 | 2.12 | 2.135 | 2.15 | 2.165 | 2.18 | 2.195 | 2.21 | 2.225 | 2.24 | 2.255 | 2.27 | 2.285 | 2.3 | 2.315 | 2.3203 | 2.3257 | 2.331 | 2.3363 | 2.3417 | 2.347 | 2.3523 | 2.3577 | 2.363 | 2.3683 | 2.3737 | 2.379 | 2.3843 | 2.3897 | 2.395 | 2.3963 | 2.3977 | 2.399 | 2.4003 | 2.4017 | 2.403 | 2.4043 | 2.4057 | 2.407 | 2.4083 | 2.4097 | 2.411 | 2.4123 | 2.4137 | 2.415 | 2.4163 | 2.4177 | 2.419 | 2.4203 | 2.4217 | 2.423 | 2.4243 | 2.4257 | 2.427 | 2.4283 | 2.4297 | 2.431 | 2.4323 | 2.4337 | 2.435 | 2.4338 | 2.4327 | 2.4315 | 2.4303 | 2.4292 | 2.428 | 2.4268 | 2.4257 | 2.4245 | 2.4233 | 2.4222 | 2.421 | 2.4198 | 2.4187 | 2.4175 | 2.4163 | 2.4152 | 2.414 | 2.4128 | 2.4117 | 2.4105 | 2.4093 | 2.4082 | 2.407 | 2.4058 | 2.4047 | 2.4035 | 2.4023 | 2.4012 | 2.4 | 2.3988 | 2.3977 | 2.3965 | 2.3953 | 2.3942 | 2.393 | 2.3918 | 2.3907 | 2.3895 | 2.3883 | 2.3872 | 2.386 | 2.3848 | 2.3837 | 2.3825 | 2.3813 | 2.3802 | 2.379 | 2.3778 | 2.3767 | 2.3755 | 2.3743 | 2.3732 | 2.372 | 2.3708 | 2.3697 | 2.3685 | 2.3673 | 2.3662 | 2.365 | 2.3638 | 2.3627 | 2.3615 | 2.3603 | 2.3592 | 2.358 | 2.3568 | 2.3557 | 2.3545 | 2.3533 | 2.3522 | 2.351 | 2.3498 | 2.3487 | 2.3475 | 2.3463 | 2.3452 | 2.344 | 2.3428 | 2.3417 | 2.3405 | 2.3393 | 2.3382 | 2.337 | 2.3358 | 2.3347 | 2.3335 | 2.3323 | 2.3312 | 2.33
2.3 | 0 | 0.111 | 0.222 | 0.333 | 0.444 | 0.555 | 0.666 | 0.777 | 0.888 | 0.999 | 1.11 | 1.2036 | 1.2972 | 1.3908 | 1.4844 | 1.578 | 1.6484 | 1.7188 | 1.7892 | 1.8596 | 1.93 | 1.9638 | 1.9976 | 2.0314 | 2.0652 | 2.099 | 2.1328 | 2.1666 | 2.2004 | 2.2342 | 2.268 | 2.2844 | 2.3008 | 2.3172 | 2.3336 | 2.35 | 2.3664 | 2.3828 | 2.3992 | 2.4156 | 2.432 | 2.4484 | 2.4648 | 2.4812 | 2.4976 | 2.514 | 2.5204 | 2.5268 | 2.5332 | 2.5396 | 2.546 | 2.5524 | 2.5588 | 2.5652 | 2.5716 | 2.578 | 2.5844 | 2.5908 | 2.5972 | 2.6036 | 2.61 | 2.6116 | 2.6132 | 2.6148 | 2.6164 | 2.618 | 2.6196 | 2.6212 | 2.6228 | 2.6244 | 2.626 | 2.6276 | 2.6292 | 2.6308 | 2.6324 | 2.634 | 2.6356 | 2.6372 | 2.6388 | 2.6404 | 2.642 | 2.6436 | 2.6452 | 2.6468 | 2.6484 | 2.65 | 2.6516 | 2.6532 | 2.6548 | 2.6564 | 2.658 | 2.6569 | 2.6557 | 2.6546 | 2.6535 | 2.6523 | 2.6512 | 2.6501 | 2.6489 | 2.6478 | 2.6467 | 2.6455 | 2.6444 | 2.6433 | 2.6421 | 2.641 | 2.6399 | 2.6387 | 2.6376 | 2.6365 | 2.6353 | 2.6342 | 2.6331 | 2.6319 | 2.6308 | 2.6297 | 2.6285 | 2.6274 | 2.6263 | 2.6251 | 2.624 | 2.6229 | 2.6217 | 2.6206 | 2.6195 | 2.6183 | 2.6172 | 2.6161 | 2.6149 | 2.6138 | 2.6127 | 2.6115 | 2.6104 | 2.6093 | 2.6081 | 2.607 | 2.6059 | 2.6047 | 2.6036 | 2.6025 | 2.6013 | 2.6002 | 2.5991 | 2.5979 | 2.5968 | 2.5957 | 2.5945 | 2.5934 | 2.5923 | 2.5911 | 2.59 | 2.5889 | 2.5877 | 2.5866 | 2.5855 | 2.5843 | 2.5832 | 2.5821 | 2.5809 | 2.5798 | 2.5787 | 2.5775 | 2.5764 | 2.5753 | 2.5741 | 2.573 | 2.5719 | 2.5707 | 2.5696 | 2.5685 | 2.5673 | 2.5662 | 2.5651 | 2.5639 | 2.5628 | 2.5617 | 2.5605 | 2.5594 | 2.5583 | 2.5571 | 2.556
2.35 | 0 | 0.1195 | 0.239 | 0.3585 | 0.478 | 0.5975 | 0.717 | 0.8365 | 0.956 | 1.0755 | 1.195 | 1.2962 | 1.3974 | 1.4986 | 1.5998 | 1.701 | 1.7778 | 1.8546 | 1.9314 | 2.0082 | 2.085 | 2.1211 | 2.1572 | 2.1933 | 2.2294 | 2.2655 | 2.3016 | 2.3377 | 2.3738 | 2.4099 | 2.446 | 2.4638 | 2.4816 | 2.4994 | 2.5172 | 2.535 | 2.5528 | 2.5706 | 2.5884 | 2.6062 | 2.624 | 2.6418 | 2.6596 | 2.6774 | 2.6952 | 2.713 | 2.7205 | 2.7279 | 2.7354 | 2.7429 | 2.7503 | 2.7578 | 2.7653 | 2.7727 | 2.7802 | 2.7877 | 2.7951 | 2.8026 | 2.8101 | 2.8175 | 2.825 | 2.8269 | 2.8287 | 2.8306 | 2.8325 | 2.8343 | 2.8362 | 2.8381 | 2.8399 | 2.8418 | 2.8437 | 2.8455 | 2.8474 | 2.8493 | 2.8511 | 2.853 | 2.8549 | 2.8567 | 2.8586 | 2.8605 | 2.8623 | 2.8642 | 2.8661 | 2.8679 | 2.8698 | 2.8717 | 2.8735 | 2.8754 | 2.8773 | 2.8791 | 2.881 | 2.8799 | 2.8788 | 2.8777 | 2.8766 | 2.8755 | 2.8744 | 2.8733 | 2.8722 | 2.8711 | 2.87 | 2.8689 | 2.8678 | 2.8667 | 2.8656 | 2.8645 | 2.8634 | 2.8623 | 2.8612 | 2.8601 | 2.859 | 2.8579 | 2.8568 | 2.8557 | 2.8546 | 2.8535 | 2.8524 | 2.8513 | 2.8502 | 2.8491 | 2.848 | 2.8469 | 2.8458 | 2.8447 | 2.8436 | 2.8425 | 2.8414 | 2.8403 | 2.8392 | 2.8381 | 2.837 | 2.8359 | 2.8348 | 2.8337 | 2.8326 | 2.8315 | 2.8304 | 2.8293 | 2.8282 | 2.8271 | 2.826 | 2.8249 | 2.8238 | 2.8227 | 2.8216 | 2.8205 | 2.8194 | 2.8183 | 2.8172 | 2.8161 | 2.815 | 2.8139 | 2.8128 | 2.8117 | 2.8106 | 2.8095 | 2.8084 | 2.8073 | 2.8062 | 2.8051 | 2.804 | 2.8029 | 2.8018 | 2.8007 | 2.7996 | 2.7985 | 2.7974 | 2.7963 | 2.7952 | 2.7941 | 2.793 | 2.7919 | 2.7908 | 2.7897 | 2.7886 | 2.7875 | 2.7864 | 2.7853 | 2.7842 | 2.7831 | 2.782
2.4 | 0 | 0.128 | 0.256 | 0.384 | 0.512 | 0.64 | 0.768 | 0.896 | 1.024 | 1.152 | 1.28 | 1.3888 | 1.4976 | 1.6064 | 1.7152 | 1.824 | 1.9072 | 1.9904 | 2.0736 | 2.1568 | 2.24 | 2.2784 | 2.3168 | 2.3552 | 2.3936 | 2.432 | 2.4704 | 2.5088 | 2.5472 | 2.5856 | 2.624 | 2.6432 | 2.6624 | 2.6816 | 2.7008 | 2.72 | 2.7392 | 2.7584 | 2.7776 | 2.7968 | 2.816 | 2.8352 | 2.8544 | 2.8736 | 2.8928 | 2.912 | 2.9205 | 2.9291 | 2.9376 | 2.9461 | 2.9547 | 2.9632 | 2.9717 | 2.9803 | 2.9888 | 2.9973 | 3.0059 | 3.0144 | 3.0229 | 3.0315 | 3.04 | 3.0421 | 3.0443 | 3.0464 | 3.0485 | 3.0507 | 3.0528 | 3.0549 | 3.0571 | 3.0592 | 3.0613 | 3.0635 | 3.0656 | 3.0677 | 3.0699 | 3.072 | 3.0741 | 3.0763 | 3.0784 | 3.0805 | 3.0827 | 3.0848 | 3.0869 | 3.0891 | 3.0912 | 3.0933 | 3.0955 | 3.0976 | 3.0997 | 3.1019 | 3.104 | 3.1029 | 3.1019 | 3.1008 | 3.0997 | 3.0987 | 3.0976 | 3.0965 | 3.0955 | 3.0944 | 3.0933 | 3.0923 | 3.0912 | 3.0901 | 3.0891 | 3.088 | 3.0869 | 3.0859 | 3.0848 | 3.0837 | 3.0827 | 3.0816 | 3.0805 | 3.0795 | 3.0784 | 3.0773 | 3.0763 | 3.0752 | 3.0741 | 3.0731 | 3.072 | 3.0709 | 3.0699 | 3.0688 | 3.0677 | 3.0667 | 3.0656 | 3.0645 | 3.0635 | 3.0624 | 3.0613 | 3.0603 | 3.0592 | 3.0581 | 3.0571 | 3.056 | 3.0549 | 3.0539 | 3.0528 | 3.0517 | 3.0507 | 3.0496 | 3.0485 | 3.0475 | 3.0464 | 3.0453 | 3.0443 | 3.0432 | 3.0421 | 3.0411 | 3.04 | 3.0389 | 3.0379 | 3.0368 | 3.0357 | 3.0347 | 3.0336 | 3.0325 | 3.0315 | 3.0304 | 3.0293 | 3.0283 | 3.0272 | 3.0261 | 3.0251 | 3.024 | 3.0229 | 3.0219 | 3.0208 | 3.0197 | 3.0187 | 3.0176 | 3.0165 | 3.0155 | 3.0144 | 3.0133 | 3.0123 | 3.0112 | 3.0101 | 3.0091 | 3.008
2.45 | 0 | 0.1365 | 0.273 | 0.4095 | 0.546 | 0.6825 | 0.819 | 0.9555 | 1.092 | 1.2285 | 1.365 | 1.4814 | 1.5978 | 1.7142 | 1.8306 | 1.947 | 2.0366 | 2.1262 | 2.2158 | 2.3054 | 2.395 | 2.4357 | 2.4764 | 2.5171 | 2.5578 | 2.5985 | 2.6392 | 2.6799 | 2.7206 | 2.7613 | 2.802 | 2.8226 | 2.8432 | 2.8638 | 2.8844 | 2.905 | 2.9256 | 2.9462 | 2.9668 | 2.9874 | 3.008 | 3.0286 | 3.0492 | 3.0698 | 3.0904 | 3.111 | 3.1206 | 3.1302 | 3.1398 | 3.1494 | 3.159 | 3.1686 | 3.1782 | 3.1878 | 3.1974 | 3.207 | 3.2166 | 3.2262 | 3.2358 | 3.2454 | 3.255 | 3.2574 | 3.2598 | 3.2622 | 3.2646 | 3.267 | 3.2694 | 3.2718 | 3.2742 | 3.2766 | 3.279 | 3.2814 | 3.2838 | 3.2862 | 3.2886 | 3.291 | 3.2934 | 3.2958 | 3.2982 | 3.3006 | 3.303 | 3.3054 | 3.3078 | 3.3102 | 3.3126 | 3.315 | 3.3174 | 3.3198 | 3.3222 | 3.3246 | 3.327 | 3.326 | 3.3249 | 3.3239 | 3.3229 | 3.3218 | 3.3208 | 3.3198 | 3.3187 | 3.3177 | 3.3167 | 3.3156 | 3.3146 | 3.3136 | 3.3125 | 3.3115 | 3.3105 | 3.3094 | 3.3084 | 3.3074 | 3.3063 | 3.3053 | 3.3043 | 3.3032 | 3.3022 | 3.3012 | 3.3001 | 3.2991 | 3.2981 | 3.297 | 3.296 | 3.295 | 3.2939 | 3.2929 | 3.2919 | 3.2908 | 3.2898 | 3.2888 | 3.2877 | 3.2867 | 3.2857 | 3.2846 | 3.2836 | 3.2826 | 3.2815 | 3.2805 | 3.2795 | 3.2784 | 3.2774 | 3.2764 | 3.2753 | 3.2743 | 3.2733 | 3.2722 | 3.2712 | 3.2702 | 3.2691 | 3.2681 | 3.2671 | 3.266 | 3.265 | 3.264 | 3.2629 | 3.2619 | 3.2609 | 3.2598 | 3.2588 | 3.2578 | 3.2567 | 3.2557 | 3.2547 | 3.2536 | 3.2526 | 3.2516 | 3.2505 | 3.2495 | 3.2485 | 3.2474 | 3.2464 | 3.2454 | 3.2443 | 3.2433 | 3.2423 | 3.2412 | 3.2402 | 3.2392 | 3.2381 | 3.2371 | 3.2361 | 3.235 | 3.234
2.5 | 0 | 0.145 | 0.29 | 0.435 | 0.58 | 0.725 | 0.87 | 1.015 | 1.16 | 1.305 | 1.45 | 1.574 | 1.698 | 1.822 | 1.946 | 2.07 | 2.166 | 2.262 | 2.358 | 2.454 | 2.55 | 2.593 | 2.636 | 2.679 | 2.722 | 2.765 | 2.808 | 2.851 | 2.894 | 2.937 | 2.98 | 3.002 | 3.024 | 3.046 | 3.068 | 3.09 | 3.112 | 3.134 | 3.156 | 3.178 | 3.2 | 3.222 | 3.244 | 3.266 | 3.288 | 3.31 | 3.3207 | 3.3313 | 3.342 | 3.3527 | 3.3633 | 3.374 | 3.3847 | 3.3953 | 3.406 | 3.4167 | 3.4273 | 3.438 | 3.4487 | 3.4593 | 3.47 | 3.4727 | 3.4753 | 3.478 | 3.4807 | 3.4833 | 3.486 | 3.4887 | 3.4913 | 3.494 | 3.4967 | 3.4993 | 3.502 | 3.5047 | 3.5073 | 3.51 | 3.5127 | 3.5153 | 3.518 | 3.5207 | 3.5233 | 3.526 | 3.5287 | 3.5313 | 3.534 | 3.5367 | 3.5393 | 3.542 | 3.5447 | 3.5473 | 3.55 | 3.549 | 3.548 | 3.547 | 3.546 | 3.545 | 3.544 | 3.543 | 3.542 | 3.541 | 3.54 | 3.539 | 3.538 | 3.537 | 3.536 | 3.535 | 3.534 | 3.533 | 3.532 | 3.531 | 3.53 | 3.529 | 3.528 | 3.527 | 3.526 | 3.525 | 3.524 | 3.523 | 3.522 | 3.521 | 3.52 | 3.519 | 3.518 | 3.517 | 3.516 | 3.515 | 3.514 | 3.513 | 3.512 | 3.511 | 3.51 | 3.509 | 3.508 | 3.507 | 3.506 | 3.505 | 3.504 | 3.503 | 3.502 | 3.501 | 3.5 | 3.499 | 3.498 | 3.497 | 3.496 | 3.495 | 3.494 | 3.493 | 3.492 | 3.491 | 3.49 | 3.489 | 3.488 | 3.487 | 3.486 | 3.485 | 3.484 | 3.483 | 3.482 | 3.481 | 3.48 | 3.479 | 3.478 | 3.477 | 3.476 | 3.475 | 3.474 | 3.473 | 3.472 | 3.471 | 3.47 | 3.469 | 3.468 | 3.467 | 3.466 | 3.465 | 3.464 | 3.463 | 3.462 | 3.461 | 3.46
2.55 | 0 | 0.1535 | 0.307 | 0.4605 | 0.614 | 0.7675 | 0.921 | 1.0745 | 1.228 | 1.3815 | 1.535 | 1.6666 | 1.7982 | 1.9298 | 2.0614 | 2.193 | 2.2954 | 2.3978 | 2.5002 | 2.6026 | 2.705 | 2.7503 | 2.7956 | 2.8409 | 2.8862 | 2.9315 | 2.9768 | 3.0221 | 3.0674 | 3.1127 | 3.158 | 3.1814 | 3.2048 | 3.2282 | 3.2516 | 3.275 | 3.2984 | 3.3218 | 3.3452 | 3.3686 | 3.392 | 3.4154 | 3.4388 | 3.4622 | 3.4856 | 3.509 | 3.5207 | 3.5325 | 3.5442 | 3.5559 | 3.5677 | 3.5794 | 3.5911 | 3.6029 | 3.6146 | 3.6263 | 3.6381 | 3.6498 | 3.6615 | 3.6733 | 3.685 | 3.6879 | 3.6909 | 3.6938 | 3.6967 | 3.6997 | 3.7026 | 3.7055 | 3.7085 | 3.7114 | 3.7143 | 3.7173 | 3.7202 | 3.7231 | 3.7261 | 3.729 | 3.7319 | 3.7349 | 3.7378 | 3.7407 | 3.7437 | 3.7466 | 3.7495 | 3.7525 | 3.7554 | 3.7583 | 3.7613 | 3.7642 | 3.7671 | 3.7701 | 3.773 | 3.772 | 3.7711 | 3.7701 | 3.7691 | 3.7682 | 3.7672 | 3.7662 | 3.7653 | 3.7643 | 3.7633 | 3.7624 | 3.7614 | 3.7604 | 3.7595 | 3.7585 | 3.7575 | 3.7566 | 3.7556 | 3.7546 | 3.7537 | 3.7527 | 3.7517 | 3.7508 | 3.7498 | 3.7488 | 3.7479 | 3.7469 | 3.7459 | 3.745 | 3.744 | 3.743 | 3.7421 | 3.7411 | 3.7401 | 3.7392 | 3.7382 | 3.7372 | 3.7363 | 3.7353 | 3.7343 | 3.7334 | 3.7324 | 3.7314 | 3.7305 | 3.7295 | 3.7285 | 3.7276 | 3.7266 | 3.7256 | 3.7247 | 3.7237 | 3.7227 | 3.7218 | 3.7208 | 3.7198 | 3.7189 | 3.7179 | 3.7169 | 3.716 | 3.715 | 3.714 | 3.7131 | 3.7121 | 3.7111 | 3.7102 | 3.7092 | 3.7082 | 3.7073 | 3.7063 | 3.7053 | 3.7044 | 3.7034 | 3.7024 | 3.7015 | 3.7005 | 3.6995 | 3.6986 | 3.6976 | 3.6966 | 3.6957 | 3.6947 | 3.6937 | 3.6928 | 3.6918 | 3.6908 | 3.6899 | 3.6889 | 3.6879 | 3.687 | 3.686
2.6 | 0 | 0.162 | 0.324 | 0.486 | 0.648 | 0.81 | 0.972 | 1.134 | 1.296 | 1.458 | 1.62 | 1.7592 | 1.8984 | 2.0376 | 2.1768 | 2.316 | 2.4248 | 2.5336 | 2.6424 | 2.7512 | 2.86 | 2.9076 | 2.9552 | 3.0028 | 3.0504 | 3.098 | 3.1456 | 3.1932 | 3.2408 | 3.2884 | 3.336 | 3.3608 | 3.3856 | 3.4104 | 3.4352 | 3.46 | 3.4848 | 3.5096 | 3.5344 | 3.5592 | 3.584 | 3.6088 | 3.6336 | 3.6584 | 3.6832 | 3.708 | 3.7208 | 3.7336 | 3.7464 | 3.7592 | 3.772 | 3.7848 | 3.7976 | 3.8104 | 3.8232 | 3.836 | 3.8488 | 3.8616 | 3.8744 | 3.8872 | 3.9 | 3.9032 | 3.9064 | 3.9096 | 3.9128 | 3.916 | 3.9192 | 3.9224 | 3.9256 | 3.9288 | 3.932 | 3.9352 | 3.9384 | 3.9416 | 3.9448 | 3.948 | 3.9512 | 3.9544 | 3.9576 | 3.9608 | 3.964 | 3.9672 | 3.9704 | 3.9736 | 3.9768 | 3.98 | 3.9832 | 3.9864 | 3.9896 | 3.9928 | 3.996 | 3.9951 | 3.9941 | 3.9932 | 3.9923 | 3.9913 | 3.9904 | 3.9895 | 3.9885 | 3.9876 | 3.9867 | 3.9857 | 3.9848 | 3.9839 | 3.9829 | 3.982 | 3.9811 | 3.9801 | 3.9792 | 3.9783 | 3.9773 | 3.9764 | 3.9755 | 3.9745 | 3.9736 | 3.9727 | 3.9717 | 3.9708 | 3.9699 | 3.9689 | 3.968 | 3.9671 | 3.9661 | 3.9652 | 3.9643 | 3.9633 | 3.9624 | 3.9615 | 3.9605 | 3.9596 | 3.9587 | 3.9577 | 3.9568 | 3.9559 | 3.9549 | 3.954 | 3.9531 | 3.9521 | 3.9512 | 3.9503 | 3.9493 | 3.9484 | 3.9475 | 3.9465 | 3.9456 | 3.9447 | 3.9437 | 3.9428 | 3.9419 | 3.9409 | 3.94 | 3.9391 | 3.9381 | 3.9372 | 3.9363 | 3.9353 | 3.9344 | 3.9335 | 3.9325 | 3.9316 | 3.9307 | 3.9297 | 3.9288 | 3.9279 | 3.9269 | 3.926 | 3.9251 | 3.9241 | 3.9232 | 3.9223 | 3.9213 | 3.9204 | 3.9195 | 3.9185 | 3.9176 | 3.9167 | 3.9157 | 3.9148 | 3.9139 | 3.9129 | 3.912
2.65 | 0 | 0.1705 | 0.341 | 0.5115 | 0.682 | 0.8525 | 1.023 | 1.1935 | 1.364 | 1.5345 | 1.705 | 1.8518 | 1.9986 | 2.1454 | 2.2922 | 2.439 | 2.5542 | 2.6694 | 2.7846 | 2.8998 | 3.015 | 3.0649 | 3.1148 | 3.1647 | 3.2146 | 3.2645 | 3.3144 | 3.3643 | 3.4142 | 3.4641 | 3.514 | 3.5402 | 3.5664 | 3.5926 | 3.6188 | 3.645 | 3.6712 | 3.6974 | 3.7236 | 3.7498 | 3.776 | 3.8022 | 3.8284 | 3.8546 | 3.8808 | 3.907 | 3.9209 | 3.9347 | 3.9486 | 3.9625 | 3.9763 | 3.9902 | 4.0041 | 4.0179 | 4.0318 | 4.0457 | 4.0595 | 4.0734 | 4.0873 | 4.1011 | 4.115 | 4.1185 | 4.1219 | 4.1254 | 4.1289 | 4.1323 | 4.1358 | 4.1393 | 4.1427 | 4.1462 | 4.1497 | 4.1531 | 4.1566 | 4.1601 | 4.1635 | 4.167 | 4.1705 | 4.1739 | 4.1774 | 4.1809 | 4.1843 | 4.1878 | 4.1913 | 4.1947 | 4.1982 | 4.2017 | 4.2051 | 4.2086 | 4.2121 | 4.2155 | 4.219 | 4.2181 | 4.2172 | 4.2163 | 4.2154 | 4.2145 | 4.2136 | 4.2127 | 4.2118 | 4.2109 | 4.21 | 4.2091 | 4.2082 | 4.2073 | 4.2064 | 4.2055 | 4.2046 | 4.2037 | 4.2028 | 4.2019 | 4.201 | 4.2001 | 4.1992 | 4.1983 | 4.1974 | 4.1965 | 4.1956 | 4.1947 | 4.1938 | 4.1929 | 4.192 | 4.1911 | 4.1902 | 4.1893 | 4.1884 | 4.1875 | 4.1866 | 4.1857 | 4.1848 | 4.1839 | 4.183 | 4.1821 | 4.1812 | 4.1803 | 4.1794 | 4.1785 | 4.1776 | 4.1767 | 4.1758 | 4.1749 | 4.174 | 4.1731 | 4.1722 | 4.1713 | 4.1704 | 4.1695 | 4.1686 | 4.1677 | 4.1668 | 4.1659 | 4.165 | 4.1641 | 4.1632 | 4.1623 | 4.1614 | 4.1605 | 4.1596 | 4.1587 | 4.1578 | 4.1569 | 4.156 | 4.1551 | 4.1542 | 4.1533 | 4.1524 | 4.1515 | 4.1506 | 4.1497 | 4.1488 | 4.1479 | 4.147 | 4.1461 | 4.1452 | 4.1443 | 4.1434 | 4.1425 | 4.1416 | 4.1407 | 4.1398 | 4.1389 | 4.138
2.7 | 0 | 0.179 | 0.358 | 0.537 | 0.716 | 0.895 | 1.074 | 1.253 | 1.432 | 1.611 | 1.79 | 1.9444 | 2.0988 | 2.2532 | 2.4076 | 2.562 | 2.6836 | 2.8052 | 2.9268 | 3.0484 | 3.17 | 3.2222 | 3.2744 | 3.3266 | 3.3788 | 3.431 | 3.4832 | 3.5354 | 3.5876 | 3.6398 | 3.692 | 3.7196 | 3.7472 | 3.7748 | 3.8024 | 3.83 | 3.8576 | 3.8852 | 3.9128 | 3.9404 | 3.968 | 3.9956 | 4.0232 | 4.0508 | 4.0784 | 4.106 | 4.1209 | 4.1359 | 4.1508 | 4.1657 | 4.1807 | 4.1956 | 4.2105 | 4.2255 | 4.2404 | 4.2553 | 4.2703 | 4.2852 | 4.3001 | 4.3151 | 4.33 | 4.3337 | 4.3375 | 4.3412 | 4.3449 | 4.3487 | 4.3524 | 4.3561 | 4.3599 | 4.3636 | 4.3673 | 4.3711 | 4.3748 | 4.3785 | 4.3823 | 4.386 | 4.3897 | 4.3935 | 4.3972 | 4.4009 | 4.4047 | 4.4084 | 4.4121 | 4.4159 | 4.4196 | 4.4233 | 4.4271 | 4.4308 | 4.4345 | 4.4383 | 4.442 | 4.4411 | 4.4403 | 4.4394 | 4.4385 | 4.4377 | 4.4368 | 4.4359 | 4.4351 | 4.4342 | 4.4333 | 4.4325 | 4.4316 | 4.4307 | 4.4299 | 4.429 | 4.4281 | 4.4273 | 4.4264 | 4.4255 | 4.4247 | 4.4238 | 4.4229 | 4.4221 | 4.4212 | 4.4203 | 4.4195 | 4.4186 | 4.4177 | 4.4169 | 4.416 | 4.4151 | 4.4143 | 4.4134 | 4.4125 | 4.4117 | 4.4108 | 4.4099 | 4.4091 | 4.4082 | 4.4073 | 4.4065 | 4.4056 | 4.4047 | 4.4039 | 4.403 | 4.4021 | 4.4013 | 4.4004 | 4.3995 | 4.3987 | 4.3978 | 4.3969 | 4.3961 | 4.3952 | 4.3943 | 4.3935 | 4.3926 | 4.3917 | 4.3909 | 4.39 | 4.3891 | 4.3883 | 4.3874 | 4.3865 | 4.3857 | 4.3848 | 4.3839 | 4.3831 | 4.3822 | 4.3813 | 4.3805 | 4.3796 | 4.3787 | 4.3779 | 4.377 | 4.3761 | 4.3753 | 4.3744 | 4.3735 | 4.3727 | 4.3718 | 4.3709 | 4.3701 | 4.3692 | 4.3683 | 4.3675 | 4.3666 | 4.3657 | 4.3649 | 4.364
2.75 | 0 | 0.1875 | 0.375 | 0.5625 | 0.75 | 0.9375 | 1.125 | 1.3125 | 1.5 | 1.6875 | 1.875 | 2.037 | 2.199 | 2.361 | 2.523 | 2.685 | 2.813 | 2.941 | 3.069 | 3.197 | 3.325 | 3.3795 | 3.434 | 3.4885 | 3.543 | 3.5975 | 3.652 | 3.7065 | 3.761 | 3.8155 | 3.87 | 3.899 | 3.928 | 3.957 | 3.986 | 4.015 | 4.044 | 4.073 | 4.102 | 4.131 | 4.16 | 4.189 | 4.218 | 4.247 | 4.276 | 4.305 | 4.321 | 4.337 | 4.353 | 4.369 | 4.385 | 4.401 | 4.417 | 4.433 | 4.449 | 4.465 | 4.481 | 4.497 | 4.513 | 4.529 | 4.545 | 4.549 | 4.553 | 4.557 | 4.561 | 4.565 | 4.569 | 4.573 | 4.577 | 4.581 | 4.585 | 4.589 | 4.593 | 4.597 | 4.601 | 4.605 | 4.609 | 4.613 | 4.617 | 4.621 | 4.625 | 4.629 | 4.633 | 4.637 | 4.641 | 4.645 | 4.649 | 4.653 | 4.657 | 4.661 | 4.665 | 4.6642 | 4.6633 | 4.6625 | 4.6617 | 4.6608 | 4.66 | 4.6592 | 4.6583 | 4.6575 | 4.6567 | 4.6558 | 4.655 | 4.6542 | 4.6533 | 4.6525 | 4.6517 | 4.6508 | 4.65 | 4.6492 | 4.6483 | 4.6475 | 4.6467 | 4.6458 | 4.645 | 4.6442 | 4.6433 | 4.6425 | 4.6417 | 4.6408 | 4.64 | 4.6392 | 4.6383 | 4.6375 | 4.6367 | 4.6358 | 4.635 | 4.6342 | 4.6333 | 4.6325 | 4.6317 | 4.6308 | 4.63 | 4.6292 | 4.6283 | 4.6275 | 4.6267 | 4.6258 | 4.625 | 4.6242 | 4.6233 | 4.6225 | 4.6217 | 4.6208 | 4.62 | 4.6192 | 4.6183 | 4.6175 | 4.6167 | 4.6158 | 4.615 | 4.6142 | 4.6133 | 4.6125 | 4.6117 | 4.6108 | 4.61 | 4.6092 | 4.6083 | 4.6075 | 4.6067 | 4.6058 | 4.605 | 4.6042 | 4.6033 | 4.6025 | 4.6017 | 4.6008 | 4.6 | 4.5992 | 4.5983 | 4.5975 | 4.5967 | 4.5958 | 4.595 | 4.5942 | 4.5933 | 4.5925 | 4.5917 | 4.5908 | 4.59
2.8 | 0 | 0.196 | 0.392 | 0.588 | 0.784 | 0.98 | 1.176 | 1.372 | 1.568 | 1.764 | 1.96 | 2.1296 | 2.2992 | 2.4688 | 2.6384 | 2.808 | 2.9424 | 3.0768 | 3.2112 | 3.3456 | 3.48 | 3.5368 | 3.5936 | 3.6504 | 3.7072 | 3.764 | 3.8208 | 3.8776 | 3.9344 | 3.9912 | 4.048 | 4.0784 | 4.1088 | 4.1392 | 4.1696 | 4.2 | 4.2304 | 4.2608 | 4.2912 | 4.3216 | 4.352 | 4.3824 | 4.4128 | 4.4432 | 4.4736 | 4.504 | 4.5211 | 4.5381 | 4.5552 | 4.5723 | 4.5893 | 4.6064 | 4.6235 | 4.6405 | 4.6576 | 4.6747 | 4.6917 | 4.7088 | 4.7259 | 4.7429 | 4.76 | 4.7643 | 4.7685 | 4.7728 | 4.7771 | 4.7813 | 4.7856 | 4.7899 | 4.7941 | 4.7984 | 4.8027 | 4.8069 | 4.8112 | 4.8155 | 4.8197 | 4.824 | 4.8283 | 4.8325 | 4.8368 | 4.8411 | 4.8453 | 4.8496 | 4.8539 | 4.8581 | 4.8624 | 4.8667 | 4.8709 | 4.8752 | 4.8795 | 4.8837 | 4.888 | 4.8872 | 4.8864 | 4.8856 | 4.8848 | 4.884 | 4.8832 | 4.8824 | 4.8816 | 4.8808 | 4.88 | 4.8792 | 4.8784 | 4.8776 | 4.8768 | 4.876 | 4.8752 | 4.8744 | 4.8736 | 4.8728 | 4.872 | 4.8712 | 4.8704 | 4.8696 | 4.8688 | 4.868 | 4.8672 | 4.8664 | 4.8656 | 4.8648 | 4.864 | 4.8632 | 4.8624 | 4.8616 | 4.8608 | 4.86 | 4.8592 | 4.8584 | 4.8576 | 4.8568 | 4.856 | 4.8552 | 4.8544 | 4.8536 | 4.8528 | 4.852 | 4.8512 | 4.8504 | 4.8496 | 4.8488 | 4.848 | 4.8472 | 4.8464 | 4.8456 | 4.8448 | 4.844 | 4.8432 | 4.8424 | 4.8416 | 4.8408 | 4.84 | 4.8392 | 4.8384 | 4.8376 | 4.8368 | 4.836 | 4.8352 | 4.8344 | 4.8336 | 4.8328 | 4.832 | 4.8312 | 4.8304 | 4.8296 | 4.8288 | 4.828 | 4.8272 | 4.8264 | 4.8256 | 4.8248 | 4.824 | 4.8232 | 4.8224 | 4.8216 | 4.8208 | 4.82 | 4.8192 | 4.8184 | 4.8176 | 4.8168 | 4.816
2.85 | 0 | 0.2045 | 0.409 | 0.6135 | 0.818 | 1.0225 | 1.227 | 1.4315 | 1.636 | 1.8405 | 2.045 | 2.2222 | 2.3994 | 2.5766 | 2.7538 | 2.931 | 3.0718 | 3.2126 | 3.3534 | 3.4942 | 3.635 | 3.6941 | 3.7532 | 3.8123 | 3.8714 | 3.9305 | 3.9896 | 4.0487 | 4.1078 | 4.1669 | 4.226 | 4.2578 | 4.2896 | 4.3214 | 4.3532 | 4.385 | 4.4168 | 4.4486 | 4.4804 | 4.5122 | 4.544 | 4.5758 | 4.6076 | 4.6394 | 4.6712 | 4.703 | 4.7211 | 4.7393 | 4.7574 | 4.7755 | 4.7937 | 4.8118 | 4.8299 | 4.8481 | 4.8662 | 4.8843 | 4.9025 | 4.9206 | 4.9387 | 4.9569 | 4.975 | 4.9795 | 4.9841 | 4.9886 | 4.9931 | 4.9977 | 5.0022 | 5.0067 | 5.0113 | 5.0158 | 5.0203 | 5.0249 | 5.0294 | 5.0339 | 5.0385 | 5.043 | 5.0475 | 5.0521 | 5.0566 | 5.0611 | 5.0657 | 5.0702 | 5.0747 | 5.0793 | 5.0838 | 5.0883 | 5.0929 | 5.0974 | 5.1019 | 5.1065 | 5.111 | 5.1102 | 5.1095 | 5.1087 | 5.1079 | 5.1072 | 5.1064 | 5.1056 | 5.1049 | 5.1041 | 5.1033 | 5.1026 | 5.1018 | 5.101 | 5.1003 | 5.0995 | 5.0987 | 5.098 | 5.0972 | 5.0964 | 5.0957 | 5.0949 | 5.0941 | 5.0934 | 5.0926 | 5.0918 | 5.0911 | 5.0903 | 5.0895 | 5.0888 | 5.088 | 5.0872 | 5.0865 | 5.0857 | 5.0849 | 5.0842 | 5.0834 | 5.0826 | 5.0819 | 5.0811 | 5.0803 | 5.0796 | 5.0788 | 5.078 | 5.0773 | 5.0765 | 5.0757 | 5.075 | 5.0742 | 5.0734 | 5.0727 | 5.0719 | 5.0711 | 5.0704 | 5.0696 | 5.0688 | 5.0681 | 5.0673 | 5.0665 | 5.0658 | 5.065 | 5.0642 | 5.0635 | 5.0627 | 5.0619 | 5.0612 | 5.0604 | 5.0596 | 5.0589 | 5.0581 | 5.0573 | 5.0566 | 5.0558 | 5.055 | 5.0543 | 5.0535 | 5.0527 | 5.052 | 5.0512 | 5.0504 | 5.0497 | 5.0489 | 5.0481 | 5.0474 | 5.0466 | 5.0458 | 5.0451 | 5.0443 | 5.0435 | 5.0428 | 5.042
2.9 | 0 | 0.213 | 0.426 | 0.639 | 0.852 | 1.065 | 1.278 | 1.491 | 1.704 | 1.917 | 2.13 | 2.3148 | 2.4996 | 2.6844 | 2.8692 | 3.054 | 3.2012 | 3.3484 | 3.4956 | 3.6428 | 3.79 | 3.8514 | 3.9128 | 3.9742 | 4.0356 | 4.097 | 4.1584 | 4.2198 | 4.2812 | 4.3426 | 4.404 | 4.4372 | 4.4704 | 4.5036 | 4.5368 | 4.57 | 4.6032 | 4.6364 | 4.6696 | 4.7028 | 4.736 | 4.7692 | 4.8024 | 4.8356 | 4.8688 | 4.902 | 4.9212 | 4.9404 | 4.9596 | 4.9788 | 4.998 | 5.0172 | 5.0364 | 5.0556 | 5.0748 | 5.094 | 5.1132 | 5.1324 | 5.1516 | 5.1708 | 5.19 | 5.1948 | 5.1996 | 5.2044 | 5.2092 | 5.214 | 5.2188 | 5.2236 | 5.2284 | 5.2332 | 5.238 | 5.2428 | 5.2476 | 5.2524 | 5.2572 | 5.262 | 5.2668 | 5.2716 | 5.2764 | 5.2812 | 5.286 | 5.2908 | 5.2956 | 5.3004 | 5.3052 | 5.31 | 5.3148 | 5.3196 | 5.3244 | 5.3292 | 5.334 | 5.3333 | 5.3325 | 5.3318 | 5.3311 | 5.3303 | 5.3296 | 5.3289 | 5.3281 | 5.3274 | 5.3267 | 5.3259 | 5.3252 | 5.3245 | 5.3237 | 5.323 | 5.3223 | 5.3215 | 5.3208 | 5.3201 | 5.3193 | 5.3186 | 5.3179 | 5.3171 | 5.3164 | 5.3157 | 5.3149 | 5.3142 | 5.3135 | 5.3127 | 5.312 | 5.3113 | 5.3105 | 5.3098 | 5.3091 | 5.3083 | 5.3076 | 5.3069 | 5.3061 | 5.3054 | 5.3047 | 5.3039 | 5.3032 | 5.3025 | 5.3017 | 5.301 | 5.3003 | 5.2995 | 5.2988 | 5.2981 | 5.2973 | 5.2966 | 5.2959 | 5.2951 | 5.2944 | 5.2937 | 5.2929 | 5.2922 | 5.2915 | 5.2907 | 5.29 | 5.2893 | 5.2885 | 5.2878 | 5.2871 | 5.2863 | 5.2856 | 5.2849 | 5.2841 | 5.2834 | 5.2827 | 5.2819 | 5.2812 | 5.2805 | 5.2797 | 5.279 | 5.2783 | 5.2775 | 5.2768 | 5.2761 | 5.2753 | 5.2746 | 5.2739 | 5.2731 | 5.2724 | 5.2717 | 5.2709 | 5.2702 | 5.2695 | 5.2687 | 5.268
2.95 | 0 | 0.2215 | 0.443 | 0.6645 | 0.886 | 1.1075 | 1.329 | 1.5505 | 1.772 | 1.9935 | 2.215 | 2.4074 | 2.5998 | 2.7922 | 2.9846 | 3.177 | 3.3306 | 3.4842 | 3.6378 | 3.7914 | 3.945 | 4.0087 | 4.0724 | 4.1361 | 4.1998 | 4.2635 | 4.3272 | 4.3909 | 4.4546 | 4.5183 | 4.582 | 4.6166 | 4.6512 | 4.6858 | 4.7204 | 4.755 | 4.7896 | 4.8242 | 4.8588 | 4.8934 | 4.928 | 4.9626 | 4.9972 | 5.0318 | 5.0664 | 5.101 | 5.1213 | 5.1415 | 5.1618 | 5.1821 | 5.2023 | 5.2226 | 5.2429 | 5.2631 | 5.2834 | 5.3037 | 5.3239 | 5.3442 | 5.3645 | 5.3847 | 5.405 | 5.4101 | 5.4151 | 5.4202 | 5.4253 | 5.4303 | 5.4354 | 5.4405 | 5.4455 | 5.4506 | 5.4557 | 5.4607 | 5.4658 | 5.4709 | 5.4759 | 5.481 | 5.4861 | 5.4911 | 5.4962 | 5.5013 | 5.5063 | 5.5114 | 5.5165 | 5.5215 | 5.5266 | 5.5317 | 5.5367 | 5.5418 | 5.5469 | 5.5519 | 5.557 | 5.5563 | 5.5556 | 5.5549 | 5.5542 | 5.5535 | 5.5528 | 5.5521 | 5.5514 | 5.5507 | 5.55 | 5.5493 | 5.5486 | 5.5479 | 5.5472 | 5.5465 | 5.5458 | 5.5451 | 5.5444 | 5.5437 | 5.543 | 5.5423 | 5.5416 | 5.5409 | 5.5402 | 5.5395 | 5.5388 | 5.5381 | 5.5374 | 5.5367 | 5.536 | 5.5353 | 5.5346 | 5.5339 | 5.5332 | 5.5325 | 5.5318 | 5.5311 | 5.5304 | 5.5297 | 5.529 | 5.5283 | 5.5276 | 5.5269 | 5.5262 | 5.5255 | 5.5248 | 5.5241 | 5.5234 | 5.5227 | 5.522 | 5.5213 | 5.5206 | 5.5199 | 5.5192 | 5.5185 | 5.5178 | 5.5171 | 5.5164 | 5.5157 | 5.515 | 5.5143 | 5.5136 | 5.5129 | 5.5122 | 5.5115 | 5.5108 | 5.5101 | 5.5094 | 5.5087 | 5.508 | 5.5073 | 5.5066 | 5.5059 | 5.5052 | 5.5045 | 5.5038 | 5.5031 | 5.5024 | 5.5017 | 5.501 | 5.5003 | 5.4996 | 5.4989 | 5.4982 | 5.4975 | 5.4968 | 5.4961 | 5.4954 | 5.4947 | 5.494
3 | 0 | 0.23 | 0.46 | 0.69 | 0.92 | 1.15 | 1.38 | 1.61 | 1.84 | 2.07 | 2.3 | 2.5 | 2.7 | 2.9 | 3.1 | 3.3 | 3.46 | 3.62 | 3.78 | 3.94 | 4.1 | 4.166 | 4.232 | 4.298 | 4.364 | 4.43 | 4.496 | 4.562 | 4.628 | 4.694 | 4.76 | 4.796 | 4.832 | 4.868 | 4.904 | 4.94 | 4.976 | 5.012 | 5.048 | 5.084 | 5.12 | 5.156 | 5.192 | 5.228 | 5.264 | 5.3 | 5.3213 | 5.3427 | 5.364 | 5.3853 | 5.4067 | 5.428 | 5.4493 | 5.4707 | 5.492 | 5.5133 | 5.5347 | 5.556 | 5.5773 | 5.5987 | 5.62 | 5.6253 | 5.6307 | 5.636 | 5.6413 | 5.6467 | 5.652 | 5.6573 | 5.6627 | 5.668 | 5.6733 | 5.6787 | 5.684 | 5.6893 | 5.6947 | 5.7 | 5.7053 | 5.7107 | 5.716 | 5.7213 | 5.7267 | 5.732 | 5.7373 | 5.7427 | 5.748 | 5.7533 | 5.7587 | 5.764 | 5.7693 | 5.7747 | 5.78 | 5.7793 | 5.7787 | 5.778 | 5.7773 | 5.7767 | 5.776 | 5.7753 | 5.7747 | 5.774 | 5.7733 | 5.7727 | 5.772 | 5.7713 | 5.7707 | 5.77 | 5.7693 | 5.7687 | 5.768 | 5.7673 | 5.7667 | 5.766 | 5.7653 | 5.7647 | 5.764 | 5.7633 | 5.7627 | 5.762 | 5.7613 | 5.7607 | 5.76 | 5.7593 | 5.7587 | 5.758 | 5.7573 | 5.7567 | 5.756 | 5.7553 | 5.7547 | 5.754 | 5.7533 | 5.7527 | 5.752 | 5.7513 | 5.7507 | 5.75 | 5.7493 | 5.7487 | 5.748 | 5.7473 | 5.7467 | 5.746 | 5.7453 | 5.7447 | 5.744 | 5.7433 | 5.7427 | 5.742 | 5.7413 | 5.7407 | 5.74 | 5.7393 | 5.7387 | 5.738 | 5.7373 | 5.7367 | 5.736 | 5.7353 | 5.7347 | 5.734 | 5.7333 | 5.7327 | 5.732 | 5.7313 | 5.7307 | 5.73 | 5.7293 | 5.7287 | 5.728 | 5.7273 | 5.7267 | 5.726 | 5.7253 | 5.7247 | 5.724 | 5.7233 | 5.7227 | 5.722 | 5.7213 | 5.7207 | 5.72
3.05 | 0 | 0.2385 | 0.477 | 0.7155 | 0.954 | 1.1925 | 1.431 | 1.6695 | 1.908 | 2.1465 | 2.385 | 2.5926 | 2.8002 | 3.0078 | 3.2154 | 3.423 | 3.5894 | 3.7558 | 3.9222 | 4.0886 | 4.255 | 4.3233 | 4.3916 | 4.4599 | 4.5282 | 4.5965 | 4.6648 | 4.7331 | 4.8014 | 4.8697 | 4.938 | 4.9754 | 5.0128 | 5.0502 | 5.0876 | 5.125 | 5.1624 | 5.1998 | 5.2372 | 5.2746 | 5.312 | 5.3494 | 5.3868 | 5.4242 | 5.4616 | 5.499 | 5.5214 | 5.5438 | 5.5662 | 5.5886 | 5.611 | 5.6334 | 5.6558 | 5.6782 | 5.7006 | 5.723 | 5.7454 | 5.7678 | 5.7902 | 5.8126 | 5.835 | 5.8406 | 5.8462 | 5.8518 | 5.8574 | 5.863 | 5.8686 | 5.8742 | 5.8798 | 5.8854 | 5.891 | 5.8966 | 5.9022 | 5.9078 | 5.9134 | 5.919 | 5.9246 | 5.9302 | 5.9358 | 5.9414 | 5.947 | 5.9526 | 5.9582 | 5.9638 | 5.9694 | 5.975 | 5.9806 | 5.9862 | 5.9918 | 5.9974 | 6.003 | 6.0024 | 6.0017 | 6.0011 | 6.0005 | 5.9998 | 5.9992 | 5.9986 | 5.9979 | 5.9973 | 5.9967 | 5.996 | 5.9954 | 5.9948 | 5.9941 | 5.9935 | 5.9929 | 5.9922 | 5.9916 | 5.991 | 5.9903 | 5.9897 | 5.9891 | 5.9884 | 5.9878 | 5.9872 | 5.9865 | 5.9859 | 5.9853 | 5.9846 | 5.984 | 5.9834 | 5.9827 | 5.9821 | 5.9815 | 5.9808 | 5.9802 | 5.9796 | 5.9789 | 5.9783 | 5.9777 | 5.977 | 5.9764 | 5.9758 | 5.9751 | 5.9745 | 5.9739 | 5.9732 | 5.9726 | 5.972 | 5.9713 | 5.9707 | 5.9701 | 5.9694 | 5.9688 | 5.9682 | 5.9675 | 5.9669 | 5.9663 | 5.9656 | 5.965 | 5.9644 | 5.9637 | 5.9631 | 5.9625 | 5.9618 | 5.9612 | 5.9606 | 5.9599 | 5.9593 | 5.9587 | 5.958 | 5.9574 | 5.9568 | 5.9561 | 5.9555 | 5.9549 | 5.9542 | 5.9536 | 5.953 | 5.9523 | 5.9517 | 5.9511 | 5.9504 | 5.9498 | 5.9492 | 5.9485 | 5.9479 | 5.9473 | 5.9466 | 5.946
3.1 | 0 | 0.247 | 0.494 | 0.741 | 0.988 | 1.235 | 1.482 | 1.729 | 1.976 | 2.223 | 2.47 | 2.6852 | 2.9004 | 3.1156 | 3.3308 | 3.546 | 3.7188 | 3.8916 | 4.0644 | 4.2372 | 4.41 | 4.4806 | 4.5512 | 4.6218 | 4.6924 | 4.763 | 4.8336 | 4.9042 | 4.9748 | 5.0454 | 5.116 | 5.1548 | 5.1936 | 5.2324 | 5.2712 | 5.31 | 5.3488 | 5.3876 | 5.4264 | 5.4652 | 5.504 | 5.5428 | 5.5816 | 5.6204 | 5.6592 | 5.698 | 5.7215 | 5.7449 | 5.7684 | 5.7919 | 5.8153 | 5.8388 | 5.8623 | 5.8857 | 5.9092 | 5.9327 | 5.9561 | 5.9796 | 6.0031 | 6.0265 | 6.05 | 6.0559 | 6.0617 | 6.0676 | 6.0735 | 6.0793 | 6.0852 | 6.0911 | 6.0969 | 6.1028 | 6.1087 | 6.1145 | 6.1204 | 6.1263 | 6.1321 | 6.138 | 6.1439 | 6.1497 | 6.1556 | 6.1615 | 6.1673 | 6.1732 | 6.1791 | 6.1849 | 6.1908 | 6.1967 | 6.2025 | 6.2084 | 6.2143 | 6.2201 | 6.226 | 6.2254 | 6.2248 | 6.2242 | 6.2236 | 6.223 | 6.2224 | 6.2218 | 6.2212 | 6.2206 | 6.22 | 6.2194 | 6.2188 | 6.2182 | 6.2176 | 6.217 | 6.2164 | 6.2158 | 6.2152 | 6.2146 | 6.214 | 6.2134 | 6.2128 | 6.2122 | 6.2116 | 6.211 | 6.2104 | 6.2098 | 6.2092 | 6.2086 | 6.208 | 6.2074 | 6.2068 | 6.2062 | 6.2056 | 6.205 | 6.2044 | 6.2038 | 6.2032 | 6.2026 | 6.202 | 6.2014 | 6.2008 | 6.2002 | 6.1996 | 6.199 | 6.1984 | 6.1978 | 6.1972 | 6.1966 | 6.196 | 6.1954 | 6.1948 | 6.1942 | 6.1936 | 6.193 | 6.1924 | 6.1918 | 6.1912 | 6.1906 | 6.19 | 6.1894 | 6.1888 | 6.1882 | 6.1876 | 6.187 | 6.1864 | 6.1858 | 6.1852 | 6.1846 | 6.184 | 6.1834 | 6.1828 | 6.1822 | 6.1816 | 6.181 | 6.1804 | 6.1798 | 6.1792 | 6.1786 | 6.178 | 6.1774 | 6.1768 | 6.1762 | 6.1756 | 6.175 | 6.1744 | 6.1738 | 6.1732 | 6.1726 | 6.172
3.15 | 0 | 0.2555 | 0.511 | 0.7665 | 1.022 | 1.2775 | 1.533 | 1.7885 | 2.044 | 2.2995 | 2.555 | 2.7778 | 3.0006 | 3.2234 | 3.4462 | 3.669 | 3.8482 | 4.0274 | 4.2066 | 4.3858 | 4.565 | 4.6379 | 4.7108 | 4.7837 | 4.8566 | 4.9295 | 5.0024 | 5.0753 | 5.1482 | 5.2211 | 5.294 | 5.3342 | 5.3744 | 5.4146 | 5.4548 | 5.495 | 5.5352 | 5.5754 | 5.6156 | 5.6558 | 5.696 | 5.7362 | 5.7764 | 5.8166 | 5.8568 | 5.897 | 5.9215 | 5.9461 | 5.9706 | 5.9951 | 6.0197 | 6.0442 | 6.0687 | 6.0933 | 6.1178 | 6.1423 | 6.1669 | 6.1914 | 6.2159 | 6.2405 | 6.265 | 6.2711 | 6.2773 | 6.2834 | 6.2895 | 6.2957 | 6.3018 | 6.3079 | 6.3141 | 6.3202 | 6.3263 | 6.3325 | 6.3386 | 6.3447 | 6.3509 | 6.357 | 6.3631 | 6.3693 | 6.3754 | 6.3815 | 6.3877 | 6.3938 | 6.3999 | 6.4061 | 6.4122 | 6.4183 | 6.4245 | 6.4306 | 6.4367 | 6.4429 | 6.449 | 6.4484 | 6.4479 | 6.4473 | 6.4467 | 6.4462 | 6.4456 | 6.445 | 6.4445 | 6.4439 | 6.4433 | 6.4428 | 6.4422 | 6.4416 | 6.4411 | 6.4405 | 6.4399 | 6.4394 | 6.4388 | 6.4382 | 6.4377 | 6.4371 | 6.4365 | 6.436 | 6.4354 | 6.4348 | 6.4343 | 6.4337 | 6.4331 | 6.4326 | 6.432 | 6.4314 | 6.4309 | 6.4303 | 6.4297 | 6.4292 | 6.4286 | 6.428 | 6.4275 | 6.4269 | 6.4263 | 6.4258 | 6.4252 | 6.4246 | 6.4241 | 6.4235 | 6.4229 | 6.4224 | 6.4218 | 6.4212 | 6.4207 | 6.4201 | 6.4195 | 6.419 | 6.4184 | 6.4178 | 6.4173 | 6.4167 | 6.4161 | 6.4156 | 6.415 | 6.4144 | 6.4139 | 6.4133 | 6.4127 | 6.4122 | 6.4116 | 6.411 | 6.4105 | 6.4099 | 6.4093 | 6.4088 | 6.4082 | 6.4076 | 6.4071 | 6.4065 | 6.4059 | 6.4054 | 6.4048 | 6.4042 | 6.4037 | 6.4031 | 6.4025 | 6.402 | 6.4014 | 6.4008 | 6.4003 | 6.3997 | 6.3991 | 6.3986 | 6.398
3.2 | 0 | 0.264 | 0.528 | 0.792 | 1.056 | 1.32 | 1.584 | 1.848 | 2.112 | 2.376 | 2.64 | 2.8704 | 3.1008 | 3.3312 | 3.5616 | 3.792 | 3.9776 | 4.1632 | 4.3488 | 4.5344 | 4.72 | 4.7952 | 4.8704 | 4.9456 | 5.0208 | 5.096 | 5.1712 | 5.2464 | 5.3216 | 5.3968 | 5.472 | 5.5136 | 5.5552 | 5.5968 | 5.6384 | 5.68 | 5.7216 | 5.7632 | 5.8048 | 5.8464 | 5.888 | 5.9296 | 5.9712 | 6.0128 | 6.0544 | 6.096 | 6.1216 | 6.1472 | 6.1728 | 6.1984 | 6.224 | 6.2496 | 6.2752 | 6.3008 | 6.3264 | 6.352 | 6.3776 | 6.4032 | 6.4288 | 6.4544 | 6.48 | 6.4864 | 6.4928 | 6.4992 | 6.5056 | 6.512 | 6.5184 | 6.5248 | 6.5312 | 6.5376 | 6.544 | 6.5504 | 6.5568 | 6.5632 | 6.5696 | 6.576 | 6.5824 | 6.5888 | 6.5952 | 6.6016 | 6.608 | 6.6144 | 6.6208 | 6.6272 | 6.6336 | 6.64 | 6.6464 | 6.6528 | 6.6592 | 6.6656 | 6.672 | 6.6715 | 6.6709 | 6.6704 | 6.6699 | 6.6693 | 6.6688 | 6.6683 | 6.6677 | 6.6672 | 6.6667 | 6.6661 | 6.6656 | 6.6651 | 6.6645 | 6.664 | 6.6635 | 6.6629 | 6.6624 | 6.6619 | 6.6613 | 6.6608 | 6.6603 | 6.6597 | 6.6592 | 6.6587 | 6.6581 | 6.6576 | 6.6571 | 6.6565 | 6.656 | 6.6555 | 6.6549 | 6.6544 | 6.6539 | 6.6533 | 6.6528 | 6.6523 | 6.6517 | 6.6512 | 6.6507 | 6.6501 | 6.6496 | 6.6491 | 6.6485 | 6.648 | 6.6475 | 6.6469 | 6.6464 | 6.6459 | 6.6453 | 6.6448 | 6.6443 | 6.6437 | 6.6432 | 6.6427 | 6.6421 | 6.6416 | 6.6411 | 6.6405 | 6.64 | 6.6395 | 6.6389 | 6.6384 | 6.6379 | 6.6373 | 6.6368 | 6.6363 | 6.6357 | 6.6352 | 6.6347 | 6.6341 | 6.6336 | 6.6331 | 6.6325 | 6.632 | 6.6315 | 6.6309 | 6.6304 | 6.6299 | 6.6293 | 6.6288 | 6.6283 | 6.6277 | 6.6272 | 6.6267 | 6.6261 | 6.6256 | 6.6251 | 6.6245 | 6.624
3.25 | 0 | 0.2725 | 0.545 | 0.8175 | 1.09 | 1.3625 | 1.635 | 1.9075 | 2.18 | 2.4525 | 2.725 | 2.963 | 3.201 | 3.439 | 3.677 | 3.915 | 4.107 | 4.299 | 4.491 | 4.683 | 4.875 | 4.9525 | 5.03 | 5.1075 | 5.185 | 5.2625 | 5.34 | 5.4175 | 5.495 | 5.5725 | 5.65 | 5.693 | 5.736 | 5.779 | 5.822 | 5.865 | 5.908 | 5.951 | 5.994 | 6.037 | 6.08 | 6.123 | 6.166 | 6.209 | 6.252 | 6.295 | 6.3217 | 6.3483 | 6.375 | 6.4017 | 6.4283 | 6.455 | 6.4817 | 6.5083 | 6.535 | 6.5617 | 6.5883 | 6.615 | 6.6417 | 6.6683 | 6.695 | 6.7017 | 6.7083 | 6.715 | 6.7217 | 6.7283 | 6.735 | 6.7417 | 6.7483 | 6.755 | 6.7617 | 6.7683 | 6.775 | 6.7817 | 6.7883 | 6.795 | 6.8017 | 6.8083 | 6.815 | 6.8217 | 6.8283 | 6.835 | 6.8417 | 6.8483 | 6.855 | 6.8617 | 6.8683 | 6.875 | 6.8817 | 6.8883 | 6.895 | 6.8945 | 6.894 | 6.8935 | 6.893 | 6.8925 | 6.892 | 6.8915 | 6.891 | 6.8905 | 6.89 | 6.8895 | 6.889 | 6.8885 | 6.888 | 6.8875 | 6.887 | 6.8865 | 6.886 | 6.8855 | 6.885 | 6.8845 | 6.884 | 6.8835 | 6.883 | 6.8825 | 6.882 | 6.8815 | 6.881 | 6.8805 | 6.88 | 6.8795 | 6.879 | 6.8785 | 6.878 | 6.8775 | 6.877 | 6.8765 | 6.876 | 6.8755 | 6.875 | 6.8745 | 6.874 | 6.8735 | 6.873 | 6.8725 | 6.872 | 6.8715 | 6.871 | 6.8705 | 6.87 | 6.8695 | 6.869 | 6.8685 | 6.868 | 6.8675 | 6.867 | 6.8665 | 6.866 | 6.8655 | 6.865 | 6.8645 | 6.864 | 6.8635 | 6.863 | 6.8625 | 6.862 | 6.8615 | 6.861 | 6.8605 | 6.86 | 6.8595 | 6.859 | 6.8585 | 6.858 | 6.8575 | 6.857 | 6.8565 | 6.856 | 6.8555 | 6.855 | 6.8545 | 6.854 | 6.8535 | 6.853 | 6.8525 | 6.852 | 6.8515 | 6.851 | 6.8505 | 6.85
3.3 | 0 | 0.281 | 0.562 | 0.843 | 1.124 | 1.405 | 1.686 | 1.967 | 2.248 | 2.529 | 2.81 | 3.0556 | 3.3012 | 3.5468 | 3.7924 | 4.038 | 4.2364 | 4.4348 | 4.6332 | 4.8316 | 5.03 | 5.1098 | 5.1896 | 5.2694 | 5.3492 | 5.429 | 5.5088 | 5.5886 | 5.6684 | 5.7482 | 5.828 | 5.8724 | 5.9168 | 5.9612 | 6.0056 | 6.05 | 6.0944 | 6.1388 | 6.1832 | 6.2276 | 6.272 | 6.3164 | 6.3608 | 6.4052 | 6.4496 | 6.494 | 6.5217 | 6.5495 | 6.5772 | 6.6049 | 6.6327 | 6.6604 | 6.6881 | 6.7159 | 6.7436 | 6.7713 | 6.7991 | 6.8268 | 6.8545 | 6.8823 | 6.91 | 6.9169 | 6.9239 | 6.9308 | 6.9377 | 6.9447 | 6.9516 | 6.9585 | 6.9655 | 6.9724 | 6.9793 | 6.9863 | 6.9932 | 7.0001 | 7.0071 | 7.014 | 7.0209 | 7.0279 | 7.0348 | 7.0417 | 7.0487 | 7.0556 | 7.0625 | 7.0695 | 7.0764 | 7.0833 | 7.0903 | 7.0972 | 7.1041 | 7.1111 | 7.118 | 7.1175 | 7.1171 | 7.1166 | 7.1161 | 7.1157 | 7.1152 | 7.1147 | 7.1143 | 7.1138 | 7.1133 | 7.1129 | 7.1124 | 7.1119 | 7.1115 | 7.111 | 7.1105 | 7.1101 | 7.1096 | 7.1091 | 7.1087 | 7.1082 | 7.1077 | 7.1073 | 7.1068 | 7.1063 | 7.1059 | 7.1054 | 7.1049 | 7.1045 | 7.104 | 7.1035 | 7.1031 | 7.1026 | 7.1021 | 7.1017 | 7.1012 | 7.1007 | 7.1003 | 7.0998 | 7.0993 | 7.0989 | 7.0984 | 7.0979 | 7.0975 | 7.097 | 7.0965 | 7.0961 | 7.0956 | 7.0951 | 7.0947 | 7.0942 | 7.0937 | 7.0933 | 7.0928 | 7.0923 | 7.0919 | 7.0914 | 7.0909 | 7.0905 | 7.09 | 7.0895 | 7.0891 | 7.0886 | 7.0881 | 7.0877 | 7.0872 | 7.0867 | 7.0863 | 7.0858 | 7.0853 | 7.0849 | 7.0844 | 7.0839 | 7.0835 | 7.083 | 7.0825 | 7.0821 | 7.0816 | 7.0811 | 7.0807 | 7.0802 | 7.0797 | 7.0793 | 7.0788 | 7.0783 | 7.0779 | 7.0774 | 7.0769 | 7.0765 | 7.076
3.35 | 0 | 0.2895 | 0.579 | 0.8685 | 1.158 | 1.4475 | 1.737 | 2.0265 | 2.316 | 2.6055 | 2.895 | 3.1482 | 3.4014 | 3.6546 | 3.9078 | 4.161 | 4.3658 | 4.5706 | 4.7754 | 4.9802 | 5.185 | 5.2671 | 5.3492 | 5.4313 | 5.5134 | 5.5955 | 5.6776 | 5.7597 | 5.8418 | 5.9239 | 6.006 | 6.0518 | 6.0976 | 6.1434 | 6.1892 | 6.235 | 6.2808 | 6.3266 | 6.3724 | 6.4182 | 6.464 | 6.5098 | 6.5556 | 6.6014 | 6.6472 | 6.693 | 6.7218 | 6.7506 | 6.7794 | 6.8082 | 6.837 | 6.8658 | 6.8946 | 6.9234 | 6.9522 | 6.981 | 7.0098 | 7.0386 | 7.0674 | 7.0962 | 7.125 | 7.1322 | 7.1394 | 7.1466 | 7.1538 | 7.161 | 7.1682 | 7.1754 | 7.1826 | 7.1898 | 7.197 | 7.2042 | 7.2114 | 7.2186 | 7.2258 | 7.233 | 7.2402 | 7.2474 | 7.2546 | 7.2618 | 7.269 | 7.2762 | 7.2834 | 7.2906 | 7.2978 | 7.305 | 7.3122 | 7.3194 | 7.3266 | 7.3338 | 7.341 | 7.3406 | 7.3401 | 7.3397 | 7.3393 | 7.3388 | 7.3384 | 7.338 | 7.3375 | 7.3371 | 7.3367 | 7.3362 | 7.3358 | 7.3354 | 7.3349 | 7.3345 | 7.3341 | 7.3336 | 7.3332 | 7.3328 | 7.3323 | 7.3319 | 7.3315 | 7.331 | 7.3306 | 7.3302 | 7.3297 | 7.3293 | 7.3289 | 7.3284 | 7.328 | 7.3276 | 7.3271 | 7.3267 | 7.3263 | 7.3258 | 7.3254 | 7.325 | 7.3245 | 7.3241 | 7.3237 | 7.3232 | 7.3228 | 7.3224 | 7.3219 | 7.3215 | 7.3211 | 7.3206 | 7.3202 | 7.3198 | 7.3193 | 7.3189 | 7.3185 | 7.318 | 7.3176 | 7.3172 | 7.3167 | 7.3163 | 7.3159 | 7.3154 | 7.315 | 7.3146 | 7.3141 | 7.3137 | 7.3133 | 7.3128 | 7.3124 | 7.312 | 7.3115 | 7.3111 | 7.3107 | 7.3102 | 7.3098 | 7.3094 | 7.3089 | 7.3085 | 7.3081 | 7.3076 | 7.3072 | 7.3068 | 7.3063 | 7.3059 | 7.3055 | 7.305 | 7.3046 | 7.3042 | 7.3037 | 7.3033 | 7.3029 | 7.3024 | 7.302
3.4 | 0 | 0.298 | 0.596 | 0.894 | 1.192 | 1.49 | 1.788 | 2.086 | 2.384 | 2.682 | 2.98 | 3.2408 | 3.5016 | 3.7624 | 4.0232 | 4.284 | 4.4952 | 4.7064 | 4.9176 | 5.1288 | 5.34 | 5.4244 | 5.5088 | 5.5932 | 5.6776 | 5.762 | 5.8464 | 5.9308 | 6.0152 | 6.0996 | 6.184 | 6.2312 | 6.2784 | 6.3256 | 6.3728 | 6.42 | 6.4672 | 6.5144 | 6.5616 | 6.6088 | 6.656 | 6.7032 | 6.7504 | 6.7976 | 6.8448 | 6.892 | 6.9219 | 6.9517 | 6.9816 | 7.0115 | 7.0413 | 7.0712 | 7.1011 | 7.1309 | 7.1608 | 7.1907 | 7.2205 | 7.2504 | 7.2803 | 7.3101 | 7.34 | 7.3475 | 7.3549 | 7.3624 | 7.3699 | 7.3773 | 7.3848 | 7.3923 | 7.3997 | 7.4072 | 7.4147 | 7.4221 | 7.4296 | 7.4371 | 7.4445 | 7.452 | 7.4595 | 7.4669 | 7.4744 | 7.4819 | 7.4893 | 7.4968 | 7.5043 | 7.5117 | 7.5192 | 7.5267 | 7.5341 | 7.5416 | 7.5491 | 7.5565 | 7.564 | 7.5636 | 7.5632 | 7.5628 | 7.5624 | 7.562 | 7.5616 | 7.5612 | 7.5608 | 7.5604 | 7.56 | 7.5596 | 7.5592 | 7.5588 | 7.5584 | 7.558 | 7.5576 | 7.5572 | 7.5568 | 7.5564 | 7.556 | 7.5556 | 7.5552 | 7.5548 | 7.5544 | 7.554 | 7.5536 | 7.5532 | 7.5528 | 7.5524 | 7.552 | 7.5516 | 7.5512 | 7.5508 | 7.5504 | 7.55 | 7.5496 | 7.5492 | 7.5488 | 7.5484 | 7.548 | 7.5476 | 7.5472 | 7.5468 | 7.5464 | 7.546 | 7.5456 | 7.5452 | 7.5448 | 7.5444 | 7.544 | 7.5436 | 7.5432 | 7.5428 | 7.5424 | 7.542 | 7.5416 | 7.5412 | 7.5408 | 7.5404 | 7.54 | 7.5396 | 7.5392 | 7.5388 | 7.5384 | 7.538 | 7.5376 | 7.5372 | 7.5368 | 7.5364 | 7.536 | 7.5356 | 7.5352 | 7.5348 | 7.5344 | 7.534 | 7.5336 | 7.5332 | 7.5328 | 7.5324 | 7.532 | 7.5316 | 7.5312 | 7.5308 | 7.5304 | 7.53 | 7.5296 | 7.5292 | 7.5288 | 7.5284 | 7.528
3.45 | 0 | 0.3065 | 0.613 | 0.9195 | 1.226 | 1.5325 | 1.839 | 2.1455 | 2.452 | 2.7585 | 3.065 | 3.3334 | 3.6018 | 3.8702 | 4.1386 | 4.407 | 4.6246 | 4.8422 | 5.0598 | 5.2774 | 5.495 | 5.5817 | 5.6684 | 5.7551 | 5.8418 | 5.9285 | 6.0152 | 6.1019 | 6.1886 | 6.2753 | 6.362 | 6.4106 | 6.4592 | 6.5078 | 6.5564 | 6.605 | 6.6536 | 6.7022 | 6.7508 | 6.7994 | 6.848 | 6.8966 | 6.9452 | 6.9938 | 7.0424 | 7.091 | 7.1219 | 7.1529 | 7.1838 | 7.2147 | 7.2457 | 7.2766 | 7.3075 | 7.3385 | 7.3694 | 7.4003 | 7.4313 | 7.4622 | 7.4931 | 7.5241 | 7.555 | 7.5627 | 7.5705 | 7.5782 | 7.5859 | 7.5937 | 7.6014 | 7.6091 | 7.6169 | 7.6246 | 7.6323 | 7.6401 | 7.6478 | 7.6555 | 7.6633 | 7.671 | 7.6787 | 7.6865 | 7.6942 | 7.7019 | 7.7097 | 7.7174 | 7.7251 | 7.7329 | 7.7406 | 7.7483 | 7.7561 | 7.7638 | 7.7715 | 7.7793 | 7.787 | 7.7866 | 7.7863 | 7.7859 | 7.7855 | 7.7852 | 7.7848 | 7.7844 | 7.7841 | 7.7837 | 7.7833 | 7.783 | 7.7826 | 7.7822 | 7.7819 | 7.7815 | 7.7811 | 7.7808 | 7.7804 | 7.78 | 7.7797 | 7.7793 | 7.7789 | 7.7786 | 7.7782 | 7.7778 | 7.7775 | 7.7771 | 7.7767 | 7.7764 | 7.776 | 7.7756 | 7.7753 | 7.7749 | 7.7745 | 7.7742 | 7.7738 | 7.7734 | 7.7731 | 7.7727 | 7.7723 | 7.772 | 7.7716 | 7.7712 | 7.7709 | 7.7705 | 7.7701 | 7.7698 | 7.7694 | 7.769 | 7.7687 | 7.7683 | 7.7679 | 7.7676 | 7.7672 | 7.7668 | 7.7665 | 7.7661 | 7.7657 | 7.7654 | 7.765 | 7.7646 | 7.7643 | 7.7639 | 7.7635 | 7.7632 | 7.7628 | 7.7624 | 7.7621 | 7.7617 | 7.7613 | 7.761 | 7.7606 | 7.7602 | 7.7599 | 7.7595 | 7.7591 | 7.7588 | 7.7584 | 7.758 | 7.7577 | 7.7573 | 7.7569 | 7.7566 | 7.7562 | 7.7558 | 7.7555 | 7.7551 | 7.7547 | 7.7544 | 7.754
3.5 | 0 | 0.315 | 0.63 | 0.945 | 1.26 | 1.575 | 1.89 | 2.205 | 2.52 | 2.835 | 3.15 | 3.426 | 3.702 | 3.978 | 4.254 | 4.53 | 4.754 | 4.978 | 5.202 | 5.426 | 5.65 | 5.739 | 5.828 | 5.917 | 6.006 | 6.095 | 6.184 | 6.273 | 6.362 | 6.451 | 6.54 | 6.59 | 6.64 | 6.69 | 6.74 | 6.79 | 6.84 | 6.89 | 6.94 | 6.99 | 7.04 | 7.09 | 7.14 | 7.19 | 7.24 | 7.29 | 7.322 | 7.354 | 7.386 | 7.418 | 7.45 | 7.482 | 7.514 | 7.546 | 7.578 | 7.61 | 7.642 | 7.674 | 7.706 | 7.738 | 7.77 | 7.778 | 7.786 | 7.794 | 7.802 | 7.81 | 7.818 | 7.826 | 7.834 | 7.842 | 7.85 | 7.858 | 7.866 | 7.874 | 7.882 | 7.89 | 7.898 | 7.906 | 7.914 | 7.922 | 7.93 | 7.938 | 7.946 | 7.954 | 7.962 | 7.97 | 7.978 | 7.986 | 7.994 | 8.002 | 8.01 | 8.0097 | 8.0093 | 8.009 | 8.0087 | 8.0083 | 8.008 | 8.0077 | 8.0073 | 8.007 | 8.0067 | 8.0063 | 8.006 | 8.0057 | 8.0053 | 8.005 | 8.0047 | 8.0043 | 8.004 | 8.0037 | 8.0033 | 8.003 | 8.0027 | 8.0023 | 8.002 | 8.0017 | 8.0013 | 8.001 | 8.0007 | 8.0003 | 8 | 7.9997 | 7.9993 | 7.999 | 7.9987 | 7.9983 | 7.998 | 7.9977 | 7.9973 | 7.997 | 7.9967 | 7.9963 | 7.996 | 7.9957 | 7.9953 | 7.995 | 7.9947 | 7.9943 | 7.994 | 7.9937 | 7.9933 | 7.993 | 7.9927 | 7.9923 | 7.992 | 7.9917 | 7.9913 | 7.991 | 7.9907 | 7.9903 | 7.99 | 7.9897 | 7.9893 | 7.989 | 7.9887 | 7.9883 | 7.988 | 7.9877 | 7.9873 | 7.987 | 7.9867 | 7.9863 | 7.986 | 7.9857 | 7.9853 | 7.985 | 7.9847 | 7.9843 | 7.984 | 7.9837 | 7.9833 | 7.983 | 7.9827 | 7.9823 | 7.982 | 7.9817 | 7.9813 | 7.981 | 7.9807 | 7.9803 | 7.98
3.55 | 0 | 0.3235 | 0.647 | 0.9705 | 1.294 | 1.6175 | 1.941 | 2.2645 | 2.588 | 2.9115 | 3.235 | 3.5186 | 3.8022 | 4.0858 | 4.3694 | 4.653 | 4.8834 | 5.1138 | 5.3442 | 5.5746 | 5.805 | 5.8963 | 5.9876 | 6.0789 | 6.1702 | 6.2615 | 6.3528 | 6.4441 | 6.5354 | 6.6267 | 6.718 | 6.7694 | 6.8208 | 6.8722 | 6.9236 | 6.975 | 7.0264 | 7.0778 | 7.1292 | 7.1806 | 7.232 | 7.2834 | 7.3348 | 7.3862 | 7.4376 | 7.489 | 7.5221 | 7.5551 | 7.5882 | 7.6213 | 7.6543 | 7.6874 | 7.7205 | 7.7535 | 7.7866 | 7.8197 | 7.8527 | 7.8858 | 7.9189 | 7.9519 | 7.985 | 7.9933 | 8.0015 | 8.0098 | 8.0181 | 8.0263 | 8.0346 | 8.0429 | 8.0511 | 8.0594 | 8.0677 | 8.0759 | 8.0842 | 8.0925 | 8.1007 | 8.109 | 8.1173 | 8.1255 | 8.1338 | 8.1421 | 8.1503 | 8.1586 | 8.1669 | 8.1751 | 8.1834 | 8.1917 | 8.1999 | 8.2082 | 8.2165 | 8.2247 | 8.233 | 8.2327 | 8.2324 | 8.2321 | 8.2318 | 8.2315 | 8.2312 | 8.2309 | 8.2306 | 8.2303 | 8.23 | 8.2297 | 8.2294 | 8.2291 | 8.2288 | 8.2285 | 8.2282 | 8.2279 | 8.2276 | 8.2273 | 8.227 | 8.2267 | 8.2264 | 8.2261 | 8.2258 | 8.2255 | 8.2252 | 8.2249 | 8.2246 | 8.2243 | 8.224 | 8.2237 | 8.2234 | 8.2231 | 8.2228 | 8.2225 | 8.2222 | 8.2219 | 8.2216 | 8.2213 | 8.221 | 8.2207 | 8.2204 | 8.2201 | 8.2198 | 8.2195 | 8.2192 | 8.2189 | 8.2186 | 8.2183 | 8.218 | 8.2177 | 8.2174 | 8.2171 | 8.2168 | 8.2165 | 8.2162 | 8.2159 | 8.2156 | 8.2153 | 8.215 | 8.2147 | 8.2144 | 8.2141 | 8.2138 | 8.2135 | 8.2132 | 8.2129 | 8.2126 | 8.2123 | 8.212 | 8.2117 | 8.2114 | 8.2111 | 8.2108 | 8.2105 | 8.2102 | 8.2099 | 8.2096 | 8.2093 | 8.209 | 8.2087 | 8.2084 | 8.2081 | 8.2078 | 8.2075 | 8.2072 | 8.2069 | 8.2066 | 8.2063 | 8.206
3.6 | 0 | 0.332 | 0.664 | 0.996 | 1.328 | 1.66 | 1.992 | 2.324 | 2.656 | 2.988 | 3.32 | 3.6112 | 3.9024 | 4.1936 | 4.4848 | 4.776 | 5.0128 | 5.2496 | 5.4864 | 5.7232 | 5.96 | 6.0536 | 6.1472 | 6.2408 | 6.3344 | 6.428 | 6.5216 | 6.6152 | 6.7088 | 6.8024 | 6.896 | 6.9488 | 7.0016 | 7.0544 | 7.1072 | 7.16 | 7.2128 | 7.2656 | 7.3184 | 7.3712 | 7.424 | 7.4768 | 7.5296 | 7.5824 | 7.6352 | 7.688 | 7.7221 | 7.7563 | 7.7904 | 7.8245 | 7.8587 | 7.8928 | 7.9269 | 7.9611 | 7.9952 | 8.0293 | 8.0635 | 8.0976 | 8.1317 | 8.1659 | 8.2 | 8.2085 | 8.2171 | 8.2256 | 8.2341 | 8.2427 | 8.2512 | 8.2597 | 8.2683 | 8.2768 | 8.2853 | 8.2939 | 8.3024 | 8.3109 | 8.3195 | 8.328 | 8.3365 | 8.3451 | 8.3536 | 8.3621 | 8.3707 | 8.3792 | 8.3877 | 8.3963 | 8.4048 | 8.4133 | 8.4219 | 8.4304 | 8.4389 | 8.4475 | 8.456 | 8.4557 | 8.4555 | 8.4552 | 8.4549 | 8.4547 | 8.4544 | 8.4541 | 8.4539 | 8.4536 | 8.4533 | 8.4531 | 8.4528 | 8.4525 | 8.4523 | 8.452 | 8.4517 | 8.4515 | 8.4512 | 8.4509 | 8.4507 | 8.4504 | 8.4501 | 8.4499 | 8.4496 | 8.4493 | 8.4491 | 8.4488 | 8.4485 | 8.4483 | 8.448 | 8.4477 | 8.4475 | 8.4472 | 8.4469 | 8.4467 | 8.4464 | 8.4461 | 8.4459 | 8.4456 | 8.4453 | 8.4451 | 8.4448 | 8.4445 | 8.4443 | 8.444 | 8.4437 | 8.4435 | 8.4432 | 8.4429 | 8.4427 | 8.4424 | 8.4421 | 8.4419 | 8.4416 | 8.4413 | 8.4411 | 8.4408 | 8.4405 | 8.4403 | 8.44 | 8.4397 | 8.4395 | 8.4392 | 8.4389 | 8.4387 | 8.4384 | 8.4381 | 8.4379 | 8.4376 | 8.4373 | 8.4371 | 8.4368 | 8.4365 | 8.4363 | 8.436 | 8.4357 | 8.4355 | 8.4352 | 8.4349 | 8.4347 | 8.4344 | 8.4341 | 8.4339 | 8.4336 | 8.4333 | 8.4331 | 8.4328 | 8.4325 | 8.4323 | 8.432
3.65 | 0 | 0.3405 | 0.681 | 1.0215 | 1.362 | 1.7025 | 2.043 | 2.3835 | 2.724 | 3.0645 | 3.405 | 3.7038 | 4.0026 | 4.3014 | 4.6002 | 4.899 | 5.1422 | 5.3854 | 5.6286 | 5.8718 | 6.115 | 6.2109 | 6.3068 | 6.4027 | 6.4986 | 6.5945 | 6.6904 | 6.7863 | 6.8822 | 6.9781 | 7.074 | 7.1282 | 7.1824 | 7.2366 | 7.2908 | 7.345 | 7.3992 | 7.4534 | 7.5076 | 7.5618 | 7.616 | 7.6702 | 7.7244 | 7.7786 | 7.8328 | 7.887 | 7.9222 | 7.9574 | 7.9926 | 8.0278 | 8.063 | 8.0982 | 8.1334 | 8.1686 | 8.2038 | 8.239 | 8.2742 | 8.3094 | 8.3446 | 8.3798 | 8.415 | 8.4238 | 8.4326 | 8.4414 | 8.4502 | 8.459 | 8.4678 | 8.4766 | 8.4854 | 8.4942 | 8.503 | 8.5118 | 8.5206 | 8.5294 | 8.5382 | 8.547 | 8.5558 | 8.5646 | 8.5734 | 8.5822 | 8.591 | 8.5998 | 8.6086 | 8.6174 | 8.6262 | 8.635 | 8.6438 | 8.6526 | 8.6614 | 8.6702 | 8.679 | 8.6788 | 8.6785 | 8.6783 | 8.6781 | 8.6778 | 8.6776 | 8.6774 | 8.6771 | 8.6769 | 8.6767 | 8.6764 | 8.6762 | 8.676 | 8.6757 | 8.6755 | 8.6753 | 8.675 | 8.6748 | 8.6746 | 8.6743 | 8.6741 | 8.6739 | 8.6736 | 8.6734 | 8.6732 | 8.6729 | 8.6727 | 8.6725 | 8.6722 | 8.672 | 8.6718 | 8.6715 | 8.6713 | 8.6711 | 8.6708 | 8.6706 | 8.6704 | 8.6701 | 8.6699 | 8.6697 | 8.6694 | 8.6692 | 8.669 | 8.6687 | 8.6685 | 8.6683 | 8.668 | 8.6678 | 8.6676 | 8.6673 | 8.6671 | 8.6669 | 8.6666 | 8.6664 | 8.6662 | 8.6659 | 8.6657 | 8.6655 | 8.6652 | 8.665 | 8.6648 | 8.6645 | 8.6643 | 8.6641 | 8.6638 | 8.6636 | 8.6634 | 8.6631 | 8.6629 | 8.6627 | 8.6624 | 8.6622 | 8.662 | 8.6617 | 8.6615 | 8.6613 | 8.661 | 8.6608 | 8.6606 | 8.6603 | 8.6601 | 8.6599 | 8.6596 | 8.6594 | 8.6592 | 8.6589 | 8.6587 | 8.6585 | 8.6582 | 8.658
3.7 | 0 | 0.349 | 0.698 | 1.047 | 1.396 | 1.745 | 2.094 | 2.443 | 2.792 | 3.141 | 3.49 | 3.7964 | 4.1028 | 4.4092 | 4.7156 | 5.022 | 5.2716 | 5.5212 | 5.7708 | 6.0204 | 6.27 | 6.3682 | 6.4664 | 6.5646 | 6.6628 | 6.761 | 6.8592 | 6.9574 | 7.0556 | 7.1538 | 7.252 | 7.3076 | 7.3632 | 7.4188 | 7.4744 | 7.53 | 7.5856 | 7.6412 | 7.6968 | 7.7524 | 7.808 | 7.8636 | 7.9192 | 7.9748 | 8.0304 | 8.086 | 8.1223 | 8.1585 | 8.1948 | 8.2311 | 8.2673 | 8.3036 | 8.3399 | 8.3761 | 8.4124 | 8.4487 | 8.4849 | 8.5212 | 8.5575 | 8.5937 | 8.63 | 8.6391 | 8.6481 | 8.6572 | 8.6663 | 8.6753 | 8.6844 | 8.6935 | 8.7025 | 8.7116 | 8.7207 | 8.7297 | 8.7388 | 8.7479 | 8.7569 | 8.766 | 8.7751 | 8.7841 | 8.7932 | 8.8023 | 8.8113 | 8.8204 | 8.8295 | 8.8385 | 8.8476 | 8.8567 | 8.8657 | 8.8748 | 8.8839 | 8.8929 | 8.902 | 8.9018 | 8.9016 | 8.9014 | 8.9012 | 8.901 | 8.9008 | 8.9006 | 8.9004 | 8.9002 | 8.9 | 8.8998 | 8.8996 | 8.8994 | 8.8992 | 8.899 | 8.8988 | 8.8986 | 8.8984 | 8.8982 | 8.898 | 8.8978 | 8.8976 | 8.8974 | 8.8972 | 8.897 | 8.8968 | 8.8966 | 8.8964 | 8.8962 | 8.896 | 8.8958 | 8.8956 | 8.8954 | 8.8952 | 8.895 | 8.8948 | 8.8946 | 8.8944 | 8.8942 | 8.894 | 8.8938 | 8.8936 | 8.8934 | 8.8932 | 8.893 | 8.8928 | 8.8926 | 8.8924 | 8.8922 | 8.892 | 8.8918 | 8.8916 | 8.8914 | 8.8912 | 8.891 | 8.8908 | 8.8906 | 8.8904 | 8.8902 | 8.89 | 8.8898 | 8.8896 | 8.8894 | 8.8892 | 8.889 | 8.8888 | 8.8886 | 8.8884 | 8.8882 | 8.888 | 8.8878 | 8.8876 | 8.8874 | 8.8872 | 8.887 | 8.8868 | 8.8866 | 8.8864 | 8.8862 | 8.886 | 8.8858 | 8.8856 | 8.8854 | 8.8852 | 8.885 | 8.8848 | 8.8846 | 8.8844 | 8.8842 | 8.884
3.75 | 0 | 0.3575 | 0.715 | 1.0725 | 1.43 | 1.7875 | 2.145 | 2.5025 | 2.86 | 3.2175 | 3.575 | 3.889 | 4.203 | 4.517 | 4.831 | 5.145 | 5.401 | 5.657 | 5.913 | 6.169 | 6.425 | 6.5255 | 6.626 | 6.7265 | 6.827 | 6.9275 | 7.028 | 7.1285 | 7.229 | 7.3295 | 7.43 | 7.487 | 7.544 | 7.601 | 7.658 | 7.715 | 7.772 | 7.829 | 7.886 | 7.943 | 8 | 8.057 | 8.114 | 8.171 | 8.228 | 8.285 | 8.3223 | 8.3597 | 8.397 | 8.4343 | 8.4717 | 8.509 | 8.5463 | 8.5837 | 8.621 | 8.6583 | 8.6957 | 8.733 | 8.7703 | 8.8077 | 8.845 | 8.8543 | 8.8637 | 8.873 | 8.8823 | 8.8917 | 8.901 | 8.9103 | 8.9197 | 8.929 | 8.9383 | 8.9477 | 8.957 | 8.9663 | 8.9757 | 8.985 | 8.9943 | 9.0037 | 9.013 | 9.0223 | 9.0317 | 9.041 | 9.0503 | 9.0597 | 9.069 | 9.0783 | 9.0877 | 9.097 | 9.1063 | 9.1157 | 9.125 | 9.1248 | 9.1247 | 9.1245 | 9.1243 | 9.1242 | 9.124 | 9.1238 | 9.1237 | 9.1235 | 9.1233 | 9.1232 | 9.123 | 9.1228 | 9.1227 | 9.1225 | 9.1223 | 9.1222 | 9.122 | 9.1218 | 9.1217 | 9.1215 | 9.1213 | 9.1212 | 9.121 | 9.1208 | 9.1207 | 9.1205 | 9.1203 | 9.1202 | 9.12 | 9.1198 | 9.1197 | 9.1195 | 9.1193 | 9.1192 | 9.119 | 9.1188 | 9.1187 | 9.1185 | 9.1183 | 9.1182 | 9.118 | 9.1178 | 9.1177 | 9.1175 | 9.1173 | 9.1172 | 9.117 | 9.1168 | 9.1167 | 9.1165 | 9.1163 | 9.1162 | 9.116 | 9.1158 | 9.1157 | 9.1155 | 9.1153 | 9.1152 | 9.115 | 9.1148 | 9.1147 | 9.1145 | 9.1143 | 9.1142 | 9.114 | 9.1138 | 9.1137 | 9.1135 | 9.1133 | 9.1132 | 9.113 | 9.1128 | 9.1127 | 9.1125 | 9.1123 | 9.1122 | 9.112 | 9.1118 | 9.1117 | 9.1115 | 9.1113 | 9.1112 | 9.111 | 9.1108 | 9.1107 | 9.1105 | 9.1103 | 9.1102 | 9.11
3.8 | 0 | 0.366 | 0.732 | 1.098 | 1.464 | 1.83 | 2.196 | 2.562 | 2.928 | 3.294 | 3.66 | 3.9816 | 4.3032 | 4.6248 | 4.9464 | 5.268 | 5.5304 | 5.7928 | 6.0552 | 6.3176 | 6.58 | 6.6828 | 6.7856 | 6.8884 | 6.9912 | 7.094 | 7.1968 | 7.2996 | 7.4024 | 7.5052 | 7.608 | 7.6664 | 7.7248 | 7.7832 | 7.8416 | 7.9 | 7.9584 | 8.0168 | 8.0752 | 8.1336 | 8.192 | 8.2504 | 8.3088 | 8.3672 | 8.4256 | 8.484 | 8.5224 | 8.5608 | 8.5992 | 8.6376 | 8.676 | 8.7144 | 8.7528 | 8.7912 | 8.8296 | 8.868 | 8.9064 | 8.9448 | 8.9832 | 9.0216 | 9.06 | 9.0696 | 9.0792 | 9.0888 | 9.0984 | 9.108 | 9.1176 | 9.1272 | 9.1368 | 9.1464 | 9.156 | 9.1656 | 9.1752 | 9.1848 | 9.1944 | 9.204 | 9.2136 | 9.2232 | 9.2328 | 9.2424 | 9.252 | 9.2616 | 9.2712 | 9.2808 | 9.2904 | 9.3 | 9.3096 | 9.3192 | 9.3288 | 9.3384 | 9.348 | 9.3479 | 9.3477 | 9.3476 | 9.3475 | 9.3473 | 9.3472 | 9.3471 | 9.3469 | 9.3468 | 9.3467 | 9.3465 | 9.3464 | 9.3463 | 9.3461 | 9.346 | 9.3459 | 9.3457 | 9.3456 | 9.3455 | 9.3453 | 9.3452 | 9.3451 | 9.3449 | 9.3448 | 9.3447 | 9.3445 | 9.3444 | 9.3443 | 9.3441 | 9.344 | 9.3439 | 9.3437 | 9.3436 | 9.3435 | 9.3433 | 9.3432 | 9.3431 | 9.3429 | 9.3428 | 9.3427 | 9.3425 | 9.3424 | 9.3423 | 9.3421 | 9.342 | 9.3419 | 9.3417 | 9.3416 | 9.3415 | 9.3413 | 9.3412 | 9.3411 | 9.3409 | 9.3408 | 9.3407 | 9.3405 | 9.3404 | 9.3403 | 9.3401 | 9.34 | 9.3399 | 9.3397 | 9.3396 | 9.3395 | 9.3393 | 9.3392 | 9.3391 | 9.3389 | 9.3388 | 9.3387 | 9.3385 | 9.3384 | 9.3383 | 9.3381 | 9.338 | 9.3379 | 9.3377 | 9.3376 | 9.3375 | 9.3373 | 9.3372 | 9.3371 | 9.3369 | 9.3368 | 9.3367 | 9.3365 | 9.3364 | 9.3363 | 9.3361 | 9.336
3.85 | 0 | 0.3745 | 0.749 | 1.1235 | 1.498 | 1.8725 | 2.247 | 2.6215 | 2.996 | 3.3705 | 3.745 | 4.0742 | 4.4034 | 4.7326 | 5.0618 | 5.391 | 5.6598 | 5.9286 | 6.1974 | 6.4662 | 6.735 | 6.8401 | 6.9452 | 7.0503 | 7.1554 | 7.2605 | 7.3656 | 7.4707 | 7.5758 | 7.6809 | 7.786 | 7.8458 | 7.9056 | 7.9654 | 8.0252 | 8.085 | 8.1448 | 8.2046 | 8.2644 | 8.3242 | 8.384 | 8.4438 | 8.5036 | 8.5634 | 8.6232 | 8.683 | 8.7225 | 8.7619 | 8.8014 | 8.8409 | 8.8803 | 8.9198 | 8.9593 | 8.9987 | 9.0382 | 9.0777 | 9.1171 | 9.1566 | 9.1961 | 9.2355 | 9.275 | 9.2849 | 9.2947 | 9.3046 | 9.3145 | 9.3243 | 9.3342 | 9.3441 | 9.3539 | 9.3638 | 9.3737 | 9.3835 | 9.3934 | 9.4033 | 9.4131 | 9.423 | 9.4329 | 9.4427 | 9.4526 | 9.4625 | 9.4723 | 9.4822 | 9.4921 | 9.5019 | 9.5118 | 9.5217 | 9.5315 | 9.5414 | 9.5513 | 9.5611 | 9.571 | 9.5709 | 9.5708 | 9.5707 | 9.5706 | 9.5705 | 9.5704 | 9.5703 | 9.5702 | 9.5701 | 9.57 | 9.5699 | 9.5698 | 9.5697 | 9.5696 | 9.5695 | 9.5694 | 9.5693 | 9.5692 | 9.5691 | 9.569 | 9.5689 | 9.5688 | 9.5687 | 9.5686 | 9.5685 | 9.5684 | 9.5683 | 9.5682 | 9.5681 | 9.568 | 9.5679 | 9.5678 | 9.5677 | 9.5676 | 9.5675 | 9.5674 | 9.5673 | 9.5672 | 9.5671 | 9.567 | 9.5669 | 9.5668 | 9.5667 | 9.5666 | 9.5665 | 9.5664 | 9.5663 | 9.5662 | 9.5661 | 9.566 | 9.5659 | 9.5658 | 9.5657 | 9.5656 | 9.5655 | 9.5654 | 9.5653 | 9.5652 | 9.5651 | 9.565 | 9.5649 | 9.5648 | 9.5647 | 9.5646 | 9.5645 | 9.5644 | 9.5643 | 9.5642 | 9.5641 | 9.564 | 9.5639 | 9.5638 | 9.5637 | 9.5636 | 9.5635 | 9.5634 | 9.5633 | 9.5632 | 9.5631 | 9.563 | 9.5629 | 9.5628 | 9.5627 | 9.5626 | 9.5625 | 9.5624 | 9.5623 | 9.5622 | 9.5621 | 9.562
3.9 | 0 | 0.383 | 0.766 | 1.149 | 1.532 | 1.915 | 2.298 | 2.681 | 3.064 | 3.447 | 3.83 | 4.1668 | 4.5036 | 4.8404 | 5.1772 | 5.514 | 5.7892 | 6.0644 | 6.3396 | 6.6148 | 6.89 | 6.9974 | 7.1048 | 7.2122 | 7.3196 | 7.427 | 7.5344 | 7.6418 | 7.7492 | 7.8566 | 7.964 | 8.0252 | 8.0864 | 8.1476 | 8.2088 | 8.27 | 8.3312 | 8.3924 | 8.4536 | 8.5148 | 8.576 | 8.6372 | 8.6984 | 8.7596 | 8.8208 | 8.882 | 8.9225 | 8.9631 | 9.0036 | 9.0441 | 9.0847 | 9.1252 | 9.1657 | 9.2063 | 9.2468 | 9.2873 | 9.3279 | 9.3684 | 9.4089 | 9.4495 | 9.49 | 9.5001 | 9.5103 | 9.5204 | 9.5305 | 9.5407 | 9.5508 | 9.5609 | 9.5711 | 9.5812 | 9.5913 | 9.6015 | 9.6116 | 9.6217 | 9.6319 | 9.642 | 9.6521 | 9.6623 | 9.6724 | 9.6825 | 9.6927 | 9.7028 | 9.7129 | 9.7231 | 9.7332 | 9.7433 | 9.7535 | 9.7636 | 9.7737 | 9.7839 | 9.794 | 9.7939 | 9.7939 | 9.7938 | 9.7937 | 9.7937 | 9.7936 | 9.7935 | 9.7935 | 9.7934 | 9.7933 | 9.7933 | 9.7932 | 9.7931 | 9.7931 | 9.793 | 9.7929 | 9.7929 | 9.7928 | 9.7927 | 9.7927 | 9.7926 | 9.7925 | 9.7925 | 9.7924 | 9.7923 | 9.7923 | 9.7922 | 9.7921 | 9.7921 | 9.792 | 9.7919 | 9.7919 | 9.7918 | 9.7917 | 9.7917 | 9.7916 | 9.7915 | 9.7915 | 9.7914 | 9.7913 | 9.7913 | 9.7912 | 9.7911 | 9.7911 | 9.791 | 9.7909 | 9.7909 | 9.7908 | 9.7907 | 9.7907 | 9.7906 | 9.7905 | 9.7905 | 9.7904 | 9.7903 | 9.7903 | 9.7902 | 9.7901 | 9.7901 | 9.79 | 9.7899 | 9.7899 | 9.7898 | 9.7897 | 9.7897 | 9.7896 | 9.7895 | 9.7895 | 9.7894 | 9.7893 | 9.7893 | 9.7892 | 9.7891 | 9.7891 | 9.789 | 9.7889 | 9.7889 | 9.7888 | 9.7887 | 9.7887 | 9.7886 | 9.7885 | 9.7885 | 9.7884 | 9.7883 | 9.7883 | 9.7882 | 9.7881 | 9.7881 | 9.788
3.95 | 0 | 0.3915 | 0.783 | 1.1745 | 1.566 | 1.9575 | 2.349 | 2.7405 | 3.132 | 3.5235 | 3.915 | 4.2594 | 4.6038 | 4.9482 | 5.2926 | 5.637 | 5.9186 | 6.2002 | 6.4818 | 6.7634 | 7.045 | 7.1547 | 7.2644 | 7.3741 | 7.4838 | 7.5935 | 7.7032 | 7.8129 | 7.9226 | 8.0323 | 8.142 | 8.2046 | 8.2672 | 8.3298 | 8.3924 | 8.455 | 8.5176 | 8.5802 | 8.6428 | 8.7054 | 8.768 | 8.8306 | 8.8932 | 8.9558 | 9.0184 | 9.081 | 9.1226 | 9.1642 | 9.2058 | 9.2474 | 9.289 | 9.3306 | 9.3722 | 9.4138 | 9.4554 | 9.497 | 9.5386 | 9.5802 | 9.6218 | 9.6634 | 9.705 | 9.7154 | 9.7258 | 9.7362 | 9.7466 | 9.757 | 9.7674 | 9.7778 | 9.7882 | 9.7986 | 9.809 | 9.8194 | 9.8298 | 9.8402 | 9.8506 | 9.861 | 9.8714 | 9.8818 | 9.8922 | 9.9026 | 9.913 | 9.9234 | 9.9338 | 9.9442 | 9.9546 | 9.965 | 9.9754 | 9.9858 | 9.9962 | 10.0066 | 10.017 | 10.017 | 10.0169 | 10.0169 | 10.0169 | 10.0168 | 10.0168 | 10.0168 | 10.0167 | 10.0167 | 10.0167 | 10.0166 | 10.0166 | 10.0166 | 10.0165 | 10.0165 | 10.0165 | 10.0164 | 10.0164 | 10.0164 | 10.0163 | 10.0163 | 10.0163 | 10.0162 | 10.0162 | 10.0162 | 10.0161 | 10.0161 | 10.0161 | 10.016 | 10.016 | 10.016 | 10.0159 | 10.0159 | 10.0159 | 10.0158 | 10.0158 | 10.0158 | 10.0157 | 10.0157 | 10.0157 | 10.0156 | 10.0156 | 10.0156 | 10.0155 | 10.0155 | 10.0155 | 10.0154 | 10.0154 | 10.0154 | 10.0153 | 10.0153 | 10.0153 | 10.0152 | 10.0152 | 10.0152 | 10.0151 | 10.0151 | 10.0151 | 10.015 | 10.015 | 10.015 | 10.0149 | 10.0149 | 10.0149 | 10.0148 | 10.0148 | 10.0148 | 10.0147 | 10.0147 | 10.0147 | 10.0146 | 10.0146 | 10.0146 | 10.0145 | 10.0145 | 10.0145 | 10.0144 | 10.0144 | 10.0144 | 10.0143 | 10.0143 | 10.0143 | 10.0142 | 10.0142 | 10.0142 | 10.0141 | 10.0141 | 10.0141 | 10.014 | 10.014
4 | 0 | 0.4 | 0.8 | 1.2 | 1.6 | 2 | 2.4 | 2.8 | 3.2 | 3.6 | 4 | 4.352 | 4.704 | 5.056 | 5.408 | 5.76 | 6.048 | 6.336 | 6.624 | 6.912 | 7.2 | 7.312 | 7.424 | 7.536 | 7.648 | 7.76 | 7.872 | 7.984 | 8.096 | 8.208 | 8.32 | 8.384 | 8.448 | 8.512 | 8.576 | 8.64 | 8.704 | 8.768 | 8.832 | 8.896 | 8.96 | 9.024 | 9.088 | 9.152 | 9.216 | 9.28 | 9.3227 | 9.3653 | 9.408 | 9.4507 | 9.4933 | 9.536 | 9.5787 | 9.6213 | 9.664 | 9.7067 | 9.7493 | 9.792 | 9.8347 | 9.8773 | 9.92 | 9.9307 | 9.9413 | 9.952 | 9.9627 | 9.9733 | 9.984 | 9.9947 | 10.0053 | 10.016 | 10.0267 | 10.0373 | 10.048 | 10.0587 | 10.0693 | 10.08 | 10.0907 | 10.1013 | 10.112 | 10.1227 | 10.1333 | 10.144 | 10.1547 | 10.1653 | 10.176 | 10.1867 | 10.1973 | 10.208 | 10.2187 | 10.2293 | 10.24 | 10.24 | 10.24 | 10.24 | 10.24 | 10.24 | 10.24 | 10.24 | 10.24 | 10.24 | 10.24 | 10.24 | 10.24 | 10.24 | 10.24 | 10.24 | 10.24 | 10.24 | 10.24 | 10.24 | 10.24 | 10.24 | 10.24 | 10.24 | 10.24 | 10.24 | 10.24 | 10.24 | 10.24 | 10.24 | 10.24 | 10.24 | 10.24 | 10.24 | 10.24 | 10.24 | 10.24 | 10.24 | 10.24 | 10.24 | 10.24 | 10.24 | 10.24 | 10.24 | 10.24 | 10.24 | 10.24 | 10.24 | 10.24 | 10.24 | 10.24 | 10.24 | 10.24 | 10.24 | 10.24 | 10.24 | 10.24 | 10.24 | 10.24 | 10.24 | 10.24 | 10.24 | 10.24 | 10.24 | 10.24 | 10.24 | 10.24 | 10.24 | 10.24 | 10.24 | 10.24 | 10.24 | 10.24 | 10.24 | 10.24 | 10.24 | 10.24 | 10.24 | 10.24 | 10.24 | 10.24 | 10.24 | 10.24 | 10.24 | 10.24 | 10.24 | 10.24 | 10.24 | 10.24 | 10.24 | 10.24
4.05 | 0 | 0.42167 | 0.84333 | 1.265 | 1.6867 | 2.1083 | 2.53 | 2.9517 | 3.3733 | 3.795 | 4.2167 | 4.5991 | 4.9815 | 5.3639 | 5.7463 | 6.1287 | 6.4193 | 6.7099 | 7.0005 | 7.2911 | 7.5817 | 7.7019 | 7.8221 | 7.9424 | 8.0626 | 8.1828 | 8.3031 | 8.4233 | 8.5435 | 8.6638 | 8.784 | 8.8536 | 8.9232 | 8.9927 | 9.0623 | 9.1319 | 9.2015 | 9.271 | 9.3406 | 9.4102 | 9.4798 | 9.5494 | 9.6189 | 9.6885 | 9.7581 | 9.8277 | 9.875 | 9.9223 | 9.9696 | 10.0169 | 10.0642 | 10.1115 | 10.1588 | 10.2062 | 10.2535 | 10.3008 | 10.3481 | 10.3954 | 10.4427 | 10.49 | 10.5373 | 10.5493 | 10.5613 | 10.5732 | 10.5852 | 10.5972 | 10.6091 | 10.6211 | 10.6331 | 10.645 | 10.657 | 10.669 | 10.6809 | 10.6929 | 10.7049 | 10.7168 | 10.7288 | 10.7408 | 10.7527 | 10.7647 | 10.7767 | 10.7886 | 10.8006 | 10.8126 | 10.8245 | 10.8365 | 10.8485 | 10.8604 | 10.8724 | 10.8844 | 10.8963 | 10.8969 | 10.8974 | 10.898 | 10.8986 | 10.8991 | 10.8997 | 10.9002 | 10.9008 | 10.9013 | 10.9019 | 10.9024 | 10.903 | 10.9036 | 10.9041 | 10.9047 | 10.9052 | 10.9058 | 10.9063 | 10.9069 | 10.9074 | 10.908 | 10.9086 | 10.9091 | 10.9097 | 10.9102 | 10.9108 | 10.9113 | 10.9119 | 10.9124 | 10.913 | 10.913 | 10.913 | 10.913 | 10.913 | 10.913 | 10.913 | 10.913 | 10.913 | 10.913 | 10.913 | 10.913 | 10.913 | 10.913 | 10.913 | 10.913 | 10.913 | 10.913 | 10.913 | 10.913 | 10.913 | 10.913 | 10.913 | 10.913 | 10.913 | 10.913 | 10.913 | 10.913 | 10.913 | 10.913 | 10.913 | 10.9122 | 10.9113 | 10.9105 | 10.9097 | 10.9088 | 10.908 | 10.9072 | 10.9063 | 10.9055 | 10.9047 | 10.9038 | 10.903 | 10.9022 | 10.9013 | 10.9005 | 10.8997 | 10.8988 | 10.898 | 10.8972 | 10.8963 | 10.8955 | 10.8947 | 10.8938 | 10.893 | 10.8922 | 10.8913 | 10.8905 | 10.8897 | 10.8888 | 10.888
4.1 | 0 | 0.44333 | 0.88667 | 1.33 | 1.7733 | 2.2167 | 2.66 | 3.1033 | 3.5467 | 3.99 | 4.4333 | 4.8461 | 5.2589 | 5.6717 | 6.0845 | 6.4973 | 6.7905 | 7.0837 | 7.3769 | 7.6701 | 7.9633 | 8.0918 | 8.2203 | 8.3487 | 8.4772 | 8.6057 | 8.7341 | 8.8626 | 8.9911 | 9.1195 | 9.248 | 9.3232 | 9.3983 | 9.4735 | 9.5486 | 9.6238 | 9.6989 | 9.7741 | 9.8492 | 9.9244 | 9.9996 | 10.0747 | 10.1499 | 10.225 | 10.3002 | 10.3753 | 10.4273 | 10.4792 | 10.5312 | 10.5832 | 10.6351 | 10.6871 | 10.739 | 10.791 | 10.8429 | 10.8949 | 10.9468 | 10.9988 | 11.0508 | 11.1027 | 11.1547 | 11.1679 | 11.1812 | 11.1945 | 11.2077 | 11.221 | 11.2343 | 11.2475 | 11.2608 | 11.2741 | 11.2873 | 11.3006 | 11.3139 | 11.3271 | 11.3404 | 11.3537 | 11.3669 | 11.3802 | 11.3935 | 11.4067 | 11.42 | 11.4333 | 11.4465 | 11.4598 | 11.4731 | 11.4863 | 11.4996 | 11.5129 | 11.5261 | 11.5394 | 11.5527 | 11.5538 | 11.5549 | 11.556 | 11.5571 | 11.5582 | 11.5593 | 11.5604 | 11.5616 | 11.5627 | 11.5638 | 11.5649 | 11.566 | 11.5671 | 11.5682 | 11.5693 | 11.5704 | 11.5716 | 11.5727 | 11.5738 | 11.5749 | 11.576 | 11.5771 | 11.5782 | 11.5793 | 11.5804 | 11.5816 | 11.5827 | 11.5838 | 11.5849 | 11.586 | 11.586 | 11.586 | 11.586 | 11.586 | 11.586 | 11.586 | 11.586 | 11.586 | 11.586 | 11.586 | 11.586 | 11.586 | 11.586 | 11.586 | 11.586 | 11.586 | 11.586 | 11.586 | 11.586 | 11.586 | 11.586 | 11.586 | 11.586 | 11.586 | 11.586 | 11.586 | 11.586 | 11.586 | 11.586 | 11.586 | 11.5843 | 11.5827 | 11.581 | 11.5793 | 11.5777 | 11.576 | 11.5743 | 11.5727 | 11.571 | 11.5693 | 11.5677 | 11.566 | 11.5643 | 11.5627 | 11.561 | 11.5593 | 11.5577 | 11.556 | 11.5543 | 11.5527 | 11.551 | 11.5493 | 11.5477 | 11.546 | 11.5443 | 11.5427 | 11.541 | 11.5393 | 11.5377 | 11.536
4.15 | 0 | 0.465 | 0.93 | 1.395 | 1.86 | 2.325 | 2.79 | 3.255 | 3.72 | 4.185 | 4.65 | 5.0932 | 5.5364 | 5.9796 | 6.4228 | 6.866 | 7.1618 | 7.4576 | 7.7534 | 8.0492 | 8.345 | 8.4817 | 8.6184 | 8.7551 | 8.8918 | 9.0285 | 9.1652 | 9.3019 | 9.4386 | 9.5753 | 9.712 | 9.7927 | 9.8735 | 9.9542 | 10.0349 | 10.1157 | 10.1964 | 10.2771 | 10.3579 | 10.4386 | 10.5193 | 10.6001 | 10.6808 | 10.7615 | 10.8423 | 10.923 | 10.9796 | 11.0362 | 11.0928 | 11.1494 | 11.206 | 11.2626 | 11.3192 | 11.3758 | 11.4324 | 11.489 | 11.5456 | 11.6022 | 11.6588 | 11.7154 | 11.772 | 11.7866 | 11.8011 | 11.8157 | 11.8303 | 11.8448 | 11.8594 | 11.874 | 11.8885 | 11.9031 | 11.9177 | 11.9322 | 11.9468 | 11.9614 | 11.9759 | 11.9905 | 12.0051 | 12.0196 | 12.0342 | 12.0488 | 12.0633 | 12.0779 | 12.0925 | 12.107 | 12.1216 | 12.1362 | 12.1507 | 12.1653 | 12.1799 | 12.1944 | 12.209 | 12.2107 | 12.2123 | 12.214 | 12.2157 | 12.2173 | 12.219 | 12.2207 | 12.2223 | 12.224 | 12.2257 | 12.2273 | 12.229 | 12.2307 | 12.2323 | 12.234 | 12.2357 | 12.2373 | 12.239 | 12.2407 | 12.2423 | 12.244 | 12.2457 | 12.2473 | 12.249 | 12.2507 | 12.2523 | 12.254 | 12.2557 | 12.2573 | 12.259 | 12.259 | 12.259 | 12.259 | 12.259 | 12.259 | 12.259 | 12.259 | 12.259 | 12.259 | 12.259 | 12.259 | 12.259 | 12.259 | 12.259 | 12.259 | 12.259 | 12.259 | 12.259 | 12.259 | 12.259 | 12.259 | 12.259 | 12.259 | 12.259 | 12.259 | 12.259 | 12.259 | 12.259 | 12.259 | 12.259 | 12.2565 | 12.254 | 12.2515 | 12.249 | 12.2465 | 12.244 | 12.2415 | 12.239 | 12.2365 | 12.234 | 12.2315 | 12.229 | 12.2265 | 12.224 | 12.2215 | 12.219 | 12.2165 | 12.214 | 12.2115 | 12.209 | 12.2065 | 12.204 | 12.2015 | 12.199 | 12.1965 | 12.194 | 12.1915 | 12.189 | 12.1865 | 12.184
4.2 | 0 | 0.48667 | 0.97333 | 1.46 | 1.9467 | 2.4333 | 2.92 | 3.4067 | 3.8933 | 4.38 | 4.8667 | 5.3403 | 5.8139 | 6.2875 | 6.7611 | 7.2347 | 7.5331 | 7.8315 | 8.1299 | 8.4283 | 8.7267 | 8.8716 | 9.0165 | 9.1615 | 9.3064 | 9.4513 | 9.5963 | 9.7412 | 9.8861 | 10.0311 | 10.176 | 10.2623 | 10.3486 | 10.4349 | 10.5212 | 10.6076 | 10.6939 | 10.7802 | 10.8665 | 10.9528 | 11.0391 | 11.1254 | 11.2117 | 11.298 | 11.3844 | 11.4707 | 11.5319 | 11.5932 | 11.6544 | 11.7156 | 11.7769 | 11.8381 | 11.8994 | 11.9606 | 12.0219 | 12.0831 | 12.1444 | 12.2056 | 12.2668 | 12.3281 | 12.3893 | 12.4052 | 12.4211 | 12.4369 | 12.4528 | 12.4687 | 12.4845 | 12.5004 | 12.5163 | 12.5321 | 12.548 | 12.5639 | 12.5797 | 12.5956 | 12.6115 | 12.6273 | 12.6432 | 12.6591 | 12.6749 | 12.6908 | 12.7067 | 12.7225 | 12.7384 | 12.7543 | 12.7701 | 12.786 | 12.8019 | 12.8177 | 12.8336 | 12.8495 | 12.8653 | 12.8676 | 12.8698 | 12.872 | 12.8742 | 12.8764 | 12.8787 | 12.8809 | 12.8831 | 12.8853 | 12.8876 | 12.8898 | 12.892 | 12.8942 | 12.8964 | 12.8987 | 12.9009 | 12.9031 | 12.9053 | 12.9076 | 12.9098 | 12.912 | 12.9142 | 12.9164 | 12.9187 | 12.9209 | 12.9231 | 12.9253 | 12.9276 | 12.9298 | 12.932 | 12.932 | 12.932 | 12.932 | 12.932 | 12.932 | 12.932 | 12.932 | 12.932 | 12.932 | 12.932 | 12.932 | 12.932 | 12.932 | 12.932 | 12.932 | 12.932 | 12.932 | 12.932 | 12.932 | 12.932 | 12.932 | 12.932 | 12.932 | 12.932 | 12.932 | 12.932 | 12.932 | 12.932 | 12.932 | 12.932 | 12.9287 | 12.9253 | 12.922 | 12.9187 | 12.9153 | 12.912 | 12.9087 | 12.9053 | 12.902 | 12.8987 | 12.8953 | 12.892 | 12.8887 | 12.8853 | 12.882 | 12.8787 | 12.8753 | 12.872 | 12.8687 | 12.8653 | 12.862 | 12.8587 | 12.8553 | 12.852 | 12.8487 | 12.8453 | 12.842 | 12.8387 | 12.8353 | 12.832
4.25 | 0 | 0.50833 | 1.0167 | 1.525 | 2.0333 | 2.5417 | 3.05 | 3.5583 | 4.0667 | 4.575 | 5.0833 | 5.5873 | 6.0913 | 6.5953 | 7.0993 | 7.6033 | 7.9043 | 8.2053 | 8.5063 | 8.8073 | 9.1083 | 9.2615 | 9.4147 | 9.5678 | 9.721 | 9.8742 | 10.0273 | 10.1805 | 10.3337 | 10.4868 | 10.64 | 10.7319 | 10.8238 | 10.9157 | 11.0076 | 11.0994 | 11.1913 | 11.2832 | 11.3751 | 11.467 | 11.5589 | 11.6508 | 11.7427 | 11.8346 | 11.9264 | 12.0183 | 12.0842 | 12.1501 | 12.216 | 12.2819 | 12.3478 | 12.4137 | 12.4796 | 12.5454 | 12.6113 | 12.6772 | 12.7431 | 12.809 | 12.8749 | 12.9408 | 13.0067 | 13.0238 | 13.041 | 13.0582 | 13.0753 | 13.0925 | 13.1097 | 13.1268 | 13.144 | 13.1612 | 13.1783 | 13.1955 | 13.2127 | 13.2298 | 13.247 | 13.2642 | 13.2813 | 13.2985 | 13.3157 | 13.3328 | 13.35 | 13.3672 | 13.3843 | 13.4015 | 13.4187 | 13.4358 | 13.453 | 13.4702 | 13.4873 | 13.5045 | 13.5217 | 13.5244 | 13.5272 | 13.53 | 13.5328 | 13.5356 | 13.5383 | 13.5411 | 13.5439 | 13.5467 | 13.5494 | 13.5522 | 13.555 | 13.5578 | 13.5606 | 13.5633 | 13.5661 | 13.5689 | 13.5717 | 13.5744 | 13.5772 | 13.58 | 13.5828 | 13.5856 | 13.5883 | 13.5911 | 13.5939 | 13.5967 | 13.5994 | 13.6022 | 13.605 | 13.605 | 13.605 | 13.605 | 13.605 | 13.605 | 13.605 | 13.605 | 13.605 | 13.605 | 13.605 | 13.605 | 13.605 | 13.605 | 13.605 | 13.605 | 13.605 | 13.605 | 13.605 | 13.605 | 13.605 | 13.605 | 13.605 | 13.605 | 13.605 | 13.605 | 13.605 | 13.605 | 13.605 | 13.605 | 13.605 | 13.6008 | 13.5967 | 13.5925 | 13.5883 | 13.5842 | 13.58 | 13.5758 | 13.5717 | 13.5675 | 13.5633 | 13.5592 | 13.555 | 13.5508 | 13.5467 | 13.5425 | 13.5383 | 13.5342 | 13.53 | 13.5258 | 13.5217 | 13.5175 | 13.5133 | 13.5092 | 13.505 | 13.5008 | 13.4967 | 13.4925 | 13.4883 | 13.4842 | 13.48
4.3 | 0 | 0.53 | 1.06 | 1.59 | 2.12 | 2.65 | 3.18 | 3.71 | 4.24 | 4.77 | 5.3 | 5.8344 | 6.3688 | 6.9032 | 7.4376 | 7.972 | 8.2756 | 8.5792 | 8.8828 | 9.1864 | 9.49 | 9.6514 | 9.8128 | 9.9742 | 10.1356 | 10.297 | 10.4584 | 10.6198 | 10.7812 | 10.9426 | 11.104 | 11.2015 | 11.2989 | 11.3964 | 11.4939 | 11.5913 | 11.6888 | 11.7863 | 11.8837 | 11.9812 | 12.0787 | 12.1761 | 12.2736 | 12.3711 | 12.4685 | 12.566 | 12.6365 | 12.7071 | 12.7776 | 12.8481 | 12.9187 | 12.9892 | 13.0597 | 13.1303 | 13.2008 | 13.2713 | 13.3419 | 13.4124 | 13.4829 | 13.5535 | 13.624 | 13.6425 | 13.6609 | 13.6794 | 13.6979 | 13.7163 | 13.7348 | 13.7533 | 13.7717 | 13.7902 | 13.8087 | 13.8271 | 13.8456 | 13.8641 | 13.8825 | 13.901 | 13.9195 | 13.9379 | 13.9564 | 13.9749 | 13.9933 | 14.0118 | 14.0303 | 14.0487 | 14.0672 | 14.0857 | 14.1041 | 14.1226 | 14.1411 | 14.1595 | 14.178 | 14.1813 | 14.1847 | 14.188 | 14.1913 | 14.1947 | 14.198 | 14.2013 | 14.2047 | 14.208 | 14.2113 | 14.2147 | 14.218 | 14.2213 | 14.2247 | 14.228 | 14.2313 | 14.2347 | 14.238 | 14.2413 | 14.2447 | 14.248 | 14.2513 | 14.2547 | 14.258 | 14.2613 | 14.2647 | 14.268 | 14.2713 | 14.2747 | 14.278 | 14.278 | 14.278 | 14.278 | 14.278 | 14.278 | 14.278 | 14.278 | 14.278 | 14.278 | 14.278 | 14.278 | 14.278 | 14.278 | 14.278 | 14.278 | 14.278 | 14.278 | 14.278 | 14.278 | 14.278 | 14.278 | 14.278 | 14.278 | 14.278 | 14.278 | 14.278 | 14.278 | 14.278 | 14.278 | 14.278 | 14.273 | 14.268 | 14.263 | 14.258 | 14.253 | 14.248 | 14.243 | 14.238 | 14.233 | 14.228 | 14.223 | 14.218 | 14.213 | 14.208 | 14.203 | 14.198 | 14.193 | 14.188 | 14.183 | 14.178 | 14.173 | 14.168 | 14.163 | 14.158 | 14.153 | 14.148 | 14.143 | 14.138 | 14.133 | 14.128
4.35 | 0 | 0.55167 | 1.1033 | 1.655 | 2.2067 | 2.7583 | 3.31 | 3.8617 | 4.4133 | 4.965 | 5.5167 | 6.0815 | 6.6463 | 7.2111 | 7.7759 | 8.3407 | 8.6469 | 8.9531 | 9.2593 | 9.5655 | 9.8717 | 10.0413 | 10.2109 | 10.3806 | 10.5502 | 10.7198 | 10.8895 | 11.0591 | 11.2287 | 11.3984 | 11.568 | 11.671 | 11.7741 | 11.8771 | 11.9802 | 12.0832 | 12.1863 | 12.2893 | 12.3924 | 12.4954 | 12.5984 | 12.7015 | 12.8045 | 12.9076 | 13.0106 | 13.1137 | 13.1888 | 13.264 | 13.3392 | 13.4144 | 13.4896 | 13.5647 | 13.6399 | 13.7151 | 13.7903 | 13.8654 | 13.9406 | 14.0158 | 14.091 | 14.1662 | 14.2413 | 14.2611 | 14.2809 | 14.3006 | 14.3204 | 14.3402 | 14.3599 | 14.3797 | 14.3995 | 14.4192 | 14.439 | 14.4588 | 14.4785 | 14.4983 | 14.5181 | 14.5378 | 14.5576 | 14.5774 | 14.5971 | 14.6169 | 14.6367 | 14.6564 | 14.6762 | 14.696 | 14.7157 | 14.7355 | 14.7553 | 14.775 | 14.7948 | 14.8146 | 14.8343 | 14.8382 | 14.8421 | 14.846 | 14.8499 | 14.8538 | 14.8577 | 14.8616 | 14.8654 | 14.8693 | 14.8732 | 14.8771 | 14.881 | 14.8849 | 14.8888 | 14.8927 | 14.8966 | 14.9004 | 14.9043 | 14.9082 | 14.9121 | 14.916 | 14.9199 | 14.9238 | 14.9277 | 14.9316 | 14.9354 | 14.9393 | 14.9432 | 14.9471 | 14.951 | 14.951 | 14.951 | 14.951 | 14.951 | 14.951 | 14.951 | 14.951 | 14.951 | 14.951 | 14.951 | 14.951 | 14.951 | 14.951 | 14.951 | 14.951 | 14.951 | 14.951 | 14.951 | 14.951 | 14.951 | 14.951 | 14.951 | 14.951 | 14.951 | 14.951 | 14.951 | 14.951 | 14.951 | 14.951 | 14.951 | 14.9452 | 14.9393 | 14.9335 | 14.9277 | 14.9218 | 14.916 | 14.9102 | 14.9043 | 14.8985 | 14.8927 | 14.8868 | 14.881 | 14.8752 | 14.8693 | 14.8635 | 14.8577 | 14.8518 | 14.846 | 14.8402 | 14.8343 | 14.8285 | 14.8227 | 14.8168 | 14.811 | 14.8052 | 14.7993 | 14.7935 | 14.7877 | 14.7818 | 14.776
4.4 | 0 | 0.57333 | 1.1467 | 1.72 | 2.2933 | 2.8667 | 3.44 | 4.0133 | 4.5867 | 5.16 | 5.7333 | 6.3285 | 6.9237 | 7.5189 | 8.1141 | 8.7093 | 9.0181 | 9.3269 | 9.6357 | 9.9445 | 10.2533 | 10.4312 | 10.6091 | 10.7869 | 10.9648 | 11.1427 | 11.3205 | 11.4984 | 11.6763 | 11.8541 | 12.032 | 12.1406 | 12.2492 | 12.3579 | 12.4665 | 12.5751 | 12.6837 | 12.7924 | 12.901 | 13.0096 | 13.1182 | 13.2268 | 13.3355 | 13.4441 | 13.5527 | 13.6613 | 13.7412 | 13.821 | 13.9008 | 13.9806 | 14.0604 | 14.1403 | 14.2201 | 14.2999 | 14.3797 | 14.4596 | 14.5394 | 14.6192 | 14.699 | 14.7788 | 14.8587 | 14.8797 | 14.9008 | 14.9219 | 14.9429 | 14.964 | 14.9851 | 15.0061 | 15.0272 | 15.0483 | 15.0693 | 15.0904 | 15.1115 | 15.1325 | 15.1536 | 15.1747 | 15.1957 | 15.2168 | 15.2379 | 15.2589 | 15.28 | 15.3011 | 15.3221 | 15.3432 | 15.3643 | 15.3853 | 15.4064 | 15.4275 | 15.4485 | 15.4696 | 15.4907 | 15.4951 | 15.4996 | 15.504 | 15.5084 | 15.5129 | 15.5173 | 15.5218 | 15.5262 | 15.5307 | 15.5351 | 15.5396 | 15.544 | 15.5484 | 15.5529 | 15.5573 | 15.5618 | 15.5662 | 15.5707 | 15.5751 | 15.5796 | 15.584 | 15.5884 | 15.5929 | 15.5973 | 15.6018 | 15.6062 | 15.6107 | 15.6151 | 15.6196 | 15.624 | 15.624 | 15.624 | 15.624 | 15.624 | 15.624 | 15.624 | 15.624 | 15.624 | 15.624 | 15.624 | 15.624 | 15.624 | 15.624 | 15.624 | 15.624 | 15.624 | 15.624 | 15.624 | 15.624 | 15.624 | 15.624 | 15.624 | 15.624 | 15.624 | 15.624 | 15.624 | 15.624 | 15.624 | 15.624 | 15.624 | 15.6173 | 15.6107 | 15.604 | 15.5973 | 15.5907 | 15.584 | 15.5773 | 15.5707 | 15.564 | 15.5573 | 15.5507 | 15.544 | 15.5373 | 15.5307 | 15.524 | 15.5173 | 15.5107 | 15.504 | 15.4973 | 15.4907 | 15.484 | 15.4773 | 15.4707 | 15.464 | 15.4573 | 15.4507 | 15.444 | 15.4373 | 15.4307 | 15.424
4.45 | 0 | 0.595 | 1.19 | 1.785 | 2.38 | 2.975 | 3.57 | 4.165 | 4.76 | 5.355 | 5.95 | 6.5756 | 7.2012 | 7.8268 | 8.4524 | 9.078 | 9.3894 | 9.7008 | 10.0122 | 10.3236 | 10.635 | 10.8211 | 11.0072 | 11.1933 | 11.3794 | 11.5655 | 11.7516 | 11.9377 | 12.1238 | 12.3099 | 12.496 | 12.6102 | 12.7244 | 12.8386 | 12.9528 | 13.067 | 13.1812 | 13.2954 | 13.4096 | 13.5238 | 13.638 | 13.7522 | 13.8664 | 13.9806 | 14.0948 | 14.209 | 14.2935 | 14.3779 | 14.4624 | 14.5469 | 14.6313 | 14.7158 | 14.8003 | 14.8847 | 14.9692 | 15.0537 | 15.1381 | 15.2226 | 15.3071 | 15.3915 | 15.476 | 15.4984 | 15.5207 | 15.5431 | 15.5655 | 15.5878 | 15.6102 | 15.6326 | 15.6549 | 15.6773 | 15.6997 | 15.722 | 15.7444 | 15.7668 | 15.7891 | 15.8115 | 15.8339 | 15.8562 | 15.8786 | 15.901 | 15.9233 | 15.9457 | 15.9681 | 15.9904 | 16.0128 | 16.0352 | 16.0575 | 16.0799 | 16.1023 | 16.1246 | 16.147 | 16.152 | 16.157 | 16.162 | 16.167 | 16.172 | 16.177 | 16.182 | 16.187 | 16.192 | 16.197 | 16.202 | 16.207 | 16.212 | 16.217 | 16.222 | 16.227 | 16.232 | 16.237 | 16.242 | 16.247 | 16.252 | 16.257 | 16.262 | 16.267 | 16.272 | 16.277 | 16.282 | 16.287 | 16.292 | 16.297 | 16.297 | 16.297 | 16.297 | 16.297 | 16.297 | 16.297 | 16.297 | 16.297 | 16.297 | 16.297 | 16.297 | 16.297 | 16.297 | 16.297 | 16.297 | 16.297 | 16.297 | 16.297 | 16.297 | 16.297 | 16.297 | 16.297 | 16.297 | 16.297 | 16.297 | 16.297 | 16.297 | 16.297 | 16.297 | 16.297 | 16.2895 | 16.282 | 16.2745 | 16.267 | 16.2595 | 16.252 | 16.2445 | 16.237 | 16.2295 | 16.222 | 16.2145 | 16.207 | 16.1995 | 16.192 | 16.1845 | 16.177 | 16.1695 | 16.162 | 16.1545 | 16.147 | 16.1395 | 16.132 | 16.1245 | 16.117 | 16.1095 | 16.102 | 16.0945 | 16.087 | 16.0795 | 16.072
4.5 | 0 | 0.61667 | 1.2333 | 1.85 | 2.4667 | 3.0833 | 3.7 | 4.3167 | 4.9333 | 5.55 | 6.1667 | 6.8227 | 7.4787 | 8.1347 | 8.7907 | 9.4467 | 9.7607 | 10.0747 | 10.3887 | 10.7027 | 11.0167 | 11.211 | 11.4053 | 11.5997 | 11.794 | 11.9883 | 12.1827 | 12.377 | 12.5713 | 12.7657 | 12.96 | 13.0798 | 13.1996 | 13.3193 | 13.4391 | 13.5589 | 13.6787 | 13.7984 | 13.9182 | 14.038 | 14.1578 | 14.2776 | 14.3973 | 14.5171 | 14.6369 | 14.7567 | 14.8458 | 14.9349 | 15.024 | 15.1131 | 15.2022 | 15.2913 | 15.3804 | 15.4696 | 15.5587 | 15.6478 | 15.7369 | 15.826 | 15.9151 | 16.0042 | 16.0933 | 16.117 | 16.1407 | 16.1643 | 16.188 | 16.2117 | 16.2353 | 16.259 | 16.2827 | 16.3063 | 16.33 | 16.3537 | 16.3773 | 16.401 | 16.4247 | 16.4483 | 16.472 | 16.4957 | 16.5193 | 16.543 | 16.5667 | 16.5903 | 16.614 | 16.6377 | 16.6613 | 16.685 | 16.7087 | 16.7323 | 16.756 | 16.7797 | 16.8033 | 16.8089 | 16.8144 | 16.82 | 16.8256 | 16.8311 | 16.8367 | 16.8422 | 16.8478 | 16.8533 | 16.8589 | 16.8644 | 16.87 | 16.8756 | 16.8811 | 16.8867 | 16.8922 | 16.8978 | 16.9033 | 16.9089 | 16.9144 | 16.92 | 16.9256 | 16.9311 | 16.9367 | 16.9422 | 16.9478 | 16.9533 | 16.9589 | 16.9644 | 16.97 | 16.97 | 16.97 | 16.97 | 16.97 | 16.97 | 16.97 | 16.97 | 16.97 | 16.97 | 16.97 | 16.97 | 16.97 | 16.97 | 16.97 | 16.97 | 16.97 | 16.97 | 16.97 | 16.97 | 16.97 | 16.97 | 16.97 | 16.97 | 16.97 | 16.97 | 16.97 | 16.97 | 16.97 | 16.97 | 16.97 | 16.9617 | 16.9533 | 16.945 | 16.9367 | 16.9283 | 16.92 | 16.9117 | 16.9033 | 16.895 | 16.8867 | 16.8783 | 16.87 | 16.8617 | 16.8533 | 16.845 | 16.8367 | 16.8283 | 16.82 | 16.8117 | 16.8033 | 16.795 | 16.7867 | 16.7783 | 16.77 | 16.7617 | 16.7533 | 16.745 | 16.7367 | 16.7283 | 16.72
4.55 | 0 | 0.63833 | 1.2767 | 1.915 | 2.5533 | 3.1917 | 3.83 | 4.4683 | 5.1067 | 5.745 | 6.3833 | 7.0697 | 7.7561 | 8.4425 | 9.1289 | 9.8153 | 10.1319 | 10.4485 | 10.7651 | 11.0817 | 11.3983 | 11.6009 | 11.8035 | 12.006 | 12.2086 | 12.4112 | 12.6137 | 12.8163 | 13.0189 | 13.2214 | 13.424 | 13.5494 | 13.6747 | 13.8001 | 13.9254 | 14.0508 | 14.1761 | 14.3015 | 14.4268 | 14.5522 | 14.6776 | 14.8029 | 14.9283 | 15.0536 | 15.179 | 15.3043 | 15.3981 | 15.4918 | 15.5856 | 15.6794 | 15.7731 | 15.8669 | 15.9606 | 16.0544 | 16.1481 | 16.2419 | 16.3356 | 16.4294 | 16.5232 | 16.6169 | 16.7107 | 16.7356 | 16.7606 | 16.7856 | 16.8105 | 16.8355 | 16.8605 | 16.8854 | 16.9104 | 16.9354 | 16.9603 | 16.9853 | 17.0103 | 17.0352 | 17.0602 | 17.0852 | 17.1101 | 17.1351 | 17.1601 | 17.185 | 17.21 | 17.235 | 17.2599 | 17.2849 | 17.3099 | 17.3348 | 17.3598 | 17.3848 | 17.4097 | 17.4347 | 17.4597 | 17.4658 | 17.4719 | 17.478 | 17.4841 | 17.4902 | 17.4963 | 17.5024 | 17.5086 | 17.5147 | 17.5208 | 17.5269 | 17.533 | 17.5391 | 17.5452 | 17.5513 | 17.5574 | 17.5636 | 17.5697 | 17.5758 | 17.5819 | 17.588 | 17.5941 | 17.6002 | 17.6063 | 17.6124 | 17.6186 | 17.6247 | 17.6308 | 17.6369 | 17.643 | 17.643 | 17.643 | 17.643 | 17.643 | 17.643 | 17.643 | 17.643 | 17.643 | 17.643 | 17.643 | 17.643 | 17.643 | 17.643 | 17.643 | 17.643 | 17.643 | 17.643 | 17.643 | 17.643 | 17.643 | 17.643 | 17.643 | 17.643 | 17.643 | 17.643 | 17.643 | 17.643 | 17.643 | 17.643 | 17.643 | 17.6338 | 17.6247 | 17.6155 | 17.6063 | 17.5972 | 17.588 | 17.5788 | 17.5697 | 17.5605 | 17.5513 | 17.5422 | 17.533 | 17.5238 | 17.5147 | 17.5055 | 17.4963 | 17.4872 | 17.478 | 17.4688 | 17.4597 | 17.4505 | 17.4413 | 17.4322 | 17.423 | 17.4138 | 17.4047 | 17.3955 | 17.3863 | 17.3772 | 17.368
4.6 | 0 | 0.66 | 1.32 | 1.98 | 2.64 | 3.3 | 3.96 | 4.62 | 5.28 | 5.94 | 6.6 | 7.3168 | 8.0336 | 8.7504 | 9.4672 | 10.184 | 10.5032 | 10.8224 | 11.1416 | 11.4608 | 11.78 | 11.9908 | 12.2016 | 12.4124 | 12.6232 | 12.834 | 13.0448 | 13.2556 | 13.4664 | 13.6772 | 13.888 | 14.0189 | 14.1499 | 14.2808 | 14.4117 | 14.5427 | 14.6736 | 14.8045 | 14.9355 | 15.0664 | 15.1973 | 15.3283 | 15.4592 | 15.5901 | 15.7211 | 15.852 | 15.9504 | 16.0488 | 16.1472 | 16.2456 | 16.344 | 16.4424 | 16.5408 | 16.6392 | 16.7376 | 16.836 | 16.9344 | 17.0328 | 17.1312 | 17.2296 | 17.328 | 17.3543 | 17.3805 | 17.4068 | 17.4331 | 17.4593 | 17.4856 | 17.5119 | 17.5381 | 17.5644 | 17.5907 | 17.6169 | 17.6432 | 17.6695 | 17.6957 | 17.722 | 17.7483 | 17.7745 | 17.8008 | 17.8271 | 17.8533 | 17.8796 | 17.9059 | 17.9321 | 17.9584 | 17.9847 | 18.0109 | 18.0372 | 18.0635 | 18.0897 | 18.116 | 18.1227 | 18.1293 | 18.136 | 18.1427 | 18.1493 | 18.156 | 18.1627 | 18.1693 | 18.176 | 18.1827 | 18.1893 | 18.196 | 18.2027 | 18.2093 | 18.216 | 18.2227 | 18.2293 | 18.236 | 18.2427 | 18.2493 | 18.256 | 18.2627 | 18.2693 | 18.276 | 18.2827 | 18.2893 | 18.296 | 18.3027 | 18.3093 | 18.316 | 18.316 | 18.316 | 18.316 | 18.316 | 18.316 | 18.316 | 18.316 | 18.316 | 18.316 | 18.316 | 18.316 | 18.316 | 18.316 | 18.316 | 18.316 | 18.316 | 18.316 | 18.316 | 18.316 | 18.316 | 18.316 | 18.316 | 18.316 | 18.316 | 18.316 | 18.316 | 18.316 | 18.316 | 18.316 | 18.316 | 18.306 | 18.296 | 18.286 | 18.276 | 18.266 | 18.256 | 18.246 | 18.236 | 18.226 | 18.216 | 18.206 | 18.196 | 18.186 | 18.176 | 18.166 | 18.156 | 18.146 | 18.136 | 18.126 | 18.116 | 18.106 | 18.096 | 18.086 | 18.076 | 18.066 | 18.056 | 18.046 | 18.036 | 18.026 | 18.016
4.65 | 0 | 0.68167 | 1.3633 | 2.045 | 2.7267 | 3.4083 | 4.09 | 4.7717 | 5.4533 | 6.135 | 6.8167 | 7.5639 | 8.3111 | 9.0583 | 9.8055 | 10.5527 | 10.8745 | 11.1963 | 11.5181 | 11.8399 | 12.1617 | 12.3807 | 12.5997 | 12.8188 | 13.0378 | 13.2568 | 13.4759 | 13.6949 | 13.9139 | 14.133 | 14.352 | 14.4885 | 14.625 | 14.7615 | 14.898 | 15.0346 | 15.1711 | 15.3076 | 15.4441 | 15.5806 | 15.7171 | 15.8536 | 15.9901 | 16.1266 | 16.2632 | 16.3997 | 16.5027 | 16.6058 | 16.7088 | 16.8118 | 16.9149 | 17.0179 | 17.121 | 17.224 | 17.3271 | 17.4301 | 17.5332 | 17.6362 | 17.7392 | 17.8423 | 17.9453 | 17.9729 | 18.0005 | 18.028 | 18.0556 | 18.0832 | 18.1107 | 18.1383 | 18.1659 | 18.1934 | 18.221 | 18.2486 | 18.2761 | 18.3037 | 18.3313 | 18.3588 | 18.3864 | 18.414 | 18.4415 | 18.4691 | 18.4967 | 18.5242 | 18.5518 | 18.5794 | 18.6069 | 18.6345 | 18.6621 | 18.6896 | 18.7172 | 18.7448 | 18.7723 | 18.7796 | 18.7868 | 18.794 | 18.8012 | 18.8084 | 18.8157 | 18.8229 | 18.8301 | 18.8373 | 18.8446 | 18.8518 | 18.859 | 18.8662 | 18.8734 | 18.8807 | 18.8879 | 18.8951 | 18.9023 | 18.9096 | 18.9168 | 18.924 | 18.9312 | 18.9384 | 18.9457 | 18.9529 | 18.9601 | 18.9673 | 18.9746 | 18.9818 | 18.989 | 18.989 | 18.989 | 18.989 | 18.989 | 18.989 | 18.989 | 18.989 | 18.989 | 18.989 | 18.989 | 18.989 | 18.989 | 18.989 | 18.989 | 18.989 | 18.989 | 18.989 | 18.989 | 18.989 | 18.989 | 18.989 | 18.989 | 18.989 | 18.989 | 18.989 | 18.989 | 18.989 | 18.989 | 18.989 | 18.989 | 18.9782 | 18.9673 | 18.9565 | 18.9457 | 18.9348 | 18.924 | 18.9132 | 18.9023 | 18.8915 | 18.8807 | 18.8698 | 18.859 | 18.8482 | 18.8373 | 18.8265 | 18.8157 | 18.8048 | 18.794 | 18.7832 | 18.7723 | 18.7615 | 18.7507 | 18.7398 | 18.729 | 18.7182 | 18.7073 | 18.6965 | 18.6857 | 18.6748 | 18.664
4.7 | 0 | 0.70333 | 1.4067 | 2.11 | 2.8133 | 3.5167 | 4.22 | 4.9233 | 5.6267 | 6.33 | 7.0333 | 7.8109 | 8.5885 | 9.3661 | 10.1437 | 10.9213 | 11.2457 | 11.5701 | 11.8945 | 12.2189 | 12.5433 | 12.7706 | 12.9979 | 13.2251 | 13.4524 | 13.6797 | 13.9069 | 14.1342 | 14.3615 | 14.5887 | 14.816 | 14.9581 | 15.1002 | 15.2423 | 15.3844 | 15.5264 | 15.6685 | 15.8106 | 15.9527 | 16.0948 | 16.2369 | 16.379 | 16.5211 | 16.6632 | 16.8052 | 16.9473 | 17.055 | 17.1627 | 17.2704 | 17.3781 | 17.4858 | 17.5935 | 17.7012 | 17.8088 | 17.9165 | 18.0242 | 18.1319 | 18.2396 | 18.3473 | 18.455 | 18.5627 | 18.5915 | 18.6204 | 18.6493 | 18.6781 | 18.707 | 18.7359 | 18.7647 | 18.7936 | 18.8225 | 18.8513 | 18.8802 | 18.9091 | 18.9379 | 18.9668 | 18.9957 | 19.0245 | 19.0534 | 19.0823 | 19.1111 | 19.14 | 19.1689 | 19.1977 | 19.2266 | 19.2555 | 19.2843 | 19.3132 | 19.3421 | 19.3709 | 19.3998 | 19.4287 | 19.4364 | 19.4442 | 19.452 | 19.4598 | 19.4676 | 19.4753 | 19.4831 | 19.4909 | 19.4987 | 19.5064 | 19.5142 | 19.522 | 19.5298 | 19.5376 | 19.5453 | 19.5531 | 19.5609 | 19.5687 | 19.5764 | 19.5842 | 19.592 | 19.5998 | 19.6076 | 19.6153 | 19.6231 | 19.6309 | 19.6387 | 19.6464 | 19.6542 | 19.662 | 19.662 | 19.662 | 19.662 | 19.662 | 19.662 | 19.662 | 19.662 | 19.662 | 19.662 | 19.662 | 19.662 | 19.662 | 19.662 | 19.662 | 19.662 | 19.662 | 19.662 | 19.662 | 19.662 | 19.662 | 19.662 | 19.662 | 19.662 | 19.662 | 19.662 | 19.662 | 19.662 | 19.662 | 19.662 | 19.662 | 19.6503 | 19.6387 | 19.627 | 19.6153 | 19.6037 | 19.592 | 19.5803 | 19.5687 | 19.557 | 19.5453 | 19.5337 | 19.522 | 19.5103 | 19.4987 | 19.487 | 19.4753 | 19.4637 | 19.452 | 19.4403 | 19.4287 | 19.417 | 19.4053 | 19.3937 | 19.382 | 19.3703 | 19.3587 | 19.347 | 19.3353 | 19.3237 | 19.312
4.75 | 0 | 0.725 | 1.45 | 2.175 | 2.9 | 3.625 | 4.35 | 5.075 | 5.8 | 6.525 | 7.25 | 8.058 | 8.866 | 9.674 | 10.482 | 11.29 | 11.617 | 11.944 | 12.271 | 12.598 | 12.925 | 13.1605 | 13.396 | 13.6315 | 13.867 | 14.1025 | 14.338 | 14.5735 | 14.809 | 15.0445 | 15.28 | 15.4277 | 15.5753 | 15.723 | 15.8707 | 16.0183 | 16.166 | 16.3137 | 16.4613 | 16.609 | 16.7567 | 16.9043 | 17.052 | 17.1997 | 17.3473 | 17.495 | 17.6073 | 17.7197 | 17.832 | 17.9443 | 18.0567 | 18.169 | 18.2813 | 18.3937 | 18.506 | 18.6183 | 18.7307 | 18.843 | 18.9553 | 19.0677 | 19.18 | 19.2102 | 19.2403 | 19.2705 | 19.3007 | 19.3308 | 19.361 | 19.3912 | 19.4213 | 19.4515 | 19.4817 | 19.5118 | 19.542 | 19.5722 | 19.6023 | 19.6325 | 19.6627 | 19.6928 | 19.723 | 19.7532 | 19.7833 | 19.8135 | 19.8437 | 19.8738 | 19.904 | 19.9342 | 19.9643 | 19.9945 | 20.0247 | 20.0548 | 20.085 | 20.0933 | 20.1017 | 20.11 | 20.1183 | 20.1267 | 20.135 | 20.1433 | 20.1517 | 20.16 | 20.1683 | 20.1767 | 20.185 | 20.1933 | 20.2017 | 20.21 | 20.2183 | 20.2267 | 20.235 | 20.2433 | 20.2517 | 20.26 | 20.2683 | 20.2767 | 20.285 | 20.2933 | 20.3017 | 20.31 | 20.3183 | 20.3267 | 20.335 | 20.335 | 20.335 | 20.335 | 20.335 | 20.335 | 20.335 | 20.335 | 20.335 | 20.335 | 20.335 | 20.335 | 20.335 | 20.335 | 20.335 | 20.335 | 20.335 | 20.335 | 20.335 | 20.335 | 20.335 | 20.335 | 20.335 | 20.335 | 20.335 | 20.335 | 20.335 | 20.335 | 20.335 | 20.335 | 20.335 | 20.3225 | 20.31 | 20.2975 | 20.285 | 20.2725 | 20.26 | 20.2475 | 20.235 | 20.2225 | 20.21 | 20.1975 | 20.185 | 20.1725 | 20.16 | 20.1475 | 20.135 | 20.1225 | 20.11 | 20.0975 | 20.085 | 20.0725 | 20.06 | 20.0475 | 20.035 | 20.0225 | 20.01 | 19.9975 | 19.985 | 19.9725 | 19.96
4.8 | 0 | 0.74667 | 1.4933 | 2.24 | 2.9867 | 3.7333 | 4.48 | 5.2267 | 5.9733 | 6.72 | 7.4667 | 8.3051 | 9.1435 | 9.9819 | 10.8203 | 11.6587 | 11.9883 | 12.3179 | 12.6475 | 12.9771 | 13.3067 | 13.5504 | 13.7941 | 14.0379 | 14.2816 | 14.5253 | 14.7691 | 15.0128 | 15.2565 | 15.5003 | 15.744 | 15.8972 | 16.0505 | 16.2037 | 16.357 | 16.5102 | 16.6635 | 16.8167 | 16.97 | 17.1232 | 17.2764 | 17.4297 | 17.5829 | 17.7362 | 17.8894 | 18.0427 | 18.1596 | 18.2766 | 18.3936 | 18.5106 | 18.6276 | 18.7445 | 18.8615 | 18.9785 | 19.0955 | 19.2124 | 19.3294 | 19.4464 | 19.5634 | 19.6804 | 19.7973 | 19.8288 | 19.8603 | 19.8917 | 19.9232 | 19.9547 | 19.9861 | 20.0176 | 20.0491 | 20.0805 | 20.112 | 20.1435 | 20.1749 | 20.2064 | 20.2379 | 20.2693 | 20.3008 | 20.3323 | 20.3637 | 20.3952 | 20.4267 | 20.4581 | 20.4896 | 20.5211 | 20.5525 | 20.584 | 20.6155 | 20.6469 | 20.6784 | 20.7099 | 20.7413 | 20.7502 | 20.7591 | 20.768 | 20.7769 | 20.7858 | 20.7947 | 20.8036 | 20.8124 | 20.8213 | 20.8302 | 20.8391 | 20.848 | 20.8569 | 20.8658 | 20.8747 | 20.8836 | 20.8924 | 20.9013 | 20.9102 | 20.9191 | 20.928 | 20.9369 | 20.9458 | 20.9547 | 20.9636 | 20.9724 | 20.9813 | 20.9902 | 20.9991 | 21.008 | 21.008 | 21.008 | 21.008 | 21.008 | 21.008 | 21.008 | 21.008 | 21.008 | 21.008 | 21.008 | 21.008 | 21.008 | 21.008 | 21.008 | 21.008 | 21.008 | 21.008 | 21.008 | 21.008 | 21.008 | 21.008 | 21.008 | 21.008 | 21.008 | 21.008 | 21.008 | 21.008 | 21.008 | 21.008 | 21.008 | 20.9947 | 20.9813 | 20.968 | 20.9547 | 20.9413 | 20.928 | 20.9147 | 20.9013 | 20.888 | 20.8747 | 20.8613 | 20.848 | 20.8347 | 20.8213 | 20.808 | 20.7947 | 20.7813 | 20.768 | 20.7547 | 20.7413 | 20.728 | 20.7147 | 20.7013 | 20.688 | 20.6747 | 20.6613 | 20.648 | 20.6347 | 20.6213 | 20.608
4.85 | 0 | 0.76833 | 1.5367 | 2.305 | 3.0733 | 3.8417 | 4.61 | 5.3783 | 6.1467 | 6.915 | 7.6833 | 8.5521 | 9.4209 | 10.2897 | 11.1585 | 12.0273 | 12.3595 | 12.6917 | 13.0239 | 13.3561 | 13.6883 | 13.9403 | 14.1923 | 14.4442 | 14.6962 | 14.9482 | 15.2001 | 15.4521 | 15.7041 | 15.956 | 16.208 | 16.3668 | 16.5256 | 16.6845 | 16.8433 | 17.0021 | 17.1609 | 17.3198 | 17.4786 | 17.6374 | 17.7962 | 17.955 | 18.1139 | 18.2727 | 18.4315 | 18.5903 | 18.712 | 18.8336 | 18.9552 | 19.0768 | 19.1984 | 19.3201 | 19.4417 | 19.5633 | 19.6849 | 19.8066 | 19.9282 | 20.0498 | 20.1714 | 20.293 | 20.4147 | 20.4474 | 20.4802 | 20.513 | 20.5457 | 20.5785 | 20.6113 | 20.644 | 20.6768 | 20.7096 | 20.7423 | 20.7751 | 20.8079 | 20.8406 | 20.8734 | 20.9062 | 20.9389 | 20.9717 | 21.0045 | 21.0372 | 21.07 | 21.1028 | 21.1355 | 21.1683 | 21.2011 | 21.2338 | 21.2666 | 21.2994 | 21.3321 | 21.3649 | 21.3977 | 21.4071 | 21.4166 | 21.426 | 21.4354 | 21.4449 | 21.4543 | 21.4638 | 21.4732 | 21.4827 | 21.4921 | 21.5016 | 21.511 | 21.5204 | 21.5299 | 21.5393 | 21.5488 | 21.5582 | 21.5677 | 21.5771 | 21.5866 | 21.596 | 21.6054 | 21.6149 | 21.6243 | 21.6338 | 21.6432 | 21.6527 | 21.6621 | 21.6716 | 21.681 | 21.681 | 21.681 | 21.681 | 21.681 | 21.681 | 21.681 | 21.681 | 21.681 | 21.681 | 21.681 | 21.681 | 21.681 | 21.681 | 21.681 | 21.681 | 21.681 | 21.681 | 21.681 | 21.681 | 21.681 | 21.681 | 21.681 | 21.681 | 21.681 | 21.681 | 21.681 | 21.681 | 21.681 | 21.681 | 21.681 | 21.6668 | 21.6527 | 21.6385 | 21.6243 | 21.6102 | 21.596 | 21.5818 | 21.5677 | 21.5535 | 21.5393 | 21.5252 | 21.511 | 21.4968 | 21.4827 | 21.4685 | 21.4543 | 21.4402 | 21.426 | 21.4118 | 21.3977 | 21.3835 | 21.3693 | 21.3552 | 21.341 | 21.3268 | 21.3127 | 21.2985 | 21.2843 | 21.2702 | 21.256
4.9 | 0 | 0.79 | 1.58 | 2.37 | 3.16 | 3.95 | 4.74 | 5.53 | 6.32 | 7.11 | 7.9 | 8.7992 | 9.6984 | 10.5976 | 11.4968 | 12.396 | 12.7308 | 13.0656 | 13.4004 | 13.7352 | 14.07 | 14.3302 | 14.5904 | 14.8506 | 15.1108 | 15.371 | 15.6312 | 15.8914 | 16.1516 | 16.4118 | 16.672 | 16.8364 | 17.0008 | 17.1652 | 17.3296 | 17.494 | 17.6584 | 17.8228 | 17.9872 | 18.1516 | 18.316 | 18.4804 | 18.6448 | 18.8092 | 18.9736 | 19.138 | 19.2643 | 19.3905 | 19.5168 | 19.6431 | 19.7693 | 19.8956 | 20.0219 | 20.1481 | 20.2744 | 20.4007 | 20.5269 | 20.6532 | 20.7795 | 20.9057 | 21.032 | 21.0661 | 21.1001 | 21.1342 | 21.1683 | 21.2023 | 21.2364 | 21.2705 | 21.3045 | 21.3386 | 21.3727 | 21.4067 | 21.4408 | 21.4749 | 21.5089 | 21.543 | 21.5771 | 21.6111 | 21.6452 | 21.6793 | 21.7133 | 21.7474 | 21.7815 | 21.8155 | 21.8496 | 21.8837 | 21.9177 | 21.9518 | 21.9859 | 22.0199 | 22.054 | 22.064 | 22.074 | 22.084 | 22.094 | 22.104 | 22.114 | 22.124 | 22.134 | 22.144 | 22.154 | 22.164 | 22.174 | 22.184 | 22.194 | 22.204 | 22.214 | 22.224 | 22.234 | 22.244 | 22.254 | 22.264 | 22.274 | 22.284 | 22.294 | 22.304 | 22.314 | 22.324 | 22.334 | 22.344 | 22.354 | 22.354 | 22.354 | 22.354 | 22.354 | 22.354 | 22.354 | 22.354 | 22.354 | 22.354 | 22.354 | 22.354 | 22.354 | 22.354 | 22.354 | 22.354 | 22.354 | 22.354 | 22.354 | 22.354 | 22.354 | 22.354 | 22.354 | 22.354 | 22.354 | 22.354 | 22.354 | 22.354 | 22.354 | 22.354 | 22.354 | 22.339 | 22.324 | 22.309 | 22.294 | 22.279 | 22.264 | 22.249 | 22.234 | 22.219 | 22.204 | 22.189 | 22.174 | 22.159 | 22.144 | 22.129 | 22.114 | 22.099 | 22.084 | 22.069 | 22.054 | 22.039 | 22.024 | 22.009 | 21.994 | 21.979 | 21.964 | 21.949 | 21.934 | 21.919 | 21.904
4.95 | 0 | 0.81167 | 1.6233 | 2.435 | 3.2467 | 4.0583 | 4.87 | 5.6817 | 6.4933 | 7.305 | 8.1167 | 9.0463 | 9.9759 | 10.9055 | 11.8351 | 12.7647 | 13.1021 | 13.4395 | 13.7769 | 14.1143 | 14.4517 | 14.7201 | 14.9885 | 15.257 | 15.5254 | 15.7938 | 16.0623 | 16.3307 | 16.5991 | 16.8676 | 17.136 | 17.306 | 17.476 | 17.6459 | 17.8159 | 17.9859 | 18.1559 | 18.3258 | 18.4958 | 18.6658 | 18.8358 | 19.0058 | 19.1757 | 19.3457 | 19.5157 | 19.6857 | 19.8166 | 19.9475 | 20.0784 | 20.2093 | 20.3402 | 20.4711 | 20.602 | 20.733 | 20.8639 | 20.9948 | 21.1257 | 21.2566 | 21.3875 | 21.5184 | 21.6493 | 21.6847 | 21.7201 | 21.7554 | 21.7908 | 21.8262 | 21.8615 | 21.8969 | 21.9323 | 21.9676 | 22.003 | 22.0384 | 22.0737 | 22.1091 | 22.1445 | 22.1798 | 22.2152 | 22.2506 | 22.2859 | 22.3213 | 22.3567 | 22.392 | 22.4274 | 22.4628 | 22.4981 | 22.5335 | 22.5689 | 22.6042 | 22.6396 | 22.675 | 22.7103 | 22.7209 | 22.7314 | 22.742 | 22.7526 | 22.7631 | 22.7737 | 22.7842 | 22.7948 | 22.8053 | 22.8159 | 22.8264 | 22.837 | 22.8476 | 22.8581 | 22.8687 | 22.8792 | 22.8898 | 22.9003 | 22.9109 | 22.9214 | 22.932 | 22.9426 | 22.9531 | 22.9637 | 22.9742 | 22.9848 | 22.9953 | 23.0059 | 23.0164 | 23.027 | 23.027 | 23.027 | 23.027 | 23.027 | 23.027 | 23.027 | 23.027 | 23.027 | 23.027 | 23.027 | 23.027 | 23.027 | 23.027 | 23.027 | 23.027 | 23.027 | 23.027 | 23.027 | 23.027 | 23.027 | 23.027 | 23.027 | 23.027 | 23.027 | 23.027 | 23.027 | 23.027 | 23.027 | 23.027 | 23.027 | 23.0112 | 22.9953 | 22.9795 | 22.9637 | 22.9478 | 22.932 | 22.9162 | 22.9003 | 22.8845 | 22.8687 | 22.8528 | 22.837 | 22.8212 | 22.8053 | 22.7895 | 22.7737 | 22.7578 | 22.742 | 22.7262 | 22.7103 | 22.6945 | 22.6787 | 22.6628 | 22.647 | 22.6312 | 22.6153 | 22.5995 | 22.5837 | 22.5678 | 22.552
5 | 0 | 0.83333 | 1.6667 | 2.5 | 3.3333 | 4.1667 | 5 | 5.8333 | 6.6667 | 7.5 | 8.3333 | 9.2933 | 10.2533 | 11.2133 | 12.1733 | 13.1333 | 13.4733 | 13.8133 | 14.1533 | 14.4933 | 14.8333 | 15.11 | 15.3867 | 15.6633 | 15.94 | 16.2167 | 16.4933 | 16.77 | 17.0467 | 17.3233 | 17.6 | 17.7756 | 17.9511 | 18.1267 | 18.3022 | 18.4778 | 18.6533 | 18.8289 | 19.0044 | 19.18 | 19.3556 | 19.5311 | 19.7067 | 19.8822 | 20.0578 | 20.2333 | 20.3689 | 20.5044 | 20.64 | 20.7756 | 20.9111 | 21.0467 | 21.1822 | 21.3178 | 21.4533 | 21.5889 | 21.7244 | 21.86 | 21.9956 | 22.1311 | 22.2667 | 22.3033 | 22.34 | 22.3767 | 22.4133 | 22.45 | 22.4867 | 22.5233 | 22.56 | 22.5967 | 22.6333 | 22.67 | 22.7067 | 22.7433 | 22.78 | 22.8167 | 22.8533 | 22.89 | 22.9267 | 22.9633 | 23 | 23.0367 | 23.0733 | 23.11 | 23.1467 | 23.1833 | 23.22 | 23.2567 | 23.2933 | 23.33 | 23.3667 | 23.3778 | 23.3889 | 23.4 | 23.4111 | 23.4222 | 23.4333 | 23.4444 | 23.4556 | 23.4667 | 23.4778 | 23.4889 | 23.5 | 23.5111 | 23.5222 | 23.5333 | 23.5444 | 23.5556 | 23.5667 | 23.5778 | 23.5889 | 23.6 | 23.6111 | 23.6222 | 23.6333 | 23.6444 | 23.6556 | 23.6667 | 23.6778 | 23.6889 | 23.7 | 23.7 | 23.7 | 23.7 | 23.7 | 23.7 | 23.7 | 23.7 | 23.7 | 23.7 | 23.7 | 23.7 | 23.7 | 23.7 | 23.7 | 23.7 | 23.7 | 23.7 | 23.7 | 23.7 | 23.7 | 23.7 | 23.7 | 23.7 | 23.7 | 23.7 | 23.7 | 23.7 | 23.7 | 23.7 | 23.7 | 23.6833 | 23.6667 | 23.65 | 23.6333 | 23.6167 | 23.6 | 23.5833 | 23.5667 | 23.55 | 23.5333 | 23.5167 | 23.5 | 23.4833 | 23.4667 | 23.45 | 23.4333 | 23.4167 | 23.4 | 23.3833 | 23.3667 | 23.35 | 23.3333 | 23.3167 | 23.3 | 23.2833 | 23.2667 | 23.25 | 23.2333 | 23.2167 | 23.2
5.05 | 0 | 0.855 | 1.71 | 2.565 | 3.42 | 4.275 | 5.13 | 5.985 | 6.84 | 7.695 | 8.55 | 9.5404 | 10.5308 | 11.5212 | 12.5116 | 13.502 | 13.8446 | 14.1872 | 14.5298 | 14.8724 | 15.215 | 15.4999 | 15.7848 | 16.0697 | 16.3546 | 16.6395 | 16.9244 | 17.2093 | 17.4942 | 17.7791 | 18.064 | 18.2451 | 18.4263 | 18.6074 | 18.7885 | 18.9697 | 19.1508 | 19.3319 | 19.5131 | 19.6942 | 19.8753 | 20.0565 | 20.2376 | 20.4187 | 20.5999 | 20.781 | 20.9212 | 21.0614 | 21.2016 | 21.3418 | 21.482 | 21.6222 | 21.7624 | 21.9026 | 22.0428 | 22.183 | 22.3232 | 22.4634 | 22.6036 | 22.7438 | 22.884 | 22.922 | 22.9599 | 22.9979 | 23.0359 | 23.0738 | 23.1118 | 23.1498 | 23.1877 | 23.2257 | 23.2637 | 23.3016 | 23.3396 | 23.3776 | 23.4155 | 23.4535 | 23.4915 | 23.5294 | 23.5674 | 23.6054 | 23.6433 | 23.6813 | 23.7193 | 23.7572 | 23.7952 | 23.8332 | 23.8711 | 23.9091 | 23.9471 | 23.985 | 24.023 | 24.0347 | 24.0463 | 24.058 | 24.0697 | 24.0813 | 24.093 | 24.1047 | 24.1163 | 24.128 | 24.1397 | 24.1513 | 24.163 | 24.1747 | 24.1863 | 24.198 | 24.2097 | 24.2213 | 24.233 | 24.2447 | 24.2563 | 24.268 | 24.2797 | 24.2913 | 24.303 | 24.3147 | 24.3263 | 24.338 | 24.3497 | 24.3613 | 24.373 | 24.373 | 24.373 | 24.373 | 24.373 | 24.373 | 24.373 | 24.373 | 24.373 | 24.373 | 24.373 | 24.373 | 24.373 | 24.373 | 24.373 | 24.373 | 24.373 | 24.373 | 24.373 | 24.373 | 24.373 | 24.373 | 24.373 | 24.373 | 24.373 | 24.373 | 24.373 | 24.373 | 24.373 | 24.373 | 24.373 | 24.3555 | 24.338 | 24.3205 | 24.303 | 24.2855 | 24.268 | 24.2505 | 24.233 | 24.2155 | 24.198 | 24.1805 | 24.163 | 24.1455 | 24.128 | 24.1105 | 24.093 | 24.0755 | 24.058 | 24.0405 | 24.023 | 24.0055 | 23.988 | 23.9705 | 23.953 | 23.9355 | 23.918 | 23.9005 | 23.883 | 23.8655 | 23.848
5.1 | 0 | 0.87667 | 1.7533 | 2.63 | 3.5067 | 4.3833 | 5.26 | 6.1367 | 7.0133 | 7.89 | 8.7667 | 9.7875 | 10.8083 | 11.8291 | 12.8499 | 13.8707 | 14.2159 | 14.5611 | 14.9063 | 15.2515 | 15.5967 | 15.8898 | 16.1829 | 16.4761 | 16.7692 | 17.0623 | 17.3555 | 17.6486 | 17.9417 | 18.2349 | 18.528 | 18.7147 | 18.9014 | 19.0881 | 19.2748 | 19.4616 | 19.6483 | 19.835 | 20.0217 | 20.2084 | 20.3951 | 20.5818 | 20.7685 | 20.9552 | 21.142 | 21.3287 | 21.4735 | 21.6184 | 21.7632 | 21.908 | 22.0529 | 22.1977 | 22.3426 | 22.4874 | 22.6323 | 22.7771 | 22.922 | 23.0668 | 23.2116 | 23.3565 | 23.5013 | 23.5406 | 23.5799 | 23.6191 | 23.6584 | 23.6977 | 23.7369 | 23.7762 | 23.8155 | 23.8547 | 23.894 | 23.9333 | 23.9725 | 24.0118 | 24.0511 | 24.0903 | 24.1296 | 24.1689 | 24.2081 | 24.2474 | 24.2867 | 24.3259 | 24.3652 | 24.4045 | 24.4437 | 24.483 | 24.5223 | 24.5615 | 24.6008 | 24.6401 | 24.6793 | 24.6916 | 24.7038 | 24.716 | 24.7282 | 24.7404 | 24.7527 | 24.7649 | 24.7771 | 24.7893 | 24.8016 | 24.8138 | 24.826 | 24.8382 | 24.8504 | 24.8627 | 24.8749 | 24.8871 | 24.8993 | 24.9116 | 24.9238 | 24.936 | 24.9482 | 24.9604 | 24.9727 | 24.9849 | 24.9971 | 25.0093 | 25.0216 | 25.0338 | 25.046 | 25.046 | 25.046 | 25.046 | 25.046 | 25.046 | 25.046 | 25.046 | 25.046 | 25.046 | 25.046 | 25.046 | 25.046 | 25.046 | 25.046 | 25.046 | 25.046 | 25.046 | 25.046 | 25.046 | 25.046 | 25.046 | 25.046 | 25.046 | 25.046 | 25.046 | 25.046 | 25.046 | 25.046 | 25.046 | 25.046 | 25.0277 | 25.0093 | 24.991 | 24.9727 | 24.9543 | 24.936 | 24.9177 | 24.8993 | 24.881 | 24.8627 | 24.8443 | 24.826 | 24.8077 | 24.7893 | 24.771 | 24.7527 | 24.7343 | 24.716 | 24.6977 | 24.6793 | 24.661 | 24.6427 | 24.6243 | 24.606 | 24.5877 | 24.5693 | 24.551 | 24.5327 | 24.5143 | 24.496
5.15 | 0 | 0.89833 | 1.7967 | 2.695 | 3.5933 | 4.4917 | 5.39 | 6.2883 | 7.1867 | 8.085 | 8.9833 | 10.0345 | 11.0857 | 12.1369 | 13.1881 | 14.2393 | 14.5871 | 14.9349 | 15.2827 | 15.6305 | 15.9783 | 16.2797 | 16.5811 | 16.8824 | 17.1838 | 17.4852 | 17.7865 | 18.0879 | 18.3893 | 18.6906 | 18.992 | 19.1843 | 19.3766 | 19.5689 | 19.7612 | 19.9534 | 20.1457 | 20.338 | 20.5303 | 20.7226 | 20.9149 | 21.1072 | 21.2995 | 21.4918 | 21.684 | 21.8763 | 22.0258 | 22.1753 | 22.3248 | 22.4743 | 22.6238 | 22.7733 | 22.9228 | 23.0722 | 23.2217 | 23.3712 | 23.5207 | 23.6702 | 23.8197 | 23.9692 | 24.1187 | 24.1592 | 24.1998 | 24.2404 | 24.2809 | 24.3215 | 24.3621 | 24.4026 | 24.4432 | 24.4838 | 24.5243 | 24.5649 | 24.6055 | 24.646 | 24.6866 | 24.7272 | 24.7677 | 24.8083 | 24.8489 | 24.8894 | 24.93 | 24.9706 | 25.0111 | 25.0517 | 25.0923 | 25.1328 | 25.1734 | 25.214 | 25.2545 | 25.2951 | 25.3357 | 25.3484 | 25.3612 | 25.374 | 25.3868 | 25.3996 | 25.4123 | 25.4251 | 25.4379 | 25.4507 | 25.4634 | 25.4762 | 25.489 | 25.5018 | 25.5146 | 25.5273 | 25.5401 | 25.5529 | 25.5657 | 25.5784 | 25.5912 | 25.604 | 25.6168 | 25.6296 | 25.6423 | 25.6551 | 25.6679 | 25.6807 | 25.6934 | 25.7062 | 25.719 | 25.719 | 25.719 | 25.719 | 25.719 | 25.719 | 25.719 | 25.719 | 25.719 | 25.719 | 25.719 | 25.719 | 25.719 | 25.719 | 25.719 | 25.719 | 25.719 | 25.719 | 25.719 | 25.719 | 25.719 | 25.719 | 25.719 | 25.719 | 25.719 | 25.719 | 25.719 | 25.719 | 25.719 | 25.719 | 25.719 | 25.6998 | 25.6807 | 25.6615 | 25.6423 | 25.6232 | 25.604 | 25.5848 | 25.5657 | 25.5465 | 25.5273 | 25.5082 | 25.489 | 25.4698 | 25.4507 | 25.4315 | 25.4123 | 25.3932 | 25.374 | 25.3548 | 25.3357 | 25.3165 | 25.2973 | 25.2782 | 25.259 | 25.2398 | 25.2207 | 25.2015 | 25.1823 | 25.1632 | 25.144
5.2 | 0 | 0.92 | 1.84 | 2.76 | 3.68 | 4.6 | 5.52 | 6.44 | 7.36 | 8.28 | 9.2 | 10.2816 | 11.3632 | 12.4448 | 13.5264 | 14.608 | 14.9584 | 15.3088 | 15.6592 | 16.0096 | 16.36 | 16.6696 | 16.9792 | 17.2888 | 17.5984 | 17.908 | 18.2176 | 18.5272 | 18.8368 | 19.1464 | 19.456 | 19.6539 | 19.8517 | 20.0496 | 20.2475 | 20.4453 | 20.6432 | 20.8411 | 21.0389 | 21.2368 | 21.4347 | 21.6325 | 21.8304 | 22.0283 | 22.2261 | 22.424 | 22.5781 | 22.7323 | 22.8864 | 23.0405 | 23.1947 | 23.3488 | 23.5029 | 23.6571 | 23.8112 | 23.9653 | 24.1195 | 24.2736 | 24.4277 | 24.5819 | 24.736 | 24.7779 | 24.8197 | 24.8616 | 24.9035 | 24.9453 | 24.9872 | 25.0291 | 25.0709 | 25.1128 | 25.1547 | 25.1965 | 25.2384 | 25.2803 | 25.3221 | 25.364 | 25.4059 | 25.4477 | 25.4896 | 25.5315 | 25.5733 | 25.6152 | 25.6571 | 25.6989 | 25.7408 | 25.7827 | 25.8245 | 25.8664 | 25.9083 | 25.9501 | 25.992 | 26.0053 | 26.0187 | 26.032 | 26.0453 | 26.0587 | 26.072 | 26.0853 | 26.0987 | 26.112 | 26.1253 | 26.1387 | 26.152 | 26.1653 | 26.1787 | 26.192 | 26.2053 | 26.2187 | 26.232 | 26.2453 | 26.2587 | 26.272 | 26.2853 | 26.2987 | 26.312 | 26.3253 | 26.3387 | 26.352 | 26.3653 | 26.3787 | 26.392 | 26.392 | 26.392 | 26.392 | 26.392 | 26.392 | 26.392 | 26.392 | 26.392 | 26.392 | 26.392 | 26.392 | 26.392 | 26.392 | 26.392 | 26.392 | 26.392 | 26.392 | 26.392 | 26.392 | 26.392 | 26.392 | 26.392 | 26.392 | 26.392 | 26.392 | 26.392 | 26.392 | 26.392 | 26.392 | 26.392 | 26.372 | 26.352 | 26.332 | 26.312 | 26.292 | 26.272 | 26.252 | 26.232 | 26.212 | 26.192 | 26.172 | 26.152 | 26.132 | 26.112 | 26.092 | 26.072 | 26.052 | 26.032 | 26.012 | 25.992 | 25.972 | 25.952 | 25.932 | 25.912 | 25.892 | 25.872 | 25.852 | 25.832 | 25.812 | 25.792
5.25 | 0 | 0.94167 | 1.8833 | 2.825 | 3.7667 | 4.7083 | 5.65 | 6.5917 | 7.5333 | 8.475 | 9.4167 | 10.5287 | 11.6407 | 12.7527 | 13.8647 | 14.9767 | 15.3297 | 15.6827 | 16.0357 | 16.3887 | 16.7417 | 17.0595 | 17.3773 | 17.6952 | 18.013 | 18.3308 | 18.6487 | 18.9665 | 19.2843 | 19.6022 | 19.92 | 20.1234 | 20.3269 | 20.5303 | 20.7338 | 20.9372 | 21.1407 | 21.3441 | 21.5476 | 21.751 | 21.9544 | 22.1579 | 22.3613 | 22.5648 | 22.7682 | 22.9717 | 23.1304 | 23.2892 | 23.448 | 23.6068 | 23.7656 | 23.9243 | 24.0831 | 24.2419 | 24.4007 | 24.5594 | 24.7182 | 24.877 | 25.0358 | 25.1946 | 25.3533 | 25.3965 | 25.4397 | 25.4828 | 25.526 | 25.5692 | 25.6123 | 25.6555 | 25.6987 | 25.7418 | 25.785 | 25.8282 | 25.8713 | 25.9145 | 25.9577 | 26.0008 | 26.044 | 26.0872 | 26.1303 | 26.1735 | 26.2167 | 26.2598 | 26.303 | 26.3462 | 26.3893 | 26.4325 | 26.4757 | 26.5188 | 26.562 | 26.6052 | 26.6483 | 26.6622 | 26.6761 | 26.69 | 26.7039 | 26.7178 | 26.7317 | 26.7456 | 26.7594 | 26.7733 | 26.7872 | 26.8011 | 26.815 | 26.8289 | 26.8428 | 26.8567 | 26.8706 | 26.8844 | 26.8983 | 26.9122 | 26.9261 | 26.94 | 26.9539 | 26.9678 | 26.9817 | 26.9956 | 27.0094 | 27.0233 | 27.0372 | 27.0511 | 27.065 | 27.065 | 27.065 | 27.065 | 27.065 | 27.065 | 27.065 | 27.065 | 27.065 | 27.065 | 27.065 | 27.065 | 27.065 | 27.065 | 27.065 | 27.065 | 27.065 | 27.065 | 27.065 | 27.065 | 27.065 | 27.065 | 27.065 | 27.065 | 27.065 | 27.065 | 27.065 | 27.065 | 27.065 | 27.065 | 27.065 | 27.0442 | 27.0233 | 27.0025 | 26.9817 | 26.9608 | 26.94 | 26.9192 | 26.8983 | 26.8775 | 26.8567 | 26.8358 | 26.815 | 26.7942 | 26.7733 | 26.7525 | 26.7317 | 26.7108 | 26.69 | 26.6692 | 26.6483 | 26.6275 | 26.6067 | 26.5858 | 26.565 | 26.5442 | 26.5233 | 26.5025 | 26.4817 | 26.4608 | 26.44
5.3 | 0 | 0.96333 | 1.9267 | 2.89 | 3.8533 | 4.8167 | 5.78 | 6.7433 | 7.7067 | 8.67 | 9.6333 | 10.7757 | 11.9181 | 13.0605 | 14.2029 | 15.3453 | 15.7009 | 16.0565 | 16.4121 | 16.7677 | 17.1233 | 17.4494 | 17.7755 | 18.1015 | 18.4276 | 18.7537 | 19.0797 | 19.4058 | 19.7319 | 20.0579 | 20.384 | 20.593 | 20.802 | 21.0111 | 21.2201 | 21.4291 | 21.6381 | 21.8472 | 22.0562 | 22.2652 | 22.4742 | 22.6832 | 22.8923 | 23.1013 | 23.3103 | 23.5193 | 23.6828 | 23.8462 | 24.0096 | 24.173 | 24.3364 | 24.4999 | 24.6633 | 24.8267 | 24.9901 | 25.1536 | 25.317 | 25.4804 | 25.6438 | 25.8072 | 25.9707 | 26.0151 | 26.0596 | 26.1041 | 26.1485 | 26.193 | 26.2375 | 26.2819 | 26.3264 | 26.3709 | 26.4153 | 26.4598 | 26.5043 | 26.5487 | 26.5932 | 26.6377 | 26.6821 | 26.7266 | 26.7711 | 26.8155 | 26.86 | 26.9045 | 26.9489 | 26.9934 | 27.0379 | 27.0823 | 27.1268 | 27.1713 | 27.2157 | 27.2602 | 27.3047 | 27.3191 | 27.3336 | 27.348 | 27.3624 | 27.3769 | 27.3913 | 27.4058 | 27.4202 | 27.4347 | 27.4491 | 27.4636 | 27.478 | 27.4924 | 27.5069 | 27.5213 | 27.5358 | 27.5502 | 27.5647 | 27.5791 | 27.5936 | 27.608 | 27.6224 | 27.6369 | 27.6513 | 27.6658 | 27.6802 | 27.6947 | 27.7091 | 27.7236 | 27.738 | 27.738 | 27.738 | 27.738 | 27.738 | 27.738 | 27.738 | 27.738 | 27.738 | 27.738 | 27.738 | 27.738 | 27.738 | 27.738 | 27.738 | 27.738 | 27.738 | 27.738 | 27.738 | 27.738 | 27.738 | 27.738 | 27.738 | 27.738 | 27.738 | 27.738 | 27.738 | 27.738 | 27.738 | 27.738 | 27.738 | 27.7163 | 27.6947 | 27.673 | 27.6513 | 27.6297 | 27.608 | 27.5863 | 27.5647 | 27.543 | 27.5213 | 27.4997 | 27.478 | 27.4563 | 27.4347 | 27.413 | 27.3913 | 27.3697 | 27.348 | 27.3263 | 27.3047 | 27.283 | 27.2613 | 27.2397 | 27.218 | 27.1963 | 27.1747 | 27.153 | 27.1313 | 27.1097 | 27.088
5.35 | 0 | 0.985 | 1.97 | 2.955 | 3.94 | 4.925 | 5.91 | 6.895 | 7.88 | 8.865 | 9.85 | 11.0228 | 12.1956 | 13.3684 | 14.5412 | 15.714 | 16.0722 | 16.4304 | 16.7886 | 17.1468 | 17.505 | 17.8393 | 18.1736 | 18.5079 | 18.8422 | 19.1765 | 19.5108 | 19.8451 | 20.1794 | 20.5137 | 20.848 | 21.0626 | 21.2772 | 21.4918 | 21.7064 | 21.921 | 22.1356 | 22.3502 | 22.5648 | 22.7794 | 22.994 | 23.2086 | 23.4232 | 23.6378 | 23.8524 | 24.067 | 24.2351 | 24.4031 | 24.5712 | 24.7393 | 24.9073 | 25.0754 | 25.2435 | 25.4115 | 25.5796 | 25.7477 | 25.9157 | 26.0838 | 26.2519 | 26.4199 | 26.588 | 26.6338 | 26.6795 | 26.7253 | 26.7711 | 26.8168 | 26.8626 | 26.9084 | 26.9541 | 26.9999 | 27.0457 | 27.0914 | 27.1372 | 27.183 | 27.2287 | 27.2745 | 27.3203 | 27.366 | 27.4118 | 27.4576 | 27.5033 | 27.5491 | 27.5949 | 27.6406 | 27.6864 | 27.7322 | 27.7779 | 27.8237 | 27.8695 | 27.9152 | 27.961 | 27.976 | 27.991 | 28.006 | 28.021 | 28.036 | 28.051 | 28.066 | 28.081 | 28.096 | 28.111 | 28.126 | 28.141 | 28.156 | 28.171 | 28.186 | 28.201 | 28.216 | 28.231 | 28.246 | 28.261 | 28.276 | 28.291 | 28.306 | 28.321 | 28.336 | 28.351 | 28.366 | 28.381 | 28.396 | 28.411 | 28.411 | 28.411 | 28.411 | 28.411 | 28.411 | 28.411 | 28.411 | 28.411 | 28.411 | 28.411 | 28.411 | 28.411 | 28.411 | 28.411 | 28.411 | 28.411 | 28.411 | 28.411 | 28.411 | 28.411 | 28.411 | 28.411 | 28.411 | 28.411 | 28.411 | 28.411 | 28.411 | 28.411 | 28.411 | 28.411 | 28.3885 | 28.366 | 28.3435 | 28.321 | 28.2985 | 28.276 | 28.2535 | 28.231 | 28.2085 | 28.186 | 28.1635 | 28.141 | 28.1185 | 28.096 | 28.0735 | 28.051 | 28.0285 | 28.006 | 27.9835 | 27.961 | 27.9385 | 27.916 | 27.8935 | 27.871 | 27.8485 | 27.826 | 27.8035 | 27.781 | 27.7585 | 27.736
5.4 | 0 | 1.0067 | 2.0133 | 3.02 | 4.0267 | 5.0333 | 6.04 | 7.0467 | 8.0533 | 9.06 | 10.0667 | 11.2699 | 12.4731 | 13.6763 | 14.8795 | 16.0827 | 16.4435 | 16.8043 | 17.1651 | 17.5259 | 17.8867 | 18.2292 | 18.5717 | 18.9143 | 19.2568 | 19.5993 | 19.9419 | 20.2844 | 20.6269 | 20.9695 | 21.312 | 21.5322 | 21.7524 | 21.9725 | 22.1927 | 22.4129 | 22.6331 | 22.8532 | 23.0734 | 23.2936 | 23.5138 | 23.734 | 23.9541 | 24.1743 | 24.3945 | 24.6147 | 24.7874 | 24.9601 | 25.1328 | 25.3055 | 25.4782 | 25.6509 | 25.8236 | 25.9964 | 26.1691 | 26.3418 | 26.5145 | 26.6872 | 26.8599 | 27.0326 | 27.2053 | 27.2524 | 27.2995 | 27.3465 | 27.3936 | 27.4407 | 27.4877 | 27.5348 | 27.5819 | 27.6289 | 27.676 | 27.7231 | 27.7701 | 27.8172 | 27.8643 | 27.9113 | 27.9584 | 28.0055 | 28.0525 | 28.0996 | 28.1467 | 28.1937 | 28.2408 | 28.2879 | 28.3349 | 28.382 | 28.4291 | 28.4761 | 28.5232 | 28.5703 | 28.6173 | 28.6329 | 28.6484 | 28.664 | 28.6796 | 28.6951 | 28.7107 | 28.7262 | 28.7418 | 28.7573 | 28.7729 | 28.7884 | 28.804 | 28.8196 | 28.8351 | 28.8507 | 28.8662 | 28.8818 | 28.8973 | 28.9129 | 28.9284 | 28.944 | 28.9596 | 28.9751 | 28.9907 | 29.0062 | 29.0218 | 29.0373 | 29.0529 | 29.0684 | 29.084 | 29.084 | 29.084 | 29.084 | 29.084 | 29.084 | 29.084 | 29.084 | 29.084 | 29.084 | 29.084 | 29.084 | 29.084 | 29.084 | 29.084 | 29.084 | 29.084 | 29.084 | 29.084 | 29.084 | 29.084 | 29.084 | 29.084 | 29.084 | 29.084 | 29.084 | 29.084 | 29.084 | 29.084 | 29.084 | 29.084 | 29.0607 | 29.0373 | 29.014 | 28.9907 | 28.9673 | 28.944 | 28.9207 | 28.8973 | 28.874 | 28.8507 | 28.8273 | 28.804 | 28.7807 | 28.7573 | 28.734 | 28.7107 | 28.6873 | 28.664 | 28.6407 | 28.6173 | 28.594 | 28.5707 | 28.5473 | 28.524 | 28.5007 | 28.4773 | 28.454 | 28.4307 | 28.4073 | 28.384
5.45 | 0 | 1.0283 | 2.0567 | 3.085 | 4.1133 | 5.1417 | 6.17 | 7.1983 | 8.2267 | 9.255 | 10.2833 | 11.5169 | 12.7505 | 13.9841 | 15.2177 | 16.4513 | 16.8147 | 17.1781 | 17.5415 | 17.9049 | 18.2683 | 18.6191 | 18.9699 | 19.3206 | 19.6714 | 20.0222 | 20.3729 | 20.7237 | 21.0745 | 21.4252 | 21.776 | 22.0018 | 22.2275 | 22.4533 | 22.679 | 22.9048 | 23.1305 | 23.3563 | 23.582 | 23.8078 | 24.0336 | 24.2593 | 24.4851 | 24.7108 | 24.9366 | 25.1623 | 25.3397 | 25.517 | 25.6944 | 25.8718 | 26.0491 | 26.2265 | 26.4038 | 26.5812 | 26.7585 | 26.9359 | 27.1132 | 27.2906 | 27.468 | 27.6453 | 27.8227 | 27.871 | 27.9194 | 27.9678 | 28.0161 | 28.0645 | 28.1129 | 28.1612 | 28.2096 | 28.258 | 28.3063 | 28.3547 | 28.4031 | 28.4514 | 28.4998 | 28.5482 | 28.5965 | 28.6449 | 28.6933 | 28.7416 | 28.79 | 28.8384 | 28.8867 | 28.9351 | 28.9835 | 29.0318 | 29.0802 | 29.1286 | 29.1769 | 29.2253 | 29.2737 | 29.2898 | 29.3059 | 29.322 | 29.3381 | 29.3542 | 29.3703 | 29.3864 | 29.4026 | 29.4187 | 29.4348 | 29.4509 | 29.467 | 29.4831 | 29.4992 | 29.5153 | 29.5314 | 29.5476 | 29.5637 | 29.5798 | 29.5959 | 29.612 | 29.6281 | 29.6442 | 29.6603 | 29.6764 | 29.6926 | 29.7087 | 29.7248 | 29.7409 | 29.757 | 29.757 | 29.757 | 29.757 | 29.757 | 29.757 | 29.757 | 29.757 | 29.757 | 29.757 | 29.757 | 29.757 | 29.757 | 29.757 | 29.757 | 29.757 | 29.757 | 29.757 | 29.757 | 29.757 | 29.757 | 29.757 | 29.757 | 29.757 | 29.757 | 29.757 | 29.757 | 29.757 | 29.757 | 29.757 | 29.757 | 29.7328 | 29.7087 | 29.6845 | 29.6603 | 29.6362 | 29.612 | 29.5878 | 29.5637 | 29.5395 | 29.5153 | 29.4912 | 29.467 | 29.4428 | 29.4187 | 29.3945 | 29.3703 | 29.3462 | 29.322 | 29.2978 | 29.2737 | 29.2495 | 29.2253 | 29.2012 | 29.177 | 29.1528 | 29.1287 | 29.1045 | 29.0803 | 29.0562 | 29.032
5.5 | 0 | 1.05 | 2.1 | 3.15 | 4.2 | 5.25 | 6.3 | 7.35 | 8.4 | 9.45 | 10.5 | 11.764 | 13.028 | 14.292 | 15.556 | 16.82 | 17.186 | 17.552 | 17.918 | 18.284 | 18.65 | 19.009 | 19.368 | 19.727 | 20.086 | 20.445 | 20.804 | 21.163 | 21.522 | 21.881 | 22.24 | 22.4713 | 22.7027 | 22.934 | 23.1653 | 23.3967 | 23.628 | 23.8593 | 24.0907 | 24.322 | 24.5533 | 24.7847 | 25.016 | 25.2473 | 25.4787 | 25.71 | 25.892 | 26.074 | 26.256 | 26.438 | 26.62 | 26.802 | 26.984 | 27.166 | 27.348 | 27.53 | 27.712 | 27.894 | 28.076 | 28.258 | 28.44 | 28.4897 | 28.5393 | 28.589 | 28.6387 | 28.6883 | 28.738 | 28.7877 | 28.8373 | 28.887 | 28.9367 | 28.9863 | 29.036 | 29.0857 | 29.1353 | 29.185 | 29.2347 | 29.2843 | 29.334 | 29.3837 | 29.4333 | 29.483 | 29.5327 | 29.5823 | 29.632 | 29.6817 | 29.7313 | 29.781 | 29.8307 | 29.8803 | 29.93 | 29.9467 | 29.9633 | 29.98 | 29.9967 | 30.0133 | 30.03 | 30.0467 | 30.0633 | 30.08 | 30.0967 | 30.1133 | 30.13 | 30.1467 | 30.1633 | 30.18 | 30.1967 | 30.2133 | 30.23 | 30.2467 | 30.2633 | 30.28 | 30.2967 | 30.3133 | 30.33 | 30.3467 | 30.3633 | 30.38 | 30.3967 | 30.4133 | 30.43 | 30.43 | 30.43 | 30.43 | 30.43 | 30.43 | 30.43 | 30.43 | 30.43 | 30.43 | 30.43 | 30.43 | 30.43 | 30.43 | 30.43 | 30.43 | 30.43 | 30.43 | 30.43 | 30.43 | 30.43 | 30.43 | 30.43 | 30.43 | 30.43 | 30.43 | 30.43 | 30.43 | 30.43 | 30.43 | 30.43 | 30.405 | 30.38 | 30.355 | 30.33 | 30.305 | 30.28 | 30.255 | 30.23 | 30.205 | 30.18 | 30.155 | 30.13 | 30.105 | 30.08 | 30.055 | 30.03 | 30.005 | 29.98 | 29.955 | 29.93 | 29.905 | 29.88 | 29.855 | 29.83 | 29.805 | 29.78 | 29.755 | 29.73 | 29.705 | 29.68
5.55 | 0 | 1.0717 | 2.1433 | 3.215 | 4.2867 | 5.3583 | 6.43 | 7.5017 | 8.5733 | 9.645 | 10.7167 | 12.0111 | 13.3055 | 14.5999 | 15.8943 | 17.1887 | 17.5573 | 17.9259 | 18.2945 | 18.6631 | 19.0317 | 19.3989 | 19.7661 | 20.1334 | 20.5006 | 20.8678 | 21.2351 | 21.6023 | 21.9695 | 22.3368 | 22.704 | 22.9409 | 23.1778 | 23.4147 | 23.6516 | 23.8886 | 24.1255 | 24.3624 | 24.5993 | 24.8362 | 25.0731 | 25.31 | 25.5469 | 25.7838 | 26.0208 | 26.2577 | 26.4443 | 26.631 | 26.8176 | 27.0042 | 27.1909 | 27.3775 | 27.5642 | 27.7508 | 27.9375 | 28.1241 | 28.3108 | 28.4974 | 28.684 | 28.8707 | 29.0573 | 29.1083 | 29.1593 | 29.2102 | 29.2612 | 29.3122 | 29.3631 | 29.4141 | 29.4651 | 29.516 | 29.567 | 29.618 | 29.6689 | 29.7199 | 29.7709 | 29.8218 | 29.8728 | 29.9238 | 29.9747 | 30.0257 | 30.0767 | 30.1276 | 30.1786 | 30.2296 | 30.2805 | 30.3315 | 30.3825 | 30.4334 | 30.4844 | 30.5354 | 30.5863 | 30.6036 | 30.6208 | 30.638 | 30.6552 | 30.6724 | 30.6897 | 30.7069 | 30.7241 | 30.7413 | 30.7586 | 30.7758 | 30.793 | 30.8102 | 30.8274 | 30.8447 | 30.8619 | 30.8791 | 30.8963 | 30.9136 | 30.9308 | 30.948 | 30.9652 | 30.9824 | 30.9997 | 31.0169 | 31.0341 | 31.0513 | 31.0686 | 31.0858 | 31.103 | 31.103 | 31.103 | 31.103 | 31.103 | 31.103 | 31.103 | 31.103 | 31.103 | 31.103 | 31.103 | 31.103 | 31.103 | 31.103 | 31.103 | 31.103 | 31.103 | 31.103 | 31.103 | 31.103 | 31.103 | 31.103 | 31.103 | 31.103 | 31.103 | 31.103 | 31.103 | 31.103 | 31.103 | 31.103 | 31.103 | 31.0772 | 31.0513 | 31.0255 | 30.9997 | 30.9738 | 30.948 | 30.9222 | 30.8963 | 30.8705 | 30.8447 | 30.8188 | 30.793 | 30.7672 | 30.7413 | 30.7155 | 30.6897 | 30.6638 | 30.638 | 30.6122 | 30.5863 | 30.5605 | 30.5347 | 30.5088 | 30.483 | 30.4572 | 30.4313 | 30.4055 | 30.3797 | 30.3538 | 30.328
5.6 | 0 | 1.0933 | 2.1867 | 3.28 | 4.3733 | 5.4667 | 6.56 | 7.6533 | 8.7467 | 9.84 | 10.9333 | 12.2581 | 13.5829 | 14.9077 | 16.2325 | 17.5573 | 17.9285 | 18.2997 | 18.6709 | 19.0421 | 19.4133 | 19.7888 | 20.1643 | 20.5397 | 20.9152 | 21.2907 | 21.6661 | 22.0416 | 22.4171 | 22.7925 | 23.168 | 23.4105 | 23.653 | 23.8955 | 24.138 | 24.3804 | 24.6229 | 24.8654 | 25.1079 | 25.3504 | 25.5929 | 25.8354 | 26.0779 | 26.3204 | 26.5628 | 26.8053 | 26.9966 | 27.1879 | 27.3792 | 27.5705 | 27.7618 | 27.9531 | 28.1444 | 28.3356 | 28.5269 | 28.7182 | 28.9095 | 29.1008 | 29.2921 | 29.4834 | 29.6747 | 29.7269 | 29.7792 | 29.8315 | 29.8837 | 29.936 | 29.9883 | 30.0405 | 30.0928 | 30.1451 | 30.1973 | 30.2496 | 30.3019 | 30.3541 | 30.4064 | 30.4587 | 30.5109 | 30.5632 | 30.6155 | 30.6677 | 30.72 | 30.7723 | 30.8245 | 30.8768 | 30.9291 | 30.9813 | 31.0336 | 31.0859 | 31.1381 | 31.1904 | 31.2427 | 31.2604 | 31.2782 | 31.296 | 31.3138 | 31.3316 | 31.3493 | 31.3671 | 31.3849 | 31.4027 | 31.4204 | 31.4382 | 31.456 | 31.4738 | 31.4916 | 31.5093 | 31.5271 | 31.5449 | 31.5627 | 31.5804 | 31.5982 | 31.616 | 31.6338 | 31.6516 | 31.6693 | 31.6871 | 31.7049 | 31.7227 | 31.7404 | 31.7582 | 31.776 | 31.776 | 31.776 | 31.776 | 31.776 | 31.776 | 31.776 | 31.776 | 31.776 | 31.776 | 31.776 | 31.776 | 31.776 | 31.776 | 31.776 | 31.776 | 31.776 | 31.776 | 31.776 | 31.776 | 31.776 | 31.776 | 31.776 | 31.776 | 31.776 | 31.776 | 31.776 | 31.776 | 31.776 | 31.776 | 31.776 | 31.7493 | 31.7227 | 31.696 | 31.6693 | 31.6427 | 31.616 | 31.5893 | 31.5627 | 31.536 | 31.5093 | 31.4827 | 31.456 | 31.4293 | 31.4027 | 31.376 | 31.3493 | 31.3227 | 31.296 | 31.2693 | 31.2427 | 31.216 | 31.1893 | 31.1627 | 31.136 | 31.1093 | 31.0827 | 31.056 | 31.0293 | 31.0027 | 30.976
5.65 | 0 | 1.115 | 2.23 | 3.345 | 4.46 | 5.575 | 6.69 | 7.805 | 8.92 | 10.035 | 11.15 | 12.5052 | 13.8604 | 15.2156 | 16.5708 | 17.926 | 18.2998 | 18.6736 | 19.0474 | 19.4212 | 19.795 | 20.1787 | 20.5624 | 20.9461 | 21.3298 | 21.7135 | 22.0972 | 22.4809 | 22.8646 | 23.2483 | 23.632 | 23.8801 | 24.1281 | 24.3762 | 24.6243 | 24.8723 | 25.1204 | 25.3685 | 25.6165 | 25.8646 | 26.1127 | 26.3607 | 26.6088 | 26.8569 | 27.1049 | 27.353 | 27.5489 | 27.7449 | 27.9408 | 28.1367 | 28.3327 | 28.5286 | 28.7245 | 28.9205 | 29.1164 | 29.3123 | 29.5083 | 29.7042 | 29.9001 | 30.0961 | 30.292 | 30.3456 | 30.3991 | 30.4527 | 30.5063 | 30.5598 | 30.6134 | 30.667 | 30.7205 | 30.7741 | 30.8277 | 30.8812 | 30.9348 | 30.9884 | 31.0419 | 31.0955 | 31.1491 | 31.2026 | 31.2562 | 31.3098 | 31.3633 | 31.4169 | 31.4705 | 31.524 | 31.5776 | 31.6312 | 31.6847 | 31.7383 | 31.7919 | 31.8454 | 31.899 | 31.9173 | 31.9357 | 31.954 | 31.9723 | 31.9907 | 32.009 | 32.0273 | 32.0457 | 32.064 | 32.0823 | 32.1007 | 32.119 | 32.1373 | 32.1557 | 32.174 | 32.1923 | 32.2107 | 32.229 | 32.2473 | 32.2657 | 32.284 | 32.3023 | 32.3207 | 32.339 | 32.3573 | 32.3757 | 32.394 | 32.4123 | 32.4307 | 32.449 | 32.449 | 32.449 | 32.449 | 32.449 | 32.449 | 32.449 | 32.449 | 32.449 | 32.449 | 32.449 | 32.449 | 32.449 | 32.449 | 32.449 | 32.449 | 32.449 | 32.449 | 32.449 | 32.449 | 32.449 | 32.449 | 32.449 | 32.449 | 32.449 | 32.449 | 32.449 | 32.449 | 32.449 | 32.449 | 32.449 | 32.4215 | 32.394 | 32.3665 | 32.339 | 32.3115 | 32.284 | 32.2565 | 32.229 | 32.2015 | 32.174 | 32.1465 | 32.119 | 32.0915 | 32.064 | 32.0365 | 32.009 | 31.9815 | 31.954 | 31.9265 | 31.899 | 31.8715 | 31.844 | 31.8165 | 31.789 | 31.7615 | 31.734 | 31.7065 | 31.679 | 31.6515 | 31.624
5.7 | 0 | 1.1367 | 2.2733 | 3.41 | 4.5467 | 5.6833 | 6.82 | 7.9567 | 9.0933 | 10.23 | 11.3667 | 12.7523 | 14.1379 | 15.5235 | 16.9091 | 18.2947 | 18.6711 | 19.0475 | 19.4239 | 19.8003 | 20.1767 | 20.5686 | 20.9605 | 21.3525 | 21.7444 | 22.1363 | 22.5283 | 22.9202 | 23.3121 | 23.7041 | 24.096 | 24.3496 | 24.6033 | 24.8569 | 25.1106 | 25.3642 | 25.6179 | 25.8715 | 26.1252 | 26.3788 | 26.6324 | 26.8861 | 27.1397 | 27.3934 | 27.647 | 27.9007 | 28.1012 | 28.3018 | 28.5024 | 28.703 | 28.9036 | 29.1041 | 29.3047 | 29.5053 | 29.7059 | 29.9064 | 30.107 | 30.3076 | 30.5082 | 30.7088 | 30.9093 | 30.9642 | 31.0191 | 31.0739 | 31.1288 | 31.1837 | 31.2385 | 31.2934 | 31.3483 | 31.4031 | 31.458 | 31.5129 | 31.5677 | 31.6226 | 31.6775 | 31.7323 | 31.7872 | 31.8421 | 31.8969 | 31.9518 | 32.0067 | 32.0615 | 32.1164 | 32.1713 | 32.2261 | 32.281 | 32.3359 | 32.3907 | 32.4456 | 32.5005 | 32.5553 | 32.5742 | 32.5931 | 32.612 | 32.6309 | 32.6498 | 32.6687 | 32.6876 | 32.7064 | 32.7253 | 32.7442 | 32.7631 | 32.782 | 32.8009 | 32.8198 | 32.8387 | 32.8576 | 32.8764 | 32.8953 | 32.9142 | 32.9331 | 32.952 | 32.9709 | 32.9898 | 33.0087 | 33.0276 | 33.0464 | 33.0653 | 33.0842 | 33.1031 | 33.122 | 33.122 | 33.122 | 33.122 | 33.122 | 33.122 | 33.122 | 33.122 | 33.122 | 33.122 | 33.122 | 33.122 | 33.122 | 33.122 | 33.122 | 33.122 | 33.122 | 33.122 | 33.122 | 33.122 | 33.122 | 33.122 | 33.122 | 33.122 | 33.122 | 33.122 | 33.122 | 33.122 | 33.122 | 33.122 | 33.122 | 33.0937 | 33.0653 | 33.037 | 33.0087 | 32.9803 | 32.952 | 32.9237 | 32.8953 | 32.867 | 32.8387 | 32.8103 | 32.782 | 32.7537 | 32.7253 | 32.697 | 32.6687 | 32.6403 | 32.612 | 32.5837 | 32.5553 | 32.527 | 32.4987 | 32.4703 | 32.442 | 32.4137 | 32.3853 | 32.357 | 32.3287 | 32.3003 | 32.272
5.75 | 0 | 1.1583 | 2.3167 | 3.475 | 4.6333 | 5.7917 | 6.95 | 8.1083 | 9.2667 | 10.425 | 11.5833 | 12.9993 | 14.4153 | 15.8313 | 17.2473 | 18.6633 | 19.0423 | 19.4213 | 19.8003 | 20.1793 | 20.5583 | 20.9585 | 21.3587 | 21.7588 | 22.159 | 22.5592 | 22.9593 | 23.3595 | 23.7597 | 24.1598 | 24.56 | 24.8192 | 25.0784 | 25.3377 | 25.5969 | 25.8561 | 26.1153 | 26.3746 | 26.6338 | 26.893 | 27.1522 | 27.4114 | 27.6707 | 27.9299 | 28.1891 | 28.4483 | 28.6536 | 28.8588 | 29.064 | 29.2692 | 29.4744 | 29.6797 | 29.8849 | 30.0901 | 30.2953 | 30.5006 | 30.7058 | 30.911 | 31.1162 | 31.3214 | 31.5267 | 31.5828 | 31.639 | 31.6952 | 31.7513 | 31.8075 | 31.8637 | 31.9198 | 31.976 | 32.0322 | 32.0883 | 32.1445 | 32.2007 | 32.2568 | 32.313 | 32.3692 | 32.4253 | 32.4815 | 32.5377 | 32.5938 | 32.65 | 32.7062 | 32.7623 | 32.8185 | 32.8747 | 32.9308 | 32.987 | 33.0432 | 33.0993 | 33.1555 | 33.2117 | 33.2311 | 33.2506 | 33.27 | 33.2894 | 33.3089 | 33.3283 | 33.3478 | 33.3672 | 33.3867 | 33.4061 | 33.4256 | 33.445 | 33.4644 | 33.4839 | 33.5033 | 33.5228 | 33.5422 | 33.5617 | 33.5811 | 33.6006 | 33.62 | 33.6394 | 33.6589 | 33.6783 | 33.6978 | 33.7172 | 33.7367 | 33.7561 | 33.7756 | 33.795 | 33.795 | 33.795 | 33.795 | 33.795 | 33.795 | 33.795 | 33.795 | 33.795 | 33.795 | 33.795 | 33.795 | 33.795 | 33.795 | 33.795 | 33.795 | 33.795 | 33.795 | 33.795 | 33.795 | 33.795 | 33.795 | 33.795 | 33.795 | 33.795 | 33.795 | 33.795 | 33.795 | 33.795 | 33.795 | 33.795 | 33.7658 | 33.7367 | 33.7075 | 33.6783 | 33.6492 | 33.62 | 33.5908 | 33.5617 | 33.5325 | 33.5033 | 33.4742 | 33.445 | 33.4158 | 33.3867 | 33.3575 | 33.3283 | 33.2992 | 33.27 | 33.2408 | 33.2117 | 33.1825 | 33.1533 | 33.1242 | 33.095 | 33.0658 | 33.0367 | 33.0075 | 32.9783 | 32.9492 | 32.92
5.8 | 0 | 1.18 | 2.36 | 3.54 | 4.72 | 5.9 | 7.08 | 8.26 | 9.44 | 10.62 | 11.8 | 13.2464 | 14.6928 | 16.1392 | 17.5856 | 19.032 | 19.4136 | 19.7952 | 20.1768 | 20.5584 | 20.94 | 21.3484 | 21.7568 | 22.1652 | 22.5736 | 22.982 | 23.3904 | 23.7988 | 24.2072 | 24.6156 | 25.024 | 25.2888 | 25.5536 | 25.8184 | 26.0832 | 26.348 | 26.6128 | 26.8776 | 27.1424 | 27.4072 | 27.672 | 27.9368 | 28.2016 | 28.4664 | 28.7312 | 28.996 | 29.2059 | 29.4157 | 29.6256 | 29.8355 | 30.0453 | 30.2552 | 30.4651 | 30.6749 | 30.8848 | 31.0947 | 31.3045 | 31.5144 | 31.7243 | 31.9341 | 32.144 | 32.2015 | 32.2589 | 32.3164 | 32.3739 | 32.4313 | 32.4888 | 32.5463 | 32.6037 | 32.6612 | 32.7187 | 32.7761 | 32.8336 | 32.8911 | 32.9485 | 33.006 | 33.0635 | 33.1209 | 33.1784 | 33.2359 | 33.2933 | 33.3508 | 33.4083 | 33.4657 | 33.5232 | 33.5807 | 33.6381 | 33.6956 | 33.7531 | 33.8105 | 33.868 | 33.888 | 33.908 | 33.928 | 33.948 | 33.968 | 33.988 | 34.008 | 34.028 | 34.048 | 34.068 | 34.088 | 34.108 | 34.128 | 34.148 | 34.168 | 34.188 | 34.208 | 34.228 | 34.248 | 34.268 | 34.288 | 34.308 | 34.328 | 34.348 | 34.368 | 34.388 | 34.408 | 34.428 | 34.448 | 34.468 | 34.468 | 34.468 | 34.468 | 34.468 | 34.468 | 34.468 | 34.468 | 34.468 | 34.468 | 34.468 | 34.468 | 34.468 | 34.468 | 34.468 | 34.468 | 34.468 | 34.468 | 34.468 | 34.468 | 34.468 | 34.468 | 34.468 | 34.468 | 34.468 | 34.468 | 34.468 | 34.468 | 34.468 | 34.468 | 34.468 | 34.438 | 34.408 | 34.378 | 34.348 | 34.318 | 34.288 | 34.258 | 34.228 | 34.198 | 34.168 | 34.138 | 34.108 | 34.078 | 34.048 | 34.018 | 33.988 | 33.958 | 33.928 | 33.898 | 33.868 | 33.838 | 33.808 | 33.778 | 33.748 | 33.718 | 33.688 | 33.658 | 33.628 | 33.598 | 33.568
5.85 | 0 | 1.2017 | 2.4033 | 3.605 | 4.8067 | 6.0083 | 7.21 | 8.4117 | 9.6133 | 10.815 | 12.0167 | 13.4935 | 14.9703 | 16.4471 | 17.9239 | 19.4007 | 19.7849 | 20.1691 | 20.5533 | 20.9375 | 21.3217 | 21.7383 | 22.1549 | 22.5716 | 22.9882 | 23.4048 | 23.8215 | 24.2381 | 24.6547 | 25.0714 | 25.488 | 25.7584 | 26.0288 | 26.2991 | 26.5695 | 26.8399 | 27.1103 | 27.3806 | 27.651 | 27.9214 | 28.1918 | 28.4622 | 28.7325 | 29.0029 | 29.2733 | 29.5437 | 29.7582 | 29.9727 | 30.1872 | 30.4017 | 30.6162 | 30.8307 | 31.0452 | 31.2598 | 31.4743 | 31.6888 | 31.9033 | 32.1178 | 32.3323 | 32.5468 | 32.7613 | 32.8201 | 32.8789 | 32.9376 | 32.9964 | 33.0552 | 33.1139 | 33.1727 | 33.2315 | 33.2902 | 33.349 | 33.4078 | 33.4665 | 33.5253 | 33.5841 | 33.6428 | 33.7016 | 33.7604 | 33.8191 | 33.8779 | 33.9367 | 33.9954 | 34.0542 | 34.113 | 34.1717 | 34.2305 | 34.2893 | 34.348 | 34.4068 | 34.4656 | 34.5243 | 34.5449 | 34.5654 | 34.586 | 34.6066 | 34.6271 | 34.6477 | 34.6682 | 34.6888 | 34.7093 | 34.7299 | 34.7504 | 34.771 | 34.7916 | 34.8121 | 34.8327 | 34.8532 | 34.8738 | 34.8943 | 34.9149 | 34.9354 | 34.956 | 34.9766 | 34.9971 | 35.0177 | 35.0382 | 35.0588 | 35.0793 | 35.0999 | 35.1204 | 35.141 | 35.141 | 35.141 | 35.141 | 35.141 | 35.141 | 35.141 | 35.141 | 35.141 | 35.141 | 35.141 | 35.141 | 35.141 | 35.141 | 35.141 | 35.141 | 35.141 | 35.141 | 35.141 | 35.141 | 35.141 | 35.141 | 35.141 | 35.141 | 35.141 | 35.141 | 35.141 | 35.141 | 35.141 | 35.141 | 35.141 | 35.1102 | 35.0793 | 35.0485 | 35.0177 | 34.9868 | 34.956 | 34.9252 | 34.8943 | 34.8635 | 34.8327 | 34.8018 | 34.771 | 34.7402 | 34.7093 | 34.6785 | 34.6477 | 34.6168 | 34.586 | 34.5552 | 34.5243 | 34.4935 | 34.4627 | 34.4318 | 34.401 | 34.3702 | 34.3393 | 34.3085 | 34.2777 | 34.2468 | 34.216
5.9 | 0 | 1.2233 | 2.4467 | 3.67 | 4.8933 | 6.1167 | 7.34 | 8.5633 | 9.7867 | 11.01 | 12.2333 | 13.7405 | 15.2477 | 16.7549 | 18.2621 | 19.7693 | 20.1561 | 20.5429 | 20.9297 | 21.3165 | 21.7033 | 22.1282 | 22.5531 | 22.9779 | 23.4028 | 23.8277 | 24.2525 | 24.6774 | 25.1023 | 25.5271 | 25.952 | 26.228 | 26.5039 | 26.7799 | 27.0558 | 27.3318 | 27.6077 | 27.8837 | 28.1596 | 28.4356 | 28.7116 | 28.9875 | 29.2635 | 29.5394 | 29.8154 | 30.0913 | 30.3105 | 30.5296 | 30.7488 | 30.968 | 31.1871 | 31.4063 | 31.6254 | 31.8446 | 32.0637 | 32.2829 | 32.502 | 32.7212 | 32.9404 | 33.1595 | 33.3787 | 33.4387 | 33.4988 | 33.5589 | 33.6189 | 33.679 | 33.7391 | 33.7991 | 33.8592 | 33.9193 | 33.9793 | 34.0394 | 34.0995 | 34.1595 | 34.2196 | 34.2797 | 34.3397 | 34.3998 | 34.4599 | 34.5199 | 34.58 | 34.6401 | 34.7001 | 34.7602 | 34.8203 | 34.8803 | 34.9404 | 35.0005 | 35.0605 | 35.1206 | 35.1807 | 35.2018 | 35.2229 | 35.244 | 35.2651 | 35.2862 | 35.3073 | 35.3284 | 35.3496 | 35.3707 | 35.3918 | 35.4129 | 35.434 | 35.4551 | 35.4762 | 35.4973 | 35.5184 | 35.5396 | 35.5607 | 35.5818 | 35.6029 | 35.624 | 35.6451 | 35.6662 | 35.6873 | 35.7084 | 35.7296 | 35.7507 | 35.7718 | 35.7929 | 35.814 | 35.814 | 35.814 | 35.814 | 35.814 | 35.814 | 35.814 | 35.814 | 35.814 | 35.814 | 35.814 | 35.814 | 35.814 | 35.814 | 35.814 | 35.814 | 35.814 | 35.814 | 35.814 | 35.814 | 35.814 | 35.814 | 35.814 | 35.814 | 35.814 | 35.814 | 35.814 | 35.814 | 35.814 | 35.814 | 35.814 | 35.7823 | 35.7507 | 35.719 | 35.6873 | 35.6557 | 35.624 | 35.5923 | 35.5607 | 35.529 | 35.4973 | 35.4657 | 35.434 | 35.4023 | 35.3707 | 35.339 | 35.3073 | 35.2757 | 35.244 | 35.2123 | 35.1807 | 35.149 | 35.1173 | 35.0857 | 35.054 | 35.0223 | 34.9907 | 34.959 | 34.9273 | 34.8957 | 34.864
5.95 | 0 | 1.245 | 2.49 | 3.735 | 4.98 | 6.225 | 7.47 | 8.715 | 9.96 | 11.205 | 12.45 | 13.9876 | 15.5252 | 17.0628 | 18.6004 | 20.138 | 20.5274 | 20.9168 | 21.3062 | 21.6956 | 22.085 | 22.5181 | 22.9512 | 23.3843 | 23.8174 | 24.2505 | 24.6836 | 25.1167 | 25.5498 | 25.9829 | 26.416 | 26.6975 | 26.9791 | 27.2606 | 27.5421 | 27.8237 | 28.1052 | 28.3867 | 28.6683 | 28.9498 | 29.2313 | 29.5129 | 29.7944 | 30.0759 | 30.3575 | 30.639 | 30.8628 | 31.0866 | 31.3104 | 31.5342 | 31.758 | 31.9818 | 32.2056 | 32.4294 | 32.6532 | 32.877 | 33.1008 | 33.3246 | 33.5484 | 33.7722 | 33.996 | 34.0574 | 34.1187 | 34.1801 | 34.2415 | 34.3028 | 34.3642 | 34.4256 | 34.4869 | 34.5483 | 34.6097 | 34.671 | 34.7324 | 34.7938 | 34.8551 | 34.9165 | 34.9779 | 35.0392 | 35.1006 | 35.162 | 35.2233 | 35.2847 | 35.3461 | 35.4074 | 35.4688 | 35.5302 | 35.5915 | 35.6529 | 35.7143 | 35.7756 | 35.837 | 35.8587 | 35.8803 | 35.902 | 35.9237 | 35.9453 | 35.967 | 35.9887 | 36.0103 | 36.032 | 36.0537 | 36.0753 | 36.097 | 36.1187 | 36.1403 | 36.162 | 36.1837 | 36.2053 | 36.227 | 36.2487 | 36.2703 | 36.292 | 36.3137 | 36.3353 | 36.357 | 36.3787 | 36.4003 | 36.422 | 36.4437 | 36.4653 | 36.487 | 36.487 | 36.487 | 36.487 | 36.487 | 36.487 | 36.487 | 36.487 | 36.487 | 36.487 | 36.487 | 36.487 | 36.487 | 36.487 | 36.487 | 36.487 | 36.487 | 36.487 | 36.487 | 36.487 | 36.487 | 36.487 | 36.487 | 36.487 | 36.487 | 36.487 | 36.487 | 36.487 | 36.487 | 36.487 | 36.487 | 36.4545 | 36.422 | 36.3895 | 36.357 | 36.3245 | 36.292 | 36.2595 | 36.227 | 36.1945 | 36.162 | 36.1295 | 36.097 | 36.0645 | 36.032 | 35.9995 | 35.967 | 35.9345 | 35.902 | 35.8695 | 35.837 | 35.8045 | 35.772 | 35.7395 | 35.707 | 35.6745 | 35.642 | 35.6095 | 35.577 | 35.5445 | 35.512
6 | 0 | 1.2667 | 2.5333 | 3.8 | 5.0667 | 6.3333 | 7.6 | 8.8667 | 10.1333 | 11.4 | 12.6667 | 14.2347 | 15.8027 | 17.3707 | 18.9387 | 20.5067 | 20.8987 | 21.2907 | 21.6827 | 22.0747 | 22.4667 | 22.908 | 23.3493 | 23.7907 | 24.232 | 24.6733 | 25.1147 | 25.556 | 25.9973 | 26.4387 | 26.88 | 27.1671 | 27.4542 | 27.7413 | 28.0284 | 28.3156 | 28.6027 | 28.8898 | 29.1769 | 29.464 | 29.7511 | 30.0382 | 30.3253 | 30.6124 | 30.8996 | 31.1867 | 31.4151 | 31.6436 | 31.872 | 32.1004 | 32.3289 | 32.5573 | 32.7858 | 33.0142 | 33.2427 | 33.4711 | 33.6996 | 33.928 | 34.1564 | 34.3849 | 34.6133 | 34.676 | 34.7387 | 34.8013 | 34.864 | 34.9267 | 34.9893 | 35.052 | 35.1147 | 35.1773 | 35.24 | 35.3027 | 35.3653 | 35.428 | 35.4907 | 35.5533 | 35.616 | 35.6787 | 35.7413 | 35.804 | 35.8667 | 35.9293 | 35.992 | 36.0547 | 36.1173 | 36.18 | 36.2427 | 36.3053 | 36.368 | 36.4307 | 36.4933 | 36.5156 | 36.5378 | 36.56 | 36.5822 | 36.6044 | 36.6267 | 36.6489 | 36.6711 | 36.6933 | 36.7156 | 36.7378 | 36.76 | 36.7822 | 36.8044 | 36.8267 | 36.8489 | 36.8711 | 36.8933 | 36.9156 | 36.9378 | 36.96 | 36.9822 | 37.0044 | 37.0267 | 37.0489 | 37.0711 | 37.0933 | 37.1156 | 37.1378 | 37.16 | 37.16 | 37.16 | 37.16 | 37.16 | 37.16 | 37.16 | 37.16 | 37.16 | 37.16 | 37.16 | 37.16 | 37.16 | 37.16 | 37.16 | 37.16 | 37.16 | 37.16 | 37.16 | 37.16 | 37.16 | 37.16 | 37.16 | 37.16 | 37.16 | 37.16 | 37.16 | 37.16 | 37.16 | 37.16 | 37.16 | 37.1267 | 37.0933 | 37.06 | 37.0267 | 36.9933 | 36.96 | 36.9267 | 36.8933 | 36.86 | 36.8267 | 36.7933 | 36.76 | 36.7267 | 36.6933 | 36.66 | 36.6267 | 36.5933 | 36.56 | 36.5267 | 36.4933 | 36.46 | 36.4267 | 36.3933 | 36.36 | 36.3267 | 36.2933 | 36.26 | 36.2267 | 36.1933 | 36.16
6.05 | 0 | 1.2883 | 2.5767 | 3.865 | 5.1533 | 6.4417 | 7.73 | 9.0183 | 10.3067 | 11.595 | 12.8833 | 14.4817 | 16.0801 | 17.6785 | 19.2769 | 20.8753 | 21.2699 | 21.6645 | 22.0591 | 22.4537 | 22.8483 | 23.2979 | 23.7475 | 24.197 | 24.6466 | 25.0962 | 25.5457 | 25.9953 | 26.4449 | 26.8944 | 27.344 | 27.6367 | 27.9294 | 28.2221 | 28.5148 | 28.8074 | 29.1001 | 29.3928 | 29.6855 | 29.9782 | 30.2709 | 30.5636 | 30.8563 | 31.149 | 31.4416 | 31.7343 | 31.9674 | 32.2005 | 32.4336 | 32.6667 | 32.8998 | 33.1329 | 33.366 | 33.599 | 33.8321 | 34.0652 | 34.2983 | 34.5314 | 34.7645 | 34.9976 | 35.2307 | 35.2946 | 35.3586 | 35.4226 | 35.4865 | 35.5505 | 35.6145 | 35.6784 | 35.7424 | 35.8064 | 35.8703 | 35.9343 | 35.9983 | 36.0622 | 36.1262 | 36.1902 | 36.2541 | 36.3181 | 36.3821 | 36.446 | 36.51 | 36.574 | 36.6379 | 36.7019 | 36.7659 | 36.8298 | 36.8938 | 36.9578 | 37.0217 | 37.0857 | 37.1497 | 37.1724 | 37.1952 | 37.218 | 37.2408 | 37.2636 | 37.2863 | 37.3091 | 37.3319 | 37.3547 | 37.3774 | 37.4002 | 37.423 | 37.4458 | 37.4686 | 37.4913 | 37.5141 | 37.5369 | 37.5597 | 37.5824 | 37.6052 | 37.628 | 37.6508 | 37.6736 | 37.6963 | 37.7191 | 37.7419 | 37.7647 | 37.7874 | 37.8102 | 37.833 | 37.833 | 37.833 | 37.833 | 37.833 | 37.833 | 37.833 | 37.833 | 37.833 | 37.833 | 37.833 | 37.833 | 37.833 | 37.833 | 37.833 | 37.833 | 37.833 | 37.833 | 37.833 | 37.833 | 37.833 | 37.833 | 37.833 | 37.833 | 37.833 | 37.833 | 37.833 | 37.833 | 37.833 | 37.833 | 37.833 | 37.7988 | 37.7647 | 37.7305 | 37.6963 | 37.6622 | 37.628 | 37.5938 | 37.5597 | 37.5255 | 37.4913 | 37.4572 | 37.423 | 37.3888 | 37.3547 | 37.3205 | 37.2863 | 37.2522 | 37.218 | 37.1838 | 37.1497 | 37.1155 | 37.0813 | 37.0472 | 37.013 | 36.9788 | 36.9447 | 36.9105 | 36.8763 | 36.8422 | 36.808
6.1 | 0 | 1.31 | 2.62 | 3.93 | 5.24 | 6.55 | 7.86 | 9.17 | 10.48 | 11.79 | 13.1 | 14.7288 | 16.3576 | 17.9864 | 19.6152 | 21.244 | 21.6412 | 22.0384 | 22.4356 | 22.8328 | 23.23 | 23.6878 | 24.1456 | 24.6034 | 25.0612 | 25.519 | 25.9768 | 26.4346 | 26.8924 | 27.3502 | 27.808 | 28.1063 | 28.4045 | 28.7028 | 29.0011 | 29.2993 | 29.5976 | 29.8959 | 30.1941 | 30.4924 | 30.7907 | 31.0889 | 31.3872 | 31.6855 | 31.9837 | 32.282 | 32.5197 | 32.7575 | 32.9952 | 33.2329 | 33.4707 | 33.7084 | 33.9461 | 34.1839 | 34.4216 | 34.6593 | 34.8971 | 35.1348 | 35.3725 | 35.6103 | 35.848 | 35.9133 | 35.9785 | 36.0438 | 36.1091 | 36.1743 | 36.2396 | 36.3049 | 36.3701 | 36.4354 | 36.5007 | 36.5659 | 36.6312 | 36.6965 | 36.7617 | 36.827 | 36.8923 | 36.9575 | 37.0228 | 37.0881 | 37.1533 | 37.2186 | 37.2839 | 37.3491 | 37.4144 | 37.4797 | 37.5449 | 37.6102 | 37.6755 | 37.7407 | 37.806 | 37.8293 | 37.8527 | 37.876 | 37.8993 | 37.9227 | 37.946 | 37.9693 | 37.9927 | 38.016 | 38.0393 | 38.0627 | 38.086 | 38.1093 | 38.1327 | 38.156 | 38.1793 | 38.2027 | 38.226 | 38.2493 | 38.2727 | 38.296 | 38.3193 | 38.3427 | 38.366 | 38.3893 | 38.4127 | 38.436 | 38.4593 | 38.4827 | 38.506 | 38.506 | 38.506 | 38.506 | 38.506 | 38.506 | 38.506 | 38.506 | 38.506 | 38.506 | 38.506 | 38.506 | 38.506 | 38.506 | 38.506 | 38.506 | 38.506 | 38.506 | 38.506 | 38.506 | 38.506 | 38.506 | 38.506 | 38.506 | 38.506 | 38.506 | 38.506 | 38.506 | 38.506 | 38.506 | 38.506 | 38.471 | 38.436 | 38.401 | 38.366 | 38.331 | 38.296 | 38.261 | 38.226 | 38.191 | 38.156 | 38.121 | 38.086 | 38.051 | 38.016 | 37.981 | 37.946 | 37.911 | 37.876 | 37.841 | 37.806 | 37.771 | 37.736 | 37.701 | 37.666 | 37.631 | 37.596 | 37.561 | 37.526 | 37.491 | 37.456
6.15 | 0 | 1.3317 | 2.6633 | 3.995 | 5.3267 | 6.6583 | 7.99 | 9.3217 | 10.6533 | 11.985 | 13.3167 | 14.9759 | 16.6351 | 18.2943 | 19.9535 | 21.6127 | 22.0125 | 22.4123 | 22.8121 | 23.2119 | 23.6117 | 24.0777 | 24.5437 | 25.0098 | 25.4758 | 25.9418 | 26.4079 | 26.8739 | 27.3399 | 27.806 | 28.272 | 28.5758 | 28.8797 | 29.1835 | 29.4874 | 29.7912 | 30.0951 | 30.3989 | 30.7028 | 31.0066 | 31.3104 | 31.6143 | 31.9181 | 32.222 | 32.5258 | 32.8297 | 33.072 | 33.3144 | 33.5568 | 33.7992 | 34.0416 | 34.2839 | 34.5263 | 34.7687 | 35.0111 | 35.2534 | 35.4958 | 35.7382 | 35.9806 | 36.223 | 36.4653 | 36.5319 | 36.5985 | 36.665 | 36.7316 | 36.7982 | 36.8647 | 36.9313 | 36.9979 | 37.0644 | 37.131 | 37.1976 | 37.2641 | 37.3307 | 37.3973 | 37.4638 | 37.5304 | 37.597 | 37.6635 | 37.7301 | 37.7967 | 37.8632 | 37.9298 | 37.9964 | 38.0629 | 38.1295 | 38.1961 | 38.2626 | 38.3292 | 38.3958 | 38.4623 | 38.4862 | 38.5101 | 38.534 | 38.5579 | 38.5818 | 38.6057 | 38.6296 | 38.6534 | 38.6773 | 38.7012 | 38.7251 | 38.749 | 38.7729 | 38.7968 | 38.8207 | 38.8446 | 38.8684 | 38.8923 | 38.9162 | 38.9401 | 38.964 | 38.9879 | 39.0118 | 39.0357 | 39.0596 | 39.0834 | 39.1073 | 39.1312 | 39.1551 | 39.179 | 39.179 | 39.179 | 39.179 | 39.179 | 39.179 | 39.179 | 39.179 | 39.179 | 39.179 | 39.179 | 39.179 | 39.179 | 39.179 | 39.179 | 39.179 | 39.179 | 39.179 | 39.179 | 39.179 | 39.179 | 39.179 | 39.179 | 39.179 | 39.179 | 39.179 | 39.179 | 39.179 | 39.179 | 39.179 | 39.179 | 39.1432 | 39.1073 | 39.0715 | 39.0357 | 38.9998 | 38.964 | 38.9282 | 38.8923 | 38.8565 | 38.8207 | 38.7848 | 38.749 | 38.7132 | 38.6773 | 38.6415 | 38.6057 | 38.5698 | 38.534 | 38.4982 | 38.4623 | 38.4265 | 38.3907 | 38.3548 | 38.319 | 38.2832 | 38.2473 | 38.2115 | 38.1757 | 38.1398 | 38.104
6.2 | 0 | 1.3533 | 2.7067 | 4.06 | 5.4133 | 6.7667 | 8.12 | 9.4733 | 10.8267 | 12.18 | 13.5333 | 15.2229 | 16.9125 | 18.6021 | 20.2917 | 21.9813 | 22.3837 | 22.7861 | 23.1885 | 23.5909 | 23.9933 | 24.4676 | 24.9419 | 25.4161 | 25.8904 | 26.3647 | 26.8389 | 27.3132 | 27.7875 | 28.2617 | 28.736 | 29.0454 | 29.3548 | 29.6643 | 29.9737 | 30.2831 | 30.5925 | 30.902 | 31.2114 | 31.5208 | 31.8302 | 32.1396 | 32.4491 | 32.7585 | 33.0679 | 33.3773 | 33.6244 | 33.8714 | 34.1184 | 34.3654 | 34.6124 | 34.8595 | 35.1065 | 35.3535 | 35.6005 | 35.8476 | 36.0946 | 36.3416 | 36.5886 | 36.8356 | 37.0827 | 37.1505 | 37.2184 | 37.2863 | 37.3541 | 37.422 | 37.4899 | 37.5577 | 37.6256 | 37.6935 | 37.7613 | 37.8292 | 37.8971 | 37.9649 | 38.0328 | 38.1007 | 38.1685 | 38.2364 | 38.3043 | 38.3721 | 38.44 | 38.5079 | 38.5757 | 38.6436 | 38.7115 | 38.7793 | 38.8472 | 38.9151 | 38.9829 | 39.0508 | 39.1187 | 39.1431 | 39.1676 | 39.192 | 39.2164 | 39.2409 | 39.2653 | 39.2898 | 39.3142 | 39.3387 | 39.3631 | 39.3876 | 39.412 | 39.4364 | 39.4609 | 39.4853 | 39.5098 | 39.5342 | 39.5587 | 39.5831 | 39.6076 | 39.632 | 39.6564 | 39.6809 | 39.7053 | 39.7298 | 39.7542 | 39.7787 | 39.8031 | 39.8276 | 39.852 | 39.852 | 39.852 | 39.852 | 39.852 | 39.852 | 39.852 | 39.852 | 39.852 | 39.852 | 39.852 | 39.852 | 39.852 | 39.852 | 39.852 | 39.852 | 39.852 | 39.852 | 39.852 | 39.852 | 39.852 | 39.852 | 39.852 | 39.852 | 39.852 | 39.852 | 39.852 | 39.852 | 39.852 | 39.852 | 39.852 | 39.8153 | 39.7787 | 39.742 | 39.7053 | 39.6687 | 39.632 | 39.5953 | 39.5587 | 39.522 | 39.4853 | 39.4487 | 39.412 | 39.3753 | 39.3387 | 39.302 | 39.2653 | 39.2287 | 39.192 | 39.1553 | 39.1187 | 39.082 | 39.0453 | 39.0087 | 38.972 | 38.9353 | 38.8987 | 38.862 | 38.8253 | 38.7887 | 38.752
6.25 | 0 | 1.375 | 2.75 | 4.125 | 5.5 | 6.875 | 8.25 | 9.625 | 11 | 12.375 | 13.75 | 15.47 | 17.19 | 18.91 | 20.63 | 22.35 | 22.755 | 23.16 | 23.565 | 23.97 | 24.375 | 24.8575 | 25.34 | 25.8225 | 26.305 | 26.7875 | 27.27 | 27.7525 | 28.235 | 28.7175 | 29.2 | 29.515 | 29.83 | 30.145 | 30.46 | 30.775 | 31.09 | 31.405 | 31.72 | 32.035 | 32.35 | 32.665 | 32.98 | 33.295 | 33.61 | 33.925 | 34.1767 | 34.4283 | 34.68 | 34.9317 | 35.1833 | 35.435 | 35.6867 | 35.9383 | 36.19 | 36.4417 | 36.6933 | 36.945 | 37.1967 | 37.4483 | 37.7 | 37.7692 | 37.8383 | 37.9075 | 37.9767 | 38.0458 | 38.115 | 38.1842 | 38.2533 | 38.3225 | 38.3917 | 38.4608 | 38.53 | 38.5992 | 38.6683 | 38.7375 | 38.8067 | 38.8758 | 38.945 | 39.0142 | 39.0833 | 39.1525 | 39.2217 | 39.2908 | 39.36 | 39.4292 | 39.4983 | 39.5675 | 39.6367 | 39.7058 | 39.775 | 39.8 | 39.825 | 39.85 | 39.875 | 39.9 | 39.925 | 39.95 | 39.975 | 40 | 40.025 | 40.05 | 40.075 | 40.1 | 40.125 | 40.15 | 40.175 | 40.2 | 40.225 | 40.25 | 40.275 | 40.3 | 40.325 | 40.35 | 40.375 | 40.4 | 40.425 | 40.45 | 40.475 | 40.5 | 40.525 | 40.525 | 40.525 | 40.525 | 40.525 | 40.525 | 40.525 | 40.525 | 40.525 | 40.525 | 40.525 | 40.525 | 40.525 | 40.525 | 40.525 | 40.525 | 40.525 | 40.525 | 40.525 | 40.525 | 40.525 | 40.525 | 40.525 | 40.525 | 40.525 | 40.525 | 40.525 | 40.525 | 40.525 | 40.525 | 40.525 | 40.4875 | 40.45 | 40.4125 | 40.375 | 40.3375 | 40.3 | 40.2625 | 40.225 | 40.1875 | 40.15 | 40.1125 | 40.075 | 40.0375 | 40 | 39.9625 | 39.925 | 39.8875 | 39.85 | 39.8125 | 39.775 | 39.7375 | 39.7 | 39.6625 | 39.625 | 39.5875 | 39.55 | 39.5125 | 39.475 | 39.4375 | 39.4
6.3 | 0 | 1.3967 | 2.7933 | 4.19 | 5.5867 | 6.9833 | 8.38 | 9.7767 | 11.1733 | 12.57 | 13.9667 | 15.7171 | 17.4675 | 19.2179 | 20.9683 | 22.7187 | 23.1263 | 23.5339 | 23.9415 | 24.3491 | 24.7567 | 25.2474 | 25.7381 | 26.2289 | 26.7196 | 27.2103 | 27.7011 | 28.1918 | 28.6825 | 29.1733 | 29.664 | 29.9846 | 30.3052 | 30.6257 | 30.9463 | 31.2669 | 31.5875 | 31.908 | 32.2286 | 32.5492 | 32.8698 | 33.1904 | 33.5109 | 33.8315 | 34.1521 | 34.4727 | 34.729 | 34.9853 | 35.2416 | 35.4979 | 35.7542 | 36.0105 | 36.2668 | 36.5232 | 36.7795 | 37.0358 | 37.2921 | 37.5484 | 37.8047 | 38.061 | 38.3173 | 38.3878 | 38.4583 | 38.5287 | 38.5992 | 38.6697 | 38.7401 | 38.8106 | 38.8811 | 38.9515 | 39.022 | 39.0925 | 39.1629 | 39.2334 | 39.3039 | 39.3743 | 39.4448 | 39.5153 | 39.5857 | 39.6562 | 39.7267 | 39.7971 | 39.8676 | 39.9381 | 40.0085 | 40.079 | 40.1495 | 40.2199 | 40.2904 | 40.3609 | 40.4313 | 40.4569 | 40.4824 | 40.508 | 40.5336 | 40.5591 | 40.5847 | 40.6102 | 40.6358 | 40.6613 | 40.6869 | 40.7124 | 40.738 | 40.7636 | 40.7891 | 40.8147 | 40.8402 | 40.8658 | 40.8913 | 40.9169 | 40.9424 | 40.968 | 40.9936 | 41.0191 | 41.0447 | 41.0702 | 41.0958 | 41.1213 | 41.1469 | 41.1724 | 41.198 | 41.198 | 41.198 | 41.198 | 41.198 | 41.198 | 41.198 | 41.198 | 41.198 | 41.198 | 41.198 | 41.198 | 41.198 | 41.198 | 41.198 | 41.198 | 41.198 | 41.198 | 41.198 | 41.198 | 41.198 | 41.198 | 41.198 | 41.198 | 41.198 | 41.198 | 41.198 | 41.198 | 41.198 | 41.198 | 41.198 | 41.1597 | 41.1213 | 41.083 | 41.0447 | 41.0063 | 40.968 | 40.9297 | 40.8913 | 40.853 | 40.8147 | 40.7763 | 40.738 | 40.6997 | 40.6613 | 40.623 | 40.5847 | 40.5463 | 40.508 | 40.4697 | 40.4313 | 40.393 | 40.3547 | 40.3163 | 40.278 | 40.2397 | 40.2013 | 40.163 | 40.1247 | 40.0863 | 40.048
6.35 | 0 | 1.4183 | 2.8367 | 4.255 | 5.6733 | 7.0917 | 8.51 | 9.9283 | 11.3467 | 12.765 | 14.1833 | 15.9641 | 17.7449 | 19.5257 | 21.3065 | 23.0873 | 23.4975 | 23.9077 | 24.3179 | 24.7281 | 25.1383 | 25.6373 | 26.1363 | 26.6352 | 27.1342 | 27.6332 | 28.1321 | 28.6311 | 29.1301 | 29.629 | 30.128 | 30.4542 | 30.7803 | 31.1065 | 31.4326 | 31.7588 | 32.0849 | 32.4111 | 32.7372 | 33.0634 | 33.3896 | 33.7157 | 34.0419 | 34.368 | 34.6942 | 35.0203 | 35.2813 | 35.5422 | 35.8032 | 36.0642 | 36.3251 | 36.5861 | 36.847 | 37.108 | 37.3689 | 37.6299 | 37.8908 | 38.1518 | 38.4128 | 38.6737 | 38.9347 | 39.0064 | 39.0782 | 39.15 | 39.2217 | 39.2935 | 39.3653 | 39.437 | 39.5088 | 39.5806 | 39.6523 | 39.7241 | 39.7959 | 39.8676 | 39.9394 | 40.0112 | 40.0829 | 40.1547 | 40.2265 | 40.2982 | 40.37 | 40.4418 | 40.5135 | 40.5853 | 40.6571 | 40.7288 | 40.8006 | 40.8724 | 40.9441 | 41.0159 | 41.0877 | 41.1138 | 41.1399 | 41.166 | 41.1921 | 41.2182 | 41.2443 | 41.2704 | 41.2966 | 41.3227 | 41.3488 | 41.3749 | 41.401 | 41.4271 | 41.4532 | 41.4793 | 41.5054 | 41.5316 | 41.5577 | 41.5838 | 41.6099 | 41.636 | 41.6621 | 41.6882 | 41.7143 | 41.7404 | 41.7666 | 41.7927 | 41.8188 | 41.8449 | 41.871 | 41.871 | 41.871 | 41.871 | 41.871 | 41.871 | 41.871 | 41.871 | 41.871 | 41.871 | 41.871 | 41.871 | 41.871 | 41.871 | 41.871 | 41.871 | 41.871 | 41.871 | 41.871 | 41.871 | 41.871 | 41.871 | 41.871 | 41.871 | 41.871 | 41.871 | 41.871 | 41.871 | 41.871 | 41.871 | 41.871 | 41.8318 | 41.7927 | 41.7535 | 41.7143 | 41.6752 | 41.636 | 41.5968 | 41.5577 | 41.5185 | 41.4793 | 41.4402 | 41.401 | 41.3618 | 41.3227 | 41.2835 | 41.2443 | 41.2052 | 41.166 | 41.1268 | 41.0877 | 41.0485 | 41.0093 | 40.9702 | 40.931 | 40.8918 | 40.8527 | 40.8135 | 40.7743 | 40.7352 | 40.696
6.4 | 0 | 1.44 | 2.88 | 4.32 | 5.76 | 7.2 | 8.64 | 10.08 | 11.52 | 12.96 | 14.4 | 16.2112 | 18.0224 | 19.8336 | 21.6448 | 23.456 | 23.8688 | 24.2816 | 24.6944 | 25.1072 | 25.52 | 26.0272 | 26.5344 | 27.0416 | 27.5488 | 28.056 | 28.5632 | 29.0704 | 29.5776 | 30.0848 | 30.592 | 30.9237 | 31.2555 | 31.5872 | 31.9189 | 32.2507 | 32.5824 | 32.9141 | 33.2459 | 33.5776 | 33.9093 | 34.2411 | 34.5728 | 34.9045 | 35.2363 | 35.568 | 35.8336 | 36.0992 | 36.3648 | 36.6304 | 36.896 | 37.1616 | 37.4272 | 37.6928 | 37.9584 | 38.224 | 38.4896 | 38.7552 | 39.0208 | 39.2864 | 39.552 | 39.6251 | 39.6981 | 39.7712 | 39.8443 | 39.9173 | 39.9904 | 40.0635 | 40.1365 | 40.2096 | 40.2827 | 40.3557 | 40.4288 | 40.5019 | 40.5749 | 40.648 | 40.7211 | 40.7941 | 40.8672 | 40.9403 | 41.0133 | 41.0864 | 41.1595 | 41.2325 | 41.3056 | 41.3787 | 41.4517 | 41.5248 | 41.5979 | 41.6709 | 41.744 | 41.7707 | 41.7973 | 41.824 | 41.8507 | 41.8773 | 41.904 | 41.9307 | 41.9573 | 41.984 | 42.0107 | 42.0373 | 42.064 | 42.0907 | 42.1173 | 42.144 | 42.1707 | 42.1973 | 42.224 | 42.2507 | 42.2773 | 42.304 | 42.3307 | 42.3573 | 42.384 | 42.4107 | 42.4373 | 42.464 | 42.4907 | 42.5173 | 42.544 | 42.544 | 42.544 | 42.544 | 42.544 | 42.544 | 42.544 | 42.544 | 42.544 | 42.544 | 42.544 | 42.544 | 42.544 | 42.544 | 42.544 | 42.544 | 42.544 | 42.544 | 42.544 | 42.544 | 42.544 | 42.544 | 42.544 | 42.544 | 42.544 | 42.544 | 42.544 | 42.544 | 42.544 | 42.544 | 42.544 | 42.504 | 42.464 | 42.424 | 42.384 | 42.344 | 42.304 | 42.264 | 42.224 | 42.184 | 42.144 | 42.104 | 42.064 | 42.024 | 41.984 | 41.944 | 41.904 | 41.864 | 41.824 | 41.784 | 41.744 | 41.704 | 41.664 | 41.624 | 41.584 | 41.544 | 41.504 | 41.464 | 41.424 | 41.384 | 41.344
6.45 | 0 | 1.4617 | 2.9233 | 4.385 | 5.8467 | 7.3083 | 8.77 | 10.2317 | 11.6933 | 13.155 | 14.6167 | 16.4583 | 18.2999 | 20.1415 | 21.9831 | 23.8247 | 24.2401 | 24.6555 | 25.0709 | 25.4863 | 25.9017 | 26.4171 | 26.9325 | 27.448 | 27.9634 | 28.4788 | 28.9943 | 29.5097 | 30.0251 | 30.5406 | 31.056 | 31.3933 | 31.7306 | 32.0679 | 32.4052 | 32.7426 | 33.0799 | 33.4172 | 33.7545 | 34.0918 | 34.4291 | 34.7664 | 35.1037 | 35.441 | 35.7784 | 36.1157 | 36.3859 | 36.6562 | 36.9264 | 37.1966 | 37.4669 | 37.7371 | 38.0074 | 38.2776 | 38.5479 | 38.8181 | 39.0884 | 39.3586 | 39.6288 | 39.8991 | 40.1693 | 40.2437 | 40.3181 | 40.3924 | 40.4668 | 40.5412 | 40.6155 | 40.6899 | 40.7643 | 40.8386 | 40.913 | 40.9874 | 41.0617 | 41.1361 | 41.2105 | 41.2848 | 41.3592 | 41.4336 | 41.5079 | 41.5823 | 41.6567 | 41.731 | 41.8054 | 41.8798 | 41.9541 | 42.0285 | 42.1029 | 42.1772 | 42.2516 | 42.326 | 42.4003 | 42.4276 | 42.4548 | 42.482 | 42.5092 | 42.5364 | 42.5637 | 42.5909 | 42.6181 | 42.6453 | 42.6726 | 42.6998 | 42.727 | 42.7542 | 42.7814 | 42.8087 | 42.8359 | 42.8631 | 42.8903 | 42.9176 | 42.9448 | 42.972 | 42.9992 | 43.0264 | 43.0537 | 43.0809 | 43.1081 | 43.1353 | 43.1626 | 43.1898 | 43.217 | 43.217 | 43.217 | 43.217 | 43.217 | 43.217 | 43.217 | 43.217 | 43.217 | 43.217 | 43.217 | 43.217 | 43.217 | 43.217 | 43.217 | 43.217 | 43.217 | 43.217 | 43.217 | 43.217 | 43.217 | 43.217 | 43.217 | 43.217 | 43.217 | 43.217 | 43.217 | 43.217 | 43.217 | 43.217 | 43.217 | 43.1762 | 43.1353 | 43.0945 | 43.0537 | 43.0128 | 42.972 | 42.9312 | 42.8903 | 42.8495 | 42.8087 | 42.7678 | 42.727 | 42.6862 | 42.6453 | 42.6045 | 42.5637 | 42.5228 | 42.482 | 42.4412 | 42.4003 | 42.3595 | 42.3187 | 42.2778 | 42.237 | 42.1962 | 42.1553 | 42.1145 | 42.0737 | 42.0328 | 41.992
6.5 | 0 | 1.4833 | 2.9667 | 4.45 | 5.9333 | 7.4167 | 8.9 | 10.3833 | 11.8667 | 13.35 | 14.8333 | 16.7053 | 18.5773 | 20.4493 | 22.3213 | 24.1933 | 24.6113 | 25.0293 | 25.4473 | 25.8653 | 26.2833 | 26.807 | 27.3307 | 27.8543 | 28.378 | 28.9017 | 29.4253 | 29.949 | 30.4727 | 30.9963 | 31.52 | 31.8629 | 32.2058 | 32.5487 | 32.8916 | 33.2344 | 33.5773 | 33.9202 | 34.2631 | 34.606 | 34.9489 | 35.2918 | 35.6347 | 35.9776 | 36.3204 | 36.6633 | 36.9382 | 37.2131 | 37.488 | 37.7629 | 38.0378 | 38.3127 | 38.5876 | 38.8624 | 39.1373 | 39.4122 | 39.6871 | 39.962 | 40.2369 | 40.5118 | 40.7867 | 40.8623 | 40.938 | 41.0137 | 41.0893 | 41.165 | 41.2407 | 41.3163 | 41.392 | 41.4677 | 41.5433 | 41.619 | 41.6947 | 41.7703 | 41.846 | 41.9217 | 41.9973 | 42.073 | 42.1487 | 42.2243 | 42.3 | 42.3757 | 42.4513 | 42.527 | 42.6027 | 42.6783 | 42.754 | 42.8297 | 42.9053 | 42.981 | 43.0567 | 43.0844 | 43.1122 | 43.14 | 43.1678 | 43.1956 | 43.2233 | 43.2511 | 43.2789 | 43.3067 | 43.3344 | 43.3622 | 43.39 | 43.4178 | 43.4456 | 43.4733 | 43.5011 | 43.5289 | 43.5567 | 43.5844 | 43.6122 | 43.64 | 43.6678 | 43.6956 | 43.7233 | 43.7511 | 43.7789 | 43.8067 | 43.8344 | 43.8622 | 43.89 | 43.89 | 43.89 | 43.89 | 43.89 | 43.89 | 43.89 | 43.89 | 43.89 | 43.89 | 43.89 | 43.89 | 43.89 | 43.89 | 43.89 | 43.89 | 43.89 | 43.89 | 43.89 | 43.89 | 43.89 | 43.89 | 43.89 | 43.89 | 43.89 | 43.89 | 43.89 | 43.89 | 43.89 | 43.89 | 43.89 | 43.8483 | 43.8067 | 43.765 | 43.7233 | 43.6817 | 43.64 | 43.5983 | 43.5567 | 43.515 | 43.4733 | 43.4317 | 43.39 | 43.3483 | 43.3067 | 43.265 | 43.2233 | 43.1817 | 43.14 | 43.0983 | 43.0567 | 43.015 | 42.9733 | 42.9317 | 42.89 | 42.8483 | 42.8067 | 42.765 | 42.7233 | 42.6817 | 42.64
6.55 | 0 | 1.505 | 3.01 | 4.515 | 6.02 | 7.525 | 9.03 | 10.535 | 12.04 | 13.545 | 15.05 | 16.9524 | 18.8548 | 20.7572 | 22.6596 | 24.562 | 24.9826 | 25.4032 | 25.8238 | 26.2444 | 26.665 | 27.1969 | 27.7288 | 28.2607 | 28.7926 | 29.3245 | 29.8564 | 30.3883 | 30.9202 | 31.4521 | 31.984 | 32.3325 | 32.6809 | 33.0294 | 33.3779 | 33.7263 | 34.0748 | 34.4233 | 34.7717 | 35.1202 | 35.4687 | 35.8171 | 36.1656 | 36.5141 | 36.8625 | 37.211 | 37.4905 | 37.7701 | 38.0496 | 38.3291 | 38.6087 | 38.8882 | 39.1677 | 39.4473 | 39.7268 | 40.0063 | 40.2859 | 40.5654 | 40.8449 | 41.1245 | 41.404 | 41.481 | 41.5579 | 41.6349 | 41.7119 | 41.7888 | 41.8658 | 41.9428 | 42.0197 | 42.0967 | 42.1737 | 42.2506 | 42.3276 | 42.4046 | 42.4815 | 42.5585 | 42.6355 | 42.7124 | 42.7894 | 42.8664 | 42.9433 | 43.0203 | 43.0973 | 43.1742 | 43.2512 | 43.3282 | 43.4051 | 43.4821 | 43.5591 | 43.636 | 43.713 | 43.7413 | 43.7697 | 43.798 | 43.8263 | 43.8547 | 43.883 | 43.9113 | 43.9397 | 43.968 | 43.9963 | 44.0247 | 44.053 | 44.0813 | 44.1097 | 44.138 | 44.1663 | 44.1947 | 44.223 | 44.2513 | 44.2797 | 44.308 | 44.3363 | 44.3647 | 44.393 | 44.4213 | 44.4497 | 44.478 | 44.5063 | 44.5347 | 44.563 | 44.563 | 44.563 | 44.563 | 44.563 | 44.563 | 44.563 | 44.563 | 44.563 | 44.563 | 44.563 | 44.563 | 44.563 | 44.563 | 44.563 | 44.563 | 44.563 | 44.563 | 44.563 | 44.563 | 44.563 | 44.563 | 44.563 | 44.563 | 44.563 | 44.563 | 44.563 | 44.563 | 44.563 | 44.563 | 44.563 | 44.5205 | 44.478 | 44.4355 | 44.393 | 44.3505 | 44.308 | 44.2655 | 44.223 | 44.1805 | 44.138 | 44.0955 | 44.053 | 44.0105 | 43.968 | 43.9255 | 43.883 | 43.8405 | 43.798 | 43.7555 | 43.713 | 43.6705 | 43.628 | 43.5855 | 43.543 | 43.5005 | 43.458 | 43.4155 | 43.373 | 43.3305 | 43.288
6.6 | 0 | 1.5267 | 3.0533 | 4.58 | 6.1067 | 7.6333 | 9.16 | 10.6867 | 12.2133 | 13.74 | 15.2667 | 17.1995 | 19.1323 | 21.0651 | 22.9979 | 24.9307 | 25.3539 | 25.7771 | 26.2003 | 26.6235 | 27.0467 | 27.5868 | 28.1269 | 28.6671 | 29.2072 | 29.7473 | 30.2875 | 30.8276 | 31.3677 | 31.9079 | 32.448 | 32.802 | 33.1561 | 33.5101 | 33.8642 | 34.2182 | 34.5723 | 34.9263 | 35.2804 | 35.6344 | 35.9884 | 36.3425 | 36.6965 | 37.0506 | 37.4046 | 37.7587 | 38.0428 | 38.327 | 38.6112 | 38.8954 | 39.1796 | 39.4637 | 39.7479 | 40.0321 | 40.3163 | 40.6004 | 40.8846 | 41.1688 | 41.453 | 41.7372 | 42.0213 | 42.0996 | 42.1779 | 42.2561 | 42.3344 | 42.4127 | 42.4909 | 42.5692 | 42.6475 | 42.7257 | 42.804 | 42.8823 | 42.9605 | 43.0388 | 43.1171 | 43.1953 | 43.2736 | 43.3519 | 43.4301 | 43.5084 | 43.5867 | 43.6649 | 43.7432 | 43.8215 | 43.8997 | 43.978 | 44.0563 | 44.1345 | 44.2128 | 44.2911 | 44.3693 | 44.3982 | 44.4271 | 44.456 | 44.4849 | 44.5138 | 44.5427 | 44.5716 | 44.6004 | 44.6293 | 44.6582 | 44.6871 | 44.716 | 44.7449 | 44.7738 | 44.8027 | 44.8316 | 44.8604 | 44.8893 | 44.9182 | 44.9471 | 44.976 | 45.0049 | 45.0338 | 45.0627 | 45.0916 | 45.1204 | 45.1493 | 45.1782 | 45.2071 | 45.236 | 45.236 | 45.236 | 45.236 | 45.236 | 45.236 | 45.236 | 45.236 | 45.236 | 45.236 | 45.236 | 45.236 | 45.236 | 45.236 | 45.236 | 45.236 | 45.236 | 45.236 | 45.236 | 45.236 | 45.236 | 45.236 | 45.236 | 45.236 | 45.236 | 45.236 | 45.236 | 45.236 | 45.236 | 45.236 | 45.236 | 45.1927 | 45.1493 | 45.106 | 45.0627 | 45.0193 | 44.976 | 44.9327 | 44.8893 | 44.846 | 44.8027 | 44.7593 | 44.716 | 44.6727 | 44.6293 | 44.586 | 44.5427 | 44.4993 | 44.456 | 44.4127 | 44.3693 | 44.326 | 44.2827 | 44.2393 | 44.196 | 44.1527 | 44.1093 | 44.066 | 44.0227 | 43.9793 | 43.936
6.65 | 0 | 1.5483 | 3.0967 | 4.645 | 6.1933 | 7.7417 | 9.29 | 10.8383 | 12.3867 | 13.935 | 15.4833 | 17.4465 | 19.4097 | 21.3729 | 23.3361 | 25.2993 | 25.7251 | 26.1509 | 26.5767 | 27.0025 | 27.4283 | 27.9767 | 28.5251 | 29.0734 | 29.6218 | 30.1702 | 30.7185 | 31.2669 | 31.8153 | 32.3636 | 32.912 | 33.2716 | 33.6312 | 33.9909 | 34.3505 | 34.7101 | 35.0697 | 35.4294 | 35.789 | 36.1486 | 36.5082 | 36.8678 | 37.2275 | 37.5871 | 37.9467 | 38.3063 | 38.5952 | 38.884 | 39.1728 | 39.4616 | 39.7504 | 40.0393 | 40.3281 | 40.6169 | 40.9057 | 41.1946 | 41.4834 | 41.7722 | 42.061 | 42.3498 | 42.6387 | 42.7182 | 42.7978 | 42.8774 | 42.9569 | 43.0365 | 43.1161 | 43.1956 | 43.2752 | 43.3548 | 43.4343 | 43.5139 | 43.5935 | 43.673 | 43.7526 | 43.8322 | 43.9117 | 43.9913 | 44.0709 | 44.1504 | 44.23 | 44.3096 | 44.3891 | 44.4687 | 44.5483 | 44.6278 | 44.7074 | 44.787 | 44.8665 | 44.9461 | 45.0257 | 45.0551 | 45.0846 | 45.114 | 45.1434 | 45.1729 | 45.2023 | 45.2318 | 45.2612 | 45.2907 | 45.3201 | 45.3496 | 45.379 | 45.4084 | 45.4379 | 45.4673 | 45.4968 | 45.5262 | 45.5557 | 45.5851 | 45.6146 | 45.644 | 45.6734 | 45.7029 | 45.7323 | 45.7618 | 45.7912 | 45.8207 | 45.8501 | 45.8796 | 45.909 | 45.909 | 45.909 | 45.909 | 45.909 | 45.909 | 45.909 | 45.909 | 45.909 | 45.909 | 45.909 | 45.909 | 45.909 | 45.909 | 45.909 | 45.909 | 45.909 | 45.909 | 45.909 | 45.909 | 45.909 | 45.909 | 45.909 | 45.909 | 45.909 | 45.909 | 45.909 | 45.909 | 45.909 | 45.909 | 45.909 | 45.8648 | 45.8207 | 45.7765 | 45.7323 | 45.6882 | 45.644 | 45.5998 | 45.5557 | 45.5115 | 45.4673 | 45.4232 | 45.379 | 45.3348 | 45.2907 | 45.2465 | 45.2023 | 45.1582 | 45.114 | 45.0698 | 45.0257 | 44.9815 | 44.9373 | 44.8932 | 44.849 | 44.8048 | 44.7607 | 44.7165 | 44.6723 | 44.6282 | 44.584
6.7 | 0 | 1.57 | 3.14 | 4.71 | 6.28 | 7.85 | 9.42 | 10.99 | 12.56 | 14.13 | 15.7 | 17.6936 | 19.6872 | 21.6808 | 23.6744 | 25.668 | 26.0964 | 26.5248 | 26.9532 | 27.3816 | 27.81 | 28.3666 | 28.9232 | 29.4798 | 30.0364 | 30.593 | 31.1496 | 31.7062 | 32.2628 | 32.8194 | 33.376 | 33.7412 | 34.1064 | 34.4716 | 34.8368 | 35.202 | 35.5672 | 35.9324 | 36.2976 | 36.6628 | 37.028 | 37.3932 | 37.7584 | 38.1236 | 38.4888 | 38.854 | 39.1475 | 39.4409 | 39.7344 | 40.0279 | 40.3213 | 40.6148 | 40.9083 | 41.2017 | 41.4952 | 41.7887 | 42.0821 | 42.3756 | 42.6691 | 42.9625 | 43.256 | 43.3369 | 43.4177 | 43.4986 | 43.5795 | 43.6603 | 43.7412 | 43.8221 | 43.9029 | 43.9838 | 44.0647 | 44.1455 | 44.2264 | 44.3073 | 44.3881 | 44.469 | 44.5499 | 44.6307 | 44.7116 | 44.7925 | 44.8733 | 44.9542 | 45.0351 | 45.1159 | 45.1968 | 45.2777 | 45.3585 | 45.4394 | 45.5203 | 45.6011 | 45.682 | 45.712 | 45.742 | 45.772 | 45.802 | 45.832 | 45.862 | 45.892 | 45.922 | 45.952 | 45.982 | 46.012 | 46.042 | 46.072 | 46.102 | 46.132 | 46.162 | 46.192 | 46.222 | 46.252 | 46.282 | 46.312 | 46.342 | 46.372 | 46.402 | 46.432 | 46.462 | 46.492 | 46.522 | 46.552 | 46.582 | 46.582 | 46.582 | 46.582 | 46.582 | 46.582 | 46.582 | 46.582 | 46.582 | 46.582 | 46.582 | 46.582 | 46.582 | 46.582 | 46.582 | 46.582 | 46.582 | 46.582 | 46.582 | 46.582 | 46.582 | 46.582 | 46.582 | 46.582 | 46.582 | 46.582 | 46.582 | 46.582 | 46.582 | 46.582 | 46.582 | 46.537 | 46.492 | 46.447 | 46.402 | 46.357 | 46.312 | 46.267 | 46.222 | 46.177 | 46.132 | 46.087 | 46.042 | 45.997 | 45.952 | 45.907 | 45.862 | 45.817 | 45.772 | 45.727 | 45.682 | 45.637 | 45.592 | 45.547 | 45.502 | 45.457 | 45.412 | 45.367 | 45.322 | 45.277 | 45.232
6.75 | 0 | 1.5917 | 3.1833 | 4.775 | 6.3667 | 7.9583 | 9.55 | 11.1417 | 12.7333 | 14.325 | 15.9167 | 17.9407 | 19.9647 | 21.9887 | 24.0127 | 26.0367 | 26.4677 | 26.8987 | 27.3297 | 27.7607 | 28.1917 | 28.7565 | 29.3213 | 29.8862 | 30.451 | 31.0158 | 31.5807 | 32.1455 | 32.7103 | 33.2752 | 33.84 | 34.2108 | 34.5816 | 34.9523 | 35.3231 | 35.6939 | 36.0647 | 36.4354 | 36.8062 | 37.177 | 37.5478 | 37.9186 | 38.2893 | 38.6601 | 39.0309 | 39.4017 | 39.6998 | 39.9979 | 40.296 | 40.5941 | 40.8922 | 41.1903 | 41.4884 | 41.7866 | 42.0847 | 42.3828 | 42.6809 | 42.979 | 43.2771 | 43.5752 | 43.8733 | 43.9555 | 44.0377 | 44.1198 | 44.202 | 44.2842 | 44.3663 | 44.4485 | 44.5307 | 44.6128 | 44.695 | 44.7772 | 44.8593 | 44.9415 | 45.0237 | 45.1058 | 45.188 | 45.2702 | 45.3523 | 45.4345 | 45.5167 | 45.5988 | 45.681 | 45.7632 | 45.8453 | 45.9275 | 46.0097 | 46.0918 | 46.174 | 46.2562 | 46.3383 | 46.3689 | 46.3994 | 46.43 | 46.4606 | 46.4911 | 46.5217 | 46.5522 | 46.5828 | 46.6133 | 46.6439 | 46.6744 | 46.705 | 46.7356 | 46.7661 | 46.7967 | 46.8272 | 46.8578 | 46.8883 | 46.9189 | 46.9494 | 46.98 | 47.0106 | 47.0411 | 47.0717 | 47.1022 | 47.1328 | 47.1633 | 47.1939 | 47.2244 | 47.255 | 47.255 | 47.255 | 47.255 | 47.255 | 47.255 | 47.255 | 47.255 | 47.255 | 47.255 | 47.255 | 47.255 | 47.255 | 47.255 | 47.255 | 47.255 | 47.255 | 47.255 | 47.255 | 47.255 | 47.255 | 47.255 | 47.255 | 47.255 | 47.255 | 47.255 | 47.255 | 47.255 | 47.255 | 47.255 | 47.255 | 47.2092 | 47.1633 | 47.1175 | 47.0717 | 47.0258 | 46.98 | 46.9342 | 46.8883 | 46.8425 | 46.7967 | 46.7508 | 46.705 | 46.6592 | 46.6133 | 46.5675 | 46.5217 | 46.4758 | 46.43 | 46.3842 | 46.3383 | 46.2925 | 46.2467 | 46.2008 | 46.155 | 46.1092 | 46.0633 | 46.0175 | 45.9717 | 45.9258 | 45.88
6.8 | 0 | 1.6133 | 3.2267 | 4.84 | 6.4533 | 8.0667 | 9.68 | 11.2933 | 12.9067 | 14.52 | 16.1333 | 18.1877 | 20.2421 | 22.2965 | 24.3509 | 26.4053 | 26.8389 | 27.2725 | 27.7061 | 28.1397 | 28.5733 | 29.1464 | 29.7195 | 30.2925 | 30.8656 | 31.4387 | 32.0117 | 32.5848 | 33.1579 | 33.7309 | 34.304 | 34.6804 | 35.0567 | 35.4331 | 35.8094 | 36.1858 | 36.5621 | 36.9385 | 37.3148 | 37.6912 | 38.0676 | 38.4439 | 38.8203 | 39.1966 | 39.573 | 39.9493 | 40.2521 | 40.5548 | 40.8576 | 41.1604 | 41.4631 | 41.7659 | 42.0686 | 42.3714 | 42.6741 | 42.9769 | 43.2796 | 43.5824 | 43.8852 | 44.1879 | 44.4907 | 44.5741 | 44.6576 | 44.7411 | 44.8245 | 44.908 | 44.9915 | 45.0749 | 45.1584 | 45.2419 | 45.3253 | 45.4088 | 45.4923 | 45.5757 | 45.6592 | 45.7427 | 45.8261 | 45.9096 | 45.9931 | 46.0765 | 46.16 | 46.2435 | 46.3269 | 46.4104 | 46.4939 | 46.5773 | 46.6608 | 46.7443 | 46.8277 | 46.9112 | 46.9947 | 47.0258 | 47.0569 | 47.088 | 47.1191 | 47.1502 | 47.1813 | 47.2124 | 47.2436 | 47.2747 | 47.3058 | 47.3369 | 47.368 | 47.3991 | 47.4302 | 47.4613 | 47.4924 | 47.5236 | 47.5547 | 47.5858 | 47.6169 | 47.648 | 47.6791 | 47.7102 | 47.7413 | 47.7724 | 47.8036 | 47.8347 | 47.8658 | 47.8969 | 47.928 | 47.928 | 47.928 | 47.928 | 47.928 | 47.928 | 47.928 | 47.928 | 47.928 | 47.928 | 47.928 | 47.928 | 47.928 | 47.928 | 47.928 | 47.928 | 47.928 | 47.928 | 47.928 | 47.928 | 47.928 | 47.928 | 47.928 | 47.928 | 47.928 | 47.928 | 47.928 | 47.928 | 47.928 | 47.928 | 47.928 | 47.8813 | 47.8347 | 47.788 | 47.7413 | 47.6947 | 47.648 | 47.6013 | 47.5547 | 47.508 | 47.4613 | 47.4147 | 47.368 | 47.3213 | 47.2747 | 47.228 | 47.1813 | 47.1347 | 47.088 | 47.0413 | 46.9947 | 46.948 | 46.9013 | 46.8547 | 46.808 | 46.7613 | 46.7147 | 46.668 | 46.6213 | 46.5747 | 46.528
6.85 | 0 | 1.635 | 3.27 | 4.905 | 6.54 | 8.175 | 9.81 | 11.445 | 13.08 | 14.715 | 16.35 | 18.4348 | 20.5196 | 22.6044 | 24.6892 | 26.774 | 27.2102 | 27.6464 | 28.0826 | 28.5188 | 28.955 | 29.5363 | 30.1176 | 30.6989 | 31.2802 | 31.8615 | 32.4428 | 33.0241 | 33.6054 | 34.1867 | 34.768 | 35.1499 | 35.5319 | 35.9138 | 36.2957 | 36.6777 | 37.0596 | 37.4415 | 37.8235 | 38.2054 | 38.5873 | 38.9693 | 39.3512 | 39.7331 | 40.1151 | 40.497 | 40.8044 | 41.1118 | 41.4192 | 41.7266 | 42.034 | 42.3414 | 42.6488 | 42.9562 | 43.2636 | 43.571 | 43.8784 | 44.1858 | 44.4932 | 44.8006 | 45.108 | 45.1928 | 45.2775 | 45.3623 | 45.4471 | 45.5318 | 45.6166 | 45.7014 | 45.7861 | 45.8709 | 45.9557 | 46.0404 | 46.1252 | 46.21 | 46.2947 | 46.3795 | 46.4643 | 46.549 | 46.6338 | 46.7186 | 46.8033 | 46.8881 | 46.9729 | 47.0576 | 47.1424 | 47.2272 | 47.3119 | 47.3967 | 47.4815 | 47.5662 | 47.651 | 47.6827 | 47.7143 | 47.746 | 47.7777 | 47.8093 | 47.841 | 47.8727 | 47.9043 | 47.936 | 47.9677 | 47.9993 | 48.031 | 48.0627 | 48.0943 | 48.126 | 48.1577 | 48.1893 | 48.221 | 48.2527 | 48.2843 | 48.316 | 48.3477 | 48.3793 | 48.411 | 48.4427 | 48.4743 | 48.506 | 48.5377 | 48.5693 | 48.601 | 48.601 | 48.601 | 48.601 | 48.601 | 48.601 | 48.601 | 48.601 | 48.601 | 48.601 | 48.601 | 48.601 | 48.601 | 48.601 | 48.601 | 48.601 | 48.601 | 48.601 | 48.601 | 48.601 | 48.601 | 48.601 | 48.601 | 48.601 | 48.601 | 48.601 | 48.601 | 48.601 | 48.601 | 48.601 | 48.601 | 48.5535 | 48.506 | 48.4585 | 48.411 | 48.3635 | 48.316 | 48.2685 | 48.221 | 48.1735 | 48.126 | 48.0785 | 48.031 | 47.9835 | 47.936 | 47.8885 | 47.841 | 47.7935 | 47.746 | 47.6985 | 47.651 | 47.6035 | 47.556 | 47.5085 | 47.461 | 47.4135 | 47.366 | 47.3185 | 47.271 | 47.2235 | 47.176
6.9 | 0 | 1.6567 | 3.3133 | 4.97 | 6.6267 | 8.2833 | 9.94 | 11.5967 | 13.2533 | 14.91 | 16.5667 | 18.6819 | 20.7971 | 22.9123 | 25.0275 | 27.1427 | 27.5815 | 28.0203 | 28.4591 | 28.8979 | 29.3367 | 29.9262 | 30.5157 | 31.1053 | 31.6948 | 32.2843 | 32.8739 | 33.4634 | 34.0529 | 34.6425 | 35.232 | 35.6195 | 36.007 | 36.3945 | 36.782 | 37.1696 | 37.5571 | 37.9446 | 38.3321 | 38.7196 | 39.1071 | 39.4946 | 39.8821 | 40.2696 | 40.6572 | 41.0447 | 41.3567 | 41.6688 | 41.9808 | 42.2928 | 42.6049 | 42.9169 | 43.229 | 43.541 | 43.8531 | 44.1651 | 44.4772 | 44.7892 | 45.1012 | 45.4133 | 45.7253 | 45.8114 | 45.8975 | 45.9835 | 46.0696 | 46.1557 | 46.2417 | 46.3278 | 46.4139 | 46.4999 | 46.586 | 46.6721 | 46.7581 | 46.8442 | 46.9303 | 47.0163 | 47.1024 | 47.1885 | 47.2745 | 47.3606 | 47.4467 | 47.5327 | 47.6188 | 47.7049 | 47.7909 | 47.877 | 47.9631 | 48.0491 | 48.1352 | 48.2213 | 48.3073 | 48.3396 | 48.3718 | 48.404 | 48.4362 | 48.4684 | 48.5007 | 48.5329 | 48.5651 | 48.5973 | 48.6296 | 48.6618 | 48.694 | 48.7262 | 48.7584 | 48.7907 | 48.8229 | 48.8551 | 48.8873 | 48.9196 | 48.9518 | 48.984 | 49.0162 | 49.0484 | 49.0807 | 49.1129 | 49.1451 | 49.1773 | 49.2096 | 49.2418 | 49.274 | 49.274 | 49.274 | 49.274 | 49.274 | 49.274 | 49.274 | 49.274 | 49.274 | 49.274 | 49.274 | 49.274 | 49.274 | 49.274 | 49.274 | 49.274 | 49.274 | 49.274 | 49.274 | 49.274 | 49.274 | 49.274 | 49.274 | 49.274 | 49.274 | 49.274 | 49.274 | 49.274 | 49.274 | 49.274 | 49.274 | 49.2257 | 49.1773 | 49.129 | 49.0807 | 49.0323 | 48.984 | 48.9357 | 48.8873 | 48.839 | 48.7907 | 48.7423 | 48.694 | 48.6457 | 48.5973 | 48.549 | 48.5007 | 48.4523 | 48.404 | 48.3557 | 48.3073 | 48.259 | 48.2107 | 48.1623 | 48.114 | 48.0657 | 48.0173 | 47.969 | 47.9207 | 47.8723 | 47.824
6.95 | 0 | 1.6783 | 3.3567 | 5.035 | 6.7133 | 8.3917 | 10.07 | 11.7483 | 13.4267 | 15.105 | 16.7833 | 18.9289 | 21.0745 | 23.2201 | 25.3657 | 27.5113 | 27.9527 | 28.3941 | 28.8355 | 29.2769 | 29.7183 | 30.3161 | 30.9139 | 31.5116 | 32.1094 | 32.7072 | 33.3049 | 33.9027 | 34.5005 | 35.0982 | 35.696 | 36.0891 | 36.4822 | 36.8753 | 37.2684 | 37.6614 | 38.0545 | 38.4476 | 38.8407 | 39.2338 | 39.6269 | 40.02 | 40.4131 | 40.8062 | 41.1992 | 41.5923 | 41.909 | 42.2257 | 42.5424 | 42.8591 | 43.1758 | 43.4925 | 43.8092 | 44.1258 | 44.4425 | 44.7592 | 45.0759 | 45.3926 | 45.7093 | 46.026 | 46.3427 | 46.43 | 46.5174 | 46.6048 | 46.6921 | 46.7795 | 46.8669 | 46.9542 | 47.0416 | 47.129 | 47.2163 | 47.3037 | 47.3911 | 47.4784 | 47.5658 | 47.6532 | 47.7405 | 47.8279 | 47.9153 | 48.0026 | 48.09 | 48.1774 | 48.2647 | 48.3521 | 48.4395 | 48.5268 | 48.6142 | 48.7016 | 48.7889 | 48.8763 | 48.9637 | 48.9964 | 49.0292 | 49.062 | 49.0948 | 49.1276 | 49.1603 | 49.1931 | 49.2259 | 49.2587 | 49.2914 | 49.3242 | 49.357 | 49.3898 | 49.4226 | 49.4553 | 49.4881 | 49.5209 | 49.5537 | 49.5864 | 49.6192 | 49.652 | 49.6848 | 49.7176 | 49.7503 | 49.7831 | 49.8159 | 49.8487 | 49.8814 | 49.9142 | 49.947 | 49.947 | 49.947 | 49.947 | 49.947 | 49.947 | 49.947 | 49.947 | 49.947 | 49.947 | 49.947 | 49.947 | 49.947 | 49.947 | 49.947 | 49.947 | 49.947 | 49.947 | 49.947 | 49.947 | 49.947 | 49.947 | 49.947 | 49.947 | 49.947 | 49.947 | 49.947 | 49.947 | 49.947 | 49.947 | 49.947 | 49.8978 | 49.8487 | 49.7995 | 49.7503 | 49.7012 | 49.652 | 49.6028 | 49.5537 | 49.5045 | 49.4553 | 49.4062 | 49.357 | 49.3078 | 49.2587 | 49.2095 | 49.1603 | 49.1112 | 49.062 | 49.0128 | 48.9637 | 48.9145 | 48.8653 | 48.8162 | 48.767 | 48.7178 | 48.6687 | 48.6195 | 48.5703 | 48.5212 | 48.472
7 | 0 | 1.7 | 3.4 | 5.1 | 6.8 | 8.5 | 10.2 | 11.9 | 13.6 | 15.3 | 17 | 19.176 | 21.352 | 23.528 | 25.704 | 27.88 | 28.324 | 28.768 | 29.212 | 29.656 | 30.1 | 30.706 | 31.312 | 31.918 | 32.524 | 33.13 | 33.736 | 34.342 | 34.948 | 35.554 | 36.16 | 36.5587 | 36.9573 | 37.356 | 37.7547 | 38.1533 | 38.552 | 38.9507 | 39.3493 | 39.748 | 40.1467 | 40.5453 | 40.944 | 41.3427 | 41.7413 | 42.14 | 42.4613 | 42.7827 | 43.104 | 43.4253 | 43.7467 | 44.068 | 44.3893 | 44.7107 | 45.032 | 45.3533 | 45.6747 | 45.996 | 46.3173 | 46.6387 | 46.96 | 47.0487 | 47.1373 | 47.226 | 47.3147 | 47.4033 | 47.492 | 47.5807 | 47.6693 | 47.758 | 47.8467 | 47.9353 | 48.024 | 48.1127 | 48.2013 | 48.29 | 48.3787 | 48.4673 | 48.556 | 48.6447 | 48.7333 | 48.822 | 48.9107 | 48.9993 | 49.088 | 49.1767 | 49.2653 | 49.354 | 49.4427 | 49.5313 | 49.62 | 49.6533 | 49.6867 | 49.72 | 49.7533 | 49.7867 | 49.82 | 49.8533 | 49.8867 | 49.92 | 49.9533 | 49.9867 | 50.02 | 50.0533 | 50.0867 | 50.12 | 50.1533 | 50.1867 | 50.22 | 50.2533 | 50.2867 | 50.32 | 50.3533 | 50.3867 | 50.42 | 50.4533 | 50.4867 | 50.52 | 50.5533 | 50.5867 | 50.62 | 50.62 | 50.62 | 50.62 | 50.62 | 50.62 | 50.62 | 50.62 | 50.62 | 50.62 | 50.62 | 50.62 | 50.62 | 50.62 | 50.62 | 50.62 | 50.62 | 50.62 | 50.62 | 50.62 | 50.62 | 50.62 | 50.62 | 50.62 | 50.62 | 50.62 | 50.62 | 50.62 | 50.62 | 50.62 | 50.62 | 50.57 | 50.52 | 50.47 | 50.42 | 50.37 | 50.32 | 50.27 | 50.22 | 50.17 | 50.12 | 50.07 | 50.02 | 49.97 | 49.92 | 49.87 | 49.82 | 49.77 | 49.72 | 49.67 | 49.62 | 49.57 | 49.52 | 49.47 | 49.42 | 49.37 | 49.32 | 49.27 | 49.22 | 49.17 | 49.12
7.05 | 0 | 1.7217 | 3.4433 | 5.165 | 6.8867 | 8.6083 | 10.33 | 12.0517 | 13.7733 | 15.495 | 17.2167 | 19.4231 | 21.6295 | 23.8359 | 26.0423 | 28.2487 | 28.6953 | 29.1419 | 29.5885 | 30.0351 | 30.4817 | 31.0959 | 31.7101 | 32.3244 | 32.9386 | 33.5528 | 34.1671 | 34.7813 | 35.3955 | 36.0098 | 36.624 | 37.0282 | 37.4325 | 37.8367 | 38.241 | 38.6452 | 39.0495 | 39.4537 | 39.858 | 40.2622 | 40.6664 | 41.0707 | 41.4749 | 41.8792 | 42.2834 | 42.6877 | 43.0136 | 43.3396 | 43.6656 | 43.9916 | 44.3176 | 44.6435 | 44.9695 | 45.2955 | 45.6215 | 45.9474 | 46.2734 | 46.5994 | 46.9254 | 47.2514 | 47.5773 | 47.6673 | 47.7573 | 47.8472 | 47.9372 | 48.0272 | 48.1171 | 48.2071 | 48.2971 | 48.387 | 48.477 | 48.567 | 48.6569 | 48.7469 | 48.8369 | 48.9268 | 49.0168 | 49.1068 | 49.1967 | 49.2867 | 49.3767 | 49.4666 | 49.5566 | 49.6466 | 49.7365 | 49.8265 | 49.9165 | 50.0064 | 50.0964 | 50.1864 | 50.2763 | 50.3102 | 50.3441 | 50.378 | 50.4119 | 50.4458 | 50.4797 | 50.5136 | 50.5474 | 50.5813 | 50.6152 | 50.6491 | 50.683 | 50.7169 | 50.7508 | 50.7847 | 50.8186 | 50.8524 | 50.8863 | 50.9202 | 50.9541 | 50.988 | 51.0219 | 51.0558 | 51.0897 | 51.1236 | 51.1574 | 51.1913 | 51.2252 | 51.2591 | 51.293 | 51.293 | 51.293 | 51.293 | 51.293 | 51.293 | 51.293 | 51.293 | 51.293 | 51.293 | 51.293 | 51.293 | 51.293 | 51.293 | 51.293 | 51.293 | 51.293 | 51.293 | 51.293 | 51.293 | 51.293 | 51.293 | 51.293 | 51.293 | 51.293 | 51.293 | 51.293 | 51.293 | 51.293 | 51.293 | 51.293 | 51.2422 | 51.1913 | 51.1405 | 51.0897 | 51.0388 | 50.988 | 50.9372 | 50.8863 | 50.8355 | 50.7847 | 50.7338 | 50.683 | 50.6322 | 50.5813 | 50.5305 | 50.4797 | 50.4288 | 50.378 | 50.3272 | 50.2763 | 50.2255 | 50.1747 | 50.1238 | 50.073 | 50.0222 | 49.9713 | 49.9205 | 49.8697 | 49.8188 | 49.768
7.1 | 0 | 1.7433 | 3.4867 | 5.23 | 6.9733 | 8.7167 | 10.46 | 12.2033 | 13.9467 | 15.69 | 17.4333 | 19.6701 | 21.9069 | 24.1437 | 26.3805 | 28.6173 | 29.0665 | 29.5157 | 29.9649 | 30.4141 | 30.8633 | 31.4858 | 32.1083 | 32.7307 | 33.3532 | 33.9757 | 34.5981 | 35.2206 | 35.8431 | 36.4655 | 37.088 | 37.4978 | 37.9076 | 38.3175 | 38.7273 | 39.1371 | 39.5469 | 39.9568 | 40.3666 | 40.7764 | 41.1862 | 41.596 | 42.0059 | 42.4157 | 42.8255 | 43.2353 | 43.566 | 43.8966 | 44.2272 | 44.5578 | 44.8884 | 45.2191 | 45.5497 | 45.8803 | 46.2109 | 46.5416 | 46.8722 | 47.2028 | 47.5334 | 47.864 | 48.1947 | 48.2859 | 48.3772 | 48.4685 | 48.5597 | 48.651 | 48.7423 | 48.8335 | 48.9248 | 49.0161 | 49.1073 | 49.1986 | 49.2899 | 49.3811 | 49.4724 | 49.5637 | 49.6549 | 49.7462 | 49.8375 | 49.9287 | 50.02 | 50.1113 | 50.2025 | 50.2938 | 50.3851 | 50.4763 | 50.5676 | 50.6589 | 50.7501 | 50.8414 | 50.9327 | 50.9671 | 51.0016 | 51.036 | 51.0704 | 51.1049 | 51.1393 | 51.1738 | 51.2082 | 51.2427 | 51.2771 | 51.3116 | 51.346 | 51.3804 | 51.4149 | 51.4493 | 51.4838 | 51.5182 | 51.5527 | 51.5871 | 51.6216 | 51.656 | 51.6904 | 51.7249 | 51.7593 | 51.7938 | 51.8282 | 51.8627 | 51.8971 | 51.9316 | 51.966 | 51.966 | 51.966 | 51.966 | 51.966 | 51.966 | 51.966 | 51.966 | 51.966 | 51.966 | 51.966 | 51.966 | 51.966 | 51.966 | 51.966 | 51.966 | 51.966 | 51.966 | 51.966 | 51.966 | 51.966 | 51.966 | 51.966 | 51.966 | 51.966 | 51.966 | 51.966 | 51.966 | 51.966 | 51.966 | 51.966 | 51.9143 | 51.8627 | 51.811 | 51.7593 | 51.7077 | 51.656 | 51.6043 | 51.5527 | 51.501 | 51.4493 | 51.3977 | 51.346 | 51.2943 | 51.2427 | 51.191 | 51.1393 | 51.0877 | 51.036 | 50.9843 | 50.9327 | 50.881 | 50.8293 | 50.7777 | 50.726 | 50.6743 | 50.6227 | 50.571 | 50.5193 | 50.4677 | 50.416
7.15 | 0 | 1.765 | 3.53 | 5.295 | 7.06 | 8.825 | 10.59 | 12.355 | 14.12 | 15.885 | 17.65 | 19.9172 | 22.1844 | 24.4516 | 26.7188 | 28.986 | 29.4378 | 29.8896 | 30.3414 | 30.7932 | 31.245 | 31.8757 | 32.5064 | 33.1371 | 33.7678 | 34.3985 | 35.0292 | 35.6599 | 36.2906 | 36.9213 | 37.552 | 37.9674 | 38.3828 | 38.7982 | 39.2136 | 39.629 | 40.0444 | 40.4598 | 40.8752 | 41.2906 | 41.706 | 42.1214 | 42.5368 | 42.9522 | 43.3676 | 43.783 | 44.1183 | 44.4535 | 44.7888 | 45.1241 | 45.4593 | 45.7946 | 46.1299 | 46.4651 | 46.8004 | 47.1357 | 47.4709 | 47.8062 | 48.1415 | 48.4767 | 48.812 | 48.9046 | 48.9971 | 49.0897 | 49.1823 | 49.2748 | 49.3674 | 49.46 | 49.5525 | 49.6451 | 49.7377 | 49.8302 | 49.9228 | 50.0154 | 50.1079 | 50.2005 | 50.2931 | 50.3856 | 50.4782 | 50.5708 | 50.6633 | 50.7559 | 50.8485 | 50.941 | 51.0336 | 51.1262 | 51.2187 | 51.3113 | 51.4039 | 51.4964 | 51.589 | 51.624 | 51.659 | 51.694 | 51.729 | 51.764 | 51.799 | 51.834 | 51.869 | 51.904 | 51.939 | 51.974 | 52.009 | 52.044 | 52.079 | 52.114 | 52.149 | 52.184 | 52.219 | 52.254 | 52.289 | 52.324 | 52.359 | 52.394 | 52.429 | 52.464 | 52.499 | 52.534 | 52.569 | 52.604 | 52.639 | 52.639 | 52.639 | 52.639 | 52.639 | 52.639 | 52.639 | 52.639 | 52.639 | 52.639 | 52.639 | 52.639 | 52.639 | 52.639 | 52.639 | 52.639 | 52.639 | 52.639 | 52.639 | 52.639 | 52.639 | 52.639 | 52.639 | 52.639 | 52.639 | 52.639 | 52.639 | 52.639 | 52.639 | 52.639 | 52.639 | 52.5865 | 52.534 | 52.4815 | 52.429 | 52.3765 | 52.324 | 52.2715 | 52.219 | 52.1665 | 52.114 | 52.0615 | 52.009 | 51.9565 | 51.904 | 51.8515 | 51.799 | 51.7465 | 51.694 | 51.6415 | 51.589 | 51.5365 | 51.484 | 51.4315 | 51.379 | 51.3265 | 51.274 | 51.2215 | 51.169 | 51.1165 | 51.064
7.2 | 0 | 1.7867 | 3.5733 | 5.36 | 7.1467 | 8.9333 | 10.72 | 12.5067 | 14.2933 | 16.08 | 17.8667 | 20.1643 | 22.4619 | 24.7595 | 27.0571 | 29.3547 | 29.8091 | 30.2635 | 30.7179 | 31.1723 | 31.6267 | 32.2656 | 32.9045 | 33.5435 | 34.1824 | 34.8213 | 35.4603 | 36.0992 | 36.7381 | 37.3771 | 38.016 | 38.437 | 38.858 | 39.2789 | 39.6999 | 40.1209 | 40.5419 | 40.9628 | 41.3838 | 41.8048 | 42.2258 | 42.6468 | 43.0677 | 43.4887 | 43.9097 | 44.3307 | 44.6706 | 45.0105 | 45.3504 | 45.6903 | 46.0302 | 46.3701 | 46.71 | 47.05 | 47.3899 | 47.7298 | 48.0697 | 48.4096 | 48.7495 | 49.0894 | 49.4293 | 49.5232 | 49.6171 | 49.7109 | 49.8048 | 49.8987 | 49.9925 | 50.0864 | 50.1803 | 50.2741 | 50.368 | 50.4619 | 50.5557 | 50.6496 | 50.7435 | 50.8373 | 50.9312 | 51.0251 | 51.1189 | 51.2128 | 51.3067 | 51.4005 | 51.4944 | 51.5883 | 51.6821 | 51.776 | 51.8699 | 51.9637 | 52.0576 | 52.1515 | 52.2453 | 52.2809 | 52.3164 | 52.352 | 52.3876 | 52.4231 | 52.4587 | 52.4942 | 52.5298 | 52.5653 | 52.6009 | 52.6364 | 52.672 | 52.7076 | 52.7431 | 52.7787 | 52.8142 | 52.8498 | 52.8853 | 52.9209 | 52.9564 | 52.992 | 53.0276 | 53.0631 | 53.0987 | 53.1342 | 53.1698 | 53.2053 | 53.2409 | 53.2764 | 53.312 | 53.312 | 53.312 | 53.312 | 53.312 | 53.312 | 53.312 | 53.312 | 53.312 | 53.312 | 53.312 | 53.312 | 53.312 | 53.312 | 53.312 | 53.312 | 53.312 | 53.312 | 53.312 | 53.312 | 53.312 | 53.312 | 53.312 | 53.312 | 53.312 | 53.312 | 53.312 | 53.312 | 53.312 | 53.312 | 53.312 | 53.2587 | 53.2053 | 53.152 | 53.0987 | 53.0453 | 52.992 | 52.9387 | 52.8853 | 52.832 | 52.7787 | 52.7253 | 52.672 | 52.6187 | 52.5653 | 52.512 | 52.4587 | 52.4053 | 52.352 | 52.2987 | 52.2453 | 52.192 | 52.1387 | 52.0853 | 52.032 | 51.9787 | 51.9253 | 51.872 | 51.8187 | 51.7653 | 51.712
7.25 | 0 | 1.8083 | 3.6167 | 5.425 | 7.2333 | 9.0417 | 10.85 | 12.6583 | 14.4667 | 16.275 | 18.0833 | 20.4113 | 22.7393 | 25.0673 | 27.3953 | 29.7233 | 30.1803 | 30.6373 | 31.0943 | 31.5513 | 32.0083 | 32.6555 | 33.3027 | 33.9498 | 34.597 | 35.2442 | 35.8913 | 36.5385 | 37.1857 | 37.8328 | 38.48 | 38.9066 | 39.3331 | 39.7597 | 40.1862 | 40.6128 | 41.0393 | 41.4659 | 41.8924 | 42.319 | 42.7456 | 43.1721 | 43.5987 | 44.0252 | 44.4518 | 44.8783 | 45.2229 | 45.5674 | 45.912 | 46.2566 | 46.6011 | 46.9457 | 47.2902 | 47.6348 | 47.9793 | 48.3239 | 48.6684 | 49.013 | 49.3576 | 49.7021 | 50.0467 | 50.1418 | 50.237 | 50.3322 | 50.4273 | 50.5225 | 50.6177 | 50.7128 | 50.808 | 50.9032 | 50.9983 | 51.0935 | 51.1887 | 51.2838 | 51.379 | 51.4742 | 51.5693 | 51.6645 | 51.7597 | 51.8548 | 51.95 | 52.0452 | 52.1403 | 52.2355 | 52.3307 | 52.4258 | 52.521 | 52.6162 | 52.7113 | 52.8065 | 52.9017 | 52.9378 | 52.9739 | 53.01 | 53.0461 | 53.0822 | 53.1183 | 53.1544 | 53.1906 | 53.2267 | 53.2628 | 53.2989 | 53.335 | 53.3711 | 53.4072 | 53.4433 | 53.4794 | 53.5156 | 53.5517 | 53.5878 | 53.6239 | 53.66 | 53.6961 | 53.7322 | 53.7683 | 53.8044 | 53.8406 | 53.8767 | 53.9128 | 53.9489 | 53.985 | 53.985 | 53.985 | 53.985 | 53.985 | 53.985 | 53.985 | 53.985 | 53.985 | 53.985 | 53.985 | 53.985 | 53.985 | 53.985 | 53.985 | 53.985 | 53.985 | 53.985 | 53.985 | 53.985 | 53.985 | 53.985 | 53.985 | 53.985 | 53.985 | 53.985 | 53.985 | 53.985 | 53.985 | 53.985 | 53.985 | 53.9308 | 53.8767 | 53.8225 | 53.7683 | 53.7142 | 53.66 | 53.6058 | 53.5517 | 53.4975 | 53.4433 | 53.3892 | 53.335 | 53.2808 | 53.2267 | 53.1725 | 53.1183 | 53.0642 | 53.01 | 52.9558 | 52.9017 | 52.8475 | 52.7933 | 52.7392 | 52.685 | 52.6308 | 52.5767 | 52.5225 | 52.4683 | 52.4142 | 52.36
7.3 | 0 | 1.83 | 3.66 | 5.49 | 7.32 | 9.15 | 10.98 | 12.81 | 14.64 | 16.47 | 18.3 | 20.6584 | 23.0168 | 25.3752 | 27.7336 | 30.092 | 30.5516 | 31.0112 | 31.4708 | 31.9304 | 32.39 | 33.0454 | 33.7008 | 34.3562 | 35.0116 | 35.667 | 36.3224 | 36.9778 | 37.6332 | 38.2886 | 38.944 | 39.3761 | 39.8083 | 40.2404 | 40.6725 | 41.1047 | 41.5368 | 41.9689 | 42.4011 | 42.8332 | 43.2653 | 43.6975 | 44.1296 | 44.5617 | 44.9939 | 45.426 | 45.7752 | 46.1244 | 46.4736 | 46.8228 | 47.172 | 47.5212 | 47.8704 | 48.2196 | 48.5688 | 48.918 | 49.2672 | 49.6164 | 49.9656 | 50.3148 | 50.664 | 50.7605 | 50.8569 | 50.9534 | 51.0499 | 51.1463 | 51.2428 | 51.3393 | 51.4357 | 51.5322 | 51.6287 | 51.7251 | 51.8216 | 51.9181 | 52.0145 | 52.111 | 52.2075 | 52.3039 | 52.4004 | 52.4969 | 52.5933 | 52.6898 | 52.7863 | 52.8827 | 52.9792 | 53.0757 | 53.1721 | 53.2686 | 53.3651 | 53.4615 | 53.558 | 53.5947 | 53.6313 | 53.668 | 53.7047 | 53.7413 | 53.778 | 53.8147 | 53.8513 | 53.888 | 53.9247 | 53.9613 | 53.998 | 54.0347 | 54.0713 | 54.108 | 54.1447 | 54.1813 | 54.218 | 54.2547 | 54.2913 | 54.328 | 54.3647 | 54.4013 | 54.438 | 54.4747 | 54.5113 | 54.548 | 54.5847 | 54.6213 | 54.658 | 54.658 | 54.658 | 54.658 | 54.658 | 54.658 | 54.658 | 54.658 | 54.658 | 54.658 | 54.658 | 54.658 | 54.658 | 54.658 | 54.658 | 54.658 | 54.658 | 54.658 | 54.658 | 54.658 | 54.658 | 54.658 | 54.658 | 54.658 | 54.658 | 54.658 | 54.658 | 54.658 | 54.658 | 54.658 | 54.658 | 54.603 | 54.548 | 54.493 | 54.438 | 54.383 | 54.328 | 54.273 | 54.218 | 54.163 | 54.108 | 54.053 | 53.998 | 53.943 | 53.888 | 53.833 | 53.778 | 53.723 | 53.668 | 53.613 | 53.558 | 53.503 | 53.448 | 53.393 | 53.338 | 53.283 | 53.228 | 53.173 | 53.118 | 53.063 | 53.008
7.35 | 0 | 1.8517 | 3.7033 | 5.555 | 7.4067 | 9.2583 | 11.11 | 12.9617 | 14.8133 | 16.665 | 18.5167 | 20.9055 | 23.2943 | 25.6831 | 28.0719 | 30.4607 | 30.9229 | 31.3851 | 31.8473 | 32.3095 | 32.7717 | 33.4353 | 34.0989 | 34.7626 | 35.4262 | 36.0898 | 36.7535 | 37.4171 | 38.0807 | 38.7444 | 39.408 | 39.8457 | 40.2834 | 40.7211 | 41.1588 | 41.5966 | 42.0343 | 42.472 | 42.9097 | 43.3474 | 43.7851 | 44.2228 | 44.6605 | 45.0982 | 45.536 | 45.9737 | 46.3275 | 46.6814 | 47.0352 | 47.389 | 47.7429 | 48.0967 | 48.4506 | 48.8044 | 49.1583 | 49.5121 | 49.866 | 50.2198 | 50.5736 | 50.9275 | 51.2813 | 51.3791 | 51.4769 | 51.5746 | 51.6724 | 51.7702 | 51.8679 | 51.9657 | 52.0635 | 52.1612 | 52.259 | 52.3568 | 52.4545 | 52.5523 | 52.6501 | 52.7478 | 52.8456 | 52.9434 | 53.0411 | 53.1389 | 53.2367 | 53.3344 | 53.4322 | 53.53 | 53.6277 | 53.7255 | 53.8233 | 53.921 | 54.0188 | 54.1166 | 54.2143 | 54.2516 | 54.2888 | 54.326 | 54.3632 | 54.4004 | 54.4377 | 54.4749 | 54.5121 | 54.5493 | 54.5866 | 54.6238 | 54.661 | 54.6982 | 54.7354 | 54.7727 | 54.8099 | 54.8471 | 54.8843 | 54.9216 | 54.9588 | 54.996 | 55.0332 | 55.0704 | 55.1077 | 55.1449 | 55.1821 | 55.2193 | 55.2566 | 55.2938 | 55.331 | 55.331 | 55.331 | 55.331 | 55.331 | 55.331 | 55.331 | 55.331 | 55.331 | 55.331 | 55.331 | 55.331 | 55.331 | 55.331 | 55.331 | 55.331 | 55.331 | 55.331 | 55.331 | 55.331 | 55.331 | 55.331 | 55.331 | 55.331 | 55.331 | 55.331 | 55.331 | 55.331 | 55.331 | 55.331 | 55.331 | 55.2752 | 55.2193 | 55.1635 | 55.1077 | 55.0518 | 54.996 | 54.9402 | 54.8843 | 54.8285 | 54.7727 | 54.7168 | 54.661 | 54.6052 | 54.5493 | 54.4935 | 54.4377 | 54.3818 | 54.326 | 54.2702 | 54.2143 | 54.1585 | 54.1027 | 54.0468 | 53.991 | 53.9352 | 53.8793 | 53.8235 | 53.7677 | 53.7118 | 53.656
7.4 | 0 | 1.8733 | 3.7467 | 5.62 | 7.4933 | 9.3667 | 11.24 | 13.1133 | 14.9867 | 16.86 | 18.7333 | 21.1525 | 23.5717 | 25.9909 | 28.4101 | 30.8293 | 31.2941 | 31.7589 | 32.2237 | 32.6885 | 33.1533 | 33.8252 | 34.4971 | 35.1689 | 35.8408 | 36.5127 | 37.1845 | 37.8564 | 38.5283 | 39.2001 | 39.872 | 40.3153 | 40.7586 | 41.2019 | 41.6452 | 42.0884 | 42.5317 | 42.975 | 43.4183 | 43.8616 | 44.3049 | 44.7482 | 45.1915 | 45.6348 | 46.078 | 46.5213 | 46.8798 | 47.2383 | 47.5968 | 47.9553 | 48.3138 | 48.6723 | 49.0308 | 49.3892 | 49.7477 | 50.1062 | 50.4647 | 50.8232 | 51.1817 | 51.5402 | 51.8987 | 51.9977 | 52.0968 | 52.1959 | 52.2949 | 52.394 | 52.4931 | 52.5921 | 52.6912 | 52.7903 | 52.8893 | 52.9884 | 53.0875 | 53.1865 | 53.2856 | 53.3847 | 53.4837 | 53.5828 | 53.6819 | 53.7809 | 53.88 | 53.9791 | 54.0781 | 54.1772 | 54.2763 | 54.3753 | 54.4744 | 54.5735 | 54.6725 | 54.7716 | 54.8707 | 54.9084 | 54.9462 | 54.984 | 55.0218 | 55.0596 | 55.0973 | 55.1351 | 55.1729 | 55.2107 | 55.2484 | 55.2862 | 55.324 | 55.3618 | 55.3996 | 55.4373 | 55.4751 | 55.5129 | 55.5507 | 55.5884 | 55.6262 | 55.664 | 55.7018 | 55.7396 | 55.7773 | 55.8151 | 55.8529 | 55.8907 | 55.9284 | 55.9662 | 56.004 | 56.004 | 56.004 | 56.004 | 56.004 | 56.004 | 56.004 | 56.004 | 56.004 | 56.004 | 56.004 | 56.004 | 56.004 | 56.004 | 56.004 | 56.004 | 56.004 | 56.004 | 56.004 | 56.004 | 56.004 | 56.004 | 56.004 | 56.004 | 56.004 | 56.004 | 56.004 | 56.004 | 56.004 | 56.004 | 56.004 | 55.9473 | 55.8907 | 55.834 | 55.7773 | 55.7207 | 55.664 | 55.6073 | 55.5507 | 55.494 | 55.4373 | 55.3807 | 55.324 | 55.2673 | 55.2107 | 55.154 | 55.0973 | 55.0407 | 54.984 | 54.9273 | 54.8707 | 54.814 | 54.7573 | 54.7007 | 54.644 | 54.5873 | 54.5307 | 54.474 | 54.4173 | 54.3607 | 54.304
7.45 | 0 | 1.895 | 3.79 | 5.685 | 7.58 | 9.475 | 11.37 | 13.265 | 15.16 | 17.055 | 18.95 | 21.3996 | 23.8492 | 26.2988 | 28.7484 | 31.198 | 31.6654 | 32.1328 | 32.6002 | 33.0676 | 33.535 | 34.2151 | 34.8952 | 35.5753 | 36.2554 | 36.9355 | 37.6156 | 38.2957 | 38.9758 | 39.6559 | 40.336 | 40.7849 | 41.2337 | 41.6826 | 42.1315 | 42.5803 | 43.0292 | 43.4781 | 43.9269 | 44.3758 | 44.8247 | 45.2735 | 45.7224 | 46.1713 | 46.6201 | 47.069 | 47.4321 | 47.7953 | 48.1584 | 48.5215 | 48.8847 | 49.2478 | 49.6109 | 49.9741 | 50.3372 | 50.7003 | 51.0635 | 51.4266 | 51.7897 | 52.1529 | 52.516 | 52.6164 | 52.7167 | 52.8171 | 52.9175 | 53.0178 | 53.1182 | 53.2186 | 53.3189 | 53.4193 | 53.5197 | 53.62 | 53.7204 | 53.8208 | 53.9211 | 54.0215 | 54.1219 | 54.2222 | 54.3226 | 54.423 | 54.5233 | 54.6237 | 54.7241 | 54.8244 | 54.9248 | 55.0252 | 55.1255 | 55.2259 | 55.3263 | 55.4266 | 55.527 | 55.5653 | 55.6037 | 55.642 | 55.6803 | 55.7187 | 55.757 | 55.7953 | 55.8337 | 55.872 | 55.9103 | 55.9487 | 55.987 | 56.0253 | 56.0637 | 56.102 | 56.1403 | 56.1787 | 56.217 | 56.2553 | 56.2937 | 56.332 | 56.3703 | 56.4087 | 56.447 | 56.4853 | 56.5237 | 56.562 | 56.6003 | 56.6387 | 56.677 | 56.677 | 56.677 | 56.677 | 56.677 | 56.677 | 56.677 | 56.677 | 56.677 | 56.677 | 56.677 | 56.677 | 56.677 | 56.677 | 56.677 | 56.677 | 56.677 | 56.677 | 56.677 | 56.677 | 56.677 | 56.677 | 56.677 | 56.677 | 56.677 | 56.677 | 56.677 | 56.677 | 56.677 | 56.677 | 56.677 | 56.6195 | 56.562 | 56.5045 | 56.447 | 56.3895 | 56.332 | 56.2745 | 56.217 | 56.1595 | 56.102 | 56.0445 | 55.987 | 55.9295 | 55.872 | 55.8145 | 55.757 | 55.6995 | 55.642 | 55.5845 | 55.527 | 55.4695 | 55.412 | 55.3545 | 55.297 | 55.2395 | 55.182 | 55.1245 | 55.067 | 55.0095 | 54.952
7.5 | 0 | 1.9167 | 3.8333 | 5.75 | 7.6667 | 9.5833 | 11.5 | 13.4167 | 15.3333 | 17.25 | 19.1667 | 21.6467 | 24.1267 | 26.6067 | 29.0867 | 31.5667 | 32.0367 | 32.5067 | 32.9767 | 33.4467 | 33.9167 | 34.605 | 35.2933 | 35.9817 | 36.67 | 37.3583 | 38.0467 | 38.735 | 39.4233 | 40.1117 | 40.8 | 41.2544 | 41.7089 | 42.1633 | 42.6178 | 43.0722 | 43.5267 | 43.9811 | 44.4356 | 44.89 | 45.3444 | 45.7989 | 46.2533 | 46.7078 | 47.1622 | 47.6167 | 47.9844 | 48.3522 | 48.72 | 49.0878 | 49.4556 | 49.8233 | 50.1911 | 50.5589 | 50.9267 | 51.2944 | 51.6622 | 52.03 | 52.3978 | 52.7656 | 53.1333 | 53.235 | 53.3367 | 53.4383 | 53.54 | 53.6417 | 53.7433 | 53.845 | 53.9467 | 54.0483 | 54.15 | 54.2517 | 54.3533 | 54.455 | 54.5567 | 54.6583 | 54.76 | 54.8617 | 54.9633 | 55.065 | 55.1667 | 55.2683 | 55.37 | 55.4717 | 55.5733 | 55.675 | 55.7767 | 55.8783 | 55.98 | 56.0817 | 56.1833 | 56.2222 | 56.2611 | 56.3 | 56.3389 | 56.3778 | 56.4167 | 56.4556 | 56.4944 | 56.5333 | 56.5722 | 56.6111 | 56.65 | 56.6889 | 56.7278 | 56.7667 | 56.8056 | 56.8444 | 56.8833 | 56.9222 | 56.9611 | 57 | 57.0389 | 57.0778 | 57.1167 | 57.1556 | 57.1944 | 57.2333 | 57.2722 | 57.3111 | 57.35 | 57.35 | 57.35 | 57.35 | 57.35 | 57.35 | 57.35 | 57.35 | 57.35 | 57.35 | 57.35 | 57.35 | 57.35 | 57.35 | 57.35 | 57.35 | 57.35 | 57.35 | 57.35 | 57.35 | 57.35 | 57.35 | 57.35 | 57.35 | 57.35 | 57.35 | 57.35 | 57.35 | 57.35 | 57.35 | 57.35 | 57.2917 | 57.2333 | 57.175 | 57.1167 | 57.0583 | 57 | 56.9417 | 56.8833 | 56.825 | 56.7667 | 56.7083 | 56.65 | 56.5917 | 56.5333 | 56.475 | 56.4167 | 56.3583 | 56.3 | 56.2417 | 56.1833 | 56.125 | 56.0667 | 56.0083 | 55.95 | 55.8917 | 55.8333 | 55.775 | 55.7167 | 55.6583 | 55.6
7.55 | 0 | 1.9383 | 3.8767 | 5.815 | 7.7533 | 9.6917 | 11.63 | 13.5683 | 15.5067 | 17.445 | 19.3833 | 21.8937 | 24.4041 | 26.9145 | 29.4249 | 31.9353 | 32.4079 | 32.8805 | 33.3531 | 33.8257 | 34.2983 | 34.9949 | 35.6915 | 36.388 | 37.0846 | 37.7812 | 38.4777 | 39.1743 | 39.8709 | 40.5674 | 41.264 | 41.724 | 42.184 | 42.6441 | 43.1041 | 43.5641 | 44.0241 | 44.4842 | 44.9442 | 45.4042 | 45.8642 | 46.3242 | 46.7843 | 47.2443 | 47.7043 | 48.1643 | 48.5368 | 48.9092 | 49.2816 | 49.654 | 50.0264 | 50.3989 | 50.7713 | 51.1437 | 51.5161 | 51.8886 | 52.261 | 52.6334 | 53.0058 | 53.3782 | 53.7507 | 53.8536 | 53.9566 | 54.0596 | 54.1625 | 54.2655 | 54.3685 | 54.4714 | 54.5744 | 54.6774 | 54.7803 | 54.8833 | 54.9863 | 55.0892 | 55.1922 | 55.2952 | 55.3981 | 55.5011 | 55.6041 | 55.707 | 55.81 | 55.913 | 56.0159 | 56.1189 | 56.2219 | 56.3248 | 56.4278 | 56.5308 | 56.6337 | 56.7367 | 56.8397 | 56.8791 | 56.9186 | 56.958 | 56.9974 | 57.0369 | 57.0763 | 57.1158 | 57.1552 | 57.1947 | 57.2341 | 57.2736 | 57.313 | 57.3524 | 57.3919 | 57.4313 | 57.4708 | 57.5102 | 57.5497 | 57.5891 | 57.6286 | 57.668 | 57.7074 | 57.7469 | 57.7863 | 57.8258 | 57.8652 | 57.9047 | 57.9441 | 57.9836 | 58.023 | 58.023 | 58.023 | 58.023 | 58.023 | 58.023 | 58.023 | 58.023 | 58.023 | 58.023 | 58.023 | 58.023 | 58.023 | 58.023 | 58.023 | 58.023 | 58.023 | 58.023 | 58.023 | 58.023 | 58.023 | 58.023 | 58.023 | 58.023 | 58.023 | 58.023 | 58.023 | 58.023 | 58.023 | 58.023 | 58.023 | 57.9638 | 57.9047 | 57.8455 | 57.7863 | 57.7272 | 57.668 | 57.6088 | 57.5497 | 57.4905 | 57.4313 | 57.3722 | 57.313 | 57.2538 | 57.1947 | 57.1355 | 57.0763 | 57.0172 | 56.958 | 56.8988 | 56.8397 | 56.7805 | 56.7213 | 56.6622 | 56.603 | 56.5438 | 56.4847 | 56.4255 | 56.3663 | 56.3072 | 56.248
7.6 | 0 | 1.96 | 3.92 | 5.88 | 7.84 | 9.8 | 11.76 | 13.72 | 15.68 | 17.64 | 19.6 | 22.1408 | 24.6816 | 27.2224 | 29.7632 | 32.304 | 32.7792 | 33.2544 | 33.7296 | 34.2048 | 34.68 | 35.3848 | 36.0896 | 36.7944 | 37.4992 | 38.204 | 38.9088 | 39.6136 | 40.3184 | 41.0232 | 41.728 | 42.1936 | 42.6592 | 43.1248 | 43.5904 | 44.056 | 44.5216 | 44.9872 | 45.4528 | 45.9184 | 46.384 | 46.8496 | 47.3152 | 47.7808 | 48.2464 | 48.712 | 49.0891 | 49.4661 | 49.8432 | 50.2203 | 50.5973 | 50.9744 | 51.3515 | 51.7285 | 52.1056 | 52.4827 | 52.8597 | 53.2368 | 53.6139 | 53.9909 | 54.368 | 54.4723 | 54.5765 | 54.6808 | 54.7851 | 54.8893 | 54.9936 | 55.0979 | 55.2021 | 55.3064 | 55.4107 | 55.5149 | 55.6192 | 55.7235 | 55.8277 | 55.932 | 56.0363 | 56.1405 | 56.2448 | 56.3491 | 56.4533 | 56.5576 | 56.6619 | 56.7661 | 56.8704 | 56.9747 | 57.0789 | 57.1832 | 57.2875 | 57.3917 | 57.496 | 57.536 | 57.576 | 57.616 | 57.656 | 57.696 | 57.736 | 57.776 | 57.816 | 57.856 | 57.896 | 57.936 | 57.976 | 58.016 | 58.056 | 58.096 | 58.136 | 58.176 | 58.216 | 58.256 | 58.296 | 58.336 | 58.376 | 58.416 | 58.456 | 58.496 | 58.536 | 58.576 | 58.616 | 58.656 | 58.696 | 58.696 | 58.696 | 58.696 | 58.696 | 58.696 | 58.696 | 58.696 | 58.696 | 58.696 | 58.696 | 58.696 | 58.696 | 58.696 | 58.696 | 58.696 | 58.696 | 58.696 | 58.696 | 58.696 | 58.696 | 58.696 | 58.696 | 58.696 | 58.696 | 58.696 | 58.696 | 58.696 | 58.696 | 58.696 | 58.696 | 58.636 | 58.576 | 58.516 | 58.456 | 58.396 | 58.336 | 58.276 | 58.216 | 58.156 | 58.096 | 58.036 | 57.976 | 57.916 | 57.856 | 57.796 | 57.736 | 57.676 | 57.616 | 57.556 | 57.496 | 57.436 | 57.376 | 57.316 | 57.256 | 57.196 | 57.136 | 57.076 | 57.016 | 56.956 | 56.896
7.65 | 0 | 1.9817 | 3.9633 | 5.945 | 7.9267 | 9.9083 | 11.89 | 13.8717 | 15.8533 | 17.835 | 19.8167 | 22.3879 | 24.9591 | 27.5303 | 30.1015 | 32.6727 | 33.1505 | 33.6283 | 34.1061 | 34.5839 | 35.0617 | 35.7747 | 36.4877 | 37.2008 | 37.9138 | 38.6268 | 39.3399 | 40.0529 | 40.7659 | 41.479 | 42.192 | 42.6632 | 43.1344 | 43.6055 | 44.0767 | 44.5479 | 45.0191 | 45.4902 | 45.9614 | 46.4326 | 46.9038 | 47.375 | 47.8461 | 48.3173 | 48.7885 | 49.2597 | 49.6414 | 50.0231 | 50.4048 | 50.7865 | 51.1682 | 51.5499 | 51.9316 | 52.3134 | 52.6951 | 53.0768 | 53.4585 | 53.8402 | 54.2219 | 54.6036 | 54.9853 | 55.0909 | 55.1965 | 55.302 | 55.4076 | 55.5132 | 55.6187 | 55.7243 | 55.8299 | 55.9354 | 56.041 | 56.1466 | 56.2521 | 56.3577 | 56.4633 | 56.5688 | 56.6744 | 56.78 | 56.8855 | 56.9911 | 57.0967 | 57.2022 | 57.3078 | 57.4134 | 57.5189 | 57.6245 | 57.7301 | 57.8356 | 57.9412 | 58.0468 | 58.1523 | 58.1929 | 58.2334 | 58.274 | 58.3146 | 58.3551 | 58.3957 | 58.4362 | 58.4768 | 58.5173 | 58.5579 | 58.5984 | 58.639 | 58.6796 | 58.7201 | 58.7607 | 58.8012 | 58.8418 | 58.8823 | 58.9229 | 58.9634 | 59.004 | 59.0446 | 59.0851 | 59.1257 | 59.1662 | 59.2068 | 59.2473 | 59.2879 | 59.3284 | 59.369 | 59.369 | 59.369 | 59.369 | 59.369 | 59.369 | 59.369 | 59.369 | 59.369 | 59.369 | 59.369 | 59.369 | 59.369 | 59.369 | 59.369 | 59.369 | 59.369 | 59.369 | 59.369 | 59.369 | 59.369 | 59.369 | 59.369 | 59.369 | 59.369 | 59.369 | 59.369 | 59.369 | 59.369 | 59.369 | 59.369 | 59.3082 | 59.2473 | 59.1865 | 59.1257 | 59.0648 | 59.004 | 58.9432 | 58.8823 | 58.8215 | 58.7607 | 58.6998 | 58.639 | 58.5782 | 58.5173 | 58.4565 | 58.3957 | 58.3348 | 58.274 | 58.2132 | 58.1523 | 58.0915 | 58.0307 | 57.9698 | 57.909 | 57.8482 | 57.7873 | 57.7265 | 57.6657 | 57.6048 | 57.544
7.7 | 0 | 2.0033 | 4.0067 | 6.01 | 8.0133 | 10.0167 | 12.02 | 14.0233 | 16.0267 | 18.03 | 20.0333 | 22.6349 | 25.2365 | 27.8381 | 30.4397 | 33.0413 | 33.5217 | 34.0021 | 34.4825 | 34.9629 | 35.4433 | 36.1646 | 36.8859 | 37.6071 | 38.3284 | 39.0497 | 39.7709 | 40.4922 | 41.2135 | 41.9347 | 42.656 | 43.1328 | 43.6095 | 44.0863 | 44.563 | 45.0398 | 45.5165 | 45.9933 | 46.47 | 46.9468 | 47.4236 | 47.9003 | 48.3771 | 48.8538 | 49.3306 | 49.8073 | 50.1937 | 50.58 | 50.9664 | 51.3528 | 51.7391 | 52.1255 | 52.5118 | 52.8982 | 53.2845 | 53.6709 | 54.0572 | 54.4436 | 54.83 | 55.2163 | 55.6027 | 55.7095 | 55.8164 | 55.9233 | 56.0301 | 56.137 | 56.2439 | 56.3507 | 56.4576 | 56.5645 | 56.6713 | 56.7782 | 56.8851 | 56.9919 | 57.0988 | 57.2057 | 57.3125 | 57.4194 | 57.5263 | 57.6331 | 57.74 | 57.8469 | 57.9537 | 58.0606 | 58.1675 | 58.2743 | 58.3812 | 58.4881 | 58.5949 | 58.7018 | 58.8087 | 58.8498 | 58.8909 | 58.932 | 58.9731 | 59.0142 | 59.0553 | 59.0964 | 59.1376 | 59.1787 | 59.2198 | 59.2609 | 59.302 | 59.3431 | 59.3842 | 59.4253 | 59.4664 | 59.5076 | 59.5487 | 59.5898 | 59.6309 | 59.672 | 59.7131 | 59.7542 | 59.7953 | 59.8364 | 59.8776 | 59.9187 | 59.9598 | 60.0009 | 60.042 | 60.042 | 60.042 | 60.042 | 60.042 | 60.042 | 60.042 | 60.042 | 60.042 | 60.042 | 60.042 | 60.042 | 60.042 | 60.042 | 60.042 | 60.042 | 60.042 | 60.042 | 60.042 | 60.042 | 60.042 | 60.042 | 60.042 | 60.042 | 60.042 | 60.042 | 60.042 | 60.042 | 60.042 | 60.042 | 60.042 | 59.9803 | 59.9187 | 59.857 | 59.7953 | 59.7337 | 59.672 | 59.6103 | 59.5487 | 59.487 | 59.4253 | 59.3637 | 59.302 | 59.2403 | 59.1787 | 59.117 | 59.0553 | 58.9937 | 58.932 | 58.8703 | 58.8087 | 58.747 | 58.6853 | 58.6237 | 58.562 | 58.5003 | 58.4387 | 58.377 | 58.3153 | 58.2537 | 58.192
7.75 | 0 | 2.025 | 4.05 | 6.075 | 8.1 | 10.125 | 12.15 | 14.175 | 16.2 | 18.225 | 20.25 | 22.882 | 25.514 | 28.146 | 30.778 | 33.41 | 33.893 | 34.376 | 34.859 | 35.342 | 35.825 | 36.5545 | 37.284 | 38.0135 | 38.743 | 39.4725 | 40.202 | 40.9315 | 41.661 | 42.3905 | 43.12 | 43.6023 | 44.0847 | 44.567 | 45.0493 | 45.5317 | 46.014 | 46.4963 | 46.9787 | 47.461 | 47.9433 | 48.4257 | 48.908 | 49.3903 | 49.8727 | 50.355 | 50.746 | 51.137 | 51.528 | 51.919 | 52.31 | 52.701 | 53.092 | 53.483 | 53.874 | 54.265 | 54.656 | 55.047 | 55.438 | 55.829 | 56.22 | 56.3282 | 56.4363 | 56.5445 | 56.6527 | 56.7608 | 56.869 | 56.9772 | 57.0853 | 57.1935 | 57.3017 | 57.4098 | 57.518 | 57.6262 | 57.7343 | 57.8425 | 57.9507 | 58.0588 | 58.167 | 58.2752 | 58.3833 | 58.4915 | 58.5997 | 58.7078 | 58.816 | 58.9242 | 59.0323 | 59.1405 | 59.2487 | 59.3568 | 59.465 | 59.5067 | 59.5483 | 59.59 | 59.6317 | 59.6733 | 59.715 | 59.7567 | 59.7983 | 59.84 | 59.8817 | 59.9233 | 59.965 | 60.0067 | 60.0483 | 60.09 | 60.1317 | 60.1733 | 60.215 | 60.2567 | 60.2983 | 60.34 | 60.3817 | 60.4233 | 60.465 | 60.5067 | 60.5483 | 60.59 | 60.6317 | 60.6733 | 60.715 | 60.715 | 60.715 | 60.715 | 60.715 | 60.715 | 60.715 | 60.715 | 60.715 | 60.715 | 60.715 | 60.715 | 60.715 | 60.715 | 60.715 | 60.715 | 60.715 | 60.715 | 60.715 | 60.715 | 60.715 | 60.715 | 60.715 | 60.715 | 60.715 | 60.715 | 60.715 | 60.715 | 60.715 | 60.715 | 60.715 | 60.6525 | 60.59 | 60.5275 | 60.465 | 60.4025 | 60.34 | 60.2775 | 60.215 | 60.1525 | 60.09 | 60.0275 | 59.965 | 59.9025 | 59.84 | 59.7775 | 59.715 | 59.6525 | 59.59 | 59.5275 | 59.465 | 59.4025 | 59.34 | 59.2775 | 59.215 | 59.1525 | 59.09 | 59.0275 | 58.965 | 58.9025 | 58.84
7.8 | 0 | 2.0467 | 4.0933 | 6.14 | 8.1867 | 10.2333 | 12.28 | 14.3267 | 16.3733 | 18.42 | 20.4667 | 23.1291 | 25.7915 | 28.4539 | 31.1163 | 33.7787 | 34.2643 | 34.7499 | 35.2355 | 35.7211 | 36.2067 | 36.9444 | 37.6821 | 38.4199 | 39.1576 | 39.8953 | 40.6331 | 41.3708 | 42.1085 | 42.8463 | 43.584 | 44.0719 | 44.5598 | 45.0477 | 45.5356 | 46.0236 | 46.5115 | 46.9994 | 47.4873 | 47.9752 | 48.4631 | 48.951 | 49.4389 | 49.9268 | 50.4148 | 50.9027 | 51.2983 | 51.694 | 52.0896 | 52.4852 | 52.8809 | 53.2765 | 53.6722 | 54.0678 | 54.4635 | 54.8591 | 55.2548 | 55.6504 | 56.046 | 56.4417 | 56.8373 | 56.9468 | 57.0563 | 57.1657 | 57.2752 | 57.3847 | 57.4941 | 57.6036 | 57.7131 | 57.8225 | 57.932 | 58.0415 | 58.1509 | 58.2604 | 58.3699 | 58.4793 | 58.5888 | 58.6983 | 58.8077 | 58.9172 | 59.0267 | 59.1361 | 59.2456 | 59.3551 | 59.4645 | 59.574 | 59.6835 | 59.7929 | 59.9024 | 60.0119 | 60.1213 | 60.1636 | 60.2058 | 60.248 | 60.2902 | 60.3324 | 60.3747 | 60.4169 | 60.4591 | 60.5013 | 60.5436 | 60.5858 | 60.628 | 60.6702 | 60.7124 | 60.7547 | 60.7969 | 60.8391 | 60.8813 | 60.9236 | 60.9658 | 61.008 | 61.0502 | 61.0924 | 61.1347 | 61.1769 | 61.2191 | 61.2613 | 61.3036 | 61.3458 | 61.388 | 61.388 | 61.388 | 61.388 | 61.388 | 61.388 | 61.388 | 61.388 | 61.388 | 61.388 | 61.388 | 61.388 | 61.388 | 61.388 | 61.388 | 61.388 | 61.388 | 61.388 | 61.388 | 61.388 | 61.388 | 61.388 | 61.388 | 61.388 | 61.388 | 61.388 | 61.388 | 61.388 | 61.388 | 61.388 | 61.388 | 61.3247 | 61.2613 | 61.198 | 61.1347 | 61.0713 | 61.008 | 60.9447 | 60.8813 | 60.818 | 60.7547 | 60.6913 | 60.628 | 60.5647 | 60.5013 | 60.438 | 60.3747 | 60.3113 | 60.248 | 60.1847 | 60.1213 | 60.058 | 59.9947 | 59.9313 | 59.868 | 59.8047 | 59.7413 | 59.678 | 59.6147 | 59.5513 | 59.488
7.85 | 0 | 2.0683 | 4.1367 | 6.205 | 8.2733 | 10.3417 | 12.41 | 14.4783 | 16.5467 | 18.615 | 20.6833 | 23.3761 | 26.0689 | 28.7617 | 31.4545 | 34.1473 | 34.6355 | 35.1237 | 35.6119 | 36.1001 | 36.5883 | 37.3343 | 38.0803 | 38.8262 | 39.5722 | 40.3182 | 41.0641 | 41.8101 | 42.5561 | 43.302 | 44.048 | 44.5415 | 45.035 | 45.5285 | 46.022 | 46.5154 | 47.0089 | 47.5024 | 47.9959 | 48.4894 | 48.9829 | 49.4764 | 49.9699 | 50.4634 | 50.9568 | 51.4503 | 51.8506 | 52.2509 | 52.6512 | 53.0515 | 53.4518 | 53.8521 | 54.2524 | 54.6526 | 55.0529 | 55.4532 | 55.8535 | 56.2538 | 56.6541 | 57.0544 | 57.4547 | 57.5654 | 57.6762 | 57.787 | 57.8977 | 58.0085 | 58.1193 | 58.23 | 58.3408 | 58.4516 | 58.5623 | 58.6731 | 58.7839 | 58.8946 | 59.0054 | 59.1162 | 59.2269 | 59.3377 | 59.4485 | 59.5592 | 59.67 | 59.7808 | 59.8915 | 60.0023 | 60.1131 | 60.2238 | 60.3346 | 60.4454 | 60.5561 | 60.6669 | 60.7777 | 60.8204 | 60.8632 | 60.906 | 60.9488 | 60.9916 | 61.0343 | 61.0771 | 61.1199 | 61.1627 | 61.2054 | 61.2482 | 61.291 | 61.3338 | 61.3766 | 61.4193 | 61.4621 | 61.5049 | 61.5477 | 61.5904 | 61.6332 | 61.676 | 61.7188 | 61.7616 | 61.8043 | 61.8471 | 61.8899 | 61.9327 | 61.9754 | 62.0182 | 62.061 | 62.061 | 62.061 | 62.061 | 62.061 | 62.061 | 62.061 | 62.061 | 62.061 | 62.061 | 62.061 | 62.061 | 62.061 | 62.061 | 62.061 | 62.061 | 62.061 | 62.061 | 62.061 | 62.061 | 62.061 | 62.061 | 62.061 | 62.061 | 62.061 | 62.061 | 62.061 | 62.061 | 62.061 | 62.061 | 62.061 | 61.9968 | 61.9327 | 61.8685 | 61.8043 | 61.7402 | 61.676 | 61.6118 | 61.5477 | 61.4835 | 61.4193 | 61.3552 | 61.291 | 61.2268 | 61.1627 | 61.0985 | 61.0343 | 60.9702 | 60.906 | 60.8418 | 60.7777 | 60.7135 | 60.6493 | 60.5852 | 60.521 | 60.4568 | 60.3927 | 60.3285 | 60.2643 | 60.2002 | 60.136
7.9 | 0 | 2.09 | 4.18 | 6.27 | 8.36 | 10.45 | 12.54 | 14.63 | 16.72 | 18.81 | 20.9 | 23.6232 | 26.3464 | 29.0696 | 31.7928 | 34.516 | 35.0068 | 35.4976 | 35.9884 | 36.4792 | 36.97 | 37.7242 | 38.4784 | 39.2326 | 39.9868 | 40.741 | 41.4952 | 42.2494 | 43.0036 | 43.7578 | 44.512 | 45.0111 | 45.5101 | 46.0092 | 46.5083 | 47.0073 | 47.5064 | 48.0055 | 48.5045 | 49.0036 | 49.5027 | 50.0017 | 50.5008 | 50.9999 | 51.4989 | 51.998 | 52.4029 | 52.8079 | 53.2128 | 53.6177 | 54.0227 | 54.4276 | 54.8325 | 55.2375 | 55.6424 | 56.0473 | 56.4523 | 56.8572 | 57.2621 | 57.6671 | 58.072 | 58.1841 | 58.2961 | 58.4082 | 58.5203 | 58.6323 | 58.7444 | 58.8565 | 58.9685 | 59.0806 | 59.1927 | 59.3047 | 59.4168 | 59.5289 | 59.6409 | 59.753 | 59.8651 | 59.9771 | 60.0892 | 60.2013 | 60.3133 | 60.4254 | 60.5375 | 60.6495 | 60.7616 | 60.8737 | 60.9857 | 61.0978 | 61.2099 | 61.3219 | 61.434 | 61.4773 | 61.5207 | 61.564 | 61.6073 | 61.6507 | 61.694 | 61.7373 | 61.7807 | 61.824 | 61.8673 | 61.9107 | 61.954 | 61.9973 | 62.0407 | 62.084 | 62.1273 | 62.1707 | 62.214 | 62.2573 | 62.3007 | 62.344 | 62.3873 | 62.4307 | 62.474 | 62.5173 | 62.5607 | 62.604 | 62.6473 | 62.6907 | 62.734 | 62.734 | 62.734 | 62.734 | 62.734 | 62.734 | 62.734 | 62.734 | 62.734 | 62.734 | 62.734 | 62.734 | 62.734 | 62.734 | 62.734 | 62.734 | 62.734 | 62.734 | 62.734 | 62.734 | 62.734 | 62.734 | 62.734 | 62.734 | 62.734 | 62.734 | 62.734 | 62.734 | 62.734 | 62.734 | 62.734 | 62.669 | 62.604 | 62.539 | 62.474 | 62.409 | 62.344 | 62.279 | 62.214 | 62.149 | 62.084 | 62.019 | 61.954 | 61.889 | 61.824 | 61.759 | 61.694 | 61.629 | 61.564 | 61.499 | 61.434 | 61.369 | 61.304 | 61.239 | 61.174 | 61.109 | 61.044 | 60.979 | 60.914 | 60.849 | 60.784
7.95 | 0 | 2.1117 | 4.2233 | 6.335 | 8.4467 | 10.5583 | 12.67 | 14.7817 | 16.8933 | 19.005 | 21.1167 | 23.8703 | 26.6239 | 29.3775 | 32.1311 | 34.8847 | 35.3781 | 35.8715 | 36.3649 | 36.8583 | 37.3517 | 38.1141 | 38.8765 | 39.639 | 40.4014 | 41.1638 | 41.9263 | 42.6887 | 43.4511 | 44.2136 | 44.976 | 45.4806 | 45.9853 | 46.4899 | 46.9946 | 47.4992 | 48.0039 | 48.5085 | 49.0132 | 49.5178 | 50.0224 | 50.5271 | 51.0317 | 51.5364 | 52.041 | 52.5457 | 52.9552 | 53.3648 | 53.7744 | 54.184 | 54.5936 | 55.0031 | 55.4127 | 55.8223 | 56.2319 | 56.6414 | 57.051 | 57.4606 | 57.8702 | 58.2798 | 58.6893 | 58.8027 | 58.9161 | 59.0294 | 59.1428 | 59.2562 | 59.3695 | 59.4829 | 59.5963 | 59.7096 | 59.823 | 59.9364 | 60.0497 | 60.1631 | 60.2765 | 60.3898 | 60.5032 | 60.6166 | 60.7299 | 60.8433 | 60.9567 | 61.07 | 61.1834 | 61.2968 | 61.4101 | 61.5235 | 61.6369 | 61.7502 | 61.8636 | 61.977 | 62.0903 | 62.1342 | 62.1781 | 62.222 | 62.2659 | 62.3098 | 62.3537 | 62.3976 | 62.4414 | 62.4853 | 62.5292 | 62.5731 | 62.617 | 62.6609 | 62.7048 | 62.7487 | 62.7926 | 62.8364 | 62.8803 | 62.9242 | 62.9681 | 63.012 | 63.0559 | 63.0998 | 63.1437 | 63.1876 | 63.2314 | 63.2753 | 63.3192 | 63.3631 | 63.407 | 63.407 | 63.407 | 63.407 | 63.407 | 63.407 | 63.407 | 63.407 | 63.407 | 63.407 | 63.407 | 63.407 | 63.407 | 63.407 | 63.407 | 63.407 | 63.407 | 63.407 | 63.407 | 63.407 | 63.407 | 63.407 | 63.407 | 63.407 | 63.407 | 63.407 | 63.407 | 63.407 | 63.407 | 63.407 | 63.407 | 63.3412 | 63.2753 | 63.2095 | 63.1437 | 63.0778 | 63.012 | 62.9462 | 62.8803 | 62.8145 | 62.7487 | 62.6828 | 62.617 | 62.5512 | 62.4853 | 62.4195 | 62.3537 | 62.2878 | 62.222 | 62.1562 | 62.0903 | 62.0245 | 61.9587 | 61.8928 | 61.827 | 61.7612 | 61.6953 | 61.6295 | 61.5637 | 61.4978 | 61.432
8 | 0 | 2.1333 | 4.2667 | 6.4 | 8.5333 | 10.6667 | 12.8 | 14.9333 | 17.0667 | 19.2 | 21.3333 | 24.1173 | 26.9013 | 29.6853 | 32.4693 | 35.2533 | 35.7493 | 36.2453 | 36.7413 | 37.2373 | 37.7333 | 38.504 | 39.2747 | 40.0453 | 40.816 | 41.5867 | 42.3573 | 43.128 | 43.8987 | 44.6693 | 45.44 | 45.9502 | 46.4604 | 46.9707 | 47.4809 | 47.9911 | 48.5013 | 49.0116 | 49.5218 | 50.032 | 50.5422 | 51.0524 | 51.5627 | 52.0729 | 52.5831 | 53.0933 | 53.5076 | 53.9218 | 54.336 | 54.7502 | 55.1644 | 55.5787 | 55.9929 | 56.4071 | 56.8213 | 57.2356 | 57.6498 | 58.064 | 58.4782 | 58.8924 | 59.3067 | 59.4213 | 59.536 | 59.6507 | 59.7653 | 59.88 | 59.9947 | 60.1093 | 60.224 | 60.3387 | 60.4533 | 60.568 | 60.6827 | 60.7973 | 60.912 | 61.0267 | 61.1413 | 61.256 | 61.3707 | 61.4853 | 61.6 | 61.7147 | 61.8293 | 61.944 | 62.0587 | 62.1733 | 62.288 | 62.4027 | 62.5173 | 62.632 | 62.7467 | 62.7911 | 62.8356 | 62.88 | 62.9244 | 62.9689 | 63.0133 | 63.0578 | 63.1022 | 63.1467 | 63.1911 | 63.2356 | 63.28 | 63.3244 | 63.3689 | 63.4133 | 63.4578 | 63.5022 | 63.5467 | 63.5911 | 63.6356 | 63.68 | 63.7244 | 63.7689 | 63.8133 | 63.8578 | 63.9022 | 63.9467 | 63.9911 | 64.0356 | 64.08 | 64.08 | 64.08 | 64.08 | 64.08 | 64.08 | 64.08 | 64.08 | 64.08 | 64.08 | 64.08 | 64.08 | 64.08 | 64.08 | 64.08 | 64.08 | 64.08 | 64.08 | 64.08 | 64.08 | 64.08 | 64.08 | 64.08 | 64.08 | 64.08 | 64.08 | 64.08 | 64.08 | 64.08 | 64.08 | 64.08 | 64.0133 | 63.9467 | 63.88 | 63.8133 | 63.7467 | 63.68 | 63.6133 | 63.5467 | 63.48 | 63.4133 | 63.3467 | 63.28 | 63.2133 | 63.1467 | 63.08 | 63.0133 | 62.9467 | 62.88 | 62.8133 | 62.7467 | 62.68 | 62.6133 | 62.5467 | 62.48 | 62.4133 | 62.3467 | 62.28 | 62.2133 | 62.1467 | 62.08
8.05 | 0 | 2.155 | 4.31 | 6.465 | 8.62 | 10.775 | 12.93 | 15.085 | 17.24 | 19.395 | 21.55 | 24.3644 | 27.1788 | 29.9932 | 32.8076 | 35.622 | 36.1206 | 36.6192 | 37.1178 | 37.6164 | 38.115 | 38.8939 | 39.6728 | 40.4517 | 41.2306 | 42.0095 | 42.7884 | 43.5673 | 44.3462 | 45.1251 | 45.904 | 46.4198 | 46.9356 | 47.4514 | 47.9672 | 48.483 | 48.9988 | 49.5146 | 50.0304 | 50.5462 | 51.062 | 51.5778 | 52.0936 | 52.6094 | 53.1252 | 53.641 | 54.0599 | 54.4787 | 54.8976 | 55.3165 | 55.7353 | 56.1542 | 56.5731 | 56.9919 | 57.4108 | 57.8297 | 58.2485 | 58.6674 | 59.0863 | 59.5051 | 59.924 | 60.04 | 60.1559 | 60.2719 | 60.3879 | 60.5038 | 60.6198 | 60.7358 | 60.8517 | 60.9677 | 61.0837 | 61.1996 | 61.3156 | 61.4316 | 61.5475 | 61.6635 | 61.7795 | 61.8954 | 62.0114 | 62.1274 | 62.2433 | 62.3593 | 62.4753 | 62.5912 | 62.7072 | 62.8232 | 62.9391 | 63.0551 | 63.1711 | 63.287 | 63.403 | 63.448 | 63.493 | 63.538 | 63.583 | 63.628 | 63.673 | 63.718 | 63.763 | 63.808 | 63.853 | 63.898 | 63.943 | 63.988 | 64.033 | 64.078 | 64.123 | 64.168 | 64.213 | 64.258 | 64.303 | 64.348 | 64.393 | 64.438 | 64.483 | 64.528 | 64.573 | 64.618 | 64.663 | 64.708 | 64.753 | 64.753 | 64.753 | 64.753 | 64.753 | 64.753 | 64.753 | 64.753 | 64.753 | 64.753 | 64.753 | 64.753 | 64.753 | 64.753 | 64.753 | 64.753 | 64.753 | 64.753 | 64.753 | 64.753 | 64.753 | 64.753 | 64.753 | 64.753 | 64.753 | 64.753 | 64.753 | 64.753 | 64.753 | 64.753 | 64.753 | 64.6855 | 64.618 | 64.5505 | 64.483 | 64.4155 | 64.348 | 64.2805 | 64.213 | 64.1455 | 64.078 | 64.0105 | 63.943 | 63.8755 | 63.808 | 63.7405 | 63.673 | 63.6055 | 63.538 | 63.4705 | 63.403 | 63.3355 | 63.268 | 63.2005 | 63.133 | 63.0655 | 62.998 | 62.9305 | 62.863 | 62.7955 | 62.728
8.1 | 0 | 2.1767 | 4.3533 | 6.53 | 8.7067 | 10.8833 | 13.06 | 15.2367 | 17.4133 | 19.59 | 21.7667 | 24.6115 | 27.4563 | 30.3011 | 33.1459 | 35.9907 | 36.4919 | 36.9931 | 37.4943 | 37.9955 | 38.4967 | 39.2838 | 40.0709 | 40.8581 | 41.6452 | 42.4323 | 43.2195 | 44.0066 | 44.7937 | 45.5809 | 46.368 | 46.8894 | 47.4108 | 47.9321 | 48.4535 | 48.9749 | 49.4963 | 50.0176 | 50.539 | 51.0604 | 51.5818 | 52.1032 | 52.6245 | 53.1459 | 53.6673 | 54.1887 | 54.6122 | 55.0357 | 55.4592 | 55.8827 | 56.3062 | 56.7297 | 57.1532 | 57.5768 | 58.0003 | 58.4238 | 58.8473 | 59.2708 | 59.6943 | 60.1178 | 60.5413 | 60.6586 | 60.7759 | 60.8931 | 61.0104 | 61.1277 | 61.2449 | 61.3622 | 61.4795 | 61.5967 | 61.714 | 61.8313 | 61.9485 | 62.0658 | 62.1831 | 62.3003 | 62.4176 | 62.5349 | 62.6521 | 62.7694 | 62.8867 | 63.0039 | 63.1212 | 63.2385 | 63.3557 | 63.473 | 63.5903 | 63.7075 | 63.8248 | 63.9421 | 64.0593 | 64.1049 | 64.1504 | 64.196 | 64.2416 | 64.2871 | 64.3327 | 64.3782 | 64.4238 | 64.4693 | 64.5149 | 64.5604 | 64.606 | 64.6516 | 64.6971 | 64.7427 | 64.7882 | 64.8338 | 64.8793 | 64.9249 | 64.9704 | 65.016 | 65.0616 | 65.1071 | 65.1527 | 65.1982 | 65.2438 | 65.2893 | 65.3349 | 65.3804 | 65.426 | 65.426 | 65.426 | 65.426 | 65.426 | 65.426 | 65.426 | 65.426 | 65.426 | 65.426 | 65.426 | 65.426 | 65.426 | 65.426 | 65.426 | 65.426 | 65.426 | 65.426 | 65.426 | 65.426 | 65.426 | 65.426 | 65.426 | 65.426 | 65.426 | 65.426 | 65.426 | 65.426 | 65.426 | 65.426 | 65.426 | 65.3577 | 65.2893 | 65.221 | 65.1527 | 65.0843 | 65.016 | 64.9477 | 64.8793 | 64.811 | 64.7427 | 64.6743 | 64.606 | 64.5377 | 64.4693 | 64.401 | 64.3327 | 64.2643 | 64.196 | 64.1277 | 64.0593 | 63.991 | 63.9227 | 63.8543 | 63.786 | 63.7177 | 63.6493 | 63.581 | 63.5127 | 63.4443 | 63.376
8.15 | 0 | 2.1983 | 4.3967 | 6.595 | 8.7933 | 10.9917 | 13.19 | 15.3883 | 17.5867 | 19.785 | 21.9833 | 24.8585 | 27.7337 | 30.6089 | 33.4841 | 36.3593 | 36.8631 | 37.3669 | 37.8707 | 38.3745 | 38.8783 | 39.6737 | 40.4691 | 41.2644 | 42.0598 | 42.8552 | 43.6505 | 44.4459 | 45.2413 | 46.0366 | 46.832 | 47.359 | 47.8859 | 48.4129 | 48.9398 | 49.4668 | 49.9937 | 50.5207 | 51.0476 | 51.5746 | 52.1016 | 52.6285 | 53.1555 | 53.6824 | 54.2094 | 54.7363 | 55.1645 | 55.5926 | 56.0208 | 56.449 | 56.8771 | 57.3053 | 57.7334 | 58.1616 | 58.5897 | 59.0179 | 59.446 | 59.8742 | 60.3024 | 60.7305 | 61.1587 | 61.2772 | 61.3958 | 61.5144 | 61.6329 | 61.7515 | 61.8701 | 61.9886 | 62.1072 | 62.2258 | 62.3443 | 62.4629 | 62.5815 | 62.7 | 62.8186 | 62.9372 | 63.0557 | 63.1743 | 63.2929 | 63.4114 | 63.53 | 63.6486 | 63.7671 | 63.8857 | 64.0043 | 64.1228 | 64.2414 | 64.36 | 64.4785 | 64.5971 | 64.7157 | 64.7618 | 64.8079 | 64.854 | 64.9001 | 64.9462 | 64.9923 | 65.0384 | 65.0846 | 65.1307 | 65.1768 | 65.2229 | 65.269 | 65.3151 | 65.3612 | 65.4073 | 65.4534 | 65.4996 | 65.5457 | 65.5918 | 65.6379 | 65.684 | 65.7301 | 65.7762 | 65.8223 | 65.8684 | 65.9146 | 65.9607 | 66.0068 | 66.0529 | 66.099 | 66.099 | 66.099 | 66.099 | 66.099 | 66.099 | 66.099 | 66.099 | 66.099 | 66.099 | 66.099 | 66.099 | 66.099 | 66.099 | 66.099 | 66.099 | 66.099 | 66.099 | 66.099 | 66.099 | 66.099 | 66.099 | 66.099 | 66.099 | 66.099 | 66.099 | 66.099 | 66.099 | 66.099 | 66.099 | 66.099 | 66.0298 | 65.9607 | 65.8915 | 65.8223 | 65.7532 | 65.684 | 65.6148 | 65.5457 | 65.4765 | 65.4073 | 65.3382 | 65.269 | 65.1998 | 65.1307 | 65.0615 | 64.9923 | 64.9232 | 64.854 | 64.7848 | 64.7157 | 64.6465 | 64.5773 | 64.5082 | 64.439 | 64.3698 | 64.3007 | 64.2315 | 64.1623 | 64.0932 | 64.024
8.2 | 0 | 2.22 | 4.44 | 6.66 | 8.88 | 11.1 | 13.32 | 15.54 | 17.76 | 19.98 | 22.2 | 25.1056 | 28.0112 | 30.9168 | 33.8224 | 36.728 | 37.2344 | 37.7408 | 38.2472 | 38.7536 | 39.26 | 40.0636 | 40.8672 | 41.6708 | 42.4744 | 43.278 | 44.0816 | 44.8852 | 45.6888 | 46.4924 | 47.296 | 47.8285 | 48.3611 | 48.8936 | 49.4261 | 49.9587 | 50.4912 | 51.0237 | 51.5563 | 52.0888 | 52.6213 | 53.1539 | 53.6864 | 54.2189 | 54.7515 | 55.284 | 55.7168 | 56.1496 | 56.5824 | 57.0152 | 57.448 | 57.8808 | 58.3136 | 58.7464 | 59.1792 | 59.612 | 60.0448 | 60.4776 | 60.9104 | 61.3432 | 61.776 | 61.8959 | 62.0157 | 62.1356 | 62.2555 | 62.3753 | 62.4952 | 62.6151 | 62.7349 | 62.8548 | 62.9747 | 63.0945 | 63.2144 | 63.3343 | 63.4541 | 63.574 | 63.6939 | 63.8137 | 63.9336 | 64.0535 | 64.1733 | 64.2932 | 64.4131 | 64.5329 | 64.6528 | 64.7727 | 64.8925 | 65.0124 | 65.1323 | 65.2521 | 65.372 | 65.4187 | 65.4653 | 65.512 | 65.5587 | 65.6053 | 65.652 | 65.6987 | 65.7453 | 65.792 | 65.8387 | 65.8853 | 65.932 | 65.9787 | 66.0253 | 66.072 | 66.1187 | 66.1653 | 66.212 | 66.2587 | 66.3053 | 66.352 | 66.3987 | 66.4453 | 66.492 | 66.5387 | 66.5853 | 66.632 | 66.6787 | 66.7253 | 66.772 | 66.772 | 66.772 | 66.772 | 66.772 | 66.772 | 66.772 | 66.772 | 66.772 | 66.772 | 66.772 | 66.772 | 66.772 | 66.772 | 66.772 | 66.772 | 66.772 | 66.772 | 66.772 | 66.772 | 66.772 | 66.772 | 66.772 | 66.772 | 66.772 | 66.772 | 66.772 | 66.772 | 66.772 | 66.772 | 66.772 | 66.702 | 66.632 | 66.562 | 66.492 | 66.422 | 66.352 | 66.282 | 66.212 | 66.142 | 66.072 | 66.002 | 65.932 | 65.862 | 65.792 | 65.722 | 65.652 | 65.582 | 65.512 | 65.442 | 65.372 | 65.302 | 65.232 | 65.162 | 65.092 | 65.022 | 64.952 | 64.882 | 64.812 | 64.742 | 64.672
8.25 | 0 | 2.2417 | 4.4833 | 6.725 | 8.9667 | 11.2083 | 13.45 | 15.6917 | 17.9333 | 20.175 | 22.4167 | 25.3527 | 28.2887 | 31.2247 | 34.1607 | 37.0967 | 37.6057 | 38.1147 | 38.6237 | 39.1327 | 39.6417 | 40.4535 | 41.2653 | 42.0772 | 42.889 | 43.7008 | 44.5127 | 45.3245 | 46.1363 | 46.9482 | 47.76 | 48.2981 | 48.8362 | 49.3743 | 49.9124 | 50.4506 | 50.9887 | 51.5268 | 52.0649 | 52.603 | 53.1411 | 53.6792 | 54.2173 | 54.7554 | 55.2936 | 55.8317 | 56.2691 | 56.7066 | 57.144 | 57.5814 | 58.0189 | 58.4563 | 58.8938 | 59.3312 | 59.7687 | 60.2061 | 60.6436 | 61.081 | 61.5184 | 61.9559 | 62.3933 | 62.5145 | 62.6357 | 62.7568 | 62.878 | 62.9992 | 63.1203 | 63.2415 | 63.3627 | 63.4838 | 63.605 | 63.7262 | 63.8473 | 63.9685 | 64.0897 | 64.2108 | 64.332 | 64.4532 | 64.5743 | 64.6955 | 64.8167 | 64.9378 | 65.059 | 65.1802 | 65.3013 | 65.4225 | 65.5437 | 65.6648 | 65.786 | 65.9072 | 66.0283 | 66.0756 | 66.1228 | 66.17 | 66.2172 | 66.2644 | 66.3117 | 66.3589 | 66.4061 | 66.4533 | 66.5006 | 66.5478 | 66.595 | 66.6422 | 66.6894 | 66.7367 | 66.7839 | 66.8311 | 66.8783 | 66.9256 | 66.9728 | 67.02 | 67.0672 | 67.1144 | 67.1617 | 67.2089 | 67.2561 | 67.3033 | 67.3506 | 67.3978 | 67.445 | 67.445 | 67.445 | 67.445 | 67.445 | 67.445 | 67.445 | 67.445 | 67.445 | 67.445 | 67.445 | 67.445 | 67.445 | 67.445 | 67.445 | 67.445 | 67.445 | 67.445 | 67.445 | 67.445 | 67.445 | 67.445 | 67.445 | 67.445 | 67.445 | 67.445 | 67.445 | 67.445 | 67.445 | 67.445 | 67.445 | 67.3742 | 67.3033 | 67.2325 | 67.1617 | 67.0908 | 67.02 | 66.9492 | 66.8783 | 66.8075 | 66.7367 | 66.6658 | 66.595 | 66.5242 | 66.4533 | 66.3825 | 66.3117 | 66.2408 | 66.17 | 66.0992 | 66.0283 | 65.9575 | 65.8867 | 65.8158 | 65.745 | 65.6742 | 65.6033 | 65.5325 | 65.4617 | 65.3908 | 65.32
8.3 | 0 | 2.2633 | 4.5267 | 6.79 | 9.0533 | 11.3167 | 13.58 | 15.8433 | 18.1067 | 20.37 | 22.6333 | 25.5997 | 28.5661 | 31.5325 | 34.4989 | 37.4653 | 37.9769 | 38.4885 | 39.0001 | 39.5117 | 40.0233 | 40.8434 | 41.6635 | 42.4835 | 43.3036 | 44.1237 | 44.9437 | 45.7638 | 46.5839 | 47.4039 | 48.224 | 48.7677 | 49.3114 | 49.8551 | 50.3988 | 50.9424 | 51.4861 | 52.0298 | 52.5735 | 53.1172 | 53.6609 | 54.2046 | 54.7483 | 55.292 | 55.8356 | 56.3793 | 56.8214 | 57.2635 | 57.7056 | 58.1477 | 58.5898 | 59.0319 | 59.474 | 59.916 | 60.3581 | 60.8002 | 61.2423 | 61.6844 | 62.1265 | 62.5686 | 63.0107 | 63.1331 | 63.2556 | 63.3781 | 63.5005 | 63.623 | 63.7455 | 63.8679 | 63.9904 | 64.1129 | 64.2353 | 64.3578 | 64.4803 | 64.6027 | 64.7252 | 64.8477 | 64.9701 | 65.0926 | 65.2151 | 65.3375 | 65.46 | 65.5825 | 65.7049 | 65.8274 | 65.9499 | 66.0723 | 66.1948 | 66.3173 | 66.4397 | 66.5622 | 66.6847 | 66.7324 | 66.7802 | 66.828 | 66.8758 | 66.9236 | 66.9713 | 67.0191 | 67.0669 | 67.1147 | 67.1624 | 67.2102 | 67.258 | 67.3058 | 67.3536 | 67.4013 | 67.4491 | 67.4969 | 67.5447 | 67.5924 | 67.6402 | 67.688 | 67.7358 | 67.7836 | 67.8313 | 67.8791 | 67.9269 | 67.9747 | 68.0224 | 68.0702 | 68.118 | 68.118 | 68.118 | 68.118 | 68.118 | 68.118 | 68.118 | 68.118 | 68.118 | 68.118 | 68.118 | 68.118 | 68.118 | 68.118 | 68.118 | 68.118 | 68.118 | 68.118 | 68.118 | 68.118 | 68.118 | 68.118 | 68.118 | 68.118 | 68.118 | 68.118 | 68.118 | 68.118 | 68.118 | 68.118 | 68.118 | 68.0463 | 67.9747 | 67.903 | 67.8313 | 67.7597 | 67.688 | 67.6163 | 67.5447 | 67.473 | 67.4013 | 67.3297 | 67.258 | 67.1863 | 67.1147 | 67.043 | 66.9713 | 66.8997 | 66.828 | 66.7563 | 66.6847 | 66.613 | 66.5413 | 66.4697 | 66.398 | 66.3263 | 66.2547 | 66.183 | 66.1113 | 66.0397 | 65.968
8.35 | 0 | 2.285 | 4.57 | 6.855 | 9.14 | 11.425 | 13.71 | 15.995 | 18.28 | 20.565 | 22.85 | 25.8468 | 28.8436 | 31.8404 | 34.8372 | 37.834 | 38.3482 | 38.8624 | 39.3766 | 39.8908 | 40.405 | 41.2333 | 42.0616 | 42.8899 | 43.7182 | 44.5465 | 45.3748 | 46.2031 | 47.0314 | 47.8597 | 48.688 | 49.2373 | 49.7865 | 50.3358 | 50.8851 | 51.4343 | 51.9836 | 52.5329 | 53.0821 | 53.6314 | 54.1807 | 54.7299 | 55.2792 | 55.8285 | 56.3777 | 56.927 | 57.3737 | 57.8205 | 58.2672 | 58.7139 | 59.1607 | 59.6074 | 60.0541 | 60.5009 | 60.9476 | 61.3943 | 61.8411 | 62.2878 | 62.7345 | 63.1813 | 63.628 | 63.7518 | 63.8755 | 63.9993 | 64.1231 | 64.2468 | 64.3706 | 64.4944 | 64.6181 | 64.7419 | 64.8657 | 64.9894 | 65.1132 | 65.237 | 65.3607 | 65.4845 | 65.6083 | 65.732 | 65.8558 | 65.9796 | 66.1033 | 66.2271 | 66.3509 | 66.4746 | 66.5984 | 66.7222 | 66.8459 | 66.9697 | 67.0935 | 67.2172 | 67.341 | 67.3893 | 67.4377 | 67.486 | 67.5343 | 67.5827 | 67.631 | 67.6793 | 67.7277 | 67.776 | 67.8243 | 67.8727 | 67.921 | 67.9693 | 68.0177 | 68.066 | 68.1143 | 68.1627 | 68.211 | 68.2593 | 68.3077 | 68.356 | 68.4043 | 68.4527 | 68.501 | 68.5493 | 68.5977 | 68.646 | 68.6943 | 68.7427 | 68.791 | 68.791 | 68.791 | 68.791 | 68.791 | 68.791 | 68.791 | 68.791 | 68.791 | 68.791 | 68.791 | 68.791 | 68.791 | 68.791 | 68.791 | 68.791 | 68.791 | 68.791 | 68.791 | 68.791 | 68.791 | 68.791 | 68.791 | 68.791 | 68.791 | 68.791 | 68.791 | 68.791 | 68.791 | 68.791 | 68.791 | 68.7185 | 68.646 | 68.5735 | 68.501 | 68.4285 | 68.356 | 68.2835 | 68.211 | 68.1385 | 68.066 | 67.9935 | 67.921 | 67.8485 | 67.776 | 67.7035 | 67.631 | 67.5585 | 67.486 | 67.4135 | 67.341 | 67.2685 | 67.196 | 67.1235 | 67.051 | 66.9785 | 66.906 | 66.8335 | 66.761 | 66.6885 | 66.616
8.4 | 0 | 2.3067 | 4.6133 | 6.92 | 9.2267 | 11.5333 | 13.84 | 16.1467 | 18.4533 | 20.76 | 23.0667 | 26.0939 | 29.1211 | 32.1483 | 35.1755 | 38.2027 | 38.7195 | 39.2363 | 39.7531 | 40.2699 | 40.7867 | 41.6232 | 42.4597 | 43.2963 | 44.1328 | 44.9693 | 45.8059 | 46.6424 | 47.4789 | 48.3155 | 49.152 | 49.7068 | 50.2617 | 50.8165 | 51.3714 | 51.9262 | 52.4811 | 53.0359 | 53.5908 | 54.1456 | 54.7004 | 55.2553 | 55.8101 | 56.365 | 56.9198 | 57.4747 | 57.926 | 58.3774 | 58.8288 | 59.2802 | 59.7316 | 60.1829 | 60.6343 | 61.0857 | 61.5371 | 61.9884 | 62.4398 | 62.8912 | 63.3426 | 63.794 | 64.2453 | 64.3704 | 64.4955 | 64.6205 | 64.7456 | 64.8707 | 64.9957 | 65.1208 | 65.2459 | 65.3709 | 65.496 | 65.6211 | 65.7461 | 65.8712 | 65.9963 | 66.1213 | 66.2464 | 66.3715 | 66.4965 | 66.6216 | 66.7467 | 66.8717 | 66.9968 | 67.1219 | 67.2469 | 67.372 | 67.4971 | 67.6221 | 67.7472 | 67.8723 | 67.9973 | 68.0462 | 68.0951 | 68.144 | 68.1929 | 68.2418 | 68.2907 | 68.3396 | 68.3884 | 68.4373 | 68.4862 | 68.5351 | 68.584 | 68.6329 | 68.6818 | 68.7307 | 68.7796 | 68.8284 | 68.8773 | 68.9262 | 68.9751 | 69.024 | 69.0729 | 69.1218 | 69.1707 | 69.2196 | 69.2684 | 69.3173 | 69.3662 | 69.4151 | 69.464 | 69.464 | 69.464 | 69.464 | 69.464 | 69.464 | 69.464 | 69.464 | 69.464 | 69.464 | 69.464 | 69.464 | 69.464 | 69.464 | 69.464 | 69.464 | 69.464 | 69.464 | 69.464 | 69.464 | 69.464 | 69.464 | 69.464 | 69.464 | 69.464 | 69.464 | 69.464 | 69.464 | 69.464 | 69.464 | 69.464 | 69.3907 | 69.3173 | 69.244 | 69.1707 | 69.0973 | 69.024 | 68.9507 | 68.8773 | 68.804 | 68.7307 | 68.6573 | 68.584 | 68.5107 | 68.4373 | 68.364 | 68.2907 | 68.2173 | 68.144 | 68.0707 | 67.9973 | 67.924 | 67.8507 | 67.7773 | 67.704 | 67.6307 | 67.5573 | 67.484 | 67.4107 | 67.3373 | 67.264
8.45 | 0 | 2.3283 | 4.6567 | 6.985 | 9.3133 | 11.6417 | 13.97 | 16.2983 | 18.6267 | 20.955 | 23.2833 | 26.3409 | 29.3985 | 32.4561 | 35.5137 | 38.5713 | 39.0907 | 39.6101 | 40.1295 | 40.6489 | 41.1683 | 42.0131 | 42.8579 | 43.7026 | 44.5474 | 45.3922 | 46.2369 | 47.0817 | 47.9265 | 48.7712 | 49.616 | 50.1764 | 50.7368 | 51.2973 | 51.8577 | 52.4181 | 52.9785 | 53.539 | 54.0994 | 54.6598 | 55.2202 | 55.7806 | 56.3411 | 56.9015 | 57.4619 | 58.0223 | 58.4784 | 58.9344 | 59.3904 | 59.8464 | 60.3024 | 60.7585 | 61.2145 | 61.6705 | 62.1265 | 62.5826 | 63.0386 | 63.4946 | 63.9506 | 64.4066 | 64.8627 | 64.989 | 65.1154 | 65.2418 | 65.3681 | 65.4945 | 65.6209 | 65.7472 | 65.8736 | 66 | 66.1263 | 66.2527 | 66.3791 | 66.5054 | 66.6318 | 66.7582 | 66.8845 | 67.0109 | 67.1373 | 67.2636 | 67.39 | 67.5164 | 67.6427 | 67.7691 | 67.8955 | 68.0218 | 68.1482 | 68.2746 | 68.4009 | 68.5273 | 68.6537 | 68.7031 | 68.7526 | 68.802 | 68.8514 | 68.9009 | 68.9503 | 68.9998 | 69.0492 | 69.0987 | 69.1481 | 69.1976 | 69.247 | 69.2964 | 69.3459 | 69.3953 | 69.4448 | 69.4942 | 69.5437 | 69.5931 | 69.6426 | 69.692 | 69.7414 | 69.7909 | 69.8403 | 69.8898 | 69.9392 | 69.9887 | 70.0381 | 70.0876 | 70.137 | 70.137 | 70.137 | 70.137 | 70.137 | 70.137 | 70.137 | 70.137 | 70.137 | 70.137 | 70.137 | 70.137 | 70.137 | 70.137 | 70.137 | 70.137 | 70.137 | 70.137 | 70.137 | 70.137 | 70.137 | 70.137 | 70.137 | 70.137 | 70.137 | 70.137 | 70.137 | 70.137 | 70.137 | 70.137 | 70.137 | 70.0628 | 69.9887 | 69.9145 | 69.8403 | 69.7662 | 69.692 | 69.6178 | 69.5437 | 69.4695 | 69.3953 | 69.3212 | 69.247 | 69.1728 | 69.0987 | 69.0245 | 68.9503 | 68.8762 | 68.802 | 68.7278 | 68.6537 | 68.5795 | 68.5053 | 68.4312 | 68.357 | 68.2828 | 68.2087 | 68.1345 | 68.0603 | 67.9862 | 67.912
8.5 | 0 | 2.35 | 4.7 | 7.05 | 9.4 | 11.75 | 14.1 | 16.45 | 18.8 | 21.15 | 23.5 | 26.588 | 29.676 | 32.764 | 35.852 | 38.94 | 39.462 | 39.984 | 40.506 | 41.028 | 41.55 | 42.403 | 43.256 | 44.109 | 44.962 | 45.815 | 46.668 | 47.521 | 48.374 | 49.227 | 50.08 | 50.646 | 51.212 | 51.778 | 52.344 | 52.91 | 53.476 | 54.042 | 54.608 | 55.174 | 55.74 | 56.306 | 56.872 | 57.438 | 58.004 | 58.57 | 59.0307 | 59.4913 | 59.952 | 60.4127 | 60.8733 | 61.334 | 61.7947 | 62.2553 | 62.716 | 63.1767 | 63.6373 | 64.098 | 64.5587 | 65.0193 | 65.48 | 65.6077 | 65.7353 | 65.863 | 65.9907 | 66.1183 | 66.246 | 66.3737 | 66.5013 | 66.629 | 66.7567 | 66.8843 | 67.012 | 67.1397 | 67.2673 | 67.395 | 67.5227 | 67.6503 | 67.778 | 67.9057 | 68.0333 | 68.161 | 68.2887 | 68.4163 | 68.544 | 68.6717 | 68.7993 | 68.927 | 69.0547 | 69.1823 | 69.31 | 69.36 | 69.41 | 69.46 | 69.51 | 69.56 | 69.61 | 69.66 | 69.71 | 69.76 | 69.81 | 69.86 | 69.91 | 69.96 | 70.01 | 70.06 | 70.11 | 70.16 | 70.21 | 70.26 | 70.31 | 70.36 | 70.41 | 70.46 | 70.51 | 70.56 | 70.61 | 70.66 | 70.71 | 70.76 | 70.81 | 70.81 | 70.81 | 70.81 | 70.81 | 70.81 | 70.81 | 70.81 | 70.81 | 70.81 | 70.81 | 70.81 | 70.81 | 70.81 | 70.81 | 70.81 | 70.81 | 70.81 | 70.81 | 70.81 | 70.81 | 70.81 | 70.81 | 70.81 | 70.81 | 70.81 | 70.81 | 70.81 | 70.81 | 70.81 | 70.81 | 70.735 | 70.66 | 70.585 | 70.51 | 70.435 | 70.36 | 70.285 | 70.21 | 70.135 | 70.06 | 69.985 | 69.91 | 69.835 | 69.76 | 69.685 | 69.61 | 69.535 | 69.46 | 69.385 | 69.31 | 69.235 | 69.16 | 69.085 | 69.01 | 68.935 | 68.86 | 68.785 | 68.71 | 68.635 | 68.56
8.55 | 0 | 2.3717 | 4.7433 | 7.115 | 9.4867 | 11.8583 | 14.23 | 16.6017 | 18.9733 | 21.345 | 23.7167 | 26.8351 | 29.9535 | 33.0719 | 36.1903 | 39.3087 | 39.8333 | 40.3579 | 40.8825 | 41.4071 | 41.9317 | 42.7929 | 43.6541 | 44.5154 | 45.3766 | 46.2378 | 47.0991 | 47.9603 | 48.8215 | 49.6828 | 50.544 | 51.1156 | 51.6872 | 52.2587 | 52.8303 | 53.4019 | 53.9735 | 54.545 | 55.1166 | 55.6882 | 56.2598 | 56.8314 | 57.4029 | 57.9745 | 58.5461 | 59.1177 | 59.583 | 60.0483 | 60.5136 | 60.9789 | 61.4442 | 61.9095 | 62.3748 | 62.8402 | 63.3055 | 63.7708 | 64.2361 | 64.7014 | 65.1667 | 65.632 | 66.0973 | 66.2263 | 66.3553 | 66.4842 | 66.6132 | 66.7422 | 66.8711 | 67.0001 | 67.1291 | 67.258 | 67.387 | 67.516 | 67.6449 | 67.7739 | 67.9029 | 68.0318 | 68.1608 | 68.2898 | 68.4187 | 68.5477 | 68.6767 | 68.8056 | 68.9346 | 69.0636 | 69.1925 | 69.3215 | 69.4505 | 69.5794 | 69.7084 | 69.8374 | 69.9663 | 70.0169 | 70.0674 | 70.118 | 70.1686 | 70.2191 | 70.2697 | 70.3202 | 70.3708 | 70.4213 | 70.4719 | 70.5224 | 70.573 | 70.6236 | 70.6741 | 70.7247 | 70.7752 | 70.8258 | 70.8763 | 70.9269 | 70.9774 | 71.028 | 71.0786 | 71.1291 | 71.1797 | 71.2302 | 71.2808 | 71.3313 | 71.3819 | 71.4324 | 71.483 | 71.483 | 71.483 | 71.483 | 71.483 | 71.483 | 71.483 | 71.483 | 71.483 | 71.483 | 71.483 | 71.483 | 71.483 | 71.483 | 71.483 | 71.483 | 71.483 | 71.483 | 71.483 | 71.483 | 71.483 | 71.483 | 71.483 | 71.483 | 71.483 | 71.483 | 71.483 | 71.483 | 71.483 | 71.483 | 71.483 | 71.4072 | 71.3313 | 71.2555 | 71.1797 | 71.1038 | 71.028 | 70.9522 | 70.8763 | 70.8005 | 70.7247 | 70.6488 | 70.573 | 70.4972 | 70.4213 | 70.3455 | 70.2697 | 70.1938 | 70.118 | 70.0422 | 69.9663 | 69.8905 | 69.8147 | 69.7388 | 69.663 | 69.5872 | 69.5113 | 69.4355 | 69.3597 | 69.2838 | 69.208
8.6 | 0 | 2.3933 | 4.7867 | 7.18 | 9.5733 | 11.9667 | 14.36 | 16.7533 | 19.1467 | 21.54 | 23.9333 | 27.0821 | 30.2309 | 33.3797 | 36.5285 | 39.6773 | 40.2045 | 40.7317 | 41.2589 | 41.7861 | 42.3133 | 43.1828 | 44.0523 | 44.9217 | 45.7912 | 46.6607 | 47.5301 | 48.3996 | 49.2691 | 50.1385 | 51.008 | 51.5852 | 52.1623 | 52.7395 | 53.3166 | 53.8938 | 54.4709 | 55.0481 | 55.6252 | 56.2024 | 56.7796 | 57.3567 | 57.9339 | 58.511 | 59.0882 | 59.6653 | 60.1353 | 60.6052 | 61.0752 | 61.5452 | 62.0151 | 62.4851 | 62.955 | 63.425 | 63.8949 | 64.3649 | 64.8348 | 65.3048 | 65.7748 | 66.2447 | 66.7147 | 66.8449 | 66.9752 | 67.1055 | 67.2357 | 67.366 | 67.4963 | 67.6265 | 67.7568 | 67.8871 | 68.0173 | 68.1476 | 68.2779 | 68.4081 | 68.5384 | 68.6687 | 68.7989 | 68.9292 | 69.0595 | 69.1897 | 69.32 | 69.4503 | 69.5805 | 69.7108 | 69.8411 | 69.9713 | 70.1016 | 70.2319 | 70.3621 | 70.4924 | 70.6227 | 70.6738 | 70.7249 | 70.776 | 70.8271 | 70.8782 | 70.9293 | 70.9804 | 71.0316 | 71.0827 | 71.1338 | 71.1849 | 71.236 | 71.2871 | 71.3382 | 71.3893 | 71.4404 | 71.4916 | 71.5427 | 71.5938 | 71.6449 | 71.696 | 71.7471 | 71.7982 | 71.8493 | 71.9004 | 71.9516 | 72.0027 | 72.0538 | 72.1049 | 72.156 | 72.156 | 72.156 | 72.156 | 72.156 | 72.156 | 72.156 | 72.156 | 72.156 | 72.156 | 72.156 | 72.156 | 72.156 | 72.156 | 72.156 | 72.156 | 72.156 | 72.156 | 72.156 | 72.156 | 72.156 | 72.156 | 72.156 | 72.156 | 72.156 | 72.156 | 72.156 | 72.156 | 72.156 | 72.156 | 72.156 | 72.0793 | 72.0027 | 71.926 | 71.8493 | 71.7727 | 71.696 | 71.6193 | 71.5427 | 71.466 | 71.3893 | 71.3127 | 71.236 | 71.1593 | 71.0827 | 71.006 | 70.9293 | 70.8527 | 70.776 | 70.6993 | 70.6227 | 70.546 | 70.4693 | 70.3927 | 70.316 | 70.2393 | 70.1627 | 70.086 | 70.0093 | 69.9327 | 69.856
8.65 | 0 | 2.415 | 4.83 | 7.245 | 9.66 | 12.075 | 14.49 | 16.905 | 19.32 | 21.735 | 24.15 | 27.3292 | 30.5084 | 33.6876 | 36.8668 | 40.046 | 40.5758 | 41.1056 | 41.6354 | 42.1652 | 42.695 | 43.5727 | 44.4504 | 45.3281 | 46.2058 | 47.0835 | 47.9612 | 48.8389 | 49.7166 | 50.5943 | 51.472 | 52.0547 | 52.6375 | 53.2202 | 53.8029 | 54.3857 | 54.9684 | 55.5511 | 56.1339 | 56.7166 | 57.2993 | 57.8821 | 58.4648 | 59.0475 | 59.6303 | 60.213 | 60.6876 | 61.1622 | 61.6368 | 62.1114 | 62.586 | 63.0606 | 63.5352 | 64.0098 | 64.4844 | 64.959 | 65.4336 | 65.9082 | 66.3828 | 66.8574 | 67.332 | 67.4636 | 67.5951 | 67.7267 | 67.8583 | 67.9898 | 68.1214 | 68.253 | 68.3845 | 68.5161 | 68.6477 | 68.7792 | 68.9108 | 69.0424 | 69.1739 | 69.3055 | 69.4371 | 69.5686 | 69.7002 | 69.8318 | 69.9633 | 70.0949 | 70.2265 | 70.358 | 70.4896 | 70.6212 | 70.7527 | 70.8843 | 71.0159 | 71.1474 | 71.279 | 71.3307 | 71.3823 | 71.434 | 71.4857 | 71.5373 | 71.589 | 71.6407 | 71.6923 | 71.744 | 71.7957 | 71.8473 | 71.899 | 71.9507 | 72.0023 | 72.054 | 72.1057 | 72.1573 | 72.209 | 72.2607 | 72.3123 | 72.364 | 72.4157 | 72.4673 | 72.519 | 72.5707 | 72.6223 | 72.674 | 72.7257 | 72.7773 | 72.829 | 72.829 | 72.829 | 72.829 | 72.829 | 72.829 | 72.829 | 72.829 | 72.829 | 72.829 | 72.829 | 72.829 | 72.829 | 72.829 | 72.829 | 72.829 | 72.829 | 72.829 | 72.829 | 72.829 | 72.829 | 72.829 | 72.829 | 72.829 | 72.829 | 72.829 | 72.829 | 72.829 | 72.829 | 72.829 | 72.829 | 72.7515 | 72.674 | 72.5965 | 72.519 | 72.4415 | 72.364 | 72.2865 | 72.209 | 72.1315 | 72.054 | 71.9765 | 71.899 | 71.8215 | 71.744 | 71.6665 | 71.589 | 71.5115 | 71.434 | 71.3565 | 71.279 | 71.2015 | 71.124 | 71.0465 | 70.969 | 70.8915 | 70.814 | 70.7365 | 70.659 | 70.5815 | 70.504
8.7 | 0 | 2.4367 | 4.8733 | 7.31 | 9.7467 | 12.1833 | 14.62 | 17.0567 | 19.4933 | 21.93 | 24.3667 | 27.5763 | 30.7859 | 33.9955 | 37.2051 | 40.4147 | 40.9471 | 41.4795 | 42.0119 | 42.5443 | 43.0767 | 43.9626 | 44.8485 | 45.7345 | 46.6204 | 47.5063 | 48.3923 | 49.2782 | 50.1641 | 51.0501 | 51.936 | 52.5243 | 53.1126 | 53.7009 | 54.2892 | 54.8776 | 55.4659 | 56.0542 | 56.6425 | 57.2308 | 57.8191 | 58.4074 | 58.9957 | 59.584 | 60.1724 | 60.7607 | 61.2399 | 61.7192 | 62.1984 | 62.6776 | 63.1569 | 63.6361 | 64.1154 | 64.5946 | 65.0739 | 65.5531 | 66.0324 | 66.5116 | 66.9908 | 67.4701 | 67.9493 | 68.0822 | 68.2151 | 68.3479 | 68.4808 | 68.6137 | 68.7465 | 68.8794 | 69.0123 | 69.1451 | 69.278 | 69.4109 | 69.5437 | 69.6766 | 69.8095 | 69.9423 | 70.0752 | 70.2081 | 70.3409 | 70.4738 | 70.6067 | 70.7395 | 70.8724 | 71.0053 | 71.1381 | 71.271 | 71.4039 | 71.5367 | 71.6696 | 71.8025 | 71.9353 | 71.9876 | 72.0398 | 72.092 | 72.1442 | 72.1964 | 72.2487 | 72.3009 | 72.3531 | 72.4053 | 72.4576 | 72.5098 | 72.562 | 72.6142 | 72.6664 | 72.7187 | 72.7709 | 72.8231 | 72.8753 | 72.9276 | 72.9798 | 73.032 | 73.0842 | 73.1364 | 73.1887 | 73.2409 | 73.2931 | 73.3453 | 73.3976 | 73.4498 | 73.502 | 73.502 | 73.502 | 73.502 | 73.502 | 73.502 | 73.502 | 73.502 | 73.502 | 73.502 | 73.502 | 73.502 | 73.502 | 73.502 | 73.502 | 73.502 | 73.502 | 73.502 | 73.502 | 73.502 | 73.502 | 73.502 | 73.502 | 73.502 | 73.502 | 73.502 | 73.502 | 73.502 | 73.502 | 73.502 | 73.502 | 73.4237 | 73.3453 | 73.267 | 73.1887 | 73.1103 | 73.032 | 72.9537 | 72.8753 | 72.797 | 72.7187 | 72.6403 | 72.562 | 72.4837 | 72.4053 | 72.327 | 72.2487 | 72.1703 | 72.092 | 72.0137 | 71.9353 | 71.857 | 71.7787 | 71.7003 | 71.622 | 71.5437 | 71.4653 | 71.387 | 71.3087 | 71.2303 | 71.152
8.75 | 0 | 2.4583 | 4.9167 | 7.375 | 9.8333 | 12.2917 | 14.75 | 17.2083 | 19.6667 | 22.125 | 24.5833 | 27.8233 | 31.0633 | 34.3033 | 37.5433 | 40.7833 | 41.3183 | 41.8533 | 42.3883 | 42.9233 | 43.4583 | 44.3525 | 45.2467 | 46.1408 | 47.035 | 47.9292 | 48.8233 | 49.7175 | 50.6117 | 51.5058 | 52.4 | 52.9939 | 53.5878 | 54.1817 | 54.7756 | 55.3694 | 55.9633 | 56.5572 | 57.1511 | 57.745 | 58.3389 | 58.9328 | 59.5267 | 60.1206 | 60.7144 | 61.3083 | 61.7922 | 62.2761 | 62.76 | 63.2439 | 63.7278 | 64.2117 | 64.6956 | 65.1794 | 65.6633 | 66.1472 | 66.6311 | 67.115 | 67.5989 | 68.0828 | 68.5667 | 68.7008 | 68.835 | 68.9692 | 69.1033 | 69.2375 | 69.3717 | 69.5058 | 69.64 | 69.7742 | 69.9083 | 70.0425 | 70.1767 | 70.3108 | 70.445 | 70.5792 | 70.7133 | 70.8475 | 70.9817 | 71.1158 | 71.25 | 71.3842 | 71.5183 | 71.6525 | 71.7867 | 71.9208 | 72.055 | 72.1892 | 72.3233 | 72.4575 | 72.5917 | 72.6444 | 72.6972 | 72.75 | 72.8028 | 72.8556 | 72.9083 | 72.9611 | 73.0139 | 73.0667 | 73.1194 | 73.1722 | 73.225 | 73.2778 | 73.3306 | 73.3833 | 73.4361 | 73.4889 | 73.5417 | 73.5944 | 73.6472 | 73.7 | 73.7528 | 73.8056 | 73.8583 | 73.9111 | 73.9639 | 74.0167 | 74.0694 | 74.1222 | 74.175 | 74.175 | 74.175 | 74.175 | 74.175 | 74.175 | 74.175 | 74.175 | 74.175 | 74.175 | 74.175 | 74.175 | 74.175 | 74.175 | 74.175 | 74.175 | 74.175 | 74.175 | 74.175 | 74.175 | 74.175 | 74.175 | 74.175 | 74.175 | 74.175 | 74.175 | 74.175 | 74.175 | 74.175 | 74.175 | 74.175 | 74.0958 | 74.0167 | 73.9375 | 73.8583 | 73.7792 | 73.7 | 73.6208 | 73.5417 | 73.4625 | 73.3833 | 73.3042 | 73.225 | 73.1458 | 73.0667 | 72.9875 | 72.9083 | 72.8292 | 72.75 | 72.6708 | 72.5917 | 72.5125 | 72.4333 | 72.3542 | 72.275 | 72.1958 | 72.1167 | 72.0375 | 71.9583 | 71.8792 | 71.8
8.8 | 0 | 2.48 | 4.96 | 7.44 | 9.92 | 12.4 | 14.88 | 17.36 | 19.84 | 22.32 | 24.8 | 28.0704 | 31.3408 | 34.6112 | 37.8816 | 41.152 | 41.6896 | 42.2272 | 42.7648 | 43.3024 | 43.84 | 44.7424 | 45.6448 | 46.5472 | 47.4496 | 48.352 | 49.2544 | 50.1568 | 51.0592 | 51.9616 | 52.864 | 53.4635 | 54.0629 | 54.6624 | 55.2619 | 55.8613 | 56.4608 | 57.0603 | 57.6597 | 58.2592 | 58.8587 | 59.4581 | 60.0576 | 60.6571 | 61.2565 | 61.856 | 62.3445 | 62.8331 | 63.3216 | 63.8101 | 64.2987 | 64.7872 | 65.2757 | 65.7643 | 66.2528 | 66.7413 | 67.2299 | 67.7184 | 68.2069 | 68.6955 | 69.184 | 69.3195 | 69.4549 | 69.5904 | 69.7259 | 69.8613 | 69.9968 | 70.1323 | 70.2677 | 70.4032 | 70.5387 | 70.6741 | 70.8096 | 70.9451 | 71.0805 | 71.216 | 71.3515 | 71.4869 | 71.6224 | 71.7579 | 71.8933 | 72.0288 | 72.1643 | 72.2997 | 72.4352 | 72.5707 | 72.7061 | 72.8416 | 72.9771 | 73.1125 | 73.248 | 73.3013 | 73.3547 | 73.408 | 73.4613 | 73.5147 | 73.568 | 73.6213 | 73.6747 | 73.728 | 73.7813 | 73.8347 | 73.888 | 73.9413 | 73.9947 | 74.048 | 74.1013 | 74.1547 | 74.208 | 74.2613 | 74.3147 | 74.368 | 74.4213 | 74.4747 | 74.528 | 74.5813 | 74.6347 | 74.688 | 74.7413 | 74.7947 | 74.848 | 74.848 | 74.848 | 74.848 | 74.848 | 74.848 | 74.848 | 74.848 | 74.848 | 74.848 | 74.848 | 74.848 | 74.848 | 74.848 | 74.848 | 74.848 | 74.848 | 74.848 | 74.848 | 74.848 | 74.848 | 74.848 | 74.848 | 74.848 | 74.848 | 74.848 | 74.848 | 74.848 | 74.848 | 74.848 | 74.848 | 74.768 | 74.688 | 74.608 | 74.528 | 74.448 | 74.368 | 74.288 | 74.208 | 74.128 | 74.048 | 73.968 | 73.888 | 73.808 | 73.728 | 73.648 | 73.568 | 73.488 | 73.408 | 73.328 | 73.248 | 73.168 | 73.088 | 73.008 | 72.928 | 72.848 | 72.768 | 72.688 | 72.608 | 72.528 | 72.448
8.85 | 0 | 2.5017 | 5.0033 | 7.505 | 10.0067 | 12.5083 | 15.01 | 17.5117 | 20.0133 | 22.515 | 25.0167 | 28.3175 | 31.6183 | 34.9191 | 38.2199 | 41.5207 | 42.0609 | 42.6011 | 43.1413 | 43.6815 | 44.2217 | 45.1323 | 46.0429 | 46.9536 | 47.8642 | 48.7748 | 49.6855 | 50.5961 | 51.5067 | 52.4174 | 53.328 | 53.933 | 54.5381 | 55.1431 | 55.7482 | 56.3532 | 56.9583 | 57.5633 | 58.1684 | 58.7734 | 59.3784 | 59.9835 | 60.5885 | 61.1936 | 61.7986 | 62.4037 | 62.8968 | 63.39 | 63.8832 | 64.3764 | 64.8696 | 65.3627 | 65.8559 | 66.3491 | 66.8423 | 67.3354 | 67.8286 | 68.3218 | 68.815 | 69.3082 | 69.8013 | 69.9381 | 70.0749 | 70.2116 | 70.3484 | 70.4852 | 70.6219 | 70.7587 | 70.8955 | 71.0322 | 71.169 | 71.3058 | 71.4425 | 71.5793 | 71.7161 | 71.8528 | 71.9896 | 72.1264 | 72.2631 | 72.3999 | 72.5367 | 72.6734 | 72.8102 | 72.947 | 73.0837 | 73.2205 | 73.3573 | 73.494 | 73.6308 | 73.7676 | 73.9043 | 73.9582 | 74.0121 | 74.066 | 74.1199 | 74.1738 | 74.2277 | 74.2816 | 74.3354 | 74.3893 | 74.4432 | 74.4971 | 74.551 | 74.6049 | 74.6588 | 74.7127 | 74.7666 | 74.8204 | 74.8743 | 74.9282 | 74.9821 | 75.036 | 75.0899 | 75.1438 | 75.1977 | 75.2516 | 75.3054 | 75.3593 | 75.4132 | 75.4671 | 75.521 | 75.521 | 75.521 | 75.521 | 75.521 | 75.521 | 75.521 | 75.521 | 75.521 | 75.521 | 75.521 | 75.521 | 75.521 | 75.521 | 75.521 | 75.521 | 75.521 | 75.521 | 75.521 | 75.521 | 75.521 | 75.521 | 75.521 | 75.521 | 75.521 | 75.521 | 75.521 | 75.521 | 75.521 | 75.521 | 75.521 | 75.4402 | 75.3593 | 75.2785 | 75.1977 | 75.1168 | 75.036 | 74.9552 | 74.8743 | 74.7935 | 74.7127 | 74.6318 | 74.551 | 74.4702 | 74.3893 | 74.3085 | 74.2277 | 74.1468 | 74.066 | 73.9852 | 73.9043 | 73.8235 | 73.7427 | 73.6618 | 73.581 | 73.5002 | 73.4193 | 73.3385 | 73.2577 | 73.1768 | 73.096
8.9 | 0 | 2.5233 | 5.0467 | 7.57 | 10.0933 | 12.6167 | 15.14 | 17.6633 | 20.1867 | 22.71 | 25.2333 | 28.5645 | 31.8957 | 35.2269 | 38.5581 | 41.8893 | 42.4321 | 42.9749 | 43.5177 | 44.0605 | 44.6033 | 45.5222 | 46.4411 | 47.3599 | 48.2788 | 49.1977 | 50.1165 | 51.0354 | 51.9543 | 52.8731 | 53.792 | 54.4026 | 55.0132 | 55.6239 | 56.2345 | 56.8451 | 57.4557 | 58.0664 | 58.677 | 59.2876 | 59.8982 | 60.5088 | 61.1195 | 61.7301 | 62.3407 | 62.9513 | 63.4492 | 63.947 | 64.4448 | 64.9426 | 65.4404 | 65.9383 | 66.4361 | 66.9339 | 67.4317 | 67.9296 | 68.4274 | 68.9252 | 69.423 | 69.9208 | 70.4187 | 70.5567 | 70.6948 | 70.8329 | 70.9709 | 71.109 | 71.2471 | 71.3851 | 71.5232 | 71.6613 | 71.7993 | 71.9374 | 72.0755 | 72.2135 | 72.3516 | 72.4897 | 72.6277 | 72.7658 | 72.9039 | 73.0419 | 73.18 | 73.3181 | 73.4561 | 73.5942 | 73.7323 | 73.8703 | 74.0084 | 74.1465 | 74.2845 | 74.4226 | 74.5607 | 74.6151 | 74.6696 | 74.724 | 74.7784 | 74.8329 | 74.8873 | 74.9418 | 74.9962 | 75.0507 | 75.1051 | 75.1596 | 75.214 | 75.2684 | 75.3229 | 75.3773 | 75.4318 | 75.4862 | 75.5407 | 75.5951 | 75.6496 | 75.704 | 75.7584 | 75.8129 | 75.8673 | 75.9218 | 75.9762 | 76.0307 | 76.0851 | 76.1396 | 76.194 | 76.194 | 76.194 | 76.194 | 76.194 | 76.194 | 76.194 | 76.194 | 76.194 | 76.194 | 76.194 | 76.194 | 76.194 | 76.194 | 76.194 | 76.194 | 76.194 | 76.194 | 76.194 | 76.194 | 76.194 | 76.194 | 76.194 | 76.194 | 76.194 | 76.194 | 76.194 | 76.194 | 76.194 | 76.194 | 76.194 | 76.1123 | 76.0307 | 75.949 | 75.8673 | 75.7857 | 75.704 | 75.6223 | 75.5407 | 75.459 | 75.3773 | 75.2957 | 75.214 | 75.1323 | 75.0507 | 74.969 | 74.8873 | 74.8057 | 74.724 | 74.6423 | 74.5607 | 74.479 | 74.3973 | 74.3157 | 74.234 | 74.1523 | 74.0707 | 73.989 | 73.9073 | 73.8257 | 73.744
8.95 | 0 | 2.545 | 5.09 | 7.635 | 10.18 | 12.725 | 15.27 | 17.815 | 20.36 | 22.905 | 25.45 | 28.8116 | 32.1732 | 35.5348 | 38.8964 | 42.258 | 42.8034 | 43.3488 | 43.8942 | 44.4396 | 44.985 | 45.9121 | 46.8392 | 47.7663 | 48.6934 | 49.6205 | 50.5476 | 51.4747 | 52.4018 | 53.3289 | 54.256 | 54.8722 | 55.4884 | 56.1046 | 56.7208 | 57.337 | 57.9532 | 58.5694 | 59.1856 | 59.8018 | 60.418 | 61.0342 | 61.6504 | 62.2666 | 62.8828 | 63.499 | 64.0015 | 64.5039 | 65.0064 | 65.5089 | 66.0113 | 66.5138 | 67.0163 | 67.5187 | 68.0212 | 68.5237 | 69.0261 | 69.5286 | 70.0311 | 70.5335 | 71.036 | 71.1754 | 71.3147 | 71.4541 | 71.5935 | 71.7328 | 71.8722 | 72.0116 | 72.1509 | 72.2903 | 72.4297 | 72.569 | 72.7084 | 72.8478 | 72.9871 | 73.1265 | 73.2659 | 73.4052 | 73.5446 | 73.684 | 73.8233 | 73.9627 | 74.1021 | 74.2414 | 74.3808 | 74.5202 | 74.6595 | 74.7989 | 74.9383 | 75.0776 | 75.217 | 75.272 | 75.327 | 75.382 | 75.437 | 75.492 | 75.547 | 75.602 | 75.657 | 75.712 | 75.767 | 75.822 | 75.877 | 75.932 | 75.987 | 76.042 | 76.097 | 76.152 | 76.207 | 76.262 | 76.317 | 76.372 | 76.427 | 76.482 | 76.537 | 76.592 | 76.647 | 76.702 | 76.757 | 76.812 | 76.867 | 76.867 | 76.867 | 76.867 | 76.867 | 76.867 | 76.867 | 76.867 | 76.867 | 76.867 | 76.867 | 76.867 | 76.867 | 76.867 | 76.867 | 76.867 | 76.867 | 76.867 | 76.867 | 76.867 | 76.867 | 76.867 | 76.867 | 76.867 | 76.867 | 76.867 | 76.867 | 76.867 | 76.867 | 76.867 | 76.867 | 76.7845 | 76.702 | 76.6195 | 76.537 | 76.4545 | 76.372 | 76.2895 | 76.207 | 76.1245 | 76.042 | 75.9595 | 75.877 | 75.7945 | 75.712 | 75.6295 | 75.547 | 75.4645 | 75.382 | 75.2995 | 75.217 | 75.1345 | 75.052 | 74.9695 | 74.887 | 74.8045 | 74.722 | 74.6395 | 74.557 | 74.4745 | 74.392
9 | 0 | 2.5667 | 5.1333 | 7.7 | 10.2667 | 12.8333 | 15.4 | 17.9667 | 20.5333 | 23.1 | 25.6667 | 29.0587 | 32.4507 | 35.8427 | 39.2347 | 42.6267 | 43.1747 | 43.7227 | 44.2707 | 44.8187 | 45.3667 | 46.302 | 47.2373 | 48.1727 | 49.108 | 50.0433 | 50.9787 | 51.914 | 52.8493 | 53.7847 | 54.72 | 55.3418 | 55.9636 | 56.5853 | 57.2071 | 57.8289 | 58.4507 | 59.0724 | 59.6942 | 60.316 | 60.9378 | 61.5596 | 62.1813 | 62.8031 | 63.4249 | 64.0467 | 64.5538 | 65.0609 | 65.568 | 66.0751 | 66.5822 | 67.0893 | 67.5964 | 68.1036 | 68.6107 | 69.1178 | 69.6249 | 70.132 | 70.6391 | 71.1462 | 71.6533 | 71.794 | 71.9347 | 72.0753 | 72.216 | 72.3567 | 72.4973 | 72.638 | 72.7787 | 72.9193 | 73.06 | 73.2007 | 73.3413 | 73.482 | 73.6227 | 73.7633 | 73.904 | 74.0447 | 74.1853 | 74.326 | 74.4667 | 74.6073 | 74.748 | 74.8887 | 75.0293 | 75.17 | 75.3107 | 75.4513 | 75.592 | 75.7327 | 75.8733 | 75.9289 | 75.9844 | 76.04 | 76.0956 | 76.1511 | 76.2067 | 76.2622 | 76.3178 | 76.3733 | 76.4289 | 76.4844 | 76.54 | 76.5956 | 76.6511 | 76.7067 | 76.7622 | 76.8178 | 76.8733 | 76.9289 | 76.9844 | 77.04 | 77.0956 | 77.1511 | 77.2067 | 77.2622 | 77.3178 | 77.3733 | 77.4289 | 77.4844 | 77.54 | 77.54 | 77.54 | 77.54 | 77.54 | 77.54 | 77.54 | 77.54 | 77.54 | 77.54 | 77.54 | 77.54 | 77.54 | 77.54 | 77.54 | 77.54 | 77.54 | 77.54 | 77.54 | 77.54 | 77.54 | 77.54 | 77.54 | 77.54 | 77.54 | 77.54 | 77.54 | 77.54 | 77.54 | 77.54 | 77.54 | 77.4567 | 77.3733 | 77.29 | 77.2067 | 77.1233 | 77.04 | 76.9567 | 76.8733 | 76.79 | 76.7067 | 76.6233 | 76.54 | 76.4567 | 76.3733 | 76.29 | 76.2067 | 76.1233 | 76.04 | 75.9567 | 75.8733 | 75.79 | 75.7067 | 75.6233 | 75.54 | 75.4567 | 75.3733 | 75.29 | 75.2067 | 75.1233 | 75.04
9.05 | 0 | 2.5883 | 5.1767 | 7.765 | 10.3533 | 12.9417 | 15.53 | 18.1183 | 20.7067 | 23.295 | 25.8833 | 29.3057 | 32.7281 | 36.1505 | 39.5729 | 42.9953 | 43.5459 | 44.0965 | 44.6471 | 45.1977 | 45.7483 | 46.6919 | 47.6355 | 48.579 | 49.5226 | 50.4662 | 51.4097 | 52.3533 | 53.2969 | 54.2404 | 55.184 | 55.8114 | 56.4387 | 57.0661 | 57.6934 | 58.3208 | 58.9481 | 59.5755 | 60.2028 | 60.8302 | 61.4576 | 62.0849 | 62.7123 | 63.3396 | 63.967 | 64.5943 | 65.1061 | 65.6178 | 66.1296 | 66.6414 | 67.1531 | 67.6649 | 68.1766 | 68.6884 | 69.2001 | 69.7119 | 70.2236 | 70.7354 | 71.2472 | 71.7589 | 72.2707 | 72.4126 | 72.5546 | 72.6966 | 72.8385 | 72.9805 | 73.1225 | 73.2644 | 73.4064 | 73.5484 | 73.6903 | 73.8323 | 73.9743 | 74.1162 | 74.2582 | 74.4002 | 74.5421 | 74.6841 | 74.8261 | 74.968 | 75.11 | 75.252 | 75.3939 | 75.5359 | 75.6779 | 75.8198 | 75.9618 | 76.1038 | 76.2457 | 76.3877 | 76.5297 | 76.5858 | 76.6419 | 76.698 | 76.7541 | 76.8102 | 76.8663 | 76.9224 | 76.9786 | 77.0347 | 77.0908 | 77.1469 | 77.203 | 77.2591 | 77.3152 | 77.3713 | 77.4274 | 77.4836 | 77.5397 | 77.5958 | 77.6519 | 77.708 | 77.7641 | 77.8202 | 77.8763 | 77.9324 | 77.9886 | 78.0447 | 78.1008 | 78.1569 | 78.213 | 78.213 | 78.213 | 78.213 | 78.213 | 78.213 | 78.213 | 78.213 | 78.213 | 78.213 | 78.213 | 78.213 | 78.213 | 78.213 | 78.213 | 78.213 | 78.213 | 78.213 | 78.213 | 78.213 | 78.213 | 78.213 | 78.213 | 78.213 | 78.213 | 78.213 | 78.213 | 78.213 | 78.213 | 78.213 | 78.213 | 78.1288 | 78.0447 | 77.9605 | 77.8763 | 77.7922 | 77.708 | 77.6238 | 77.5397 | 77.4555 | 77.3713 | 77.2872 | 77.203 | 77.1188 | 77.0347 | 76.9505 | 76.8663 | 76.7822 | 76.698 | 76.6138 | 76.5297 | 76.4455 | 76.3613 | 76.2772 | 76.193 | 76.1088 | 76.0247 | 75.9405 | 75.8563 | 75.7722 | 75.688
9.1 | 0 | 2.61 | 5.22 | 7.83 | 10.44 | 13.05 | 15.66 | 18.27 | 20.88 | 23.49 | 26.1 | 29.5528 | 33.0056 | 36.4584 | 39.9112 | 43.364 | 43.9172 | 44.4704 | 45.0236 | 45.5768 | 46.13 | 47.0818 | 48.0336 | 48.9854 | 49.9372 | 50.889 | 51.8408 | 52.7926 | 53.7444 | 54.6962 | 55.648 | 56.2809 | 56.9139 | 57.5468 | 58.1797 | 58.8127 | 59.4456 | 60.0785 | 60.7115 | 61.3444 | 61.9773 | 62.6103 | 63.2432 | 63.8761 | 64.5091 | 65.142 | 65.6584 | 66.1748 | 66.6912 | 67.2076 | 67.724 | 68.2404 | 68.7568 | 69.2732 | 69.7896 | 70.306 | 70.8224 | 71.3388 | 71.8552 | 72.3716 | 72.888 | 73.0313 | 73.1745 | 73.3178 | 73.4611 | 73.6043 | 73.7476 | 73.8909 | 74.0341 | 74.1774 | 74.3207 | 74.4639 | 74.6072 | 74.7505 | 74.8937 | 75.037 | 75.1803 | 75.3235 | 75.4668 | 75.6101 | 75.7533 | 75.8966 | 76.0399 | 76.1831 | 76.3264 | 76.4697 | 76.6129 | 76.7562 | 76.8995 | 77.0427 | 77.186 | 77.2427 | 77.2993 | 77.356 | 77.4127 | 77.4693 | 77.526 | 77.5827 | 77.6393 | 77.696 | 77.7527 | 77.8093 | 77.866 | 77.9227 | 77.9793 | 78.036 | 78.0927 | 78.1493 | 78.206 | 78.2627 | 78.3193 | 78.376 | 78.4327 | 78.4893 | 78.546 | 78.6027 | 78.6593 | 78.716 | 78.7727 | 78.8293 | 78.886 | 78.886 | 78.886 | 78.886 | 78.886 | 78.886 | 78.886 | 78.886 | 78.886 | 78.886 | 78.886 | 78.886 | 78.886 | 78.886 | 78.886 | 78.886 | 78.886 | 78.886 | 78.886 | 78.886 | 78.886 | 78.886 | 78.886 | 78.886 | 78.886 | 78.886 | 78.886 | 78.886 | 78.886 | 78.886 | 78.886 | 78.801 | 78.716 | 78.631 | 78.546 | 78.461 | 78.376 | 78.291 | 78.206 | 78.121 | 78.036 | 77.951 | 77.866 | 77.781 | 77.696 | 77.611 | 77.526 | 77.441 | 77.356 | 77.271 | 77.186 | 77.101 | 77.016 | 76.931 | 76.846 | 76.761 | 76.676 | 76.591 | 76.506 | 76.421 | 76.336
9.15 | 0 | 2.6317 | 5.2633 | 7.895 | 10.5267 | 13.1583 | 15.79 | 18.4217 | 21.0533 | 23.685 | 26.3167 | 29.7999 | 33.2831 | 36.7663 | 40.2495 | 43.7327 | 44.2885 | 44.8443 | 45.4001 | 45.9559 | 46.5117 | 47.4717 | 48.4317 | 49.3918 | 50.3518 | 51.3118 | 52.2719 | 53.2319 | 54.1919 | 55.152 | 56.112 | 56.7505 | 57.389 | 58.0275 | 58.666 | 59.3046 | 59.9431 | 60.5816 | 61.2201 | 61.8586 | 62.4971 | 63.1356 | 63.7741 | 64.4126 | 65.0512 | 65.6897 | 66.2107 | 66.7318 | 67.2528 | 67.7738 | 68.2949 | 68.8159 | 69.337 | 69.858 | 70.3791 | 70.9001 | 71.4212 | 71.9422 | 72.4632 | 72.9843 | 73.5053 | 73.6499 | 73.7945 | 73.939 | 74.0836 | 74.2282 | 74.3727 | 74.5173 | 74.6619 | 74.8064 | 74.951 | 75.0956 | 75.2401 | 75.3847 | 75.5293 | 75.6738 | 75.8184 | 75.963 | 76.1075 | 76.2521 | 76.3967 | 76.5412 | 76.6858 | 76.8304 | 76.9749 | 77.1195 | 77.2641 | 77.4086 | 77.5532 | 77.6978 | 77.8423 | 77.8996 | 77.9568 | 78.014 | 78.0712 | 78.1284 | 78.1857 | 78.2429 | 78.3001 | 78.3573 | 78.4146 | 78.4718 | 78.529 | 78.5862 | 78.6434 | 78.7007 | 78.7579 | 78.8151 | 78.8723 | 78.9296 | 78.9868 | 79.044 | 79.1012 | 79.1584 | 79.2157 | 79.2729 | 79.3301 | 79.3873 | 79.4446 | 79.5018 | 79.559 | 79.559 | 79.559 | 79.559 | 79.559 | 79.559 | 79.559 | 79.559 | 79.559 | 79.559 | 79.559 | 79.559 | 79.559 | 79.559 | 79.559 | 79.559 | 79.559 | 79.559 | 79.559 | 79.559 | 79.559 | 79.559 | 79.559 | 79.559 | 79.559 | 79.559 | 79.559 | 79.559 | 79.559 | 79.559 | 79.559 | 79.4732 | 79.3873 | 79.3015 | 79.2157 | 79.1298 | 79.044 | 78.9582 | 78.8723 | 78.7865 | 78.7007 | 78.6148 | 78.529 | 78.4432 | 78.3573 | 78.2715 | 78.1857 | 78.0998 | 78.014 | 77.9282 | 77.8423 | 77.7565 | 77.6707 | 77.5848 | 77.499 | 77.4132 | 77.3273 | 77.2415 | 77.1557 | 77.0698 | 76.984
9.2 | 0 | 2.6533 | 5.3067 | 7.96 | 10.6133 | 13.2667 | 15.92 | 18.5733 | 21.2267 | 23.88 | 26.5333 | 30.0469 | 33.5605 | 37.0741 | 40.5877 | 44.1013 | 44.6597 | 45.2181 | 45.7765 | 46.3349 | 46.8933 | 47.8616 | 48.8299 | 49.7981 | 50.7664 | 51.7347 | 52.7029 | 53.6712 | 54.6395 | 55.6077 | 56.576 | 57.2201 | 57.8642 | 58.5083 | 59.1524 | 59.7964 | 60.4405 | 61.0846 | 61.7287 | 62.3728 | 63.0169 | 63.661 | 64.3051 | 64.9492 | 65.5932 | 66.2373 | 66.763 | 67.2887 | 67.8144 | 68.3401 | 68.8658 | 69.3915 | 69.9172 | 70.4428 | 70.9685 | 71.4942 | 72.0199 | 72.5456 | 73.0713 | 73.597 | 74.1227 | 74.2685 | 74.4144 | 74.5603 | 74.7061 | 74.852 | 74.9979 | 75.1437 | 75.2896 | 75.4355 | 75.5813 | 75.7272 | 75.8731 | 76.0189 | 76.1648 | 76.3107 | 76.4565 | 76.6024 | 76.7483 | 76.8941 | 77.04 | 77.1859 | 77.3317 | 77.4776 | 77.6235 | 77.7693 | 77.9152 | 78.0611 | 78.2069 | 78.3528 | 78.4987 | 78.5564 | 78.6142 | 78.672 | 78.7298 | 78.7876 | 78.8453 | 78.9031 | 78.9609 | 79.0187 | 79.0764 | 79.1342 | 79.192 | 79.2498 | 79.3076 | 79.3653 | 79.4231 | 79.4809 | 79.5387 | 79.5964 | 79.6542 | 79.712 | 79.7698 | 79.8276 | 79.8853 | 79.9431 | 80.0009 | 80.0587 | 80.1164 | 80.1742 | 80.232 | 80.232 | 80.232 | 80.232 | 80.232 | 80.232 | 80.232 | 80.232 | 80.232 | 80.232 | 80.232 | 80.232 | 80.232 | 80.232 | 80.232 | 80.232 | 80.232 | 80.232 | 80.232 | 80.232 | 80.232 | 80.232 | 80.232 | 80.232 | 80.232 | 80.232 | 80.232 | 80.232 | 80.232 | 80.232 | 80.232 | 80.1453 | 80.0587 | 79.972 | 79.8853 | 79.7987 | 79.712 | 79.6253 | 79.5387 | 79.452 | 79.3653 | 79.2787 | 79.192 | 79.1053 | 79.0187 | 78.932 | 78.8453 | 78.7587 | 78.672 | 78.5853 | 78.4987 | 78.412 | 78.3253 | 78.2387 | 78.152 | 78.0653 | 77.9787 | 77.892 | 77.8053 | 77.7187 | 77.632
9.25 | 0 | 2.675 | 5.35 | 8.025 | 10.7 | 13.375 | 16.05 | 18.725 | 21.4 | 24.075 | 26.75 | 30.294 | 33.838 | 37.382 | 40.926 | 44.47 | 45.031 | 45.592 | 46.153 | 46.714 | 47.275 | 48.2515 | 49.228 | 50.2045 | 51.181 | 52.1575 | 53.134 | 54.1105 | 55.087 | 56.0635 | 57.04 | 57.6897 | 58.3393 | 58.989 | 59.6387 | 60.2883 | 60.938 | 61.5877 | 62.2373 | 62.887 | 63.5367 | 64.1863 | 64.836 | 65.4857 | 66.1353 | 66.785 | 67.3153 | 67.8457 | 68.376 | 68.9063 | 69.4367 | 69.967 | 70.4973 | 71.0277 | 71.558 | 72.0883 | 72.6187 | 73.149 | 73.6793 | 74.2097 | 74.74 | 74.8872 | 75.0343 | 75.1815 | 75.3287 | 75.4758 | 75.623 | 75.7702 | 75.9173 | 76.0645 | 76.2117 | 76.3588 | 76.506 | 76.6532 | 76.8003 | 76.9475 | 77.0947 | 77.2418 | 77.389 | 77.5362 | 77.6833 | 77.8305 | 77.9777 | 78.1248 | 78.272 | 78.4192 | 78.5663 | 78.7135 | 78.8607 | 79.0078 | 79.155 | 79.2133 | 79.2717 | 79.33 | 79.3883 | 79.4467 | 79.505 | 79.5633 | 79.6217 | 79.68 | 79.7383 | 79.7967 | 79.855 | 79.9133 | 79.9717 | 80.03 | 80.0883 | 80.1467 | 80.205 | 80.2633 | 80.3217 | 80.38 | 80.4383 | 80.4967 | 80.555 | 80.6133 | 80.6717 | 80.73 | 80.7883 | 80.8467 | 80.905 | 80.905 | 80.905 | 80.905 | 80.905 | 80.905 | 80.905 | 80.905 | 80.905 | 80.905 | 80.905 | 80.905 | 80.905 | 80.905 | 80.905 | 80.905 | 80.905 | 80.905 | 80.905 | 80.905 | 80.905 | 80.905 | 80.905 | 80.905 | 80.905 | 80.905 | 80.905 | 80.905 | 80.905 | 80.905 | 80.905 | 80.8175 | 80.73 | 80.6425 | 80.555 | 80.4675 | 80.38 | 80.2925 | 80.205 | 80.1175 | 80.03 | 79.9425 | 79.855 | 79.7675 | 79.68 | 79.5925 | 79.505 | 79.4175 | 79.33 | 79.2425 | 79.155 | 79.0675 | 78.98 | 78.8925 | 78.805 | 78.7175 | 78.63 | 78.5425 | 78.455 | 78.3675 | 78.28
9.3 | 0 | 2.6967 | 5.3933 | 8.09 | 10.7867 | 13.4833 | 16.18 | 18.8767 | 21.5733 | 24.27 | 26.9667 | 30.5411 | 34.1155 | 37.6899 | 41.2643 | 44.8387 | 45.4023 | 45.9659 | 46.5295 | 47.0931 | 47.6567 | 48.6414 | 49.6261 | 50.6109 | 51.5956 | 52.5803 | 53.5651 | 54.5498 | 55.5345 | 56.5193 | 57.504 | 58.1592 | 58.8145 | 59.4697 | 60.125 | 60.7802 | 61.4355 | 62.0907 | 62.746 | 63.4012 | 64.0564 | 64.7117 | 65.3669 | 66.0222 | 66.6774 | 67.3327 | 67.8676 | 68.4026 | 68.9376 | 69.4726 | 70.0076 | 70.5425 | 71.0775 | 71.6125 | 72.1475 | 72.6824 | 73.2174 | 73.7524 | 74.2874 | 74.8224 | 75.3573 | 75.5058 | 75.6543 | 75.8027 | 75.9512 | 76.0997 | 76.2481 | 76.3966 | 76.5451 | 76.6935 | 76.842 | 76.9905 | 77.1389 | 77.2874 | 77.4359 | 77.5843 | 77.7328 | 77.8813 | 78.0297 | 78.1782 | 78.3267 | 78.4751 | 78.6236 | 78.7721 | 78.9205 | 79.069 | 79.2175 | 79.3659 | 79.5144 | 79.6629 | 79.8113 | 79.8702 | 79.9291 | 79.988 | 80.0469 | 80.1058 | 80.1647 | 80.2236 | 80.2824 | 80.3413 | 80.4002 | 80.4591 | 80.518 | 80.5769 | 80.6358 | 80.6947 | 80.7536 | 80.8124 | 80.8713 | 80.9302 | 80.9891 | 81.048 | 81.1069 | 81.1658 | 81.2247 | 81.2836 | 81.3424 | 81.4013 | 81.4602 | 81.5191 | 81.578 | 81.578 | 81.578 | 81.578 | 81.578 | 81.578 | 81.578 | 81.578 | 81.578 | 81.578 | 81.578 | 81.578 | 81.578 | 81.578 | 81.578 | 81.578 | 81.578 | 81.578 | 81.578 | 81.578 | 81.578 | 81.578 | 81.578 | 81.578 | 81.578 | 81.578 | 81.578 | 81.578 | 81.578 | 81.578 | 81.578 | 81.4897 | 81.4013 | 81.313 | 81.2247 | 81.1363 | 81.048 | 80.9597 | 80.8713 | 80.783 | 80.6947 | 80.6063 | 80.518 | 80.4297 | 80.3413 | 80.253 | 80.1647 | 80.0763 | 79.988 | 79.8997 | 79.8113 | 79.723 | 79.6347 | 79.5463 | 79.458 | 79.3697 | 79.2813 | 79.193 | 79.1047 | 79.0163 | 78.928
9.35 | 0 | 2.7183 | 5.4367 | 8.155 | 10.8733 | 13.5917 | 16.31 | 19.0283 | 21.7467 | 24.465 | 27.1833 | 30.7881 | 34.3929 | 37.9977 | 41.6025 | 45.2073 | 45.7735 | 46.3397 | 46.9059 | 47.4721 | 48.0383 | 49.0313 | 50.0243 | 51.0172 | 52.0102 | 53.0032 | 53.9961 | 54.9891 | 55.9821 | 56.975 | 57.968 | 58.6288 | 59.2896 | 59.9505 | 60.6113 | 61.2721 | 61.9329 | 62.5938 | 63.2546 | 63.9154 | 64.5762 | 65.237 | 65.8979 | 66.5587 | 67.2195 | 67.8803 | 68.42 | 68.9596 | 69.4992 | 70.0388 | 70.5784 | 71.1181 | 71.6577 | 72.1973 | 72.7369 | 73.2766 | 73.8162 | 74.3558 | 74.8954 | 75.435 | 75.9747 | 76.1244 | 76.2742 | 76.424 | 76.5737 | 76.7235 | 76.8733 | 77.023 | 77.1728 | 77.3226 | 77.4723 | 77.6221 | 77.7719 | 77.9216 | 78.0714 | 78.2212 | 78.3709 | 78.5207 | 78.6705 | 78.8202 | 78.97 | 79.1198 | 79.2695 | 79.4193 | 79.5691 | 79.7188 | 79.8686 | 80.0184 | 80.1681 | 80.3179 | 80.4677 | 80.5271 | 80.5866 | 80.646 | 80.7054 | 80.7649 | 80.8243 | 80.8838 | 80.9432 | 81.0027 | 81.0621 | 81.1216 | 81.181 | 81.2404 | 81.2999 | 81.3593 | 81.4188 | 81.4782 | 81.5377 | 81.5971 | 81.6566 | 81.716 | 81.7754 | 81.8349 | 81.8943 | 81.9538 | 82.0132 | 82.0727 | 82.1321 | 82.1916 | 82.251 | 82.251 | 82.251 | 82.251 | 82.251 | 82.251 | 82.251 | 82.251 | 82.251 | 82.251 | 82.251 | 82.251 | 82.251 | 82.251 | 82.251 | 82.251 | 82.251 | 82.251 | 82.251 | 82.251 | 82.251 | 82.251 | 82.251 | 82.251 | 82.251 | 82.251 | 82.251 | 82.251 | 82.251 | 82.251 | 82.251 | 82.1618 | 82.0727 | 81.9835 | 81.8943 | 81.8052 | 81.716 | 81.6268 | 81.5377 | 81.4485 | 81.3593 | 81.2702 | 81.181 | 81.0918 | 81.0027 | 80.9135 | 80.8243 | 80.7352 | 80.646 | 80.5568 | 80.4677 | 80.3785 | 80.2893 | 80.2002 | 80.111 | 80.0218 | 79.9327 | 79.8435 | 79.7543 | 79.6652 | 79.576
9.4 | 0 | 2.74 | 5.48 | 8.22 | 10.96 | 13.7 | 16.44 | 19.18 | 21.92 | 24.66 | 27.4 | 31.0352 | 34.6704 | 38.3056 | 41.9408 | 45.576 | 46.1448 | 46.7136 | 47.2824 | 47.8512 | 48.42 | 49.4212 | 50.4224 | 51.4236 | 52.4248 | 53.426 | 54.4272 | 55.4284 | 56.4296 | 57.4308 | 58.432 | 59.0984 | 59.7648 | 60.4312 | 61.0976 | 61.764 | 62.4304 | 63.0968 | 63.7632 | 64.4296 | 65.096 | 65.7624 | 66.4288 | 67.0952 | 67.7616 | 68.428 | 68.9723 | 69.5165 | 70.0608 | 70.6051 | 71.1493 | 71.6936 | 72.2379 | 72.7821 | 73.3264 | 73.8707 | 74.4149 | 74.9592 | 75.5035 | 76.0477 | 76.592 | 76.7431 | 76.8941 | 77.0452 | 77.1963 | 77.3473 | 77.4984 | 77.6495 | 77.8005 | 77.9516 | 78.1027 | 78.2537 | 78.4048 | 78.5559 | 78.7069 | 78.858 | 79.0091 | 79.1601 | 79.3112 | 79.4623 | 79.6133 | 79.7644 | 79.9155 | 80.0665 | 80.2176 | 80.3687 | 80.5197 | 80.6708 | 80.8219 | 80.9729 | 81.124 | 81.184 | 81.244 | 81.304 | 81.364 | 81.424 | 81.484 | 81.544 | 81.604 | 81.664 | 81.724 | 81.784 | 81.844 | 81.904 | 81.964 | 82.024 | 82.084 | 82.144 | 82.204 | 82.264 | 82.324 | 82.384 | 82.444 | 82.504 | 82.564 | 82.624 | 82.684 | 82.744 | 82.804 | 82.864 | 82.924 | 82.924 | 82.924 | 82.924 | 82.924 | 82.924 | 82.924 | 82.924 | 82.924 | 82.924 | 82.924 | 82.924 | 82.924 | 82.924 | 82.924 | 82.924 | 82.924 | 82.924 | 82.924 | 82.924 | 82.924 | 82.924 | 82.924 | 82.924 | 82.924 | 82.924 | 82.924 | 82.924 | 82.924 | 82.924 | 82.924 | 82.834 | 82.744 | 82.654 | 82.564 | 82.474 | 82.384 | 82.294 | 82.204 | 82.114 | 82.024 | 81.934 | 81.844 | 81.754 | 81.664 | 81.574 | 81.484 | 81.394 | 81.304 | 81.214 | 81.124 | 81.034 | 80.944 | 80.854 | 80.764 | 80.674 | 80.584 | 80.494 | 80.404 | 80.314 | 80.224
9.45 | 0 | 2.7617 | 5.5233 | 8.285 | 11.0467 | 13.8083 | 16.57 | 19.3317 | 22.0933 | 24.855 | 27.6167 | 31.2823 | 34.9479 | 38.6135 | 42.2791 | 45.9447 | 46.5161 | 47.0875 | 47.6589 | 48.2303 | 48.8017 | 49.8111 | 50.8205 | 51.83 | 52.8394 | 53.8488 | 54.8583 | 55.8677 | 56.8771 | 57.8866 | 58.896 | 59.568 | 60.24 | 60.9119 | 61.5839 | 62.2559 | 62.9279 | 63.5998 | 64.2718 | 64.9438 | 65.6158 | 66.2878 | 66.9597 | 67.6317 | 68.3037 | 68.9757 | 69.5246 | 70.0735 | 70.6224 | 71.1713 | 71.7202 | 72.2691 | 72.818 | 73.367 | 73.9159 | 74.4648 | 75.0137 | 75.5626 | 76.1115 | 76.6604 | 77.2093 | 77.3617 | 77.5141 | 77.6664 | 77.8188 | 77.9712 | 78.1235 | 78.2759 | 78.4283 | 78.5806 | 78.733 | 78.8854 | 79.0377 | 79.1901 | 79.3425 | 79.4948 | 79.6472 | 79.7996 | 79.9519 | 80.1043 | 80.2567 | 80.409 | 80.5614 | 80.7138 | 80.8661 | 81.0185 | 81.1709 | 81.3232 | 81.4756 | 81.628 | 81.7803 | 81.8409 | 81.9014 | 81.962 | 82.0226 | 82.0831 | 82.1437 | 82.2042 | 82.2648 | 82.3253 | 82.3859 | 82.4464 | 82.507 | 82.5676 | 82.6281 | 82.6887 | 82.7492 | 82.8098 | 82.8703 | 82.9309 | 82.9914 | 83.052 | 83.1126 | 83.1731 | 83.2337 | 83.2942 | 83.3548 | 83.4153 | 83.4759 | 83.5364 | 83.597 | 83.597 | 83.597 | 83.597 | 83.597 | 83.597 | 83.597 | 83.597 | 83.597 | 83.597 | 83.597 | 83.597 | 83.597 | 83.597 | 83.597 | 83.597 | 83.597 | 83.597 | 83.597 | 83.597 | 83.597 | 83.597 | 83.597 | 83.597 | 83.597 | 83.597 | 83.597 | 83.597 | 83.597 | 83.597 | 83.597 | 83.5062 | 83.4153 | 83.3245 | 83.2337 | 83.1428 | 83.052 | 82.9612 | 82.8703 | 82.7795 | 82.6887 | 82.5978 | 82.507 | 82.4162 | 82.3253 | 82.2345 | 82.1437 | 82.0528 | 81.962 | 81.8712 | 81.7803 | 81.6895 | 81.5987 | 81.5078 | 81.417 | 81.3262 | 81.2353 | 81.1445 | 81.0537 | 80.9628 | 80.872
9.5 | 0 | 2.7833 | 5.5667 | 8.35 | 11.1333 | 13.9167 | 16.7 | 19.4833 | 22.2667 | 25.05 | 27.8333 | 31.5293 | 35.2253 | 38.9213 | 42.6173 | 46.3133 | 46.8873 | 47.4613 | 48.0353 | 48.6093 | 49.1833 | 50.201 | 51.2187 | 52.2363 | 53.254 | 54.2717 | 55.2893 | 56.307 | 57.3247 | 58.3423 | 59.36 | 60.0376 | 60.7151 | 61.3927 | 62.0702 | 62.7478 | 63.4253 | 64.1029 | 64.7804 | 65.458 | 66.1356 | 66.8131 | 67.4907 | 68.1682 | 68.8458 | 69.5233 | 70.0769 | 70.6304 | 71.184 | 71.7376 | 72.2911 | 72.8447 | 73.3982 | 73.9518 | 74.5053 | 75.0589 | 75.6124 | 76.166 | 76.7196 | 77.2731 | 77.8267 | 77.9803 | 78.134 | 78.2877 | 78.4413 | 78.595 | 78.7487 | 78.9023 | 79.056 | 79.2097 | 79.3633 | 79.517 | 79.6707 | 79.8243 | 79.978 | 80.1317 | 80.2853 | 80.439 | 80.5927 | 80.7463 | 80.9 | 81.0537 | 81.2073 | 81.361 | 81.5147 | 81.6683 | 81.822 | 81.9757 | 82.1293 | 82.283 | 82.4367 | 82.4978 | 82.5589 | 82.62 | 82.6811 | 82.7422 | 82.8033 | 82.8644 | 82.9256 | 82.9867 | 83.0478 | 83.1089 | 83.17 | 83.2311 | 83.2922 | 83.3533 | 83.4144 | 83.4756 | 83.5367 | 83.5978 | 83.6589 | 83.72 | 83.7811 | 83.8422 | 83.9033 | 83.9644 | 84.0256 | 84.0867 | 84.1478 | 84.2089 | 84.27 | 84.27 | 84.27 | 84.27 | 84.27 | 84.27 | 84.27 | 84.27 | 84.27 | 84.27 | 84.27 | 84.27 | 84.27 | 84.27 | 84.27 | 84.27 | 84.27 | 84.27 | 84.27 | 84.27 | 84.27 | 84.27 | 84.27 | 84.27 | 84.27 | 84.27 | 84.27 | 84.27 | 84.27 | 84.27 | 84.27 | 84.1783 | 84.0867 | 83.995 | 83.9033 | 83.8117 | 83.72 | 83.6283 | 83.5367 | 83.445 | 83.3533 | 83.2617 | 83.17 | 83.0783 | 82.9867 | 82.895 | 82.8033 | 82.7117 | 82.62 | 82.5283 | 82.4367 | 82.345 | 82.2533 | 82.1617 | 82.07 | 81.9783 | 81.8867 | 81.795 | 81.7033 | 81.6117 | 81.52
9.55 | 0 | 2.805 | 5.61 | 8.415 | 11.22 | 14.025 | 16.83 | 19.635 | 22.44 | 25.245 | 28.05 | 31.7764 | 35.5028 | 39.2292 | 42.9556 | 46.682 | 47.2586 | 47.8352 | 48.4118 | 48.9884 | 49.565 | 50.5909 | 51.6168 | 52.6427 | 53.6686 | 54.6945 | 55.7204 | 56.7463 | 57.7722 | 58.7981 | 59.824 | 60.5071 | 61.1903 | 61.8734 | 62.5565 | 63.2397 | 63.9228 | 64.6059 | 65.2891 | 65.9722 | 66.6553 | 67.3385 | 68.0216 | 68.7047 | 69.3879 | 70.071 | 70.6292 | 71.1874 | 71.7456 | 72.3038 | 72.862 | 73.4202 | 73.9784 | 74.5366 | 75.0948 | 75.653 | 76.2112 | 76.7694 | 77.3276 | 77.8858 | 78.444 | 78.599 | 78.7539 | 78.9089 | 79.0639 | 79.2188 | 79.3738 | 79.5288 | 79.6837 | 79.8387 | 79.9937 | 80.1486 | 80.3036 | 80.4586 | 80.6135 | 80.7685 | 80.9235 | 81.0784 | 81.2334 | 81.3884 | 81.5433 | 81.6983 | 81.8533 | 82.0082 | 82.1632 | 82.3182 | 82.4731 | 82.6281 | 82.7831 | 82.938 | 83.093 | 83.1547 | 83.2163 | 83.278 | 83.3397 | 83.4013 | 83.463 | 83.5247 | 83.5863 | 83.648 | 83.7097 | 83.7713 | 83.833 | 83.8947 | 83.9563 | 84.018 | 84.0797 | 84.1413 | 84.203 | 84.2647 | 84.3263 | 84.388 | 84.4497 | 84.5113 | 84.573 | 84.6347 | 84.6963 | 84.758 | 84.8197 | 84.8813 | 84.943 | 84.943 | 84.943 | 84.943 | 84.943 | 84.943 | 84.943 | 84.943 | 84.943 | 84.943 | 84.943 | 84.943 | 84.943 | 84.943 | 84.943 | 84.943 | 84.943 | 84.943 | 84.943 | 84.943 | 84.943 | 84.943 | 84.943 | 84.943 | 84.943 | 84.943 | 84.943 | 84.943 | 84.943 | 84.943 | 84.943 | 84.8505 | 84.758 | 84.6655 | 84.573 | 84.4805 | 84.388 | 84.2955 | 84.203 | 84.1105 | 84.018 | 83.9255 | 83.833 | 83.7405 | 83.648 | 83.5555 | 83.463 | 83.3705 | 83.278 | 83.1855 | 83.093 | 83.0005 | 82.908 | 82.8155 | 82.723 | 82.6305 | 82.538 | 82.4455 | 82.353 | 82.2605 | 82.168
9.6 | 0 | 2.8267 | 5.6533 | 8.48 | 11.3067 | 14.1333 | 16.96 | 19.7867 | 22.6133 | 25.44 | 28.2667 | 32.0235 | 35.7803 | 39.5371 | 43.2939 | 47.0507 | 47.6299 | 48.2091 | 48.7883 | 49.3675 | 49.9467 | 50.9808 | 52.0149 | 53.0491 | 54.0832 | 55.1173 | 56.1515 | 57.1856 | 58.2197 | 59.2539 | 60.288 | 60.9767 | 61.6654 | 62.3541 | 63.0428 | 63.7316 | 64.4203 | 65.109 | 65.7977 | 66.4864 | 67.1751 | 67.8638 | 68.5525 | 69.2412 | 69.93 | 70.6187 | 71.1815 | 71.7444 | 72.3072 | 72.87 | 73.4329 | 73.9957 | 74.5586 | 75.1214 | 75.6843 | 76.2471 | 76.81 | 77.3728 | 77.9356 | 78.4985 | 79.0613 | 79.2176 | 79.3739 | 79.5301 | 79.6864 | 79.8427 | 79.9989 | 80.1552 | 80.3115 | 80.4677 | 80.624 | 80.7803 | 80.9365 | 81.0928 | 81.2491 | 81.4053 | 81.5616 | 81.7179 | 81.8741 | 82.0304 | 82.1867 | 82.3429 | 82.4992 | 82.6555 | 82.8117 | 82.968 | 83.1243 | 83.2805 | 83.4368 | 83.5931 | 83.7493 | 83.8116 | 83.8738 | 83.936 | 83.9982 | 84.0604 | 84.1227 | 84.1849 | 84.2471 | 84.3093 | 84.3716 | 84.4338 | 84.496 | 84.5582 | 84.6204 | 84.6827 | 84.7449 | 84.8071 | 84.8693 | 84.9316 | 84.9938 | 85.056 | 85.1182 | 85.1804 | 85.2427 | 85.3049 | 85.3671 | 85.4293 | 85.4916 | 85.5538 | 85.616 | 85.616 | 85.616 | 85.616 | 85.616 | 85.616 | 85.616 | 85.616 | 85.616 | 85.616 | 85.616 | 85.616 | 85.616 | 85.616 | 85.616 | 85.616 | 85.616 | 85.616 | 85.616 | 85.616 | 85.616 | 85.616 | 85.616 | 85.616 | 85.616 | 85.616 | 85.616 | 85.616 | 85.616 | 85.616 | 85.616 | 85.5227 | 85.4293 | 85.336 | 85.2427 | 85.1493 | 85.056 | 84.9627 | 84.8693 | 84.776 | 84.6827 | 84.5893 | 84.496 | 84.4027 | 84.3093 | 84.216 | 84.1227 | 84.0293 | 83.936 | 83.8427 | 83.7493 | 83.656 | 83.5627 | 83.4693 | 83.376 | 83.2827 | 83.1893 | 83.096 | 83.0027 | 82.9093 | 82.816
9.65 | 0 | 2.8483 | 5.6967 | 8.545 | 11.3933 | 14.2417 | 17.09 | 19.9383 | 22.7867 | 25.635 | 28.4833 | 32.2705 | 36.0577 | 39.8449 | 43.6321 | 47.4193 | 48.0011 | 48.5829 | 49.1647 | 49.7465 | 50.3283 | 51.3707 | 52.4131 | 53.4554 | 54.4978 | 55.5402 | 56.5825 | 57.6249 | 58.6673 | 59.7096 | 60.752 | 61.4463 | 62.1406 | 62.8349 | 63.5292 | 64.2234 | 64.9177 | 65.612 | 66.3063 | 67.0006 | 67.6949 | 68.3892 | 69.0835 | 69.7778 | 70.472 | 71.1663 | 71.7338 | 72.3013 | 72.8688 | 73.4363 | 74.0038 | 74.5713 | 75.1388 | 75.7062 | 76.2737 | 76.8412 | 77.4087 | 77.9762 | 78.5437 | 79.1112 | 79.6787 | 79.8362 | 79.9938 | 80.1514 | 80.3089 | 80.4665 | 80.6241 | 80.7816 | 80.9392 | 81.0968 | 81.2543 | 81.4119 | 81.5695 | 81.727 | 81.8846 | 82.0422 | 82.1997 | 82.3573 | 82.5149 | 82.6724 | 82.83 | 82.9876 | 83.1451 | 83.3027 | 83.4603 | 83.6178 | 83.7754 | 83.933 | 84.0905 | 84.2481 | 84.4057 | 84.4684 | 84.5312 | 84.594 | 84.6568 | 84.7196 | 84.7823 | 84.8451 | 84.9079 | 84.9707 | 85.0334 | 85.0962 | 85.159 | 85.2218 | 85.2846 | 85.3473 | 85.4101 | 85.4729 | 85.5357 | 85.5984 | 85.6612 | 85.724 | 85.7868 | 85.8496 | 85.9123 | 85.9751 | 86.0379 | 86.1007 | 86.1634 | 86.2262 | 86.289 | 86.289 | 86.289 | 86.289 | 86.289 | 86.289 | 86.289 | 86.289 | 86.289 | 86.289 | 86.289 | 86.289 | 86.289 | 86.289 | 86.289 | 86.289 | 86.289 | 86.289 | 86.289 | 86.289 | 86.289 | 86.289 | 86.289 | 86.289 | 86.289 | 86.289 | 86.289 | 86.289 | 86.289 | 86.289 | 86.289 | 86.1948 | 86.1007 | 86.0065 | 85.9123 | 85.8182 | 85.724 | 85.6298 | 85.5357 | 85.4415 | 85.3473 | 85.2532 | 85.159 | 85.0648 | 84.9707 | 84.8765 | 84.7823 | 84.6882 | 84.594 | 84.4998 | 84.4057 | 84.3115 | 84.2173 | 84.1232 | 84.029 | 83.9348 | 83.8407 | 83.7465 | 83.6523 | 83.5582 | 83.464
9.7 | 0 | 2.87 | 5.74 | 8.61 | 11.48 | 14.35 | 17.22 | 20.09 | 22.96 | 25.83 | 28.7 | 32.5176 | 36.3352 | 40.1528 | 43.9704 | 47.788 | 48.3724 | 48.9568 | 49.5412 | 50.1256 | 50.71 | 51.7606 | 52.8112 | 53.8618 | 54.9124 | 55.963 | 57.0136 | 58.0642 | 59.1148 | 60.1654 | 61.216 | 61.9159 | 62.6157 | 63.3156 | 64.0155 | 64.7153 | 65.4152 | 66.1151 | 66.8149 | 67.5148 | 68.2147 | 68.9145 | 69.6144 | 70.3143 | 71.0141 | 71.714 | 72.2861 | 72.8583 | 73.4304 | 74.0025 | 74.5747 | 75.1468 | 75.7189 | 76.2911 | 76.8632 | 77.4353 | 78.0075 | 78.5796 | 79.1517 | 79.7239 | 80.296 | 80.4549 | 80.6137 | 80.7726 | 80.9315 | 81.0903 | 81.2492 | 81.4081 | 81.5669 | 81.7258 | 81.8847 | 82.0435 | 82.2024 | 82.3613 | 82.5201 | 82.679 | 82.8379 | 82.9967 | 83.1556 | 83.3145 | 83.4733 | 83.6322 | 83.7911 | 83.9499 | 84.1088 | 84.2677 | 84.4265 | 84.5854 | 84.7443 | 84.9031 | 85.062 | 85.1253 | 85.1887 | 85.252 | 85.3153 | 85.3787 | 85.442 | 85.5053 | 85.5687 | 85.632 | 85.6953 | 85.7587 | 85.822 | 85.8853 | 85.9487 | 86.012 | 86.0753 | 86.1387 | 86.202 | 86.2653 | 86.3287 | 86.392 | 86.4553 | 86.5187 | 86.582 | 86.6453 | 86.7087 | 86.772 | 86.8353 | 86.8987 | 86.962 | 86.962 | 86.962 | 86.962 | 86.962 | 86.962 | 86.962 | 86.962 | 86.962 | 86.962 | 86.962 | 86.962 | 86.962 | 86.962 | 86.962 | 86.962 | 86.962 | 86.962 | 86.962 | 86.962 | 86.962 | 86.962 | 86.962 | 86.962 | 86.962 | 86.962 | 86.962 | 86.962 | 86.962 | 86.962 | 86.962 | 86.867 | 86.772 | 86.677 | 86.582 | 86.487 | 86.392 | 86.297 | 86.202 | 86.107 | 86.012 | 85.917 | 85.822 | 85.727 | 85.632 | 85.537 | 85.442 | 85.347 | 85.252 | 85.157 | 85.062 | 84.967 | 84.872 | 84.777 | 84.682 | 84.587 | 84.492 | 84.397 | 84.302 | 84.207 | 84.112
9.75 | 0 | 2.8917 | 5.7833 | 8.675 | 11.5667 | 14.4583 | 17.35 | 20.2417 | 23.1333 | 26.025 | 28.9167 | 32.7647 | 36.6127 | 40.4607 | 44.3087 | 48.1567 | 48.7437 | 49.3307 | 49.9177 | 50.5047 | 51.0917 | 52.1505 | 53.2093 | 54.2682 | 55.327 | 56.3858 | 57.4447 | 58.5035 | 59.5623 | 60.6212 | 61.68 | 62.3854 | 63.0909 | 63.7963 | 64.5018 | 65.2072 | 65.9127 | 66.6181 | 67.3236 | 68.029 | 68.7344 | 69.4399 | 70.1453 | 70.8508 | 71.5562 | 72.2617 | 72.8384 | 73.4152 | 73.992 | 74.5688 | 75.1456 | 75.7223 | 76.2991 | 76.8759 | 77.4527 | 78.0294 | 78.6062 | 79.183 | 79.7598 | 80.3366 | 80.9133 | 81.0735 | 81.2337 | 81.3938 | 81.554 | 81.7142 | 81.8743 | 82.0345 | 82.1947 | 82.3548 | 82.515 | 82.6752 | 82.8353 | 82.9955 | 83.1557 | 83.3158 | 83.476 | 83.6362 | 83.7963 | 83.9565 | 84.1167 | 84.2768 | 84.437 | 84.5972 | 84.7573 | 84.9175 | 85.0777 | 85.2378 | 85.398 | 85.5582 | 85.7183 | 85.7822 | 85.8461 | 85.91 | 85.9739 | 86.0378 | 86.1017 | 86.1656 | 86.2294 | 86.2933 | 86.3572 | 86.4211 | 86.485 | 86.5489 | 86.6128 | 86.6767 | 86.7406 | 86.8044 | 86.8683 | 86.9322 | 86.9961 | 87.06 | 87.1239 | 87.1878 | 87.2517 | 87.3156 | 87.3794 | 87.4433 | 87.5072 | 87.5711 | 87.635 | 87.635 | 87.635 | 87.635 | 87.635 | 87.635 | 87.635 | 87.635 | 87.635 | 87.635 | 87.635 | 87.635 | 87.635 | 87.635 | 87.635 | 87.635 | 87.635 | 87.635 | 87.635 | 87.635 | 87.635 | 87.635 | 87.635 | 87.635 | 87.635 | 87.635 | 87.635 | 87.635 | 87.635 | 87.635 | 87.635 | 87.5392 | 87.4433 | 87.3475 | 87.2517 | 87.1558 | 87.06 | 86.9642 | 86.8683 | 86.7725 | 86.6767 | 86.5808 | 86.485 | 86.3892 | 86.2933 | 86.1975 | 86.1017 | 86.0058 | 85.91 | 85.8142 | 85.7183 | 85.6225 | 85.5267 | 85.4308 | 85.335 | 85.2392 | 85.1433 | 85.0475 | 84.9517 | 84.8558 | 84.76
9.8 | 0 | 2.9133 | 5.8267 | 8.74 | 11.6533 | 14.5667 | 17.48 | 20.3933 | 23.3067 | 26.22 | 29.1333 | 33.0117 | 36.8901 | 40.7685 | 44.6469 | 48.5253 | 49.1149 | 49.7045 | 50.2941 | 50.8837 | 51.4733 | 52.5404 | 53.6075 | 54.6745 | 55.7416 | 56.8087 | 57.8757 | 58.9428 | 60.0099 | 61.0769 | 62.144 | 62.855 | 63.566 | 64.2771 | 64.9881 | 65.6991 | 66.4101 | 67.1212 | 67.8322 | 68.5432 | 69.2542 | 69.9652 | 70.6763 | 71.3873 | 72.0983 | 72.8093 | 73.3908 | 73.9722 | 74.5536 | 75.135 | 75.7164 | 76.2979 | 76.8793 | 77.4607 | 78.0421 | 78.6236 | 79.205 | 79.7864 | 80.3678 | 80.9492 | 81.5307 | 81.6921 | 81.8536 | 82.0151 | 82.1765 | 82.338 | 82.4995 | 82.6609 | 82.8224 | 82.9839 | 83.1453 | 83.3068 | 83.4683 | 83.6297 | 83.7912 | 83.9527 | 84.1141 | 84.2756 | 84.4371 | 84.5985 | 84.76 | 84.9215 | 85.0829 | 85.2444 | 85.4059 | 85.5673 | 85.7288 | 85.8903 | 86.0517 | 86.2132 | 86.3747 | 86.4391 | 86.5036 | 86.568 | 86.6324 | 86.6969 | 86.7613 | 86.8258 | 86.8902 | 86.9547 | 87.0191 | 87.0836 | 87.148 | 87.2124 | 87.2769 | 87.3413 | 87.4058 | 87.4702 | 87.5347 | 87.5991 | 87.6636 | 87.728 | 87.7924 | 87.8569 | 87.9213 | 87.9858 | 88.0502 | 88.1147 | 88.1791 | 88.2436 | 88.308 | 88.308 | 88.308 | 88.308 | 88.308 | 88.308 | 88.308 | 88.308 | 88.308 | 88.308 | 88.308 | 88.308 | 88.308 | 88.308 | 88.308 | 88.308 | 88.308 | 88.308 | 88.308 | 88.308 | 88.308 | 88.308 | 88.308 | 88.308 | 88.308 | 88.308 | 88.308 | 88.308 | 88.308 | 88.308 | 88.308 | 88.2113 | 88.1147 | 88.018 | 87.9213 | 87.8247 | 87.728 | 87.6313 | 87.5347 | 87.438 | 87.3413 | 87.2447 | 87.148 | 87.0513 | 86.9547 | 86.858 | 86.7613 | 86.6647 | 86.568 | 86.4713 | 86.3747 | 86.278 | 86.1813 | 86.0847 | 85.988 | 85.8913 | 85.7947 | 85.698 | 85.6013 | 85.5047 | 85.408
9.85 | 0 | 2.935 | 5.87 | 8.805 | 11.74 | 14.675 | 17.61 | 20.545 | 23.48 | 26.415 | 29.35 | 33.2588 | 37.1676 | 41.0764 | 44.9852 | 48.894 | 49.4862 | 50.0784 | 50.6706 | 51.2628 | 51.855 | 52.9303 | 54.0056 | 55.0809 | 56.1562 | 57.2315 | 58.3068 | 59.3821 | 60.4574 | 61.5327 | 62.608 | 63.3246 | 64.0412 | 64.7578 | 65.4744 | 66.191 | 66.9076 | 67.6242 | 68.3408 | 69.0574 | 69.774 | 70.4906 | 71.2072 | 71.9238 | 72.6404 | 73.357 | 73.9431 | 74.5291 | 75.1152 | 75.7013 | 76.2873 | 76.8734 | 77.4595 | 78.0455 | 78.6316 | 79.2177 | 79.8037 | 80.3898 | 80.9759 | 81.5619 | 82.148 | 82.3108 | 82.4735 | 82.6363 | 82.7991 | 82.9618 | 83.1246 | 83.2874 | 83.4501 | 83.6129 | 83.7757 | 83.9384 | 84.1012 | 84.264 | 84.4267 | 84.5895 | 84.7523 | 84.915 | 85.0778 | 85.2406 | 85.4033 | 85.5661 | 85.7289 | 85.8916 | 86.0544 | 86.2172 | 86.3799 | 86.5427 | 86.7055 | 86.8682 | 87.031 | 87.096 | 87.161 | 87.226 | 87.291 | 87.356 | 87.421 | 87.486 | 87.551 | 87.616 | 87.681 | 87.746 | 87.811 | 87.876 | 87.941 | 88.006 | 88.071 | 88.136 | 88.201 | 88.266 | 88.331 | 88.396 | 88.461 | 88.526 | 88.591 | 88.656 | 88.721 | 88.786 | 88.851 | 88.916 | 88.981 | 88.981 | 88.981 | 88.981 | 88.981 | 88.981 | 88.981 | 88.981 | 88.981 | 88.981 | 88.981 | 88.981 | 88.981 | 88.981 | 88.981 | 88.981 | 88.981 | 88.981 | 88.981 | 88.981 | 88.981 | 88.981 | 88.981 | 88.981 | 88.981 | 88.981 | 88.981 | 88.981 | 88.981 | 88.981 | 88.981 | 88.8835 | 88.786 | 88.6885 | 88.591 | 88.4935 | 88.396 | 88.2985 | 88.201 | 88.1035 | 88.006 | 87.9085 | 87.811 | 87.7135 | 87.616 | 87.5185 | 87.421 | 87.3235 | 87.226 | 87.1285 | 87.031 | 86.9335 | 86.836 | 86.7385 | 86.641 | 86.5435 | 86.446 | 86.3485 | 86.251 | 86.1535 | 86.056
9.9 | 0 | 2.9567 | 5.9133 | 8.87 | 11.8267 | 14.7833 | 17.74 | 20.6967 | 23.6533 | 26.61 | 29.5667 | 33.5059 | 37.4451 | 41.3843 | 45.3235 | 49.2627 | 49.8575 | 50.4523 | 51.0471 | 51.6419 | 52.2367 | 53.3202 | 54.4037 | 55.4873 | 56.5708 | 57.6543 | 58.7379 | 59.8214 | 60.9049 | 61.9885 | 63.072 | 63.7942 | 64.5164 | 65.2385 | 65.9607 | 66.6829 | 67.4051 | 68.1272 | 68.8494 | 69.5716 | 70.2938 | 71.016 | 71.7381 | 72.4603 | 73.1825 | 73.9047 | 74.4954 | 75.0861 | 75.6768 | 76.2675 | 76.8582 | 77.4489 | 78.0396 | 78.6304 | 79.2211 | 79.8118 | 80.4025 | 80.9932 | 81.5839 | 82.1746 | 82.7653 | 82.9294 | 83.0935 | 83.2575 | 83.4216 | 83.5857 | 83.7497 | 83.9138 | 84.0779 | 84.2419 | 84.406 | 84.5701 | 84.7341 | 84.8982 | 85.0623 | 85.2263 | 85.3904 | 85.5545 | 85.7185 | 85.8826 | 86.0467 | 86.2107 | 86.3748 | 86.5389 | 86.7029 | 86.867 | 87.0311 | 87.1951 | 87.3592 | 87.5233 | 87.6873 | 87.7529 | 87.8184 | 87.884 | 87.9496 | 88.0151 | 88.0807 | 88.1462 | 88.2118 | 88.2773 | 88.3429 | 88.4084 | 88.474 | 88.5396 | 88.6051 | 88.6707 | 88.7362 | 88.8018 | 88.8673 | 88.9329 | 88.9984 | 89.064 | 89.1296 | 89.1951 | 89.2607 | 89.3262 | 89.3918 | 89.4573 | 89.5229 | 89.5884 | 89.654 | 89.654 | 89.654 | 89.654 | 89.654 | 89.654 | 89.654 | 89.654 | 89.654 | 89.654 | 89.654 | 89.654 | 89.654 | 89.654 | 89.654 | 89.654 | 89.654 | 89.654 | 89.654 | 89.654 | 89.654 | 89.654 | 89.654 | 89.654 | 89.654 | 89.654 | 89.654 | 89.654 | 89.654 | 89.654 | 89.654 | 89.5557 | 89.4573 | 89.359 | 89.2607 | 89.1623 | 89.064 | 88.9657 | 88.8673 | 88.769 | 88.6707 | 88.5723 | 88.474 | 88.3757 | 88.2773 | 88.179 | 88.0807 | 87.9823 | 87.884 | 87.7857 | 87.6873 | 87.589 | 87.4907 | 87.3923 | 87.294 | 87.1957 | 87.0973 | 86.999 | 86.9007 | 86.8023 | 86.704
9.95 | 0 | 2.9783 | 5.9567 | 8.935 | 11.9133 | 14.8917 | 17.87 | 20.8483 | 23.8267 | 26.805 | 29.7833 | 33.7529 | 37.7225 | 41.6921 | 45.6617 | 49.6313 | 50.2287 | 50.8261 | 51.4235 | 52.0209 | 52.6183 | 53.7101 | 54.8019 | 55.8936 | 56.9854 | 58.0772 | 59.1689 | 60.2607 | 61.3525 | 62.4442 | 63.536 | 64.2638 | 64.9915 | 65.7193 | 66.447 | 67.1748 | 67.9025 | 68.6303 | 69.358 | 70.0858 | 70.8136 | 71.5413 | 72.2691 | 72.9968 | 73.7246 | 74.4523 | 75.0477 | 75.643 | 76.2384 | 76.8338 | 77.4291 | 78.0245 | 78.6198 | 79.2152 | 79.8105 | 80.4059 | 81.0012 | 81.5966 | 82.192 | 82.7873 | 83.3827 | 83.548 | 83.7134 | 83.8788 | 84.0441 | 84.2095 | 84.3749 | 84.5402 | 84.7056 | 84.871 | 85.0363 | 85.2017 | 85.3671 | 85.5324 | 85.6978 | 85.8632 | 86.0285 | 86.1939 | 86.3593 | 86.5246 | 86.69 | 86.8554 | 87.0207 | 87.1861 | 87.3515 | 87.5168 | 87.6822 | 87.8476 | 88.0129 | 88.1783 | 88.3437 | 88.4098 | 88.4759 | 88.542 | 88.6081 | 88.6742 | 88.7403 | 88.8064 | 88.8726 | 88.9387 | 89.0048 | 89.0709 | 89.137 | 89.2031 | 89.2692 | 89.3353 | 89.4014 | 89.4676 | 89.5337 | 89.5998 | 89.6659 | 89.732 | 89.7981 | 89.8642 | 89.9303 | 89.9964 | 90.0626 | 90.1287 | 90.1948 | 90.2609 | 90.327 | 90.327 | 90.327 | 90.327 | 90.327 | 90.327 | 90.327 | 90.327 | 90.327 | 90.327 | 90.327 | 90.327 | 90.327 | 90.327 | 90.327 | 90.327 | 90.327 | 90.327 | 90.327 | 90.327 | 90.327 | 90.327 | 90.327 | 90.327 | 90.327 | 90.327 | 90.327 | 90.327 | 90.327 | 90.327 | 90.327 | 90.2278 | 90.1287 | 90.0295 | 89.9303 | 89.8312 | 89.732 | 89.6328 | 89.5337 | 89.4345 | 89.3353 | 89.2362 | 89.137 | 89.0378 | 88.9387 | 88.8395 | 88.7403 | 88.6412 | 88.542 | 88.4428 | 88.3437 | 88.2445 | 88.1453 | 88.0462 | 87.947 | 87.8478 | 87.7487 | 87.6495 | 87.5503 | 87.4512 | 87.352
10 | 0 | 3 | 6 | 9 | 12 | 15 | 18 | 21 | 24 | 27 | 30 | 34 | 38 | 42 | 46 | 50 | 50.6 | 51.2 | 51.8 | 52.4 | 53 | 54.1 | 55.2 | 56.3 | 57.4 | 58.5 | 59.6 | 60.7 | 61.8 | 62.9 | 64 | 64.7333 | 65.4667 | 66.2 | 66.9333 | 67.6667 | 68.4 | 69.1333 | 69.8667 | 70.6 | 71.3333 | 72.0667 | 72.8 | 73.5333 | 74.2667 | 75 | 75.6 | 76.2 | 76.8 | 77.4 | 78 | 78.6 | 79.2 | 79.8 | 80.4 | 81 | 81.6 | 82.2 | 82.8 | 83.4 | 84 | 84.1667 | 84.3333 | 84.5 | 84.6667 | 84.8333 | 85 | 85.1667 | 85.3333 | 85.5 | 85.6667 | 85.8333 | 86 | 86.1667 | 86.3333 | 86.5 | 86.6667 | 86.8333 | 87 | 87.1667 | 87.3333 | 87.5 | 87.6667 | 87.8333 | 88 | 88.1667 | 88.3333 | 88.5 | 88.6667 | 88.8333 | 89 | 89.0667 | 89.1333 | 89.2 | 89.2667 | 89.3333 | 89.4 | 89.4667 | 89.5333 | 89.6 | 89.6667 | 89.7333 | 89.8 | 89.8667 | 89.9333 | 90 | 90.0667 | 90.1333 | 90.2 | 90.2667 | 90.3333 | 90.4 | 90.4667 | 90.5333 | 90.6 | 90.6667 | 90.7333 | 90.8 | 90.8667 | 90.9333 | 91 | 91 | 91 | 91 | 91 | 91 | 91 | 91 | 91 | 91 | 91 | 91 | 91 | 91 | 91 | 91 | 91 | 91 | 91 | 91 | 91 | 91 | 91 | 91 | 91 | 91 | 91 | 91 | 91 | 91 | 91 | 90.9 | 90.8 | 90.7 | 90.6 | 90.5 | 90.4 | 90.3 | 90.2 | 90.1 | 90 | 89.9 | 89.8 | 89.7 | 89.6 | 89.5 | 89.4 | 89.3 | 89.2 | 89.1 | 89 | 88.9 | 88.8 | 88.7 | 88.6 | 88.5 | 88.4 | 88.3 | 88.2 | 88.1 | 88
10.05 | 0 | 3.039 | 6.078 | 9.117 | 12.156 | 15.195 | 18.234 | 21.273 | 24.312 | 27.351 | 30.39 | 34.4591 | 38.5281 | 42.5972 | 46.6663 | 50.7353 | 51.3261 | 51.9168 | 52.5075 | 53.0983 | 53.689 | 54.8054 | 55.9219 | 57.0383 | 58.1547 | 59.2712 | 60.3876 | 61.504 | 62.6205 | 63.7369 | 64.8533 | 65.5976 | 66.3419 | 67.0862 | 67.8305 | 68.5748 | 69.3191 | 70.0634 | 70.8076 | 71.5519 | 72.2962 | 73.0405 | 73.7848 | 74.5291 | 75.2734 | 76.0177 | 76.6283 | 77.239 | 77.8496 | 78.4602 | 79.0709 | 79.6815 | 80.2922 | 80.9028 | 81.5135 | 82.1241 | 82.7348 | 83.3454 | 83.956 | 84.5667 | 85.1773 | 85.3476 | 85.5178 | 85.6881 | 85.8584 | 86.0286 | 86.1989 | 86.3691 | 86.5394 | 86.7096 | 86.8799 | 87.0501 | 87.2204 | 87.3907 | 87.5609 | 87.7312 | 87.9014 | 88.0717 | 88.2419 | 88.4122 | 88.5824 | 88.7527 | 88.923 | 89.0932 | 89.2635 | 89.4337 | 89.604 | 89.7742 | 89.9445 | 90.1147 | 90.285 | 90.3532 | 90.4215 | 90.4897 | 90.558 | 90.6262 | 90.6945 | 90.7627 | 90.831 | 90.8992 | 90.9674 | 91.0357 | 91.1039 | 91.1722 | 91.2404 | 91.3087 | 91.3769 | 91.4452 | 91.5134 | 91.5816 | 91.6499 | 91.7181 | 91.7864 | 91.8546 | 91.9229 | 91.9911 | 92.0594 | 92.1276 | 92.1958 | 92.2641 | 92.3323 | 92.3323 | 92.3323 | 92.3323 | 92.3323 | 92.3323 | 92.3323 | 92.3323 | 92.3323 | 92.3323 | 92.3323 | 92.3323 | 92.3323 | 92.3323 | 92.3323 | 92.3323 | 92.3323 | 92.3323 | 92.3323 | 92.3323 | 92.3323 | 92.3323 | 92.3323 | 92.3323 | 92.3323 | 92.3323 | 92.3323 | 92.3323 | 92.3323 | 92.3323 | 92.3323 | 92.2332 | 92.134 | 92.0348 | 91.9357 | 91.8365 | 91.7373 | 91.6382 | 91.539 | 91.4398 | 91.3407 | 91.2415 | 91.1423 | 91.0432 | 90.944 | 90.8448 | 90.7457 | 90.6465 | 90.5473 | 90.4482 | 90.349 | 90.2498 | 90.1507 | 90.0515 | 89.9523 | 89.8532 | 89.754 | 89.6548 | 89.5557 | 89.4565 | 89.3573
10.1 | 0 | 3.078 | 6.156 | 9.234 | 12.312 | 15.39 | 18.468 | 21.546 | 24.624 | 27.702 | 30.78 | 34.9181 | 39.0563 | 43.1944 | 47.3325 | 51.4707 | 52.0521 | 52.6336 | 53.2151 | 53.7965 | 54.378 | 55.5109 | 56.6437 | 57.7766 | 58.9095 | 60.0423 | 61.1752 | 62.3081 | 63.4409 | 64.5738 | 65.7067 | 66.4619 | 67.2172 | 67.9724 | 68.7276 | 69.4829 | 70.2381 | 70.9934 | 71.7486 | 72.5039 | 73.2591 | 74.0144 | 74.7696 | 75.5248 | 76.2801 | 77.0353 | 77.6566 | 78.2779 | 78.8992 | 79.5205 | 80.1418 | 80.7631 | 81.3844 | 82.0056 | 82.6269 | 83.2482 | 83.8695 | 84.4908 | 85.1121 | 85.7334 | 86.3547 | 86.5285 | 86.7024 | 86.8762 | 87.05 | 87.2239 | 87.3977 | 87.5716 | 87.7454 | 87.9193 | 88.0931 | 88.267 | 88.4408 | 88.6146 | 88.7885 | 88.9623 | 89.1362 | 89.31 | 89.4839 | 89.6577 | 89.8316 | 90.0054 | 90.1792 | 90.3531 | 90.5269 | 90.7008 | 90.8746 | 91.0485 | 91.2223 | 91.3962 | 91.57 | 91.6398 | 91.7096 | 91.7795 | 91.8493 | 91.9191 | 91.9889 | 92.0588 | 92.1286 | 92.1984 | 92.2682 | 92.338 | 92.4079 | 92.4777 | 92.5475 | 92.6173 | 92.6872 | 92.757 | 92.8268 | 92.8966 | 92.9664 | 93.0363 | 93.1061 | 93.1759 | 93.2457 | 93.3156 | 93.3854 | 93.4552 | 93.525 | 93.5948 | 93.6647 | 93.6647 | 93.6647 | 93.6647 | 93.6647 | 93.6647 | 93.6647 | 93.6647 | 93.6647 | 93.6647 | 93.6647 | 93.6647 | 93.6647 | 93.6647 | 93.6647 | 93.6647 | 93.6647 | 93.6647 | 93.6647 | 93.6647 | 93.6647 | 93.6647 | 93.6647 | 93.6647 | 93.6647 | 93.6647 | 93.6647 | 93.6647 | 93.6647 | 93.6647 | 93.6647 | 93.5663 | 93.468 | 93.3697 | 93.2713 | 93.173 | 93.0747 | 92.9763 | 92.878 | 92.7797 | 92.6813 | 92.583 | 92.4847 | 92.3863 | 92.288 | 92.1897 | 92.0913 | 91.993 | 91.8947 | 91.7963 | 91.698 | 91.5997 | 91.5013 | 91.403 | 91.3047 | 91.2063 | 91.108 | 91.0097 | 90.9113 | 90.813 | 90.7147
10.15 | 0 | 3.117 | 6.234 | 9.351 | 12.468 | 15.585 | 18.702 | 21.819 | 24.936 | 28.053 | 31.17 | 35.3772 | 39.5844 | 43.7916 | 47.9988 | 52.206 | 52.7782 | 53.3504 | 53.9226 | 54.4948 | 55.067 | 56.2163 | 57.3656 | 58.5149 | 59.6642 | 60.8135 | 61.9628 | 63.1121 | 64.2614 | 65.4107 | 66.56 | 67.3262 | 68.0924 | 68.8586 | 69.6248 | 70.391 | 71.1572 | 71.9234 | 72.6896 | 73.4558 | 74.222 | 74.9882 | 75.7544 | 76.5206 | 77.2868 | 78.053 | 78.6849 | 79.3169 | 79.9488 | 80.5807 | 81.2127 | 81.8446 | 82.4765 | 83.1085 | 83.7404 | 84.3723 | 85.0043 | 85.6362 | 86.2681 | 86.9001 | 87.532 | 87.7094 | 87.8869 | 88.0643 | 88.2417 | 88.4192 | 88.5966 | 88.774 | 88.9515 | 89.1289 | 89.3063 | 89.4838 | 89.6612 | 89.8386 | 90.0161 | 90.1935 | 90.3709 | 90.5484 | 90.7258 | 90.9032 | 91.0807 | 91.2581 | 91.4355 | 91.613 | 91.7904 | 91.9678 | 92.1453 | 92.3227 | 92.5001 | 92.6776 | 92.855 | 92.9264 | 92.9978 | 93.0692 | 93.1406 | 93.212 | 93.2834 | 93.3548 | 93.4262 | 93.4976 | 93.569 | 93.6404 | 93.7118 | 93.7832 | 93.8546 | 93.926 | 93.9974 | 94.0688 | 94.1402 | 94.2116 | 94.283 | 94.3544 | 94.4258 | 94.4972 | 94.5686 | 94.64 | 94.7114 | 94.7828 | 94.8542 | 94.9256 | 94.997 | 94.997 | 94.997 | 94.997 | 94.997 | 94.997 | 94.997 | 94.997 | 94.997 | 94.997 | 94.997 | 94.997 | 94.997 | 94.997 | 94.997 | 94.997 | 94.997 | 94.997 | 94.997 | 94.997 | 94.997 | 94.997 | 94.997 | 94.997 | 94.997 | 94.997 | 94.997 | 94.997 | 94.997 | 94.997 | 94.997 | 94.8995 | 94.802 | 94.7045 | 94.607 | 94.5095 | 94.412 | 94.3145 | 94.217 | 94.1195 | 94.022 | 93.9245 | 93.827 | 93.7295 | 93.632 | 93.5345 | 93.437 | 93.3395 | 93.242 | 93.1445 | 93.047 | 92.9495 | 92.852 | 92.7545 | 92.657 | 92.5595 | 92.462 | 92.3645 | 92.267 | 92.1695 | 92.072
10.2 | 0 | 3.156 | 6.312 | 9.468 | 12.624 | 15.78 | 18.936 | 22.092 | 25.248 | 28.404 | 31.56 | 35.8363 | 40.1125 | 44.3888 | 48.6651 | 52.9413 | 53.5043 | 54.0672 | 54.6301 | 55.1931 | 55.756 | 56.9217 | 58.0875 | 59.2532 | 60.4189 | 61.5847 | 62.7504 | 63.9161 | 65.0819 | 66.2476 | 67.4133 | 68.1905 | 68.9676 | 69.7448 | 70.522 | 71.2991 | 72.0763 | 72.8534 | 73.6306 | 74.4077 | 75.1849 | 75.962 | 76.7392 | 77.5164 | 78.2935 | 79.0707 | 79.7132 | 80.3558 | 80.9984 | 81.641 | 82.2836 | 82.9261 | 83.5687 | 84.2113 | 84.8539 | 85.4964 | 86.139 | 86.7816 | 87.4242 | 88.0668 | 88.7093 | 88.8904 | 89.0714 | 89.2524 | 89.4334 | 89.6144 | 89.7955 | 89.9765 | 90.1575 | 90.3385 | 90.5196 | 90.7006 | 90.8816 | 91.0626 | 91.2436 | 91.4247 | 91.6057 | 91.7867 | 91.9677 | 92.1488 | 92.3298 | 92.5108 | 92.6918 | 92.8728 | 93.0539 | 93.2349 | 93.4159 | 93.5969 | 93.778 | 93.959 | 94.14 | 94.213 | 94.286 | 94.3589 | 94.4319 | 94.5049 | 94.5779 | 94.6508 | 94.7238 | 94.7968 | 94.8698 | 94.9428 | 95.0157 | 95.0887 | 95.1617 | 95.2347 | 95.3076 | 95.3806 | 95.4536 | 95.5266 | 95.5996 | 95.6725 | 95.7455 | 95.8185 | 95.8915 | 95.9644 | 96.0374 | 96.1104 | 96.1834 | 96.2564 | 96.3293 | 96.3293 | 96.3293 | 96.3293 | 96.3293 | 96.3293 | 96.3293 | 96.3293 | 96.3293 | 96.3293 | 96.3293 | 96.3293 | 96.3293 | 96.3293 | 96.3293 | 96.3293 | 96.3293 | 96.3293 | 96.3293 | 96.3293 | 96.3293 | 96.3293 | 96.3293 | 96.3293 | 96.3293 | 96.3293 | 96.3293 | 96.3293 | 96.3293 | 96.3293 | 96.3293 | 96.2327 | 96.136 | 96.0393 | 95.9427 | 95.846 | 95.7493 | 95.6527 | 95.556 | 95.4593 | 95.3627 | 95.266 | 95.1693 | 95.0727 | 94.976 | 94.8793 | 94.7827 | 94.686 | 94.5893 | 94.4927 | 94.396 | 94.2993 | 94.2027 | 94.106 | 94.0093 | 93.9127 | 93.816 | 93.7193 | 93.6227 | 93.526 | 93.4293
10.25 | 0 | 3.195 | 6.39 | 9.585 | 12.78 | 15.975 | 19.17 | 22.365 | 25.56 | 28.755 | 31.95 | 36.2953 | 40.6407 | 44.986 | 49.3313 | 53.6767 | 54.2303 | 54.784 | 55.3377 | 55.8913 | 56.445 | 57.6272 | 58.8093 | 59.9915 | 61.1737 | 62.3558 | 63.538 | 64.7202 | 65.9023 | 67.0845 | 68.2667 | 69.0548 | 69.8429 | 70.631 | 71.4191 | 72.2072 | 72.9953 | 73.7834 | 74.5716 | 75.3597 | 76.1478 | 76.9359 | 77.724 | 78.5121 | 79.3002 | 80.0883 | 80.7416 | 81.3948 | 82.048 | 82.7012 | 83.3544 | 84.0077 | 84.6609 | 85.3141 | 85.9673 | 86.6206 | 87.2738 | 87.927 | 88.5802 | 89.2334 | 89.8867 | 90.0713 | 90.2559 | 90.4405 | 90.6251 | 90.8097 | 90.9943 | 91.1789 | 91.3636 | 91.5482 | 91.7328 | 91.9174 | 92.102 | 92.2866 | 92.4712 | 92.6558 | 92.8404 | 93.0251 | 93.2097 | 93.3943 | 93.5789 | 93.7635 | 93.9481 | 94.1327 | 94.3173 | 94.5019 | 94.6866 | 94.8712 | 95.0558 | 95.2404 | 95.425 | 95.4996 | 95.5741 | 95.6487 | 95.7232 | 95.7978 | 95.8723 | 95.9469 | 96.0214 | 96.096 | 96.1706 | 96.2451 | 96.3197 | 96.3942 | 96.4688 | 96.5433 | 96.6179 | 96.6924 | 96.767 | 96.8416 | 96.9161 | 96.9907 | 97.0652 | 97.1398 | 97.2143 | 97.2889 | 97.3634 | 97.438 | 97.5126 | 97.5871 | 97.6617 | 97.6617 | 97.6617 | 97.6617 | 97.6617 | 97.6617 | 97.6617 | 97.6617 | 97.6617 | 97.6617 | 97.6617 | 97.6617 | 97.6617 | 97.6617 | 97.6617 | 97.6617 | 97.6617 | 97.6617 | 97.6617 | 97.6617 | 97.6617 | 97.6617 | 97.6617 | 97.6617 | 97.6617 | 97.6617 | 97.6617 | 97.6617 | 97.6617 | 97.6617 | 97.6617 | 97.5658 | 97.47 | 97.3742 | 97.2783 | 97.1825 | 97.0867 | 96.9908 | 96.895 | 96.7992 | 96.7033 | 96.6075 | 96.5117 | 96.4158 | 96.32 | 96.2242 | 96.1283 | 96.0325 | 95.9367 | 95.8408 | 95.745 | 95.6492 | 95.5533 | 95.4575 | 95.3617 | 95.2658 | 95.17 | 95.0742 | 94.9783 | 94.8825 | 94.7867
10.3 | 0 | 3.234 | 6.468 | 9.702 | 12.936 | 16.17 | 19.404 | 22.638 | 25.872 | 29.106 | 32.34 | 36.7544 | 41.1688 | 45.5832 | 49.9976 | 54.412 | 54.9564 | 55.5008 | 56.0452 | 56.5896 | 57.134 | 58.3326 | 59.5312 | 60.7298 | 61.9284 | 63.127 | 64.3256 | 65.5242 | 66.7228 | 67.9214 | 69.12 | 69.9191 | 70.7181 | 71.5172 | 72.3163 | 73.1153 | 73.9144 | 74.7135 | 75.5125 | 76.3116 | 77.1107 | 77.9097 | 78.7088 | 79.5079 | 80.3069 | 81.106 | 81.7699 | 82.4337 | 83.0976 | 83.7615 | 84.4253 | 85.0892 | 85.7531 | 86.4169 | 87.0808 | 87.7447 | 88.4085 | 89.0724 | 89.7363 | 90.4001 | 91.064 | 91.2522 | 91.4404 | 91.6286 | 91.8168 | 92.005 | 92.1932 | 92.3814 | 92.5696 | 92.7578 | 92.946 | 93.1342 | 93.3224 | 93.5106 | 93.6988 | 93.887 | 94.0752 | 94.2634 | 94.4516 | 94.6398 | 94.828 | 95.0162 | 95.2044 | 95.3926 | 95.5808 | 95.769 | 95.9572 | 96.1454 | 96.3336 | 96.5218 | 96.71 | 96.7861 | 96.8623 | 96.9384 | 97.0145 | 97.0907 | 97.1668 | 97.2429 | 97.3191 | 97.3952 | 97.4713 | 97.5475 | 97.6236 | 97.6997 | 97.7759 | 97.852 | 97.9281 | 98.0043 | 98.0804 | 98.1565 | 98.2327 | 98.3088 | 98.3849 | 98.4611 | 98.5372 | 98.6133 | 98.6895 | 98.7656 | 98.8417 | 98.9179 | 98.994 | 98.994 | 98.994 | 98.994 | 98.994 | 98.994 | 98.994 | 98.994 | 98.994 | 98.994 | 98.994 | 98.994 | 98.994 | 98.994 | 98.994 | 98.994 | 98.994 | 98.994 | 98.994 | 98.994 | 98.994 | 98.994 | 98.994 | 98.994 | 98.994 | 98.994 | 98.994 | 98.994 | 98.994 | 98.994 | 98.994 | 98.899 | 98.804 | 98.709 | 98.614 | 98.519 | 98.424 | 98.329 | 98.234 | 98.139 | 98.044 | 97.949 | 97.854 | 97.759 | 97.664 | 97.569 | 97.474 | 97.379 | 97.284 | 97.189 | 97.094 | 96.999 | 96.904 | 96.809 | 96.714 | 96.619 | 96.524 | 96.429 | 96.334 | 96.239 | 96.144
10.35 | 0 | 3.273 | 6.546 | 9.819 | 13.092 | 16.365 | 19.638 | 22.911 | 26.184 | 29.457 | 32.73 | 37.2135 | 41.6969 | 46.1804 | 50.6639 | 55.1473 | 55.6825 | 56.2176 | 56.7527 | 57.2879 | 57.823 | 59.038 | 60.2531 | 61.4681 | 62.6831 | 63.8982 | 65.1132 | 66.3282 | 67.5433 | 68.7583 | 69.9733 | 70.7834 | 71.5934 | 72.4034 | 73.2134 | 74.0234 | 74.8335 | 75.6435 | 76.4535 | 77.2635 | 78.0736 | 78.8836 | 79.6936 | 80.5036 | 81.3136 | 82.1237 | 82.7982 | 83.4727 | 84.1472 | 84.8217 | 85.4962 | 86.1707 | 86.8452 | 87.5198 | 88.1943 | 88.8688 | 89.5433 | 90.2178 | 90.8923 | 91.5668 | 92.2413 | 92.4331 | 92.6249 | 92.8167 | 93.0085 | 93.2003 | 93.3921 | 93.5839 | 93.7756 | 93.9674 | 94.1592 | 94.351 | 94.5428 | 94.7346 | 94.9264 | 95.1182 | 95.31 | 95.5017 | 95.6935 | 95.8853 | 96.0771 | 96.2689 | 96.4607 | 96.6525 | 96.8443 | 97.0361 | 97.2278 | 97.4196 | 97.6114 | 97.8032 | 97.995 | 98.0727 | 98.1504 | 98.2281 | 98.3058 | 98.3836 | 98.4613 | 98.539 | 98.6167 | 98.6944 | 98.7721 | 98.8498 | 98.9275 | 99.0052 | 99.083 | 99.1607 | 99.2384 | 99.3161 | 99.3938 | 99.4715 | 99.5492 | 99.6269 | 99.7046 | 99.7824 | 99.8601 | 99.9378 | 100.0155 | 100.0932 | 100.1709 | 100.2486 | 100.3263 | 100.3263 | 100.3263 | 100.3263 | 100.3263 | 100.3263 | 100.3263 | 100.3263 | 100.3263 | 100.3263 | 100.3263 | 100.3263 | 100.3263 | 100.3263 | 100.3263 | 100.3263 | 100.3263 | 100.3263 | 100.3263 | 100.3263 | 100.3263 | 100.3263 | 100.3263 | 100.3263 | 100.3263 | 100.3263 | 100.3263 | 100.3263 | 100.3263 | 100.3263 | 100.3263 | 100.2322 | 100.138 | 100.0438 | 99.9497 | 99.8555 | 99.7613 | 99.6672 | 99.573 | 99.4788 | 99.3847 | 99.2905 | 99.1963 | 99.1022 | 99.008 | 98.9138 | 98.8197 | 98.7255 | 98.6313 | 98.5372 | 98.443 | 98.3488 | 98.2547 | 98.1605 | 98.0663 | 97.9722 | 97.878 | 97.7838 | 97.6897 | 97.5955 | 97.5013
10.4 | 0 | 3.312 | 6.624 | 9.936 | 13.248 | 16.56 | 19.872 | 23.184 | 26.496 | 29.808 | 33.12 | 37.6725 | 42.2251 | 46.7776 | 51.3301 | 55.8827 | 56.4085 | 56.9344 | 57.4603 | 57.9861 | 58.512 | 59.7435 | 60.9749 | 62.2064 | 63.4379 | 64.6693 | 65.9008 | 67.1323 | 68.3637 | 69.5952 | 70.8267 | 71.6476 | 72.4686 | 73.2896 | 74.1106 | 74.9316 | 75.7525 | 76.5735 | 77.3945 | 78.2155 | 79.0364 | 79.8574 | 80.6784 | 81.4994 | 82.3204 | 83.1413 | 83.8265 | 84.5116 | 85.1968 | 85.882 | 86.5671 | 87.2523 | 87.9374 | 88.6226 | 89.3077 | 89.9929 | 90.678 | 91.3632 | 92.0484 | 92.7335 | 93.4187 | 93.614 | 93.8094 | 94.0048 | 94.2002 | 94.3956 | 94.5909 | 94.7863 | 94.9817 | 95.1771 | 95.3724 | 95.5678 | 95.7632 | 95.9586 | 96.154 | 96.3493 | 96.5447 | 96.7401 | 96.9355 | 97.1308 | 97.3262 | 97.5216 | 97.717 | 97.9124 | 98.1077 | 98.3031 | 98.4985 | 98.6939 | 98.8892 | 99.0846 | 99.28 | 99.3593 | 99.4386 | 99.5179 | 99.5972 | 99.6764 | 99.7557 | 99.835 | 99.9143 | 99.9936 | 100.0729 | 100.1522 | 100.2315 | 100.3108 | 100.39 | 100.4693 | 100.5486 | 100.6279 | 100.7072 | 100.7865 | 100.8658 | 100.9451 | 101.0244 | 101.1036 | 101.1829 | 101.2622 | 101.3415 | 101.4208 | 101.5001 | 101.5794 | 101.6587 | 101.6587 | 101.6587 | 101.6587 | 101.6587 | 101.6587 | 101.6587 | 101.6587 | 101.6587 | 101.6587 | 101.6587 | 101.6587 | 101.6587 | 101.6587 | 101.6587 | 101.6587 | 101.6587 | 101.6587 | 101.6587 | 101.6587 | 101.6587 | 101.6587 | 101.6587 | 101.6587 | 101.6587 | 101.6587 | 101.6587 | 101.6587 | 101.6587 | 101.6587 | 101.6587 | 101.5653 | 101.472 | 101.3787 | 101.2853 | 101.192 | 101.0987 | 101.0053 | 100.912 | 100.8187 | 100.7253 | 100.632 | 100.5387 | 100.4453 | 100.352 | 100.2587 | 100.1653 | 100.072 | 99.9787 | 99.8853 | 99.792 | 99.6987 | 99.6053 | 99.512 | 99.4187 | 99.3253 | 99.232 | 99.1387 | 99.0453 | 98.952 | 98.8587
10.45 | 0 | 3.351 | 6.702 | 10.053 | 13.404 | 16.755 | 20.106 | 23.457 | 26.808 | 30.159 | 33.51 | 38.1316 | 42.7532 | 47.3748 | 51.9964 | 56.618 | 57.1346 | 57.6512 | 58.1678 | 58.6844 | 59.201 | 60.4489 | 61.6968 | 62.9447 | 64.1926 | 65.4405 | 66.6884 | 67.9363 | 69.1842 | 70.4321 | 71.68 | 72.5119 | 73.3439 | 74.1758 | 75.0077 | 75.8397 | 76.6716 | 77.5035 | 78.3355 | 79.1674 | 79.9993 | 80.8313 | 81.6632 | 82.4951 | 83.3271 | 84.159 | 84.8548 | 85.5506 | 86.2464 | 86.9422 | 87.638 | 88.3338 | 89.0296 | 89.7254 | 90.4212 | 91.117 | 91.8128 | 92.5086 | 93.2044 | 93.9002 | 94.596 | 94.795 | 94.9939 | 95.1929 | 95.3919 | 95.5908 | 95.7898 | 95.9888 | 96.1877 | 96.3867 | 96.5857 | 96.7846 | 96.9836 | 97.1826 | 97.3815 | 97.5805 | 97.7795 | 97.9784 | 98.1774 | 98.3764 | 98.5753 | 98.7743 | 98.9733 | 99.1722 | 99.3712 | 99.5702 | 99.7691 | 99.9681 | 100.1671 | 100.366 | 100.565 | 100.6459 | 100.7267 | 100.8076 | 100.8885 | 100.9693 | 101.0502 | 101.1311 | 101.2119 | 101.2928 | 101.3737 | 101.4545 | 101.5354 | 101.6163 | 101.6971 | 101.778 | 101.8589 | 101.9397 | 102.0206 | 102.1015 | 102.1823 | 102.2632 | 102.3441 | 102.4249 | 102.5058 | 102.5867 | 102.6675 | 102.7484 | 102.8293 | 102.9101 | 102.991 | 102.991 | 102.991 | 102.991 | 102.991 | 102.991 | 102.991 | 102.991 | 102.991 | 102.991 | 102.991 | 102.991 | 102.991 | 102.991 | 102.991 | 102.991 | 102.991 | 102.991 | 102.991 | 102.991 | 102.991 | 102.991 | 102.991 | 102.991 | 102.991 | 102.991 | 102.991 | 102.991 | 102.991 | 102.991 | 102.991 | 102.8985 | 102.806 | 102.7135 | 102.621 | 102.5285 | 102.436 | 102.3435 | 102.251 | 102.1585 | 102.066 | 101.9735 | 101.881 | 101.7885 | 101.696 | 101.6035 | 101.511 | 101.4185 | 101.326 | 101.2335 | 101.141 | 101.0485 | 100.956 | 100.8635 | 100.771 | 100.6785 | 100.586 | 100.4935 | 100.401 | 100.3085 | 100.216
10.5 | 0 | 3.39 | 6.78 | 10.17 | 13.56 | 16.95 | 20.34 | 23.73 | 27.12 | 30.51 | 33.9 | 38.5907 | 43.2813 | 47.972 | 52.6627 | 57.3533 | 57.8607 | 58.368 | 58.8753 | 59.3827 | 59.89 | 61.1543 | 62.4187 | 63.683 | 64.9473 | 66.2117 | 67.476 | 68.7403 | 70.0047 | 71.269 | 72.5333 | 73.3762 | 74.2191 | 75.062 | 75.9049 | 76.7478 | 77.5907 | 78.4336 | 79.2764 | 80.1193 | 80.9622 | 81.8051 | 82.648 | 83.4909 | 84.3338 | 85.1767 | 85.8831 | 86.5896 | 87.296 | 88.0024 | 88.7089 | 89.4153 | 90.1218 | 90.8282 | 91.5347 | 92.2411 | 92.9476 | 93.654 | 94.3604 | 95.0669 | 95.7733 | 95.9759 | 96.1784 | 96.381 | 96.5836 | 96.7861 | 96.9887 | 97.1912 | 97.3938 | 97.5963 | 97.7989 | 98.0014 | 98.204 | 98.4066 | 98.6091 | 98.8117 | 99.0142 | 99.2168 | 99.4193 | 99.6219 | 99.8244 | 100.027 | 100.2296 | 100.4321 | 100.6347 | 100.8372 | 101.0398 | 101.2423 | 101.4449 | 101.6474 | 101.85 | 101.9324 | 102.0149 | 102.0973 | 102.1798 | 102.2622 | 102.3447 | 102.4271 | 102.5096 | 102.592 | 102.6744 | 102.7569 | 102.8393 | 102.9218 | 103.0042 | 103.0867 | 103.1691 | 103.2516 | 103.334 | 103.4164 | 103.4989 | 103.5813 | 103.6638 | 103.7462 | 103.8287 | 103.9111 | 103.9936 | 104.076 | 104.1584 | 104.2409 | 104.3233 | 104.3233 | 104.3233 | 104.3233 | 104.3233 | 104.3233 | 104.3233 | 104.3233 | 104.3233 | 104.3233 | 104.3233 | 104.3233 | 104.3233 | 104.3233 | 104.3233 | 104.3233 | 104.3233 | 104.3233 | 104.3233 | 104.3233 | 104.3233 | 104.3233 | 104.3233 | 104.3233 | 104.3233 | 104.3233 | 104.3233 | 104.3233 | 104.3233 | 104.3233 | 104.3233 | 104.2317 | 104.14 | 104.0483 | 103.9567 | 103.865 | 103.7733 | 103.6817 | 103.59 | 103.4983 | 103.4067 | 103.315 | 103.2233 | 103.1317 | 103.04 | 102.9483 | 102.8567 | 102.765 | 102.6733 | 102.5817 | 102.49 | 102.3983 | 102.3067 | 102.215 | 102.1233 | 102.0317 | 101.94 | 101.8483 | 101.7567 | 101.665 | 101.5733
10.55 | 0 | 3.429 | 6.858 | 10.287 | 13.716 | 17.145 | 20.574 | 24.003 | 27.432 | 30.861 | 34.29 | 39.0497 | 43.8095 | 48.5692 | 53.3289 | 58.0887 | 58.5867 | 59.0848 | 59.5829 | 60.0809 | 60.579 | 61.8598 | 63.1405 | 64.4213 | 65.7021 | 66.9828 | 68.2636 | 69.5444 | 70.8251 | 72.1059 | 73.3867 | 74.2405 | 75.0944 | 75.9482 | 76.802 | 77.6559 | 78.5097 | 79.3636 | 80.2174 | 81.0713 | 81.9251 | 82.779 | 83.6328 | 84.4866 | 85.3405 | 86.1943 | 86.9114 | 87.6285 | 88.3456 | 89.0627 | 89.7798 | 90.4969 | 91.214 | 91.931 | 92.6481 | 93.3652 | 94.0823 | 94.7994 | 95.5165 | 96.2336 | 96.9507 | 97.1568 | 97.363 | 97.5691 | 97.7752 | 97.9814 | 98.1875 | 98.3937 | 98.5998 | 98.806 | 99.0121 | 99.2183 | 99.4244 | 99.6305 | 99.8367 | 100.0428 | 100.249 | 100.4551 | 100.6613 | 100.8674 | 101.0736 | 101.2797 | 101.4858 | 101.692 | 101.8981 | 102.1043 | 102.3104 | 102.5166 | 102.7227 | 102.9289 | 103.135 | 103.219 | 103.303 | 103.3871 | 103.4711 | 103.5551 | 103.6391 | 103.7232 | 103.8072 | 103.8912 | 103.9752 | 104.0592 | 104.1433 | 104.2273 | 104.3113 | 104.3953 | 104.4794 | 104.5634 | 104.6474 | 104.7314 | 104.8154 | 104.8995 | 104.9835 | 105.0675 | 105.1515 | 105.2356 | 105.3196 | 105.4036 | 105.4876 | 105.5716 | 105.6557 | 105.6557 | 105.6557 | 105.6557 | 105.6557 | 105.6557 | 105.6557 | 105.6557 | 105.6557 | 105.6557 | 105.6557 | 105.6557 | 105.6557 | 105.6557 | 105.6557 | 105.6557 | 105.6557 | 105.6557 | 105.6557 | 105.6557 | 105.6557 | 105.6557 | 105.6557 | 105.6557 | 105.6557 | 105.6557 | 105.6557 | 105.6557 | 105.6557 | 105.6557 | 105.6557 | 105.5648 | 105.474 | 105.3832 | 105.2923 | 105.2015 | 105.1107 | 105.0198 | 104.929 | 104.8382 | 104.7473 | 104.6565 | 104.5657 | 104.4748 | 104.384 | 104.2932 | 104.2023 | 104.1115 | 104.0207 | 103.9298 | 103.839 | 103.7482 | 103.6573 | 103.5665 | 103.4757 | 103.3848 | 103.294 | 103.2032 | 103.1123 | 103.0215 | 102.9307
10.6 | 0 | 3.468 | 6.936 | 10.404 | 13.872 | 17.34 | 20.808 | 24.276 | 27.744 | 31.212 | 34.68 | 39.5088 | 44.3376 | 49.1664 | 53.9952 | 58.824 | 59.3128 | 59.8016 | 60.2904 | 60.7792 | 61.268 | 62.5652 | 63.8624 | 65.1596 | 66.4568 | 67.754 | 69.0512 | 70.3484 | 71.6456 | 72.9428 | 74.24 | 75.1048 | 75.9696 | 76.8344 | 77.6992 | 78.564 | 79.4288 | 80.2936 | 81.1584 | 82.0232 | 82.888 | 83.7528 | 84.6176 | 85.4824 | 86.3472 | 87.212 | 87.9397 | 88.6675 | 89.3952 | 90.1229 | 90.8507 | 91.5784 | 92.3061 | 93.0339 | 93.7616 | 94.4893 | 95.2171 | 95.9448 | 96.6725 | 97.4003 | 98.128 | 98.3377 | 98.5475 | 98.7572 | 98.9669 | 99.1767 | 99.3864 | 99.5961 | 99.8059 | 100.0156 | 100.2253 | 100.4351 | 100.6448 | 100.8545 | 101.0643 | 101.274 | 101.4837 | 101.6935 | 101.9032 | 102.1129 | 102.3227 | 102.5324 | 102.7421 | 102.9519 | 103.1616 | 103.3713 | 103.5811 | 103.7908 | 104.0005 | 104.2103 | 104.42 | 104.5056 | 104.5912 | 104.6768 | 104.7624 | 104.848 | 104.9336 | 105.0192 | 105.1048 | 105.1904 | 105.276 | 105.3616 | 105.4472 | 105.5328 | 105.6184 | 105.704 | 105.7896 | 105.8752 | 105.9608 | 106.0464 | 106.132 | 106.2176 | 106.3032 | 106.3888 | 106.4744 | 106.56 | 106.6456 | 106.7312 | 106.8168 | 106.9024 | 106.988 | 106.988 | 106.988 | 106.988 | 106.988 | 106.988 | 106.988 | 106.988 | 106.988 | 106.988 | 106.988 | 106.988 | 106.988 | 106.988 | 106.988 | 106.988 | 106.988 | 106.988 | 106.988 | 106.988 | 106.988 | 106.988 | 106.988 | 106.988 | 106.988 | 106.988 | 106.988 | 106.988 | 106.988 | 106.988 | 106.988 | 106.898 | 106.808 | 106.718 | 106.628 | 106.538 | 106.448 | 106.358 | 106.268 | 106.178 | 106.088 | 105.998 | 105.908 | 105.818 | 105.728 | 105.638 | 105.548 | 105.458 | 105.368 | 105.278 | 105.188 | 105.098 | 105.008 | 104.918 | 104.828 | 104.738 | 104.648 | 104.558 | 104.468 | 104.378 | 104.288
10.65 | 0 | 3.507 | 7.014 | 10.521 | 14.028 | 17.535 | 21.042 | 24.549 | 28.056 | 31.563 | 35.07 | 39.9679 | 44.8657 | 49.7636 | 54.6615 | 59.5593 | 60.0389 | 60.5184 | 60.9979 | 61.4775 | 61.957 | 63.2706 | 64.5843 | 65.8979 | 67.2115 | 68.5252 | 69.8388 | 71.1524 | 72.4661 | 73.7797 | 75.0933 | 75.9691 | 76.8448 | 77.7206 | 78.5964 | 79.4721 | 80.3479 | 81.2236 | 82.0994 | 82.9751 | 83.8509 | 84.7266 | 85.6024 | 86.4782 | 87.3539 | 88.2297 | 88.968 | 89.7064 | 90.4448 | 91.1832 | 91.9216 | 92.6599 | 93.3983 | 94.1367 | 94.8751 | 95.6134 | 96.3518 | 97.0902 | 97.8286 | 98.567 | 99.3053 | 99.5187 | 99.732 | 99.9453 | 100.1586 | 100.3719 | 100.5853 | 100.7986 | 101.0119 | 101.2252 | 101.4386 | 101.6519 | 101.8652 | 102.0785 | 102.2918 | 102.5052 | 102.7185 | 102.9318 | 103.1451 | 103.3585 | 103.5718 | 103.7851 | 103.9984 | 104.2117 | 104.4251 | 104.6384 | 104.8517 | 105.065 | 105.2784 | 105.4917 | 105.705 | 105.7922 | 105.8794 | 105.9665 | 106.0537 | 106.1409 | 106.2281 | 106.3152 | 106.4024 | 106.4896 | 106.5768 | 106.664 | 106.7511 | 106.8383 | 106.9255 | 107.0127 | 107.0998 | 107.187 | 107.2742 | 107.3614 | 107.4486 | 107.5357 | 107.6229 | 107.7101 | 107.7973 | 107.8844 | 107.9716 | 108.0588 | 108.146 | 108.2332 | 108.3203 | 108.3203 | 108.3203 | 108.3203 | 108.3203 | 108.3203 | 108.3203 | 108.3203 | 108.3203 | 108.3203 | 108.3203 | 108.3203 | 108.3203 | 108.3203 | 108.3203 | 108.3203 | 108.3203 | 108.3203 | 108.3203 | 108.3203 | 108.3203 | 108.3203 | 108.3203 | 108.3203 | 108.3203 | 108.3203 | 108.3203 | 108.3203 | 108.3203 | 108.3203 | 108.3203 | 108.2312 | 108.142 | 108.0528 | 107.9637 | 107.8745 | 107.7853 | 107.6962 | 107.607 | 107.5178 | 107.4287 | 107.3395 | 107.2503 | 107.1612 | 107.072 | 106.9828 | 106.8937 | 106.8045 | 106.7153 | 106.6262 | 106.537 | 106.4478 | 106.3587 | 106.2695 | 106.1803 | 106.0912 | 106.002 | 105.9128 | 105.8237 | 105.7345 | 105.6453
10.7 | 0 | 3.546 | 7.092 | 10.638 | 14.184 | 17.73 | 21.276 | 24.822 | 28.368 | 31.914 | 35.46 | 40.4269 | 45.3939 | 50.3608 | 55.3277 | 60.2947 | 60.7649 | 61.2352 | 61.7055 | 62.1757 | 62.646 | 63.9761 | 65.3061 | 66.6362 | 67.9663 | 69.2963 | 70.6264 | 71.9565 | 73.2865 | 74.6166 | 75.9467 | 76.8334 | 77.7201 | 78.6068 | 79.4935 | 80.3802 | 81.2669 | 82.1536 | 83.0404 | 83.9271 | 84.8138 | 85.7005 | 86.5872 | 87.4739 | 88.3606 | 89.2473 | 89.9964 | 90.7454 | 91.4944 | 92.2434 | 92.9924 | 93.7415 | 94.4905 | 95.2395 | 95.9885 | 96.7376 | 97.4866 | 98.2356 | 98.9846 | 99.7336 | 100.4827 | 100.6996 | 100.9165 | 101.1334 | 101.3503 | 101.5672 | 101.7841 | 102.001 | 102.218 | 102.4349 | 102.6518 | 102.8687 | 103.0856 | 103.3025 | 103.5194 | 103.7363 | 103.9532 | 104.1702 | 104.3871 | 104.604 | 104.8209 | 105.0378 | 105.2547 | 105.4716 | 105.6885 | 105.9054 | 106.1224 | 106.3393 | 106.5562 | 106.7731 | 106.99 | 107.0788 | 107.1675 | 107.2563 | 107.345 | 107.4338 | 107.5225 | 107.6113 | 107.7 | 107.7888 | 107.8776 | 107.9663 | 108.0551 | 108.1438 | 108.2326 | 108.3213 | 108.4101 | 108.4988 | 108.5876 | 108.6764 | 108.7651 | 108.8539 | 108.9426 | 109.0314 | 109.1201 | 109.2089 | 109.2976 | 109.3864 | 109.4752 | 109.5639 | 109.6527 | 109.6527 | 109.6527 | 109.6527 | 109.6527 | 109.6527 | 109.6527 | 109.6527 | 109.6527 | 109.6527 | 109.6527 | 109.6527 | 109.6527 | 109.6527 | 109.6527 | 109.6527 | 109.6527 | 109.6527 | 109.6527 | 109.6527 | 109.6527 | 109.6527 | 109.6527 | 109.6527 | 109.6527 | 109.6527 | 109.6527 | 109.6527 | 109.6527 | 109.6527 | 109.6527 | 109.5643 | 109.476 | 109.3877 | 109.2993 | 109.211 | 109.1227 | 109.0343 | 108.946 | 108.8577 | 108.7693 | 108.681 | 108.5927 | 108.5043 | 108.416 | 108.3277 | 108.2393 | 108.151 | 108.0627 | 107.9743 | 107.886 | 107.7977 | 107.7093 | 107.621 | 107.5327 | 107.4443 | 107.356 | 107.2677 | 107.1793 | 107.091 | 107.0027
10.75 | 0 | 3.585 | 7.17 | 10.755 | 14.34 | 17.925 | 21.51 | 25.095 | 28.68 | 32.265 | 35.85 | 40.886 | 45.922 | 50.958 | 55.994 | 61.03 | 61.491 | 61.952 | 62.413 | 62.874 | 63.335 | 64.6815 | 66.028 | 67.3745 | 68.721 | 70.0675 | 71.414 | 72.7605 | 74.107 | 75.4535 | 76.8 | 77.6977 | 78.5953 | 79.493 | 80.3907 | 81.2883 | 82.186 | 83.0837 | 83.9813 | 84.879 | 85.7767 | 86.6743 | 87.572 | 88.4697 | 89.3673 | 90.265 | 91.0247 | 91.7843 | 92.544 | 93.3037 | 94.0633 | 94.823 | 95.5827 | 96.3423 | 97.102 | 97.8617 | 98.6213 | 99.381 | 100.1407 | 100.9003 | 101.66 | 101.8805 | 102.101 | 102.3215 | 102.542 | 102.7625 | 102.983 | 103.2035 | 103.424 | 103.6445 | 103.865 | 104.0855 | 104.306 | 104.5265 | 104.747 | 104.9675 | 105.188 | 105.4085 | 105.629 | 105.8495 | 106.07 | 106.2905 | 106.511 | 106.7315 | 106.952 | 107.1725 | 107.393 | 107.6135 | 107.834 | 108.0545 | 108.275 | 108.3653 | 108.4557 | 108.546 | 108.6363 | 108.7267 | 108.817 | 108.9073 | 108.9977 | 109.088 | 109.1783 | 109.2687 | 109.359 | 109.4493 | 109.5397 | 109.63 | 109.7203 | 109.8107 | 109.901 | 109.9913 | 110.0817 | 110.172 | 110.2623 | 110.3527 | 110.443 | 110.5333 | 110.6237 | 110.714 | 110.8043 | 110.8947 | 110.985 | 110.985 | 110.985 | 110.985 | 110.985 | 110.985 | 110.985 | 110.985 | 110.985 | 110.985 | 110.985 | 110.985 | 110.985 | 110.985 | 110.985 | 110.985 | 110.985 | 110.985 | 110.985 | 110.985 | 110.985 | 110.985 | 110.985 | 110.985 | 110.985 | 110.985 | 110.985 | 110.985 | 110.985 | 110.985 | 110.985 | 110.8975 | 110.81 | 110.7225 | 110.635 | 110.5475 | 110.46 | 110.3725 | 110.285 | 110.1975 | 110.11 | 110.0225 | 109.935 | 109.8475 | 109.76 | 109.6725 | 109.585 | 109.4975 | 109.41 | 109.3225 | 109.235 | 109.1475 | 109.06 | 108.9725 | 108.885 | 108.7975 | 108.71 | 108.6225 | 108.535 | 108.4475 | 108.36
10.8 | 0 | 3.624 | 7.248 | 10.872 | 14.496 | 18.12 | 21.744 | 25.368 | 28.992 | 32.616 | 36.24 | 41.3451 | 46.4501 | 51.5552 | 56.6603 | 61.7653 | 62.2171 | 62.6688 | 63.1205 | 63.5723 | 64.024 | 65.3869 | 66.7499 | 68.1128 | 69.4757 | 70.8387 | 72.2016 | 73.5645 | 74.9275 | 76.2904 | 77.6533 | 78.562 | 79.4706 | 80.3792 | 81.2878 | 82.1964 | 83.1051 | 84.0137 | 84.9223 | 85.8309 | 86.7396 | 87.6482 | 88.5568 | 89.4654 | 90.374 | 91.2827 | 92.053 | 92.8233 | 93.5936 | 94.3639 | 95.1342 | 95.9045 | 96.6748 | 97.4452 | 98.2155 | 98.9858 | 99.7561 | 100.5264 | 101.2967 | 102.067 | 102.8373 | 103.0614 | 103.2855 | 103.5096 | 103.7337 | 103.9578 | 104.1819 | 104.406 | 104.63 | 104.8541 | 105.0782 | 105.3023 | 105.5264 | 105.7505 | 105.9746 | 106.1987 | 106.4228 | 106.6468 | 106.8709 | 107.095 | 107.3191 | 107.5432 | 107.7673 | 107.9914 | 108.2155 | 108.4396 | 108.6636 | 108.8877 | 109.1118 | 109.3359 | 109.56 | 109.6519 | 109.7438 | 109.8357 | 109.9276 | 110.0196 | 110.1115 | 110.2034 | 110.2953 | 110.3872 | 110.4791 | 110.571 | 110.6629 | 110.7548 | 110.8468 | 110.9387 | 111.0306 | 111.1225 | 111.2144 | 111.3063 | 111.3982 | 111.4901 | 111.582 | 111.674 | 111.7659 | 111.8578 | 111.9497 | 112.0416 | 112.1335 | 112.2254 | 112.3173 | 112.3173 | 112.3173 | 112.3173 | 112.3173 | 112.3173 | 112.3173 | 112.3173 | 112.3173 | 112.3173 | 112.3173 | 112.3173 | 112.3173 | 112.3173 | 112.3173 | 112.3173 | 112.3173 | 112.3173 | 112.3173 | 112.3173 | 112.3173 | 112.3173 | 112.3173 | 112.3173 | 112.3173 | 112.3173 | 112.3173 | 112.3173 | 112.3173 | 112.3173 | 112.3173 | 112.2307 | 112.144 | 112.0573 | 111.9707 | 111.884 | 111.7973 | 111.7107 | 111.624 | 111.5373 | 111.4507 | 111.364 | 111.2773 | 111.1907 | 111.104 | 111.0173 | 110.9307 | 110.844 | 110.7573 | 110.6707 | 110.584 | 110.4973 | 110.4107 | 110.324 | 110.2373 | 110.1507 | 110.064 | 109.9773 | 109.8907 | 109.804 | 109.7173
10.85 | 0 | 3.663 | 7.326 | 10.989 | 14.652 | 18.315 | 21.978 | 25.641 | 29.304 | 32.967 | 36.63 | 41.8041 | 46.9783 | 52.1524 | 57.3265 | 62.5007 | 62.9431 | 63.3856 | 63.8281 | 64.2705 | 64.713 | 66.0924 | 67.4717 | 68.8511 | 70.2305 | 71.6098 | 72.9892 | 74.3686 | 75.7479 | 77.1273 | 78.5067 | 79.4262 | 80.3458 | 81.2654 | 82.185 | 83.1046 | 84.0241 | 84.9437 | 85.8633 | 86.7829 | 87.7024 | 88.622 | 89.5416 | 90.4612 | 91.3808 | 92.3003 | 93.0813 | 93.8622 | 94.6432 | 95.4242 | 96.2051 | 96.9861 | 97.767 | 98.548 | 99.3289 | 100.1099 | 100.8908 | 101.6718 | 102.4528 | 103.2337 | 104.0147 | 104.2423 | 104.47 | 104.6977 | 104.9254 | 105.1531 | 105.3807 | 105.6084 | 105.8361 | 106.0638 | 106.2914 | 106.5191 | 106.7468 | 106.9745 | 107.2022 | 107.4298 | 107.6575 | 107.8852 | 108.1129 | 108.3405 | 108.5682 | 108.7959 | 109.0236 | 109.2513 | 109.4789 | 109.7066 | 109.9343 | 110.162 | 110.3896 | 110.6173 | 110.845 | 110.9385 | 111.032 | 111.1255 | 111.219 | 111.3124 | 111.4059 | 111.4994 | 111.5929 | 111.6864 | 111.7799 | 111.8734 | 111.9669 | 112.0604 | 112.1538 | 112.2473 | 112.3408 | 112.4343 | 112.5278 | 112.6213 | 112.7148 | 112.8083 | 112.9018 | 112.9952 | 113.0887 | 113.1822 | 113.2757 | 113.3692 | 113.4627 | 113.5562 | 113.6497 | 113.6497 | 113.6497 | 113.6497 | 113.6497 | 113.6497 | 113.6497 | 113.6497 | 113.6497 | 113.6497 | 113.6497 | 113.6497 | 113.6497 | 113.6497 | 113.6497 | 113.6497 | 113.6497 | 113.6497 | 113.6497 | 113.6497 | 113.6497 | 113.6497 | 113.6497 | 113.6497 | 113.6497 | 113.6497 | 113.6497 | 113.6497 | 113.6497 | 113.6497 | 113.6497 | 113.5638 | 113.478 | 113.3922 | 113.3063 | 113.2205 | 113.1347 | 113.0488 | 112.963 | 112.8772 | 112.7913 | 112.7055 | 112.6197 | 112.5338 | 112.448 | 112.3622 | 112.2763 | 112.1905 | 112.1047 | 112.0188 | 111.933 | 111.8472 | 111.7613 | 111.6755 | 111.5897 | 111.5038 | 111.418 | 111.3322 | 111.2463 | 111.1605 | 111.0747
10.9 | 0 | 3.702 | 7.404 | 11.106 | 14.808 | 18.51 | 22.212 | 25.914 | 29.616 | 33.318 | 37.02 | 42.2632 | 47.5064 | 52.7496 | 57.9928 | 63.236 | 63.6692 | 64.1024 | 64.5356 | 64.9688 | 65.402 | 66.7978 | 68.1936 | 69.5894 | 70.9852 | 72.381 | 73.7768 | 75.1726 | 76.5684 | 77.9642 | 79.36 | 80.2905 | 81.2211 | 82.1516 | 83.0821 | 84.0127 | 84.9432 | 85.8737 | 86.8043 | 87.7348 | 88.6653 | 89.5959 | 90.5264 | 91.4569 | 92.3875 | 93.318 | 94.1096 | 94.9012 | 95.6928 | 96.4844 | 97.276 | 98.0676 | 98.8592 | 99.6508 | 100.4424 | 101.234 | 102.0256 | 102.8172 | 103.6088 | 104.4004 | 105.192 | 105.4233 | 105.6545 | 105.8858 | 106.1171 | 106.3483 | 106.5796 | 106.8109 | 107.0421 | 107.2734 | 107.5047 | 107.7359 | 107.9672 | 108.1985 | 108.4297 | 108.661 | 108.8923 | 109.1235 | 109.3548 | 109.5861 | 109.8173 | 110.0486 | 110.2799 | 110.5111 | 110.7424 | 110.9737 | 111.2049 | 111.4362 | 111.6675 | 111.8987 | 112.13 | 112.2251 | 112.3201 | 112.4152 | 112.5103 | 112.6053 | 112.7004 | 112.7955 | 112.8905 | 112.9856 | 113.0807 | 113.1757 | 113.2708 | 113.3659 | 113.4609 | 113.556 | 113.6511 | 113.7461 | 113.8412 | 113.9363 | 114.0313 | 114.1264 | 114.2215 | 114.3165 | 114.4116 | 114.5067 | 114.6017 | 114.6968 | 114.7919 | 114.8869 | 114.982 | 114.982 | 114.982 | 114.982 | 114.982 | 114.982 | 114.982 | 114.982 | 114.982 | 114.982 | 114.982 | 114.982 | 114.982 | 114.982 | 114.982 | 114.982 | 114.982 | 114.982 | 114.982 | 114.982 | 114.982 | 114.982 | 114.982 | 114.982 | 114.982 | 114.982 | 114.982 | 114.982 | 114.982 | 114.982 | 114.982 | 114.897 | 114.812 | 114.727 | 114.642 | 114.557 | 114.472 | 114.387 | 114.302 | 114.217 | 114.132 | 114.047 | 113.962 | 113.877 | 113.792 | 113.707 | 113.622 | 113.537 | 113.452 | 113.367 | 113.282 | 113.197 | 113.112 | 113.027 | 112.942 | 112.857 | 112.772 | 112.687 | 112.602 | 112.517 | 112.432
10.95 | 0 | 3.741 | 7.482 | 11.223 | 14.964 | 18.705 | 22.446 | 26.187 | 29.928 | 33.669 | 37.41 | 42.7223 | 48.0345 | 53.3468 | 58.6591 | 63.9713 | 64.3953 | 64.8192 | 65.2431 | 65.6671 | 66.091 | 67.5032 | 68.9155 | 70.3277 | 71.7399 | 73.1522 | 74.5644 | 75.9766 | 77.3889 | 78.8011 | 80.2133 | 81.1548 | 82.0963 | 83.0378 | 83.9793 | 84.9208 | 85.8623 | 86.8038 | 87.7452 | 88.6867 | 89.6282 | 90.5697 | 91.5112 | 92.4527 | 93.3942 | 94.3357 | 95.1379 | 95.9402 | 96.7424 | 97.5446 | 98.3469 | 99.1491 | 99.9514 | 100.7536 | 101.5559 | 102.3581 | 103.1604 | 103.9626 | 104.7648 | 105.5671 | 106.3693 | 106.6042 | 106.839 | 107.0739 | 107.3088 | 107.5436 | 107.7785 | 108.0133 | 108.2482 | 108.483 | 108.7179 | 108.9527 | 109.1876 | 109.4225 | 109.6573 | 109.8922 | 110.127 | 110.3619 | 110.5967 | 110.8316 | 111.0664 | 111.3013 | 111.5362 | 111.771 | 112.0059 | 112.2407 | 112.4756 | 112.7104 | 112.9453 | 113.1801 | 113.415 | 113.5116 | 113.6083 | 113.7049 | 113.8016 | 113.8982 | 113.9949 | 114.0915 | 114.1882 | 114.2848 | 114.3814 | 114.4781 | 114.5747 | 114.6714 | 114.768 | 114.8647 | 114.9613 | 115.058 | 115.1546 | 115.2512 | 115.3479 | 115.4445 | 115.5412 | 115.6378 | 115.7345 | 115.8311 | 115.9278 | 116.0244 | 116.121 | 116.2177 | 116.3143 | 116.3143 | 116.3143 | 116.3143 | 116.3143 | 116.3143 | 116.3143 | 116.3143 | 116.3143 | 116.3143 | 116.3143 | 116.3143 | 116.3143 | 116.3143 | 116.3143 | 116.3143 | 116.3143 | 116.3143 | 116.3143 | 116.3143 | 116.3143 | 116.3143 | 116.3143 | 116.3143 | 116.3143 | 116.3143 | 116.3143 | 116.3143 | 116.3143 | 116.3143 | 116.3143 | 116.2302 | 116.146 | 116.0618 | 115.9777 | 115.8935 | 115.8093 | 115.7252 | 115.641 | 115.5568 | 115.4727 | 115.3885 | 115.3043 | 115.2202 | 115.136 | 115.0518 | 114.9677 | 114.8835 | 114.7993 | 114.7152 | 114.631 | 114.5468 | 114.4627 | 114.3785 | 114.2943 | 114.2102 | 114.126 | 114.0418 | 113.9577 | 113.8735 | 113.7893
11 | 0 | 3.78 | 7.56 | 11.34 | 15.12 | 18.9 | 22.68 | 26.46 | 30.24 | 34.02 | 37.8 | 43.1813 | 48.5627 | 53.944 | 59.3253 | 64.7067 | 65.1213 | 65.536 | 65.9507 | 66.3653 | 66.78 | 68.2087 | 69.6373 | 71.066 | 72.4947 | 73.9233 | 75.352 | 76.7807 | 78.2093 | 79.638 | 81.0667 | 82.0191 | 82.9716 | 83.924 | 84.8764 | 85.8289 | 86.7813 | 87.7338 | 88.6862 | 89.6387 | 90.5911 | 91.5436 | 92.496 | 93.4484 | 94.4009 | 95.3533 | 96.1662 | 96.9791 | 97.792 | 98.6049 | 99.4178 | 100.2307 | 101.0436 | 101.8564 | 102.6693 | 103.4822 | 104.2951 | 105.108 | 105.9209 | 106.7338 | 107.5467 | 107.7851 | 108.0236 | 108.262 | 108.5004 | 108.7389 | 108.9773 | 109.2158 | 109.4542 | 109.6927 | 109.9311 | 110.1696 | 110.408 | 110.6464 | 110.8849 | 111.1233 | 111.3618 | 111.6002 | 111.8387 | 112.0771 | 112.3156 | 112.554 | 112.7924 | 113.0309 | 113.2693 | 113.5078 | 113.7462 | 113.9847 | 114.2231 | 114.4616 | 114.7 | 114.7982 | 114.8964 | 114.9947 | 115.0929 | 115.1911 | 115.2893 | 115.3876 | 115.4858 | 115.584 | 115.6822 | 115.7804 | 115.8787 | 115.9769 | 116.0751 | 116.1733 | 116.2716 | 116.3698 | 116.468 | 116.5662 | 116.6644 | 116.7627 | 116.8609 | 116.9591 | 117.0573 | 117.1556 | 117.2538 | 117.352 | 117.4502 | 117.5484 | 117.6467 | 117.6467 | 117.6467 | 117.6467 | 117.6467 | 117.6467 | 117.6467 | 117.6467 | 117.6467 | 117.6467 | 117.6467 | 117.6467 | 117.6467 | 117.6467 | 117.6467 | 117.6467 | 117.6467 | 117.6467 | 117.6467 | 117.6467 | 117.6467 | 117.6467 | 117.6467 | 117.6467 | 117.6467 | 117.6467 | 117.6467 | 117.6467 | 117.6467 | 117.6467 | 117.6467 | 117.5633 | 117.48 | 117.3967 | 117.3133 | 117.23 | 117.1467 | 117.0633 | 116.98 | 116.8967 | 116.8133 | 116.73 | 116.6467 | 116.5633 | 116.48 | 116.3967 | 116.3133 | 116.23 | 116.1467 | 116.0633 | 115.98 | 115.8967 | 115.8133 | 115.73 | 115.6467 | 115.5633 | 115.48 | 115.3967 | 115.3133 | 115.23 | 115.1467
11.05 | 0 | 3.819 | 7.638 | 11.457 | 15.276 | 19.095 | 22.914 | 26.733 | 30.552 | 34.371 | 38.19 | 43.6404 | 49.0908 | 54.5412 | 59.9916 | 65.442 | 65.8474 | 66.2528 | 66.6582 | 67.0636 | 67.469 | 68.9141 | 70.3592 | 71.8043 | 73.2494 | 74.6945 | 76.1396 | 77.5847 | 79.0298 | 80.4749 | 81.92 | 82.8834 | 83.8468 | 84.8102 | 85.7736 | 86.737 | 87.7004 | 88.6638 | 89.6272 | 90.5906 | 91.554 | 92.5174 | 93.4808 | 94.4442 | 95.4076 | 96.371 | 97.1945 | 98.0181 | 98.8416 | 99.6651 | 100.4887 | 101.3122 | 102.1357 | 102.9593 | 103.7828 | 104.6063 | 105.4299 | 106.2534 | 107.0769 | 107.9005 | 108.724 | 108.966 | 109.2081 | 109.4501 | 109.6921 | 109.9342 | 110.1762 | 110.4182 | 110.6603 | 110.9023 | 111.1443 | 111.3864 | 111.6284 | 111.8704 | 112.1125 | 112.3545 | 112.5965 | 112.8386 | 113.0806 | 113.3226 | 113.5647 | 113.8067 | 114.0487 | 114.2908 | 114.5328 | 114.7748 | 115.0169 | 115.2589 | 115.5009 | 115.743 | 115.985 | 116.0848 | 116.1846 | 116.2844 | 116.3842 | 116.484 | 116.5838 | 116.6836 | 116.7834 | 116.8832 | 116.983 | 117.0828 | 117.1826 | 117.2824 | 117.3822 | 117.482 | 117.5818 | 117.6816 | 117.7814 | 117.8812 | 117.981 | 118.0808 | 118.1806 | 118.2804 | 118.3802 | 118.48 | 118.5798 | 118.6796 | 118.7794 | 118.8792 | 118.979 | 118.979 | 118.979 | 118.979 | 118.979 | 118.979 | 118.979 | 118.979 | 118.979 | 118.979 | 118.979 | 118.979 | 118.979 | 118.979 | 118.979 | 118.979 | 118.979 | 118.979 | 118.979 | 118.979 | 118.979 | 118.979 | 118.979 | 118.979 | 118.979 | 118.979 | 118.979 | 118.979 | 118.979 | 118.979 | 118.979 | 118.8965 | 118.814 | 118.7315 | 118.649 | 118.5665 | 118.484 | 118.4015 | 118.319 | 118.2365 | 118.154 | 118.0715 | 117.989 | 117.9065 | 117.824 | 117.7415 | 117.659 | 117.5765 | 117.494 | 117.4115 | 117.329 | 117.2465 | 117.164 | 117.0815 | 116.999 | 116.9165 | 116.834 | 116.7515 | 116.669 | 116.5865 | 116.504
11.1 | 0 | 3.858 | 7.716 | 11.574 | 15.432 | 19.29 | 23.148 | 27.006 | 30.864 | 34.722 | 38.58 | 44.0995 | 49.6189 | 55.1384 | 60.6579 | 66.1773 | 66.5735 | 66.9696 | 67.3657 | 67.7619 | 68.158 | 69.6195 | 71.0811 | 72.5426 | 74.0041 | 75.4657 | 76.9272 | 78.3887 | 79.8503 | 81.3118 | 82.7733 | 83.7477 | 84.722 | 85.6964 | 86.6708 | 87.6451 | 88.6195 | 89.5938 | 90.5682 | 91.5425 | 92.5169 | 93.4912 | 94.4656 | 95.44 | 96.4143 | 97.3887 | 98.2228 | 99.057 | 99.8912 | 100.7254 | 101.5596 | 102.3937 | 103.2279 | 104.0621 | 104.8963 | 105.7304 | 106.5646 | 107.3988 | 108.233 | 109.0672 | 109.9013 | 110.147 | 110.3926 | 110.6382 | 110.8838 | 111.1294 | 111.3751 | 111.6207 | 111.8663 | 112.1119 | 112.3576 | 112.6032 | 112.8488 | 113.0944 | 113.34 | 113.5857 | 113.8313 | 114.0769 | 114.3225 | 114.5682 | 114.8138 | 115.0594 | 115.305 | 115.5506 | 115.7963 | 116.0419 | 116.2875 | 116.5331 | 116.7788 | 117.0244 | 117.27 | 117.3714 | 117.4728 | 117.5741 | 117.6755 | 117.7769 | 117.8783 | 117.9796 | 118.081 | 118.1824 | 118.2838 | 118.3852 | 118.4865 | 118.5879 | 118.6893 | 118.7907 | 118.892 | 118.9934 | 119.0948 | 119.1962 | 119.2976 | 119.3989 | 119.5003 | 119.6017 | 119.7031 | 119.8044 | 119.9058 | 120.0072 | 120.1086 | 120.21 | 120.3113 | 120.3113 | 120.3113 | 120.3113 | 120.3113 | 120.3113 | 120.3113 | 120.3113 | 120.3113 | 120.3113 | 120.3113 | 120.3113 | 120.3113 | 120.3113 | 120.3113 | 120.3113 | 120.3113 | 120.3113 | 120.3113 | 120.3113 | 120.3113 | 120.3113 | 120.3113 | 120.3113 | 120.3113 | 120.3113 | 120.3113 | 120.3113 | 120.3113 | 120.3113 | 120.3113 | 120.2297 | 120.148 | 120.0663 | 119.9847 | 119.903 | 119.8213 | 119.7397 | 119.658 | 119.5763 | 119.4947 | 119.413 | 119.3313 | 119.2497 | 119.168 | 119.0863 | 119.0047 | 118.923 | 118.8413 | 118.7597 | 118.678 | 118.5963 | 118.5147 | 118.433 | 118.3513 | 118.2697 | 118.188 | 118.1063 | 118.0247 | 117.943 | 117.8613
11.15 | 0 | 3.897 | 7.794 | 11.691 | 15.588 | 19.485 | 23.382 | 27.279 | 31.176 | 35.073 | 38.97 | 44.5585 | 50.1471 | 55.7356 | 61.3241 | 66.9127 | 67.2995 | 67.6864 | 68.0733 | 68.4601 | 68.847 | 70.325 | 71.8029 | 73.2809 | 74.7589 | 76.2368 | 77.7148 | 79.1928 | 80.6707 | 82.1487 | 83.6267 | 84.612 | 85.5973 | 86.5826 | 87.5679 | 88.5532 | 89.5385 | 90.5238 | 91.5092 | 92.4945 | 93.4798 | 94.4651 | 95.4504 | 96.4357 | 97.421 | 98.4063 | 99.2512 | 100.096 | 100.9408 | 101.7856 | 102.6304 | 103.4753 | 104.3201 | 105.1649 | 106.0097 | 106.8546 | 107.6994 | 108.5442 | 109.389 | 110.2338 | 111.0787 | 111.3279 | 111.5771 | 111.8263 | 112.0755 | 112.3247 | 112.5739 | 112.8231 | 113.0724 | 113.3216 | 113.5708 | 113.82 | 114.0692 | 114.3184 | 114.5676 | 114.8168 | 115.066 | 115.3153 | 115.5645 | 115.8137 | 116.0629 | 116.3121 | 116.5613 | 116.8105 | 117.0597 | 117.3089 | 117.5582 | 117.8074 | 118.0566 | 118.3058 | 118.555 | 118.658 | 118.7609 | 118.8639 | 118.9668 | 119.0698 | 119.1727 | 119.2757 | 119.3786 | 119.4816 | 119.5846 | 119.6875 | 119.7905 | 119.8934 | 119.9964 | 120.0993 | 120.2023 | 120.3052 | 120.4082 | 120.5112 | 120.6141 | 120.7171 | 120.82 | 120.923 | 121.0259 | 121.1289 | 121.2318 | 121.3348 | 121.4378 | 121.5407 | 121.6437 | 121.6437 | 121.6437 | 121.6437 | 121.6437 | 121.6437 | 121.6437 | 121.6437 | 121.6437 | 121.6437 | 121.6437 | 121.6437 | 121.6437 | 121.6437 | 121.6437 | 121.6437 | 121.6437 | 121.6437 | 121.6437 | 121.6437 | 121.6437 | 121.6437 | 121.6437 | 121.6437 | 121.6437 | 121.6437 | 121.6437 | 121.6437 | 121.6437 | 121.6437 | 121.6437 | 121.5628 | 121.482 | 121.4012 | 121.3203 | 121.2395 | 121.1587 | 121.0778 | 120.997 | 120.9162 | 120.8353 | 120.7545 | 120.6737 | 120.5928 | 120.512 | 120.4312 | 120.3503 | 120.2695 | 120.1887 | 120.1078 | 120.027 | 119.9462 | 119.8653 | 119.7845 | 119.7037 | 119.6228 | 119.542 | 119.4612 | 119.3803 | 119.2995 | 119.2187
11.2 | 0 | 3.936 | 7.872 | 11.808 | 15.744 | 19.68 | 23.616 | 27.552 | 31.488 | 35.424 | 39.36 | 45.0176 | 50.6752 | 56.3328 | 61.9904 | 67.648 | 68.0256 | 68.4032 | 68.7808 | 69.1584 | 69.536 | 71.0304 | 72.5248 | 74.0192 | 75.5136 | 77.008 | 78.5024 | 79.9968 | 81.4912 | 82.9856 | 84.48 | 85.4763 | 86.4725 | 87.4688 | 88.4651 | 89.4613 | 90.4576 | 91.4539 | 92.4501 | 93.4464 | 94.4427 | 95.4389 | 96.4352 | 97.4315 | 98.4277 | 99.424 | 100.2795 | 101.1349 | 101.9904 | 102.8459 | 103.7013 | 104.5568 | 105.4123 | 106.2677 | 107.1232 | 107.9787 | 108.8341 | 109.6896 | 110.5451 | 111.4005 | 112.256 | 112.5088 | 112.7616 | 113.0144 | 113.2672 | 113.52 | 113.7728 | 114.0256 | 114.2784 | 114.5312 | 114.784 | 115.0368 | 115.2896 | 115.5424 | 115.7952 | 116.048 | 116.3008 | 116.5536 | 116.8064 | 117.0592 | 117.312 | 117.5648 | 117.8176 | 118.0704 | 118.3232 | 118.576 | 118.8288 | 119.0816 | 119.3344 | 119.5872 | 119.84 | 119.9445 | 120.0491 | 120.1536 | 120.2581 | 120.3627 | 120.4672 | 120.5717 | 120.6763 | 120.7808 | 120.8853 | 120.9899 | 121.0944 | 121.1989 | 121.3035 | 121.408 | 121.5125 | 121.6171 | 121.7216 | 121.8261 | 121.9307 | 122.0352 | 122.1397 | 122.2443 | 122.3488 | 122.4533 | 122.5579 | 122.6624 | 122.7669 | 122.8715 | 122.976 | 122.976 | 122.976 | 122.976 | 122.976 | 122.976 | 122.976 | 122.976 | 122.976 | 122.976 | 122.976 | 122.976 | 122.976 | 122.976 | 122.976 | 122.976 | 122.976 | 122.976 | 122.976 | 122.976 | 122.976 | 122.976 | 122.976 | 122.976 | 122.976 | 122.976 | 122.976 | 122.976 | 122.976 | 122.976 | 122.976 | 122.896 | 122.816 | 122.736 | 122.656 | 122.576 | 122.496 | 122.416 | 122.336 | 122.256 | 122.176 | 122.096 | 122.016 | 121.936 | 121.856 | 121.776 | 121.696 | 121.616 | 121.536 | 121.456 | 121.376 | 121.296 | 121.216 | 121.136 | 121.056 | 120.976 | 120.896 | 120.816 | 120.736 | 120.656 | 120.576
11.25 | 0 | 3.975 | 7.95 | 11.925 | 15.9 | 19.875 | 23.85 | 27.825 | 31.8 | 35.775 | 39.75 | 45.4767 | 51.2033 | 56.93 | 62.6567 | 68.3833 | 68.7517 | 69.12 | 69.4883 | 69.8567 | 70.225 | 71.7358 | 73.2467 | 74.7575 | 76.2683 | 77.7792 | 79.29 | 80.8008 | 82.3117 | 83.8225 | 85.3333 | 86.3406 | 87.3478 | 88.355 | 89.3622 | 90.3694 | 91.3767 | 92.3839 | 93.3911 | 94.3983 | 95.4056 | 96.4128 | 97.42 | 98.4272 | 99.4344 | 100.4417 | 101.3078 | 102.1739 | 103.04 | 103.9061 | 104.7722 | 105.6383 | 106.5044 | 107.3706 | 108.2367 | 109.1028 | 109.9689 | 110.835 | 111.7011 | 112.5672 | 113.4333 | 113.6897 | 113.9461 | 114.2025 | 114.4589 | 114.7153 | 114.9717 | 115.2281 | 115.4844 | 115.7408 | 115.9972 | 116.2536 | 116.51 | 116.7664 | 117.0228 | 117.2792 | 117.5356 | 117.7919 | 118.0483 | 118.3047 | 118.5611 | 118.8175 | 119.0739 | 119.3303 | 119.5867 | 119.8431 | 120.0994 | 120.3558 | 120.6122 | 120.8686 | 121.125 | 121.2311 | 121.3372 | 121.4433 | 121.5494 | 121.6556 | 121.7617 | 121.8678 | 121.9739 | 122.08 | 122.1861 | 122.2922 | 122.3983 | 122.5044 | 122.6106 | 122.7167 | 122.8228 | 122.9289 | 123.035 | 123.1411 | 123.2472 | 123.3533 | 123.4594 | 123.5656 | 123.6717 | 123.7778 | 123.8839 | 123.99 | 124.0961 | 124.2022 | 124.3083 | 124.3083 | 124.3083 | 124.3083 | 124.3083 | 124.3083 | 124.3083 | 124.3083 | 124.3083 | 124.3083 | 124.3083 | 124.3083 | 124.3083 | 124.3083 | 124.3083 | 124.3083 | 124.3083 | 124.3083 | 124.3083 | 124.3083 | 124.3083 | 124.3083 | 124.3083 | 124.3083 | 124.3083 | 124.3083 | 124.3083 | 124.3083 | 124.3083 | 124.3083 | 124.3083 | 124.2292 | 124.15 | 124.0708 | 123.9917 | 123.9125 | 123.8333 | 123.7542 | 123.675 | 123.5958 | 123.5167 | 123.4375 | 123.3583 | 123.2792 | 123.2 | 123.1208 | 123.0417 | 122.9625 | 122.8833 | 122.8042 | 122.725 | 122.6458 | 122.5667 | 122.4875 | 122.4083 | 122.3292 | 122.25 | 122.1708 | 122.0917 | 122.0125 | 121.9333
11.3 | 0 | 4.014 | 8.028 | 12.042 | 16.056 | 20.07 | 24.084 | 28.098 | 32.112 | 36.126 | 40.14 | 45.9357 | 51.7315 | 57.5272 | 63.3229 | 69.1187 | 69.4777 | 69.8368 | 70.1959 | 70.5549 | 70.914 | 72.4413 | 73.9685 | 75.4958 | 77.0231 | 78.5503 | 80.0776 | 81.6049 | 83.1321 | 84.6594 | 86.1867 | 87.2048 | 88.223 | 89.2412 | 90.2594 | 91.2776 | 92.2957 | 93.3139 | 94.3321 | 95.3503 | 96.3684 | 97.3866 | 98.4048 | 99.423 | 100.4412 | 101.4593 | 102.3361 | 103.2128 | 104.0896 | 104.9664 | 105.8431 | 106.7199 | 107.5966 | 108.4734 | 109.3501 | 110.2269 | 111.1036 | 111.9804 | 112.8572 | 113.7339 | 114.6107 | 114.8706 | 115.1306 | 115.3906 | 115.6506 | 115.9106 | 116.1705 | 116.4305 | 116.6905 | 116.9505 | 117.2104 | 117.4704 | 117.7304 | 117.9904 | 118.2504 | 118.5103 | 118.7703 | 119.0303 | 119.2903 | 119.5502 | 119.8102 | 120.0702 | 120.3302 | 120.5902 | 120.8501 | 121.1101 | 121.3701 | 121.6301 | 121.89 | 122.15 | 122.41 | 122.5177 | 122.6254 | 122.7331 | 122.8408 | 122.9484 | 123.0561 | 123.1638 | 123.2715 | 123.3792 | 123.4869 | 123.5946 | 123.7023 | 123.81 | 123.9176 | 124.0253 | 124.133 | 124.2407 | 124.3484 | 124.4561 | 124.5638 | 124.6715 | 124.7792 | 124.8868 | 124.9945 | 125.1022 | 125.2099 | 125.3176 | 125.4253 | 125.533 | 125.6407 | 125.6407 | 125.6407 | 125.6407 | 125.6407 | 125.6407 | 125.6407 | 125.6407 | 125.6407 | 125.6407 | 125.6407 | 125.6407 | 125.6407 | 125.6407 | 125.6407 | 125.6407 | 125.6407 | 125.6407 | 125.6407 | 125.6407 | 125.6407 | 125.6407 | 125.6407 | 125.6407 | 125.6407 | 125.6407 | 125.6407 | 125.6407 | 125.6407 | 125.6407 | 125.6407 | 125.5623 | 125.484 | 125.4057 | 125.3273 | 125.249 | 125.1707 | 125.0923 | 125.014 | 124.9357 | 124.8573 | 124.779 | 124.7007 | 124.6223 | 124.544 | 124.4657 | 124.3873 | 124.309 | 124.2307 | 124.1523 | 124.074 | 123.9957 | 123.9173 | 123.839 | 123.7607 | 123.6823 | 123.604 | 123.5257 | 123.4473 | 123.369 | 123.2907
11.35 | 0 | 4.053 | 8.106 | 12.159 | 16.212 | 20.265 | 24.318 | 28.371 | 32.424 | 36.477 | 40.53 | 46.3948 | 52.2596 | 58.1244 | 63.9892 | 69.854 | 70.2038 | 70.5536 | 70.9034 | 71.2532 | 71.603 | 73.1467 | 74.6904 | 76.2341 | 77.7778 | 79.3215 | 80.8652 | 82.4089 | 83.9526 | 85.4963 | 87.04 | 88.0691 | 89.0983 | 90.1274 | 91.1565 | 92.1857 | 93.2148 | 94.2439 | 95.2731 | 96.3022 | 97.3313 | 98.3605 | 99.3896 | 100.4187 | 101.4479 | 102.477 | 103.3644 | 104.2518 | 105.1392 | 106.0266 | 106.914 | 107.8014 | 108.6888 | 109.5762 | 110.4636 | 111.351 | 112.2384 | 113.1258 | 114.0132 | 114.9006 | 115.788 | 116.0516 | 116.3151 | 116.5787 | 116.8423 | 117.1058 | 117.3694 | 117.633 | 117.8965 | 118.1601 | 118.4237 | 118.6872 | 118.9508 | 119.2144 | 119.4779 | 119.7415 | 120.0051 | 120.2686 | 120.5322 | 120.7958 | 121.0593 | 121.3229 | 121.5865 | 121.85 | 122.1136 | 122.3772 | 122.6407 | 122.9043 | 123.1679 | 123.4314 | 123.695 | 123.8043 | 123.9135 | 124.0228 | 124.1321 | 124.2413 | 124.3506 | 124.4599 | 124.5691 | 124.6784 | 124.7877 | 124.8969 | 125.0062 | 125.1155 | 125.2247 | 125.334 | 125.4433 | 125.5525 | 125.6618 | 125.7711 | 125.8803 | 125.9896 | 126.0989 | 126.2081 | 126.3174 | 126.4267 | 126.5359 | 126.6452 | 126.7545 | 126.8637 | 126.973 | 126.973 | 126.973 | 126.973 | 126.973 | 126.973 | 126.973 | 126.973 | 126.973 | 126.973 | 126.973 | 126.973 | 126.973 | 126.973 | 126.973 | 126.973 | 126.973 | 126.973 | 126.973 | 126.973 | 126.973 | 126.973 | 126.973 | 126.973 | 126.973 | 126.973 | 126.973 | 126.973 | 126.973 | 126.973 | 126.973 | 126.8955 | 126.818 | 126.7405 | 126.663 | 126.5855 | 126.508 | 126.4305 | 126.353 | 126.2755 | 126.198 | 126.1205 | 126.043 | 125.9655 | 125.888 | 125.8105 | 125.733 | 125.6555 | 125.578 | 125.5005 | 125.423 | 125.3455 | 125.268 | 125.1905 | 125.113 | 125.0355 | 124.958 | 124.8805 | 124.803 | 124.7255 | 124.648
11.4 | 0 | 4.092 | 8.184 | 12.276 | 16.368 | 20.46 | 24.552 | 28.644 | 32.736 | 36.828 | 40.92 | 46.8539 | 52.7877 | 58.7216 | 64.6555 | 70.5893 | 70.9299 | 71.2704 | 71.6109 | 71.9515 | 72.292 | 73.8521 | 75.4123 | 76.9724 | 78.5325 | 80.0927 | 81.6528 | 83.2129 | 84.7731 | 86.3332 | 87.8933 | 88.9334 | 89.9735 | 91.0136 | 92.0537 | 93.0938 | 94.1339 | 95.174 | 96.214 | 97.2541 | 98.2942 | 99.3343 | 100.3744 | 101.4145 | 102.4546 | 103.4947 | 104.3927 | 105.2908 | 106.1888 | 107.0868 | 107.9849 | 108.8829 | 109.781 | 110.679 | 111.5771 | 112.4751 | 113.3732 | 114.2712 | 115.1692 | 116.0673 | 116.9653 | 117.2325 | 117.4996 | 117.7668 | 118.034 | 118.3011 | 118.5683 | 118.8354 | 119.1026 | 119.3697 | 119.6369 | 119.904 | 120.1712 | 120.4384 | 120.7055 | 120.9727 | 121.2398 | 121.507 | 121.7741 | 122.0413 | 122.3084 | 122.5756 | 122.8428 | 123.1099 | 123.3771 | 123.6442 | 123.9114 | 124.1785 | 124.4457 | 124.7128 | 124.98 | 125.0908 | 125.2017 | 125.3125 | 125.4234 | 125.5342 | 125.6451 | 125.7559 | 125.8668 | 125.9776 | 126.0884 | 126.1993 | 126.3101 | 126.421 | 126.5318 | 126.6427 | 126.7535 | 126.8644 | 126.9752 | 127.086 | 127.1969 | 127.3077 | 127.4186 | 127.5294 | 127.6403 | 127.7511 | 127.862 | 127.9728 | 128.0836 | 128.1945 | 128.3053 | 128.3053 | 128.3053 | 128.3053 | 128.3053 | 128.3053 | 128.3053 | 128.3053 | 128.3053 | 128.3053 | 128.3053 | 128.3053 | 128.3053 | 128.3053 | 128.3053 | 128.3053 | 128.3053 | 128.3053 | 128.3053 | 128.3053 | 128.3053 | 128.3053 | 128.3053 | 128.3053 | 128.3053 | 128.3053 | 128.3053 | 128.3053 | 128.3053 | 128.3053 | 128.3053 | 128.2287 | 128.152 | 128.0753 | 127.9987 | 127.922 | 127.8453 | 127.7687 | 127.692 | 127.6153 | 127.5387 | 127.462 | 127.3853 | 127.3087 | 127.232 | 127.1553 | 127.0787 | 127.002 | 126.9253 | 126.8487 | 126.772 | 126.6953 | 126.6187 | 126.542 | 126.4653 | 126.3887 | 126.312 | 126.2353 | 126.1587 | 126.082 | 126.0053
11.45 | 0 | 4.131 | 8.262 | 12.393 | 16.524 | 20.655 | 24.786 | 28.917 | 33.048 | 37.179 | 41.31 | 47.3129 | 53.3159 | 59.3188 | 65.3217 | 71.3247 | 71.6559 | 71.9872 | 72.3185 | 72.6497 | 72.981 | 74.5576 | 76.1341 | 77.7107 | 79.2873 | 80.8638 | 82.4404 | 84.017 | 85.5935 | 87.1701 | 88.7467 | 89.7977 | 90.8488 | 91.8998 | 92.9508 | 94.0019 | 95.0529 | 96.104 | 97.155 | 98.2061 | 99.2571 | 100.3082 | 101.3592 | 102.4102 | 103.4613 | 104.5123 | 105.421 | 106.3297 | 107.2384 | 108.1471 | 109.0558 | 109.9645 | 110.8732 | 111.7818 | 112.6905 | 113.5992 | 114.5079 | 115.4166 | 116.3253 | 117.234 | 118.1427 | 118.4134 | 118.6842 | 118.9549 | 119.2256 | 119.4964 | 119.7671 | 120.0379 | 120.3086 | 120.5794 | 120.8501 | 121.1209 | 121.3916 | 121.6623 | 121.9331 | 122.2038 | 122.4746 | 122.7453 | 123.0161 | 123.2868 | 123.5576 | 123.8283 | 124.099 | 124.3698 | 124.6405 | 124.9113 | 125.182 | 125.4528 | 125.7235 | 125.9943 | 126.265 | 126.3774 | 126.4898 | 126.6023 | 126.7147 | 126.8271 | 126.9395 | 127.052 | 127.1644 | 127.2768 | 127.3892 | 127.5016 | 127.6141 | 127.7265 | 127.8389 | 127.9513 | 128.0638 | 128.1762 | 128.2886 | 128.401 | 128.5134 | 128.6259 | 128.7383 | 128.8507 | 128.9631 | 129.0756 | 129.188 | 129.3004 | 129.4128 | 129.5252 | 129.6377 | 129.6377 | 129.6377 | 129.6377 | 129.6377 | 129.6377 | 129.6377 | 129.6377 | 129.6377 | 129.6377 | 129.6377 | 129.6377 | 129.6377 | 129.6377 | 129.6377 | 129.6377 | 129.6377 | 129.6377 | 129.6377 | 129.6377 | 129.6377 | 129.6377 | 129.6377 | 129.6377 | 129.6377 | 129.6377 | 129.6377 | 129.6377 | 129.6377 | 129.6377 | 129.6377 | 129.5618 | 129.486 | 129.4102 | 129.3343 | 129.2585 | 129.1827 | 129.1068 | 129.031 | 128.9552 | 128.8793 | 128.8035 | 128.7277 | 128.6518 | 128.576 | 128.5002 | 128.4243 | 128.3485 | 128.2727 | 128.1968 | 128.121 | 128.0452 | 127.9693 | 127.8935 | 127.8177 | 127.7418 | 127.666 | 127.5902 | 127.5143 | 127.4385 | 127.3627
11.5 | 0 | 4.17 | 8.34 | 12.51 | 16.68 | 20.85 | 25.02 | 29.19 | 33.36 | 37.53 | 41.7 | 47.772 | 53.844 | 59.916 | 65.988 | 72.06 | 72.382 | 72.704 | 73.026 | 73.348 | 73.67 | 75.263 | 76.856 | 78.449 | 80.042 | 81.635 | 83.228 | 84.821 | 86.414 | 88.007 | 89.6 | 90.662 | 91.724 | 92.786 | 93.848 | 94.91 | 95.972 | 97.034 | 98.096 | 99.158 | 100.22 | 101.282 | 102.344 | 103.406 | 104.468 | 105.53 | 106.4493 | 107.3687 | 108.288 | 109.2073 | 110.1267 | 111.046 | 111.9653 | 112.8847 | 113.804 | 114.7233 | 115.6427 | 116.562 | 117.4813 | 118.4007 | 119.32 | 119.5943 | 119.8687 | 120.143 | 120.4173 | 120.6917 | 120.966 | 121.2403 | 121.5147 | 121.789 | 122.0633 | 122.3377 | 122.612 | 122.8863 | 123.1607 | 123.435 | 123.7093 | 123.9837 | 124.258 | 124.5323 | 124.8067 | 125.081 | 125.3553 | 125.6297 | 125.904 | 126.1783 | 126.4527 | 126.727 | 127.0013 | 127.2757 | 127.55 | 127.664 | 127.778 | 127.892 | 128.006 | 128.12 | 128.234 | 128.348 | 128.462 | 128.576 | 128.69 | 128.804 | 128.918 | 129.032 | 129.146 | 129.26 | 129.374 | 129.488 | 129.602 | 129.716 | 129.83 | 129.944 | 130.058 | 130.172 | 130.286 | 130.4 | 130.514 | 130.628 | 130.742 | 130.856 | 130.97 | 130.97 | 130.97 | 130.97 | 130.97 | 130.97 | 130.97 | 130.97 | 130.97 | 130.97 | 130.97 | 130.97 | 130.97 | 130.97 | 130.97 | 130.97 | 130.97 | 130.97 | 130.97 | 130.97 | 130.97 | 130.97 | 130.97 | 130.97 | 130.97 | 130.97 | 130.97 | 130.97 | 130.97 | 130.97 | 130.97 | 130.895 | 130.82 | 130.745 | 130.67 | 130.595 | 130.52 | 130.445 | 130.37 | 130.295 | 130.22 | 130.145 | 130.07 | 129.995 | 129.92 | 129.845 | 129.77 | 129.695 | 129.62 | 129.545 | 129.47 | 129.395 | 129.32 | 129.245 | 129.17 | 129.095 | 129.02 | 128.945 | 128.87 | 128.795 | 128.72
11.55 | 0 | 4.209 | 8.418 | 12.627 | 16.836 | 21.045 | 25.254 | 29.463 | 33.672 | 37.881 | 42.09 | 48.2311 | 54.3721 | 60.5132 | 66.6543 | 72.7953 | 73.1081 | 73.4208 | 73.7335 | 74.0463 | 74.359 | 75.9684 | 77.5779 | 79.1873 | 80.7967 | 82.4062 | 84.0156 | 85.625 | 87.2345 | 88.8439 | 90.4533 | 91.5263 | 92.5992 | 93.6722 | 94.7452 | 95.8181 | 96.8911 | 97.964 | 99.037 | 100.1099 | 101.1829 | 102.2558 | 103.3288 | 104.4018 | 105.4747 | 106.5477 | 107.4776 | 108.4076 | 109.3376 | 110.2676 | 111.1976 | 112.1275 | 113.0575 | 113.9875 | 114.9175 | 115.8474 | 116.7774 | 117.7074 | 118.6374 | 119.5674 | 120.4973 | 120.7753 | 121.0532 | 121.3311 | 121.609 | 121.8869 | 122.1649 | 122.4428 | 122.7207 | 122.9986 | 123.2766 | 123.5545 | 123.8324 | 124.1103 | 124.3882 | 124.6662 | 124.9441 | 125.222 | 125.4999 | 125.7779 | 126.0558 | 126.3337 | 126.6116 | 126.8895 | 127.1675 | 127.4454 | 127.7233 | 128.0012 | 128.2792 | 128.5571 | 128.835 | 128.9506 | 129.0662 | 129.1817 | 129.2973 | 129.4129 | 129.5285 | 129.644 | 129.7596 | 129.8752 | 129.9908 | 130.1064 | 130.2219 | 130.3375 | 130.4531 | 130.5687 | 130.6842 | 130.7998 | 130.9154 | 131.031 | 131.1466 | 131.2621 | 131.3777 | 131.4933 | 131.6089 | 131.7244 | 131.84 | 131.9556 | 132.0712 | 132.1868 | 132.3023 | 132.3023 | 132.3023 | 132.3023 | 132.3023 | 132.3023 | 132.3023 | 132.3023 | 132.3023 | 132.3023 | 132.3023 | 132.3023 | 132.3023 | 132.3023 | 132.3023 | 132.3023 | 132.3023 | 132.3023 | 132.3023 | 132.3023 | 132.3023 | 132.3023 | 132.3023 | 132.3023 | 132.3023 | 132.3023 | 132.3023 | 132.3023 | 132.3023 | 132.3023 | 132.3023 | 132.2282 | 132.154 | 132.0798 | 132.0057 | 131.9315 | 131.8573 | 131.7832 | 131.709 | 131.6348 | 131.5607 | 131.4865 | 131.4123 | 131.3382 | 131.264 | 131.1898 | 131.1157 | 131.0415 | 130.9673 | 130.8932 | 130.819 | 130.7448 | 130.6707 | 130.5965 | 130.5223 | 130.4482 | 130.374 | 130.2998 | 130.2257 | 130.1515 | 130.0773
11.6 | 0 | 4.248 | 8.496 | 12.744 | 16.992 | 21.24 | 25.488 | 29.736 | 33.984 | 38.232 | 42.48 | 48.6901 | 54.9003 | 61.1104 | 67.3205 | 73.5307 | 73.8341 | 74.1376 | 74.4411 | 74.7445 | 75.048 | 76.6739 | 78.2997 | 79.9256 | 81.5515 | 83.1773 | 84.8032 | 86.4291 | 88.0549 | 89.6808 | 91.3067 | 92.3906 | 93.4745 | 94.5584 | 95.6423 | 96.7262 | 97.8101 | 98.894 | 99.978 | 101.0619 | 102.1458 | 103.2297 | 104.3136 | 105.3975 | 106.4814 | 107.5653 | 108.506 | 109.4466 | 110.3872 | 111.3278 | 112.2684 | 113.2091 | 114.1497 | 115.0903 | 116.0309 | 116.9716 | 117.9122 | 118.8528 | 119.7934 | 120.734 | 121.6747 | 121.9562 | 122.2377 | 122.5192 | 122.8007 | 123.0822 | 123.3637 | 123.6452 | 123.9268 | 124.2083 | 124.4898 | 124.7713 | 125.0528 | 125.3343 | 125.6158 | 125.8973 | 126.1788 | 126.4604 | 126.7419 | 127.0234 | 127.3049 | 127.5864 | 127.8679 | 128.1494 | 128.4309 | 128.7124 | 128.994 | 129.2755 | 129.557 | 129.8385 | 130.12 | 130.2372 | 130.3543 | 130.4715 | 130.5886 | 130.7058 | 130.8229 | 130.9401 | 131.0572 | 131.1744 | 131.2916 | 131.4087 | 131.5259 | 131.643 | 131.7602 | 131.8773 | 131.9945 | 132.1116 | 132.2288 | 132.346 | 132.4631 | 132.5803 | 132.6974 | 132.8146 | 132.9317 | 133.0489 | 133.166 | 133.2832 | 133.4004 | 133.5175 | 133.6347 | 133.6347 | 133.6347 | 133.6347 | 133.6347 | 133.6347 | 133.6347 | 133.6347 | 133.6347 | 133.6347 | 133.6347 | 133.6347 | 133.6347 | 133.6347 | 133.6347 | 133.6347 | 133.6347 | 133.6347 | 133.6347 | 133.6347 | 133.6347 | 133.6347 | 133.6347 | 133.6347 | 133.6347 | 133.6347 | 133.6347 | 133.6347 | 133.6347 | 133.6347 | 133.6347 | 133.5613 | 133.488 | 133.4147 | 133.3413 | 133.268 | 133.1947 | 133.1213 | 133.048 | 132.9747 | 132.9013 | 132.828 | 132.7547 | 132.6813 | 132.608 | 132.5347 | 132.4613 | 132.388 | 132.3147 | 132.2413 | 132.168 | 132.0947 | 132.0213 | 131.948 | 131.8747 | 131.8013 | 131.728 | 131.6547 | 131.5813 | 131.508 | 131.4347
11.65 | 0 | 4.287 | 8.574 | 12.861 | 17.148 | 21.435 | 25.722 | 30.009 | 34.296 | 38.583 | 42.87 | 49.1492 | 55.4284 | 61.7076 | 67.9868 | 74.266 | 74.5602 | 74.8544 | 75.1486 | 75.4428 | 75.737 | 77.3793 | 79.0216 | 80.6639 | 82.3062 | 83.9485 | 85.5908 | 87.2331 | 88.8754 | 90.5177 | 92.16 | 93.2549 | 94.3497 | 95.4446 | 96.5395 | 97.6343 | 98.7292 | 99.8241 | 100.9189 | 102.0138 | 103.1087 | 104.2035 | 105.2984 | 106.3933 | 107.4881 | 108.583 | 109.5343 | 110.4855 | 111.4368 | 112.3881 | 113.3393 | 114.2906 | 115.2419 | 116.1931 | 117.1444 | 118.0957 | 119.0469 | 119.9982 | 120.9495 | 121.9007 | 122.852 | 123.1371 | 123.4222 | 123.7073 | 123.9924 | 124.2775 | 124.5626 | 124.8477 | 125.1328 | 125.4179 | 125.703 | 125.9881 | 126.2732 | 126.5583 | 126.8434 | 127.1285 | 127.4136 | 127.6987 | 127.9838 | 128.2689 | 128.554 | 128.8391 | 129.1242 | 129.4093 | 129.6944 | 129.9795 | 130.2646 | 130.5497 | 130.8348 | 131.1199 | 131.405 | 131.5237 | 131.6425 | 131.7612 | 131.8799 | 131.9987 | 132.1174 | 132.2361 | 132.3549 | 132.4736 | 132.5923 | 132.7111 | 132.8298 | 132.9485 | 133.0673 | 133.186 | 133.3047 | 133.4235 | 133.5422 | 133.6609 | 133.7797 | 133.8984 | 134.0171 | 134.1359 | 134.2546 | 134.3733 | 134.4921 | 134.6108 | 134.7295 | 134.8483 | 134.967 | 134.967 | 134.967 | 134.967 | 134.967 | 134.967 | 134.967 | 134.967 | 134.967 | 134.967 | 134.967 | 134.967 | 134.967 | 134.967 | 134.967 | 134.967 | 134.967 | 134.967 | 134.967 | 134.967 | 134.967 | 134.967 | 134.967 | 134.967 | 134.967 | 134.967 | 134.967 | 134.967 | 134.967 | 134.967 | 134.967 | 134.8945 | 134.822 | 134.7495 | 134.677 | 134.6045 | 134.532 | 134.4595 | 134.387 | 134.3145 | 134.242 | 134.1695 | 134.097 | 134.0245 | 133.952 | 133.8795 | 133.807 | 133.7345 | 133.662 | 133.5895 | 133.517 | 133.4445 | 133.372 | 133.2995 | 133.227 | 133.1545 | 133.082 | 133.0095 | 132.937 | 132.8645 | 132.792
11.7 | 0 | 4.326 | 8.652 | 12.978 | 17.304 | 21.63 | 25.956 | 30.282 | 34.608 | 38.934 | 43.26 | 49.6083 | 55.9565 | 62.3048 | 68.6531 | 75.0013 | 75.2863 | 75.5712 | 75.8561 | 76.1411 | 76.426 | 78.0847 | 79.7435 | 81.4022 | 83.0609 | 84.7197 | 86.3784 | 88.0371 | 89.6959 | 91.3546 | 93.0133 | 94.1192 | 95.225 | 96.3308 | 97.4366 | 98.5424 | 99.6483 | 100.7541 | 101.8599 | 102.9657 | 104.0716 | 105.1774 | 106.2832 | 107.389 | 108.4948 | 109.6007 | 110.5626 | 111.5245 | 112.4864 | 113.4483 | 114.4102 | 115.3721 | 116.334 | 117.296 | 118.2579 | 119.2198 | 120.1817 | 121.1436 | 122.1055 | 123.0674 | 124.0293 | 124.318 | 124.6067 | 124.8954 | 125.1841 | 125.4728 | 125.7615 | 126.0502 | 126.3388 | 126.6275 | 126.9162 | 127.2049 | 127.4936 | 127.7823 | 128.071 | 128.3597 | 128.6484 | 128.937 | 129.2257 | 129.5144 | 129.8031 | 130.0918 | 130.3805 | 130.6692 | 130.9579 | 131.2466 | 131.5352 | 131.8239 | 132.1126 | 132.4013 | 132.69 | 132.8103 | 132.9306 | 133.0509 | 133.1712 | 133.2916 | 133.4119 | 133.5322 | 133.6525 | 133.7728 | 133.8931 | 134.0134 | 134.1337 | 134.254 | 134.3744 | 134.4947 | 134.615 | 134.7353 | 134.8556 | 134.9759 | 135.0962 | 135.2165 | 135.3368 | 135.4572 | 135.5775 | 135.6978 | 135.8181 | 135.9384 | 136.0587 | 136.179 | 136.2993 | 136.2993 | 136.2993 | 136.2993 | 136.2993 | 136.2993 | 136.2993 | 136.2993 | 136.2993 | 136.2993 | 136.2993 | 136.2993 | 136.2993 | 136.2993 | 136.2993 | 136.2993 | 136.2993 | 136.2993 | 136.2993 | 136.2993 | 136.2993 | 136.2993 | 136.2993 | 136.2993 | 136.2993 | 136.2993 | 136.2993 | 136.2993 | 136.2993 | 136.2993 | 136.2993 | 136.2277 | 136.156 | 136.0843 | 136.0127 | 135.941 | 135.8693 | 135.7977 | 135.726 | 135.6543 | 135.5827 | 135.511 | 135.4393 | 135.3677 | 135.296 | 135.2243 | 135.1527 | 135.081 | 135.0093 | 134.9377 | 134.866 | 134.7943 | 134.7227 | 134.651 | 134.5793 | 134.5077 | 134.436 | 134.3643 | 134.2927 | 134.221 | 134.1493
11.75 | 0 | 4.365 | 8.73 | 13.095 | 17.46 | 21.825 | 26.19 | 30.555 | 34.92 | 39.285 | 43.65 | 50.0673 | 56.4847 | 62.902 | 69.3193 | 75.7367 | 76.0123 | 76.288 | 76.5637 | 76.8393 | 77.115 | 78.7902 | 80.4653 | 82.1405 | 83.8157 | 85.4908 | 87.166 | 88.8412 | 90.5163 | 92.1915 | 93.8667 | 94.9834 | 96.1002 | 97.217 | 98.3338 | 99.4506 | 100.5673 | 101.6841 | 102.8009 | 103.9177 | 105.0344 | 106.1512 | 107.268 | 108.3848 | 109.5016 | 110.6183 | 111.5909 | 112.5634 | 113.536 | 114.5086 | 115.4811 | 116.4537 | 117.4262 | 118.3988 | 119.3713 | 120.3439 | 121.3164 | 122.289 | 123.2616 | 124.2341 | 125.2067 | 125.4989 | 125.7912 | 126.0835 | 126.3758 | 126.6681 | 126.9603 | 127.2526 | 127.5449 | 127.8372 | 128.1294 | 128.4217 | 128.714 | 129.0063 | 129.2986 | 129.5908 | 129.8831 | 130.1754 | 130.4677 | 130.7599 | 131.0522 | 131.3445 | 131.6368 | 131.9291 | 132.2213 | 132.5136 | 132.8059 | 133.0982 | 133.3904 | 133.6827 | 133.975 | 134.0969 | 134.2188 | 134.3407 | 134.4626 | 134.5844 | 134.7063 | 134.8282 | 134.9501 | 135.072 | 135.1939 | 135.3158 | 135.4377 | 135.5596 | 135.6814 | 135.8033 | 135.9252 | 136.0471 | 136.169 | 136.2909 | 136.4128 | 136.5347 | 136.6566 | 136.7784 | 136.9003 | 137.0222 | 137.1441 | 137.266 | 137.3879 | 137.5098 | 137.6317 | 137.6317 | 137.6317 | 137.6317 | 137.6317 | 137.6317 | 137.6317 | 137.6317 | 137.6317 | 137.6317 | 137.6317 | 137.6317 | 137.6317 | 137.6317 | 137.6317 | 137.6317 | 137.6317 | 137.6317 | 137.6317 | 137.6317 | 137.6317 | 137.6317 | 137.6317 | 137.6317 | 137.6317 | 137.6317 | 137.6317 | 137.6317 | 137.6317 | 137.6317 | 137.6317 | 137.5608 | 137.49 | 137.4192 | 137.3483 | 137.2775 | 137.2067 | 137.1358 | 137.065 | 136.9942 | 136.9233 | 136.8525 | 136.7817 | 136.7108 | 136.64 | 136.5692 | 136.4983 | 136.4275 | 136.3567 | 136.2858 | 136.215 | 136.1442 | 136.0733 | 136.0025 | 135.9317 | 135.8608 | 135.79 | 135.7192 | 135.6483 | 135.5775 | 135.5067
11.8 | 0 | 4.404 | 8.808 | 13.212 | 17.616 | 22.02 | 26.424 | 30.828 | 35.232 | 39.636 | 44.04 | 50.5264 | 57.0128 | 63.4992 | 69.9856 | 76.472 | 76.7384 | 77.0048 | 77.2712 | 77.5376 | 77.804 | 79.4956 | 81.1872 | 82.8788 | 84.5704 | 86.262 | 87.9536 | 89.6452 | 91.3368 | 93.0284 | 94.72 | 95.8477 | 96.9755 | 98.1032 | 99.2309 | 100.3587 | 101.4864 | 102.6141 | 103.7419 | 104.8696 | 105.9973 | 107.1251 | 108.2528 | 109.3805 | 110.5083 | 111.636 | 112.6192 | 113.6024 | 114.5856 | 115.5688 | 116.552 | 117.5352 | 118.5184 | 119.5016 | 120.4848 | 121.468 | 122.4512 | 123.4344 | 124.4176 | 125.4008 | 126.384 | 126.6799 | 126.9757 | 127.2716 | 127.5675 | 127.8633 | 128.1592 | 128.4551 | 128.7509 | 129.0468 | 129.3427 | 129.6385 | 129.9344 | 130.2303 | 130.5261 | 130.822 | 131.1179 | 131.4137 | 131.7096 | 132.0055 | 132.3013 | 132.5972 | 132.8931 | 133.1889 | 133.4848 | 133.7807 | 134.0765 | 134.3724 | 134.6683 | 134.9641 | 135.26 | 135.3835 | 135.5069 | 135.6304 | 135.7539 | 135.8773 | 136.0008 | 136.1243 | 136.2477 | 136.3712 | 136.4947 | 136.6181 | 136.7416 | 136.8651 | 136.9885 | 137.112 | 137.2355 | 137.3589 | 137.4824 | 137.6059 | 137.7293 | 137.8528 | 137.9763 | 138.0997 | 138.2232 | 138.3467 | 138.4701 | 138.5936 | 138.7171 | 138.8405 | 138.964 | 138.964 | 138.964 | 138.964 | 138.964 | 138.964 | 138.964 | 138.964 | 138.964 | 138.964 | 138.964 | 138.964 | 138.964 | 138.964 | 138.964 | 138.964 | 138.964 | 138.964 | 138.964 | 138.964 | 138.964 | 138.964 | 138.964 | 138.964 | 138.964 | 138.964 | 138.964 | 138.964 | 138.964 | 138.964 | 138.964 | 138.894 | 138.824 | 138.754 | 138.684 | 138.614 | 138.544 | 138.474 | 138.404 | 138.334 | 138.264 | 138.194 | 138.124 | 138.054 | 137.984 | 137.914 | 137.844 | 137.774 | 137.704 | 137.634 | 137.564 | 137.494 | 137.424 | 137.354 | 137.284 | 137.214 | 137.144 | 137.074 | 137.004 | 136.934 | 136.864
11.85 | 0 | 4.443 | 8.886 | 13.329 | 17.772 | 22.215 | 26.658 | 31.101 | 35.544 | 39.987 | 44.43 | 50.9855 | 57.5409 | 64.0964 | 70.6519 | 77.2073 | 77.4645 | 77.7216 | 77.9787 | 78.2359 | 78.493 | 80.201 | 81.9091 | 83.6171 | 85.3251 | 87.0332 | 88.7412 | 90.4492 | 92.1573 | 93.8653 | 95.5733 | 96.712 | 97.8507 | 98.9894 | 100.1281 | 101.2668 | 102.4055 | 103.5442 | 104.6828 | 105.8215 | 106.9602 | 108.0989 | 109.2376 | 110.3763 | 111.515 | 112.6537 | 113.6475 | 114.6414 | 115.6352 | 116.629 | 117.6229 | 118.6167 | 119.6106 | 120.6044 | 121.5983 | 122.5921 | 123.586 | 124.5798 | 125.5736 | 126.5675 | 127.5613 | 127.8608 | 128.1602 | 128.4597 | 128.7592 | 129.0586 | 129.3581 | 129.6575 | 129.957 | 130.2564 | 130.5559 | 130.8553 | 131.1548 | 131.4543 | 131.7537 | 132.0532 | 132.3526 | 132.6521 | 132.9515 | 133.251 | 133.5504 | 133.8499 | 134.1494 | 134.4488 | 134.7483 | 135.0477 | 135.3472 | 135.6466 | 135.9461 | 136.2455 | 136.545 | 136.67 | 136.7951 | 136.9201 | 137.0452 | 137.1702 | 137.2953 | 137.4203 | 137.5454 | 137.6704 | 137.7954 | 137.9205 | 138.0455 | 138.1706 | 138.2956 | 138.4207 | 138.5457 | 138.6708 | 138.7958 | 138.9208 | 139.0459 | 139.1709 | 139.296 | 139.421 | 139.5461 | 139.6711 | 139.7962 | 139.9212 | 140.0462 | 140.1713 | 140.2963 | 140.2963 | 140.2963 | 140.2963 | 140.2963 | 140.2963 | 140.2963 | 140.2963 | 140.2963 | 140.2963 | 140.2963 | 140.2963 | 140.2963 | 140.2963 | 140.2963 | 140.2963 | 140.2963 | 140.2963 | 140.2963 | 140.2963 | 140.2963 | 140.2963 | 140.2963 | 140.2963 | 140.2963 | 140.2963 | 140.2963 | 140.2963 | 140.2963 | 140.2963 | 140.2963 | 140.2272 | 140.158 | 140.0888 | 140.0197 | 139.9505 | 139.8813 | 139.8122 | 139.743 | 139.6738 | 139.6047 | 139.5355 | 139.4663 | 139.3972 | 139.328 | 139.2588 | 139.1897 | 139.1205 | 139.0513 | 138.9822 | 138.913 | 138.8438 | 138.7747 | 138.7055 | 138.6363 | 138.5672 | 138.498 | 138.4288 | 138.3597 | 138.2905 | 138.2213
11.9 | 0 | 4.482 | 8.964 | 13.446 | 17.928 | 22.41 | 26.892 | 31.374 | 35.856 | 40.338 | 44.82 | 51.4445 | 58.0691 | 64.6936 | 71.3181 | 77.9427 | 78.1905 | 78.4384 | 78.6863 | 78.9341 | 79.182 | 80.9065 | 82.6309 | 84.3554 | 86.0799 | 87.8043 | 89.5288 | 91.2533 | 92.9777 | 94.7022 | 96.4267 | 97.5763 | 98.726 | 99.8756 | 101.0252 | 102.1749 | 103.3245 | 104.4742 | 105.6238 | 106.7735 | 107.9231 | 109.0728 | 110.2224 | 111.372 | 112.5217 | 113.6713 | 114.6758 | 115.6803 | 116.6848 | 117.6893 | 118.6938 | 119.6983 | 120.7028 | 121.7072 | 122.7117 | 123.7162 | 124.7207 | 125.7252 | 126.7297 | 127.7342 | 128.7387 | 129.0417 | 129.3448 | 129.6478 | 129.9508 | 130.2539 | 130.5569 | 130.86 | 131.163 | 131.4661 | 131.7691 | 132.0722 | 132.3752 | 132.6782 | 132.9813 | 133.2843 | 133.5874 | 133.8904 | 134.1935 | 134.4965 | 134.7996 | 135.1026 | 135.4056 | 135.7087 | 136.0117 | 136.3148 | 136.6178 | 136.9209 | 137.2239 | 137.527 | 137.83 | 137.9566 | 138.0832 | 138.2099 | 138.3365 | 138.4631 | 138.5897 | 138.7164 | 138.843 | 138.9696 | 139.0962 | 139.2228 | 139.3495 | 139.4761 | 139.6027 | 139.7293 | 139.856 | 139.9826 | 140.1092 | 140.2358 | 140.3624 | 140.4891 | 140.6157 | 140.7423 | 140.8689 | 140.9956 | 141.1222 | 141.2488 | 141.3754 | 141.502 | 141.6287 | 141.6287 | 141.6287 | 141.6287 | 141.6287 | 141.6287 | 141.6287 | 141.6287 | 141.6287 | 141.6287 | 141.6287 | 141.6287 | 141.6287 | 141.6287 | 141.6287 | 141.6287 | 141.6287 | 141.6287 | 141.6287 | 141.6287 | 141.6287 | 141.6287 | 141.6287 | 141.6287 | 141.6287 | 141.6287 | 141.6287 | 141.6287 | 141.6287 | 141.6287 | 141.6287 | 141.5603 | 141.492 | 141.4237 | 141.3553 | 141.287 | 141.2187 | 141.1503 | 141.082 | 141.0137 | 140.9453 | 140.877 | 140.8087 | 140.7403 | 140.672 | 140.6037 | 140.5353 | 140.467 | 140.3987 | 140.3303 | 140.262 | 140.1937 | 140.1253 | 140.057 | 139.9887 | 139.9203 | 139.852 | 139.7837 | 139.7153 | 139.647 | 139.5787
11.95 | 0 | 4.521 | 9.042 | 13.563 | 18.084 | 22.605 | 27.126 | 31.647 | 36.168 | 40.689 | 45.21 | 51.9036 | 58.5972 | 65.2908 | 71.9844 | 78.678 | 78.9166 | 79.1552 | 79.3938 | 79.6324 | 79.871 | 81.6119 | 83.3528 | 85.0937 | 86.8346 | 88.5755 | 90.3164 | 92.0573 | 93.7982 | 95.5391 | 97.28 | 98.4406 | 99.6012 | 100.7618 | 101.9224 | 103.083 | 104.2436 | 105.4042 | 106.5648 | 107.7254 | 108.886 | 110.0466 | 111.2072 | 112.3678 | 113.5284 | 114.689 | 115.7041 | 116.7193 | 117.7344 | 118.7495 | 119.7647 | 120.7798 | 121.7949 | 122.8101 | 123.8252 | 124.8403 | 125.8555 | 126.8706 | 127.8857 | 128.9009 | 129.916 | 130.2226 | 130.5293 | 130.8359 | 131.1425 | 131.4492 | 131.7558 | 132.0624 | 132.3691 | 132.6757 | 132.9823 | 133.289 | 133.5956 | 133.9022 | 134.2089 | 134.5155 | 134.8221 | 135.1288 | 135.4354 | 135.742 | 136.0487 | 136.3553 | 136.6619 | 136.9686 | 137.2752 | 137.5818 | 137.8885 | 138.1951 | 138.5017 | 138.8084 | 139.115 | 139.2432 | 139.3714 | 139.4996 | 139.6278 | 139.756 | 139.8842 | 140.0124 | 140.1406 | 140.2688 | 140.397 | 140.5252 | 140.6534 | 140.7816 | 140.9098 | 141.038 | 141.1662 | 141.2944 | 141.4226 | 141.5508 | 141.679 | 141.8072 | 141.9354 | 142.0636 | 142.1918 | 142.32 | 142.4482 | 142.5764 | 142.7046 | 142.8328 | 142.961 | 142.961 | 142.961 | 142.961 | 142.961 | 142.961 | 142.961 | 142.961 | 142.961 | 142.961 | 142.961 | 142.961 | 142.961 | 142.961 | 142.961 | 142.961 | 142.961 | 142.961 | 142.961 | 142.961 | 142.961 | 142.961 | 142.961 | 142.961 | 142.961 | 142.961 | 142.961 | 142.961 | 142.961 | 142.961 | 142.961 | 142.8935 | 142.826 | 142.7585 | 142.691 | 142.6235 | 142.556 | 142.4885 | 142.421 | 142.3535 | 142.286 | 142.2185 | 142.151 | 142.0835 | 142.016 | 141.9485 | 141.881 | 141.8135 | 141.746 | 141.6785 | 141.611 | 141.5435 | 141.476 | 141.4085 | 141.341 | 141.2735 | 141.206 | 141.1385 | 141.071 | 141.0035 | 140.936
12 | 0 | 4.56 | 9.12 | 13.68 | 18.24 | 22.8 | 27.36 | 31.92 | 36.48 | 41.04 | 45.6 | 52.3627 | 59.1253 | 65.888 | 72.6507 | 79.4133 | 79.6427 | 79.872 | 80.1013 | 80.3307 | 80.56 | 82.3173 | 84.0747 | 85.832 | 87.5893 | 89.3467 | 91.104 | 92.8613 | 94.6187 | 96.376 | 98.1333 | 99.3049 | 100.4764 | 101.648 | 102.8196 | 103.9911 | 105.1627 | 106.3342 | 107.5058 | 108.6773 | 109.8489 | 111.0204 | 112.192 | 113.3636 | 114.5351 | 115.7067 | 116.7324 | 117.7582 | 118.784 | 119.8098 | 120.8356 | 121.8613 | 122.8871 | 123.9129 | 124.9387 | 125.9644 | 126.9902 | 128.016 | 129.0418 | 130.0676 | 131.0933 | 131.4036 | 131.7138 | 132.024 | 132.3342 | 132.6444 | 132.9547 | 133.2649 | 133.5751 | 133.8853 | 134.1956 | 134.5058 | 134.816 | 135.1262 | 135.4364 | 135.7467 | 136.0569 | 136.3671 | 136.6773 | 136.9876 | 137.2978 | 137.608 | 137.9182 | 138.2284 | 138.5387 | 138.8489 | 139.1591 | 139.4693 | 139.7796 | 140.0898 | 140.4 | 140.5298 | 140.6596 | 140.7893 | 140.9191 | 141.0489 | 141.1787 | 141.3084 | 141.4382 | 141.568 | 141.6978 | 141.8276 | 141.9573 | 142.0871 | 142.2169 | 142.3467 | 142.4764 | 142.6062 | 142.736 | 142.8658 | 142.9956 | 143.1253 | 143.2551 | 143.3849 | 143.5147 | 143.6444 | 143.7742 | 143.904 | 144.0338 | 144.1636 | 144.2933 | 144.2933 | 144.2933 | 144.2933 | 144.2933 | 144.2933 | 144.2933 | 144.2933 | 144.2933 | 144.2933 | 144.2933 | 144.2933 | 144.2933 | 144.2933 | 144.2933 | 144.2933 | 144.2933 | 144.2933 | 144.2933 | 144.2933 | 144.2933 | 144.2933 | 144.2933 | 144.2933 | 144.2933 | 144.2933 | 144.2933 | 144.2933 | 144.2933 | 144.2933 | 144.2933 | 144.2267 | 144.16 | 144.0933 | 144.0267 | 143.96 | 143.8933 | 143.8267 | 143.76 | 143.6933 | 143.6267 | 143.56 | 143.4933 | 143.4267 | 143.36 | 143.2933 | 143.2267 | 143.16 | 143.0933 | 143.0267 | 142.96 | 142.8933 | 142.8267 | 142.76 | 142.6933 | 142.6267 | 142.56 | 142.4933 | 142.4267 | 142.36 | 142.2933
12.05 | 0 | 4.599 | 9.198 | 13.797 | 18.396 | 22.995 | 27.594 | 32.193 | 36.792 | 41.391 | 45.99 | 52.8217 | 59.6535 | 66.4852 | 73.3169 | 80.1487 | 80.3687 | 80.5888 | 80.8089 | 81.0289 | 81.249 | 83.0228 | 84.7965 | 86.5703 | 88.3441 | 90.1178 | 91.8916 | 93.6654 | 95.4391 | 97.2129 | 98.9867 | 100.1692 | 101.3517 | 102.5342 | 103.7167 | 104.8992 | 106.0817 | 107.2642 | 108.4468 | 109.6293 | 110.8118 | 111.9943 | 113.1768 | 114.3593 | 115.5418 | 116.7243 | 117.7608 | 118.7972 | 119.8336 | 120.87 | 121.9064 | 122.9429 | 123.9793 | 125.0157 | 126.0521 | 127.0886 | 128.125 | 129.1614 | 130.1978 | 131.2342 | 132.2707 | 132.5845 | 132.8983 | 133.2121 | 133.5259 | 133.8397 | 134.1535 | 134.4673 | 134.7812 | 135.095 | 135.4088 | 135.7226 | 136.0364 | 136.3502 | 136.664 | 136.9778 | 137.2916 | 137.6055 | 137.9193 | 138.2331 | 138.5469 | 138.8607 | 139.1745 | 139.4883 | 139.8021 | 140.1159 | 140.4298 | 140.7436 | 141.0574 | 141.3712 | 141.685 | 141.8164 | 141.9477 | 142.0791 | 142.2104 | 142.3418 | 142.4731 | 142.6045 | 142.7358 | 142.8672 | 142.9986 | 143.1299 | 143.2613 | 143.3926 | 143.524 | 143.6553 | 143.7867 | 143.918 | 144.0494 | 144.1808 | 144.3121 | 144.4435 | 144.5748 | 144.7062 | 144.8375 | 144.9689 | 145.1002 | 145.2316 | 145.363 | 145.4943 | 145.6257 | 145.6257 | 145.6257 | 145.6257 | 145.6257 | 145.6257 | 145.6257 | 145.6257 | 145.6257 | 145.6257 | 145.6257 | 145.6257 | 145.6257 | 145.6257 | 145.6257 | 145.6257 | 145.6257 | 145.6257 | 145.6257 | 145.6257 | 145.6257 | 145.6257 | 145.6257 | 145.6257 | 145.6257 | 145.6257 | 145.6257 | 145.6257 | 145.6257 | 145.6257 | 145.6257 | 145.5598 | 145.494 | 145.4282 | 145.3623 | 145.2965 | 145.2307 | 145.1648 | 145.099 | 145.0332 | 144.9673 | 144.9015 | 144.8357 | 144.7698 | 144.704 | 144.6382 | 144.5723 | 144.5065 | 144.4407 | 144.3748 | 144.309 | 144.2432 | 144.1773 | 144.1115 | 144.0457 | 143.9798 | 143.914 | 143.8482 | 143.7823 | 143.7165 | 143.6507
12.1 | 0 | 4.638 | 9.276 | 13.914 | 18.552 | 23.19 | 27.828 | 32.466 | 37.104 | 41.742 | 46.38 | 53.2808 | 60.1816 | 67.0824 | 73.9832 | 80.884 | 81.0948 | 81.3056 | 81.5164 | 81.7272 | 81.938 | 83.7282 | 85.5184 | 87.3086 | 89.0988 | 90.889 | 92.6792 | 94.4694 | 96.2596 | 98.0498 | 99.84 | 101.0335 | 102.2269 | 103.4204 | 104.6139 | 105.8073 | 107.0008 | 108.1943 | 109.3877 | 110.5812 | 111.7747 | 112.9681 | 114.1616 | 115.3551 | 116.5485 | 117.742 | 118.7891 | 119.8361 | 120.8832 | 121.9303 | 122.9773 | 124.0244 | 125.0715 | 126.1185 | 127.1656 | 128.2127 | 129.2597 | 130.3068 | 131.3539 | 132.4009 | 133.448 | 133.7654 | 134.0828 | 134.4002 | 134.7176 | 135.035 | 135.3524 | 135.6698 | 135.9872 | 136.3046 | 136.622 | 136.9394 | 137.2568 | 137.5742 | 137.8916 | 138.209 | 138.5264 | 138.8438 | 139.1612 | 139.4786 | 139.796 | 140.1134 | 140.4308 | 140.7482 | 141.0656 | 141.383 | 141.7004 | 142.0178 | 142.3352 | 142.6526 | 142.97 | 143.1029 | 143.2359 | 143.3688 | 143.5017 | 143.6347 | 143.7676 | 143.9005 | 144.0335 | 144.1664 | 144.2993 | 144.4323 | 144.5652 | 144.6981 | 144.8311 | 144.964 | 145.0969 | 145.2299 | 145.3628 | 145.4957 | 145.6287 | 145.7616 | 145.8945 | 146.0275 | 146.1604 | 146.2933 | 146.4263 | 146.5592 | 146.6921 | 146.8251 | 146.958 | 146.958 | 146.958 | 146.958 | 146.958 | 146.958 | 146.958 | 146.958 | 146.958 | 146.958 | 146.958 | 146.958 | 146.958 | 146.958 | 146.958 | 146.958 | 146.958 | 146.958 | 146.958 | 146.958 | 146.958 | 146.958 | 146.958 | 146.958 | 146.958 | 146.958 | 146.958 | 146.958 | 146.958 | 146.958 | 146.958 | 146.893 | 146.828 | 146.763 | 146.698 | 146.633 | 146.568 | 146.503 | 146.438 | 146.373 | 146.308 | 146.243 | 146.178 | 146.113 | 146.048 | 145.983 | 145.918 | 145.853 | 145.788 | 145.723 | 145.658 | 145.593 | 145.528 | 145.463 | 145.398 | 145.333 | 145.268 | 145.203 | 145.138 | 145.073 | 145.008
12.15 | 0 | 4.677 | 9.354 | 14.031 | 18.708 | 23.385 | 28.062 | 32.739 | 37.416 | 42.093 | 46.77 | 53.7399 | 60.7097 | 67.6796 | 74.6495 | 81.6193 | 81.8209 | 82.0224 | 82.2239 | 82.4255 | 82.627 | 84.4336 | 86.2403 | 88.0469 | 89.8535 | 91.6602 | 93.4668 | 95.2734 | 97.0801 | 98.8867 | 100.6933 | 101.8978 | 103.1022 | 104.3066 | 105.511 | 106.7154 | 107.9199 | 109.1243 | 110.3287 | 111.5331 | 112.7376 | 113.942 | 115.1464 | 116.3508 | 117.5552 | 118.7597 | 119.8174 | 120.8751 | 121.9328 | 122.9905 | 124.0482 | 125.1059 | 126.1636 | 127.2214 | 128.2791 | 129.3368 | 130.3945 | 131.4522 | 132.5099 | 133.5676 | 134.6253 | 134.9463 | 135.2673 | 135.5883 | 135.9093 | 136.2303 | 136.5513 | 136.8723 | 137.1932 | 137.5142 | 137.8352 | 138.1562 | 138.4772 | 138.7982 | 139.1192 | 139.4402 | 139.7612 | 140.0821 | 140.4031 | 140.7241 | 141.0451 | 141.3661 | 141.6871 | 142.0081 | 142.3291 | 142.6501 | 142.971 | 143.292 | 143.613 | 143.934 | 144.255 | 144.3895 | 144.524 | 144.6585 | 144.793 | 144.9276 | 145.0621 | 145.1966 | 145.3311 | 145.4656 | 145.6001 | 145.7346 | 145.8691 | 146.0036 | 146.1382 | 146.2727 | 146.4072 | 146.5417 | 146.6762 | 146.8107 | 146.9452 | 147.0797 | 147.2142 | 147.3488 | 147.4833 | 147.6178 | 147.7523 | 147.8868 | 148.0213 | 148.1558 | 148.2903 | 148.2903 | 148.2903 | 148.2903 | 148.2903 | 148.2903 | 148.2903 | 148.2903 | 148.2903 | 148.2903 | 148.2903 | 148.2903 | 148.2903 | 148.2903 | 148.2903 | 148.2903 | 148.2903 | 148.2903 | 148.2903 | 148.2903 | 148.2903 | 148.2903 | 148.2903 | 148.2903 | 148.2903 | 148.2903 | 148.2903 | 148.2903 | 148.2903 | 148.2903 | 148.2903 | 148.2262 | 148.162 | 148.0978 | 148.0337 | 147.9695 | 147.9053 | 147.8412 | 147.777 | 147.7128 | 147.6487 | 147.5845 | 147.5203 | 147.4562 | 147.392 | 147.3278 | 147.2637 | 147.1995 | 147.1353 | 147.0712 | 147.007 | 146.9428 | 146.8787 | 146.8145 | 146.7503 | 146.6862 | 146.622 | 146.5578 | 146.4937 | 146.4295 | 146.3653
12.2 | 0 | 4.716 | 9.432 | 14.148 | 18.864 | 23.58 | 28.296 | 33.012 | 37.728 | 42.444 | 47.16 | 54.1989 | 61.2379 | 68.2768 | 75.3157 | 82.3547 | 82.5469 | 82.7392 | 82.9315 | 83.1237 | 83.316 | 85.1391 | 86.9621 | 88.7852 | 90.6083 | 92.4313 | 94.2544 | 96.0775 | 97.9005 | 99.7236 | 101.5467 | 102.762 | 103.9774 | 105.1928 | 106.4082 | 107.6236 | 108.8389 | 110.0543 | 111.2697 | 112.4851 | 113.7004 | 114.9158 | 116.1312 | 117.3466 | 118.562 | 119.7773 | 120.8457 | 121.914 | 122.9824 | 124.0508 | 125.1191 | 126.1875 | 127.2558 | 128.3242 | 129.3925 | 130.4609 | 131.5292 | 132.5976 | 133.666 | 134.7343 | 135.8027 | 136.1272 | 136.4518 | 136.7764 | 137.101 | 137.4256 | 137.7501 | 138.0747 | 138.3993 | 138.7239 | 139.0484 | 139.373 | 139.6976 | 140.0222 | 140.3468 | 140.6713 | 140.9959 | 141.3205 | 141.6451 | 141.9696 | 142.2942 | 142.6188 | 142.9434 | 143.268 | 143.5925 | 143.9171 | 144.2417 | 144.5663 | 144.8908 | 145.2154 | 145.54 | 145.6761 | 145.8122 | 145.9483 | 146.0844 | 146.2204 | 146.3565 | 146.4926 | 146.6287 | 146.7648 | 146.9009 | 147.037 | 147.1731 | 147.3092 | 147.4452 | 147.5813 | 147.7174 | 147.8535 | 147.9896 | 148.1257 | 148.2618 | 148.3979 | 148.534 | 148.67 | 148.8061 | 148.9422 | 149.0783 | 149.2144 | 149.3505 | 149.4866 | 149.6227 | 149.6227 | 149.6227 | 149.6227 | 149.6227 | 149.6227 | 149.6227 | 149.6227 | 149.6227 | 149.6227 | 149.6227 | 149.6227 | 149.6227 | 149.6227 | 149.6227 | 149.6227 | 149.6227 | 149.6227 | 149.6227 | 149.6227 | 149.6227 | 149.6227 | 149.6227 | 149.6227 | 149.6227 | 149.6227 | 149.6227 | 149.6227 | 149.6227 | 149.6227 | 149.6227 | 149.5593 | 149.496 | 149.4327 | 149.3693 | 149.306 | 149.2427 | 149.1793 | 149.116 | 149.0527 | 148.9893 | 148.926 | 148.8627 | 148.7993 | 148.736 | 148.6727 | 148.6093 | 148.546 | 148.4827 | 148.4193 | 148.356 | 148.2927 | 148.2293 | 148.166 | 148.1027 | 148.0393 | 147.976 | 147.9127 | 147.8493 | 147.786 | 147.7227
12.25 | 0 | 4.755 | 9.51 | 14.265 | 19.02 | 23.775 | 28.53 | 33.285 | 38.04 | 42.795 | 47.55 | 54.658 | 61.766 | 68.874 | 75.982 | 83.09 | 83.273 | 83.456 | 83.639 | 83.822 | 84.005 | 85.8445 | 87.684 | 89.5235 | 91.363 | 93.2025 | 95.042 | 96.8815 | 98.721 | 100.5605 | 102.4 | 103.6263 | 104.8527 | 106.079 | 107.3053 | 108.5317 | 109.758 | 110.9843 | 112.2107 | 113.437 | 114.6633 | 115.8897 | 117.116 | 118.3423 | 119.5687 | 120.795 | 121.874 | 122.953 | 124.032 | 125.111 | 126.19 | 127.269 | 128.348 | 129.427 | 130.506 | 131.585 | 132.664 | 133.743 | 134.822 | 135.901 | 136.98 | 137.3082 | 137.6363 | 137.9645 | 138.2927 | 138.6208 | 138.949 | 139.2772 | 139.6053 | 139.9335 | 140.2617 | 140.5898 | 140.918 | 141.2462 | 141.5743 | 141.9025 | 142.2307 | 142.5588 | 142.887 | 143.2152 | 143.5433 | 143.8715 | 144.1997 | 144.5278 | 144.856 | 145.1842 | 145.5123 | 145.8405 | 146.1687 | 146.4968 | 146.825 | 146.9627 | 147.1003 | 147.238 | 147.3757 | 147.5133 | 147.651 | 147.7887 | 147.9263 | 148.064 | 148.2017 | 148.3393 | 148.477 | 148.6147 | 148.7523 | 148.89 | 149.0277 | 149.1653 | 149.303 | 149.4407 | 149.5783 | 149.716 | 149.8537 | 149.9913 | 150.129 | 150.2667 | 150.4043 | 150.542 | 150.6797 | 150.8173 | 150.955 | 150.955 | 150.955 | 150.955 | 150.955 | 150.955 | 150.955 | 150.955 | 150.955 | 150.955 | 150.955 | 150.955 | 150.955 | 150.955 | 150.955 | 150.955 | 150.955 | 150.955 | 150.955 | 150.955 | 150.955 | 150.955 | 150.955 | 150.955 | 150.955 | 150.955 | 150.955 | 150.955 | 150.955 | 150.955 | 150.955 | 150.8925 | 150.83 | 150.7675 | 150.705 | 150.6425 | 150.58 | 150.5175 | 150.455 | 150.3925 | 150.33 | 150.2675 | 150.205 | 150.1425 | 150.08 | 150.0175 | 149.955 | 149.8925 | 149.83 | 149.7675 | 149.705 | 149.6425 | 149.58 | 149.5175 | 149.455 | 149.3925 | 149.33 | 149.2675 | 149.205 | 149.1425 | 149.08
12.3 | 0 | 4.794 | 9.588 | 14.382 | 19.176 | 23.97 | 28.764 | 33.558 | 38.352 | 43.146 | 47.94 | 55.1171 | 62.2941 | 69.4712 | 76.6483 | 83.8253 | 83.9991 | 84.1728 | 84.3465 | 84.5203 | 84.694 | 86.5499 | 88.4059 | 90.2618 | 92.1177 | 93.9737 | 95.8296 | 97.6855 | 99.5415 | 101.3974 | 103.2533 | 104.4906 | 105.7279 | 106.9652 | 108.2025 | 109.4398 | 110.6771 | 111.9144 | 113.1516 | 114.3889 | 115.6262 | 116.8635 | 118.1008 | 119.3381 | 120.5754 | 121.8127 | 122.9023 | 123.992 | 125.0816 | 126.1712 | 127.2609 | 128.3505 | 129.4402 | 130.5298 | 131.6195 | 132.7091 | 133.7988 | 134.8884 | 135.978 | 137.0677 | 138.1573 | 138.4891 | 138.8208 | 139.1526 | 139.4844 | 139.8161 | 140.1479 | 140.4796 | 140.8114 | 141.1431 | 141.4749 | 141.8066 | 142.1384 | 142.4702 | 142.8019 | 143.1337 | 143.4654 | 143.7972 | 144.1289 | 144.4607 | 144.7924 | 145.1242 | 145.456 | 145.7877 | 146.1195 | 146.4512 | 146.783 | 147.1147 | 147.4465 | 147.7782 | 148.11 | 148.2492 | 148.3885 | 148.5277 | 148.667 | 148.8062 | 148.9455 | 149.0847 | 149.224 | 149.3632 | 149.5024 | 149.6417 | 149.7809 | 149.9202 | 150.0594 | 150.1987 | 150.3379 | 150.4772 | 150.6164 | 150.7556 | 150.8949 | 151.0341 | 151.1734 | 151.3126 | 151.4519 | 151.5911 | 151.7304 | 151.8696 | 152.0088 | 152.1481 | 152.2873 | 152.2873 | 152.2873 | 152.2873 | 152.2873 | 152.2873 | 152.2873 | 152.2873 | 152.2873 | 152.2873 | 152.2873 | 152.2873 | 152.2873 | 152.2873 | 152.2873 | 152.2873 | 152.2873 | 152.2873 | 152.2873 | 152.2873 | 152.2873 | 152.2873 | 152.2873 | 152.2873 | 152.2873 | 152.2873 | 152.2873 | 152.2873 | 152.2873 | 152.2873 | 152.2873 | 152.2257 | 152.164 | 152.1023 | 152.0407 | 151.979 | 151.9173 | 151.8557 | 151.794 | 151.7323 | 151.6707 | 151.609 | 151.5473 | 151.4857 | 151.424 | 151.3623 | 151.3007 | 151.239 | 151.1773 | 151.1157 | 151.054 | 150.9923 | 150.9307 | 150.869 | 150.8073 | 150.7457 | 150.684 | 150.6223 | 150.5607 | 150.499 | 150.4373
12.35 | 0 | 4.833 | 9.666 | 14.499 | 19.332 | 24.165 | 28.998 | 33.831 | 38.664 | 43.497 | 48.33 | 55.5761 | 62.8223 | 70.0684 | 77.3145 | 84.5607 | 84.7251 | 84.8896 | 85.0541 | 85.2185 | 85.383 | 87.2554 | 89.1277 | 91.0001 | 92.8725 | 94.7448 | 96.6172 | 98.4896 | 100.3619 | 102.2343 | 104.1067 | 105.3549 | 106.6032 | 107.8514 | 109.0996 | 110.3479 | 111.5961 | 112.8444 | 114.0926 | 115.3409 | 116.5891 | 117.8374 | 119.0856 | 120.3338 | 121.5821 | 122.8303 | 123.9306 | 125.0309 | 126.1312 | 127.2315 | 128.3318 | 129.4321 | 130.5324 | 131.6326 | 132.7329 | 133.8332 | 134.9335 | 136.0338 | 137.1341 | 138.2344 | 139.3347 | 139.67 | 140.0054 | 140.3407 | 140.676 | 141.0114 | 141.3467 | 141.6821 | 142.0174 | 142.3528 | 142.6881 | 143.0235 | 143.3588 | 143.6941 | 144.0295 | 144.3648 | 144.7002 | 145.0355 | 145.3709 | 145.7062 | 146.0416 | 146.3769 | 146.7122 | 147.0476 | 147.3829 | 147.7183 | 148.0536 | 148.389 | 148.7243 | 149.0597 | 149.395 | 149.5358 | 149.6766 | 149.8175 | 149.9583 | 150.0991 | 150.2399 | 150.3808 | 150.5216 | 150.6624 | 150.8032 | 150.944 | 151.0849 | 151.2257 | 151.3665 | 151.5073 | 151.6482 | 151.789 | 151.9298 | 152.0706 | 152.2114 | 152.3523 | 152.4931 | 152.6339 | 152.7747 | 152.9156 | 153.0564 | 153.1972 | 153.338 | 153.4788 | 153.6197 | 153.6197 | 153.6197 | 153.6197 | 153.6197 | 153.6197 | 153.6197 | 153.6197 | 153.6197 | 153.6197 | 153.6197 | 153.6197 | 153.6197 | 153.6197 | 153.6197 | 153.6197 | 153.6197 | 153.6197 | 153.6197 | 153.6197 | 153.6197 | 153.6197 | 153.6197 | 153.6197 | 153.6197 | 153.6197 | 153.6197 | 153.6197 | 153.6197 | 153.6197 | 153.6197 | 153.5588 | 153.498 | 153.4372 | 153.3763 | 153.3155 | 153.2547 | 153.1938 | 153.133 | 153.0722 | 153.0113 | 152.9505 | 152.8897 | 152.8288 | 152.768 | 152.7072 | 152.6463 | 152.5855 | 152.5247 | 152.4638 | 152.403 | 152.3422 | 152.2813 | 152.2205 | 152.1597 | 152.0988 | 152.038 | 151.9772 | 151.9163 | 151.8555 | 151.7947
12.4 | 0 | 4.872 | 9.744 | 14.616 | 19.488 | 24.36 | 29.232 | 34.104 | 38.976 | 43.848 | 48.72 | 56.0352 | 63.3504 | 70.6656 | 77.9808 | 85.296 | 85.4512 | 85.6064 | 85.7616 | 85.9168 | 86.072 | 87.9608 | 89.8496 | 91.7384 | 93.6272 | 95.516 | 97.4048 | 99.2936 | 101.1824 | 103.0712 | 104.96 | 106.2192 | 107.4784 | 108.7376 | 109.9968 | 111.256 | 112.5152 | 113.7744 | 115.0336 | 116.2928 | 117.552 | 118.8112 | 120.0704 | 121.3296 | 122.5888 | 123.848 | 124.9589 | 126.0699 | 127.1808 | 128.2917 | 129.4027 | 130.5136 | 131.6245 | 132.7355 | 133.8464 | 134.9573 | 136.0683 | 137.1792 | 138.2901 | 139.4011 | 140.512 | 140.8509 | 141.1899 | 141.5288 | 141.8677 | 142.2067 | 142.5456 | 142.8845 | 143.2235 | 143.5624 | 143.9013 | 144.2403 | 144.5792 | 144.9181 | 145.2571 | 145.596 | 145.9349 | 146.2739 | 146.6128 | 146.9517 | 147.2907 | 147.6296 | 147.9685 | 148.3075 | 148.6464 | 148.9853 | 149.3243 | 149.6632 | 150.0021 | 150.3411 | 150.68 | 150.8224 | 150.9648 | 151.1072 | 151.2496 | 151.392 | 151.5344 | 151.6768 | 151.8192 | 151.9616 | 152.104 | 152.2464 | 152.3888 | 152.5312 | 152.6736 | 152.816 | 152.9584 | 153.1008 | 153.2432 | 153.3856 | 153.528 | 153.6704 | 153.8128 | 153.9552 | 154.0976 | 154.24 | 154.3824 | 154.5248 | 154.6672 | 154.8096 | 154.952 | 154.952 | 154.952 | 154.952 | 154.952 | 154.952 | 154.952 | 154.952 | 154.952 | 154.952 | 154.952 | 154.952 | 154.952 | 154.952 | 154.952 | 154.952 | 154.952 | 154.952 | 154.952 | 154.952 | 154.952 | 154.952 | 154.952 | 154.952 | 154.952 | 154.952 | 154.952 | 154.952 | 154.952 | 154.952 | 154.952 | 154.892 | 154.832 | 154.772 | 154.712 | 154.652 | 154.592 | 154.532 | 154.472 | 154.412 | 154.352 | 154.292 | 154.232 | 154.172 | 154.112 | 154.052 | 153.992 | 153.932 | 153.872 | 153.812 | 153.752 | 153.692 | 153.632 | 153.572 | 153.512 | 153.452 | 153.392 | 153.332 | 153.272 | 153.212 | 153.152
12.45 | 0 | 4.911 | 9.822 | 14.733 | 19.644 | 24.555 | 29.466 | 34.377 | 39.288 | 44.199 | 49.11 | 56.4943 | 63.8785 | 71.2628 | 78.6471 | 86.0313 | 86.1773 | 86.3232 | 86.4691 | 86.6151 | 86.761 | 88.6662 | 90.5715 | 92.4767 | 94.3819 | 96.2872 | 98.1924 | 100.0976 | 102.0029 | 103.9081 | 105.8133 | 107.0835 | 108.3536 | 109.6238 | 110.894 | 112.1641 | 113.4343 | 114.7044 | 115.9746 | 117.2447 | 118.5149 | 119.785 | 121.0552 | 122.3254 | 123.5955 | 124.8657 | 125.9872 | 127.1088 | 128.2304 | 129.352 | 130.4736 | 131.5951 | 132.7167 | 133.8383 | 134.9599 | 136.0814 | 137.203 | 138.3246 | 139.4462 | 140.5678 | 141.6893 | 142.0319 | 142.3744 | 142.7169 | 143.0594 | 143.4019 | 143.7445 | 144.087 | 144.4295 | 144.772 | 145.1146 | 145.4571 | 145.7996 | 146.1421 | 146.4846 | 146.8272 | 147.1697 | 147.5122 | 147.8547 | 148.1973 | 148.5398 | 148.8823 | 149.2248 | 149.5673 | 149.9099 | 150.2524 | 150.5949 | 150.9374 | 151.28 | 151.6225 | 151.965 | 152.109 | 152.253 | 152.3969 | 152.5409 | 152.6849 | 152.8289 | 152.9728 | 153.1168 | 153.2608 | 153.4048 | 153.5488 | 153.6927 | 153.8367 | 153.9807 | 154.1247 | 154.2686 | 154.4126 | 154.5566 | 154.7006 | 154.8446 | 154.9885 | 155.1325 | 155.2765 | 155.4205 | 155.5644 | 155.7084 | 155.8524 | 155.9964 | 156.1404 | 156.2843 | 156.2843 | 156.2843 | 156.2843 | 156.2843 | 156.2843 | 156.2843 | 156.2843 | 156.2843 | 156.2843 | 156.2843 | 156.2843 | 156.2843 | 156.2843 | 156.2843 | 156.2843 | 156.2843 | 156.2843 | 156.2843 | 156.2843 | 156.2843 | 156.2843 | 156.2843 | 156.2843 | 156.2843 | 156.2843 | 156.2843 | 156.2843 | 156.2843 | 156.2843 | 156.2843 | 156.2252 | 156.166 | 156.1068 | 156.0477 | 155.9885 | 155.9293 | 155.8702 | 155.811 | 155.7518 | 155.6927 | 155.6335 | 155.5743 | 155.5152 | 155.456 | 155.3968 | 155.3377 | 155.2785 | 155.2193 | 155.1602 | 155.101 | 155.0418 | 154.9827 | 154.9235 | 154.8643 | 154.8052 | 154.746 | 154.6868 | 154.6277 | 154.5685 | 154.5093
12.5 | 0 | 4.95 | 9.9 | 14.85 | 19.8 | 24.75 | 29.7 | 34.65 | 39.6 | 44.55 | 49.5 | 56.9533 | 64.4067 | 71.86 | 79.3133 | 86.7667 | 86.9033 | 87.04 | 87.1767 | 87.3133 | 87.45 | 89.3717 | 91.2933 | 93.215 | 95.1367 | 97.0583 | 98.98 | 100.9017 | 102.8233 | 104.745 | 106.6667 | 107.9478 | 109.2289 | 110.51 | 111.7911 | 113.0722 | 114.3533 | 115.6344 | 116.9156 | 118.1967 | 119.4778 | 120.7589 | 122.04 | 123.3211 | 124.6022 | 125.8833 | 127.0156 | 128.1478 | 129.28 | 130.4122 | 131.5444 | 132.6767 | 133.8089 | 134.9411 | 136.0733 | 137.2056 | 138.3378 | 139.47 | 140.6022 | 141.7344 | 142.8667 | 143.2128 | 143.5589 | 143.905 | 144.2511 | 144.5972 | 144.9433 | 145.2894 | 145.6356 | 145.9817 | 146.3278 | 146.6739 | 147.02 | 147.3661 | 147.7122 | 148.0583 | 148.4044 | 148.7506 | 149.0967 | 149.4428 | 149.7889 | 150.135 | 150.4811 | 150.8272 | 151.1733 | 151.5194 | 151.8656 | 152.2117 | 152.5578 | 152.9039 | 153.25 | 153.3956 | 153.5411 | 153.6867 | 153.8322 | 153.9778 | 154.1233 | 154.2689 | 154.4144 | 154.56 | 154.7056 | 154.8511 | 154.9967 | 155.1422 | 155.2878 | 155.4333 | 155.5789 | 155.7244 | 155.87 | 156.0156 | 156.1611 | 156.3067 | 156.4522 | 156.5978 | 156.7433 | 156.8889 | 157.0344 | 157.18 | 157.3256 | 157.4711 | 157.6167 | 157.6167 | 157.6167 | 157.6167 | 157.6167 | 157.6167 | 157.6167 | 157.6167 | 157.6167 | 157.6167 | 157.6167 | 157.6167 | 157.6167 | 157.6167 | 157.6167 | 157.6167 | 157.6167 | 157.6167 | 157.6167 | 157.6167 | 157.6167 | 157.6167 | 157.6167 | 157.6167 | 157.6167 | 157.6167 | 157.6167 | 157.6167 | 157.6167 | 157.6167 | 157.6167 | 157.5583 | 157.5 | 157.4417 | 157.3833 | 157.325 | 157.2667 | 157.2083 | 157.15 | 157.0917 | 157.0333 | 156.975 | 156.9167 | 156.8583 | 156.8 | 156.7417 | 156.6833 | 156.625 | 156.5667 | 156.5083 | 156.45 | 156.3917 | 156.3333 | 156.275 | 156.2167 | 156.1583 | 156.1 | 156.0417 | 155.9833 | 155.925 | 155.8667
12.55 | 0 | 4.989 | 9.978 | 14.967 | 19.956 | 24.945 | 29.934 | 34.923 | 39.912 | 44.901 | 49.89 | 57.4124 | 64.9348 | 72.4572 | 79.9796 | 87.502 | 87.6294 | 87.7568 | 87.8842 | 88.0116 | 88.139 | 90.0771 | 92.0152 | 93.9533 | 95.8914 | 97.8295 | 99.7676 | 101.7057 | 103.6438 | 105.5819 | 107.52 | 108.8121 | 110.1041 | 111.3962 | 112.6883 | 113.9803 | 115.2724 | 116.5645 | 117.8565 | 119.1486 | 120.4407 | 121.7327 | 123.0248 | 124.3169 | 125.6089 | 126.901 | 128.0439 | 129.1867 | 130.3296 | 131.4725 | 132.6153 | 133.7582 | 134.9011 | 136.0439 | 137.1868 | 138.3297 | 139.4725 | 140.6154 | 141.7583 | 142.9011 | 144.044 | 144.3937 | 144.7434 | 145.0931 | 145.4428 | 145.7925 | 146.1422 | 146.4919 | 146.8416 | 147.1913 | 147.541 | 147.8907 | 148.2404 | 148.5901 | 148.9398 | 149.2895 | 149.6392 | 149.9889 | 150.3386 | 150.6883 | 151.038 | 151.3877 | 151.7374 | 152.0871 | 152.4368 | 152.7865 | 153.1362 | 153.4859 | 153.8356 | 154.1853 | 154.535 | 154.6821 | 154.8293 | 154.9764 | 155.1235 | 155.2707 | 155.4178 | 155.5649 | 155.7121 | 155.8592 | 156.0063 | 156.1535 | 156.3006 | 156.4477 | 156.5949 | 156.742 | 156.8891 | 157.0363 | 157.1834 | 157.3305 | 157.4777 | 157.6248 | 157.7719 | 157.9191 | 158.0662 | 158.2133 | 158.3605 | 158.5076 | 158.6547 | 158.8019 | 158.949 | 158.949 | 158.949 | 158.949 | 158.949 | 158.949 | 158.949 | 158.949 | 158.949 | 158.949 | 158.949 | 158.949 | 158.949 | 158.949 | 158.949 | 158.949 | 158.949 | 158.949 | 158.949 | 158.949 | 158.949 | 158.949 | 158.949 | 158.949 | 158.949 | 158.949 | 158.949 | 158.949 | 158.949 | 158.949 | 158.949 | 158.8915 | 158.834 | 158.7765 | 158.719 | 158.6615 | 158.604 | 158.5465 | 158.489 | 158.4315 | 158.374 | 158.3165 | 158.259 | 158.2015 | 158.144 | 158.0865 | 158.029 | 157.9715 | 157.914 | 157.8565 | 157.799 | 157.7415 | 157.684 | 157.6265 | 157.569 | 157.5115 | 157.454 | 157.3965 | 157.339 | 157.2815 | 157.224
12.6 | 0 | 5.028 | 10.056 | 15.084 | 20.112 | 25.14 | 30.168 | 35.196 | 40.224 | 45.252 | 50.28 | 57.8715 | 65.4629 | 73.0544 | 80.6459 | 88.2373 | 88.3555 | 88.4736 | 88.5917 | 88.7099 | 88.828 | 90.7825 | 92.7371 | 94.6916 | 96.6461 | 98.6007 | 100.5552 | 102.5097 | 104.4643 | 106.4188 | 108.3733 | 109.6764 | 110.9794 | 112.2824 | 113.5854 | 114.8884 | 116.1915 | 117.4945 | 118.7975 | 120.1005 | 121.4036 | 122.7066 | 124.0096 | 125.3126 | 126.6156 | 127.9187 | 129.0722 | 130.2257 | 131.3792 | 132.5327 | 133.6862 | 134.8397 | 135.9932 | 137.1468 | 138.3003 | 139.4538 | 140.6073 | 141.7608 | 142.9143 | 144.0678 | 145.2213 | 145.5746 | 145.9279 | 146.2812 | 146.6345 | 146.9878 | 147.3411 | 147.6944 | 148.0476 | 148.4009 | 148.7542 | 149.1075 | 149.4608 | 149.8141 | 150.1674 | 150.5207 | 150.874 | 151.2272 | 151.5805 | 151.9338 | 152.2871 | 152.6404 | 152.9937 | 153.347 | 153.7003 | 154.0536 | 154.4068 | 154.7601 | 155.1134 | 155.4667 | 155.82 | 155.9687 | 156.1174 | 156.2661 | 156.4148 | 156.5636 | 156.7123 | 156.861 | 157.0097 | 157.1584 | 157.3071 | 157.4558 | 157.6045 | 157.7532 | 157.902 | 158.0507 | 158.1994 | 158.3481 | 158.4968 | 158.6455 | 158.7942 | 158.9429 | 159.0916 | 159.2404 | 159.3891 | 159.5378 | 159.6865 | 159.8352 | 159.9839 | 160.1326 | 160.2813 | 160.2813 | 160.2813 | 160.2813 | 160.2813 | 160.2813 | 160.2813 | 160.2813 | 160.2813 | 160.2813 | 160.2813 | 160.2813 | 160.2813 | 160.2813 | 160.2813 | 160.2813 | 160.2813 | 160.2813 | 160.2813 | 160.2813 | 160.2813 | 160.2813 | 160.2813 | 160.2813 | 160.2813 | 160.2813 | 160.2813 | 160.2813 | 160.2813 | 160.2813 | 160.2813 | 160.2247 | 160.168 | 160.1113 | 160.0547 | 159.998 | 159.9413 | 159.8847 | 159.828 | 159.7713 | 159.7147 | 159.658 | 159.6013 | 159.5447 | 159.488 | 159.4313 | 159.3747 | 159.318 | 159.2613 | 159.2047 | 159.148 | 159.0913 | 159.0347 | 158.978 | 158.9213 | 158.8647 | 158.808 | 158.7513 | 158.6947 | 158.638 | 158.5813
12.65 | 0 | 5.067 | 10.134 | 15.201 | 20.268 | 25.335 | 30.402 | 35.469 | 40.536 | 45.603 | 50.67 | 58.3305 | 65.9911 | 73.6516 | 81.3121 | 88.9727 | 89.0815 | 89.1904 | 89.2993 | 89.4081 | 89.517 | 91.488 | 93.4589 | 95.4299 | 97.4009 | 99.3718 | 101.3428 | 103.3138 | 105.2847 | 107.2557 | 109.2267 | 110.5406 | 111.8546 | 113.1686 | 114.4826 | 115.7966 | 117.1105 | 118.4245 | 119.7385 | 121.0525 | 122.3664 | 123.6804 | 124.9944 | 126.3084 | 127.6224 | 128.9363 | 130.1005 | 131.2646 | 132.4288 | 133.593 | 134.7571 | 135.9213 | 137.0854 | 138.2496 | 139.4137 | 140.5779 | 141.742 | 142.9062 | 144.0704 | 145.2345 | 146.3987 | 146.7555 | 147.1124 | 147.4693 | 147.8262 | 148.1831 | 148.5399 | 148.8968 | 149.2537 | 149.6106 | 149.9674 | 150.3243 | 150.6812 | 151.0381 | 151.395 | 151.7518 | 152.1087 | 152.4656 | 152.8225 | 153.1793 | 153.5362 | 153.8931 | 154.25 | 154.6069 | 154.9637 | 155.3206 | 155.6775 | 156.0344 | 156.3912 | 156.7481 | 157.105 | 157.2553 | 157.4056 | 157.5559 | 157.7062 | 157.8564 | 158.0067 | 158.157 | 158.3073 | 158.4576 | 158.6079 | 158.7582 | 158.9085 | 159.0588 | 159.209 | 159.3593 | 159.5096 | 159.6599 | 159.8102 | 159.9605 | 160.1108 | 160.2611 | 160.4114 | 160.5616 | 160.7119 | 160.8622 | 161.0125 | 161.1628 | 161.3131 | 161.4634 | 161.6137 | 161.6137 | 161.6137 | 161.6137 | 161.6137 | 161.6137 | 161.6137 | 161.6137 | 161.6137 | 161.6137 | 161.6137 | 161.6137 | 161.6137 | 161.6137 | 161.6137 | 161.6137 | 161.6137 | 161.6137 | 161.6137 | 161.6137 | 161.6137 | 161.6137 | 161.6137 | 161.6137 | 161.6137 | 161.6137 | 161.6137 | 161.6137 | 161.6137 | 161.6137 | 161.6137 | 161.5578 | 161.502 | 161.4462 | 161.3903 | 161.3345 | 161.2787 | 161.2228 | 161.167 | 161.1112 | 161.0553 | 160.9995 | 160.9437 | 160.8878 | 160.832 | 160.7762 | 160.7203 | 160.6645 | 160.6087 | 160.5528 | 160.497 | 160.4412 | 160.3853 | 160.3295 | 160.2737 | 160.2178 | 160.162 | 160.1062 | 160.0503 | 159.9945 | 159.9387
12.7 | 0 | 5.106 | 10.212 | 15.318 | 20.424 | 25.53 | 30.636 | 35.742 | 40.848 | 45.954 | 51.06 | 58.7896 | 66.5192 | 74.2488 | 81.9784 | 89.708 | 89.8076 | 89.9072 | 90.0068 | 90.1064 | 90.206 | 92.1934 | 94.1808 | 96.1682 | 98.1556 | 100.143 | 102.1304 | 104.1178 | 106.1052 | 108.0926 | 110.08 | 111.4049 | 112.7299 | 114.0548 | 115.3797 | 116.7047 | 118.0296 | 119.3545 | 120.6795 | 122.0044 | 123.3293 | 124.6543 | 125.9792 | 127.3041 | 128.6291 | 129.954 | 131.1288 | 132.3036 | 133.4784 | 134.6532 | 135.828 | 137.0028 | 138.1776 | 139.3524 | 140.5272 | 141.702 | 142.8768 | 144.0516 | 145.2264 | 146.4012 | 147.576 | 147.9365 | 148.2969 | 148.6574 | 149.0179 | 149.3783 | 149.7388 | 150.0993 | 150.4597 | 150.8202 | 151.1807 | 151.5411 | 151.9016 | 152.2621 | 152.6225 | 152.983 | 153.3435 | 153.7039 | 154.0644 | 154.4249 | 154.7853 | 155.1458 | 155.5063 | 155.8667 | 156.2272 | 156.5877 | 156.9481 | 157.3086 | 157.6691 | 158.0295 | 158.39 | 158.5419 | 158.6937 | 158.8456 | 158.9975 | 159.1493 | 159.3012 | 159.4531 | 159.6049 | 159.7568 | 159.9087 | 160.0605 | 160.2124 | 160.3643 | 160.5161 | 160.668 | 160.8199 | 160.9717 | 161.1236 | 161.2755 | 161.4273 | 161.5792 | 161.7311 | 161.8829 | 162.0348 | 162.1867 | 162.3385 | 162.4904 | 162.6423 | 162.7941 | 162.946 | 162.946 | 162.946 | 162.946 | 162.946 | 162.946 | 162.946 | 162.946 | 162.946 | 162.946 | 162.946 | 162.946 | 162.946 | 162.946 | 162.946 | 162.946 | 162.946 | 162.946 | 162.946 | 162.946 | 162.946 | 162.946 | 162.946 | 162.946 | 162.946 | 162.946 | 162.946 | 162.946 | 162.946 | 162.946 | 162.946 | 162.891 | 162.836 | 162.781 | 162.726 | 162.671 | 162.616 | 162.561 | 162.506 | 162.451 | 162.396 | 162.341 | 162.286 | 162.231 | 162.176 | 162.121 | 162.066 | 162.011 | 161.956 | 161.901 | 161.846 | 161.791 | 161.736 | 161.681 | 161.626 | 161.571 | 161.516 | 161.461 | 161.406 | 161.351 | 161.296
12.75 | 0 | 5.145 | 10.29 | 15.435 | 20.58 | 25.725 | 30.87 | 36.015 | 41.16 | 46.305 | 51.45 | 59.2487 | 67.0473 | 74.846 | 82.6447 | 90.4433 | 90.5337 | 90.624 | 90.7143 | 90.8047 | 90.895 | 92.8988 | 94.9027 | 96.9065 | 98.9103 | 100.9142 | 102.918 | 104.9218 | 106.9257 | 108.9295 | 110.9333 | 112.2692 | 113.6051 | 114.941 | 116.2769 | 117.6128 | 118.9487 | 120.2846 | 121.6204 | 122.9563 | 124.2922 | 125.6281 | 126.964 | 128.2999 | 129.6358 | 130.9717 | 132.1571 | 133.3426 | 134.528 | 135.7134 | 136.8989 | 138.0843 | 139.2698 | 140.4552 | 141.6407 | 142.8261 | 144.0116 | 145.197 | 146.3824 | 147.5679 | 148.7533 | 149.1174 | 149.4814 | 149.8455 | 150.2096 | 150.5736 | 150.9377 | 151.3017 | 151.6658 | 152.0298 | 152.3939 | 152.7579 | 153.122 | 153.4861 | 153.8501 | 154.2142 | 154.5782 | 154.9423 | 155.3063 | 155.6704 | 156.0344 | 156.3985 | 156.7626 | 157.1266 | 157.4907 | 157.8547 | 158.2188 | 158.5828 | 158.9469 | 159.3109 | 159.675 | 159.8284 | 159.9819 | 160.1353 | 160.2888 | 160.4422 | 160.5957 | 160.7491 | 160.9026 | 161.056 | 161.2094 | 161.3629 | 161.5163 | 161.6698 | 161.8232 | 161.9767 | 162.1301 | 162.2836 | 162.437 | 162.5904 | 162.7439 | 162.8973 | 163.0508 | 163.2042 | 163.3577 | 163.5111 | 163.6646 | 163.818 | 163.9714 | 164.1249 | 164.2783 | 164.2783 | 164.2783 | 164.2783 | 164.2783 | 164.2783 | 164.2783 | 164.2783 | 164.2783 | 164.2783 | 164.2783 | 164.2783 | 164.2783 | 164.2783 | 164.2783 | 164.2783 | 164.2783 | 164.2783 | 164.2783 | 164.2783 | 164.2783 | 164.2783 | 164.2783 | 164.2783 | 164.2783 | 164.2783 | 164.2783 | 164.2783 | 164.2783 | 164.2783 | 164.2783 | 164.2242 | 164.17 | 164.1158 | 164.0617 | 164.0075 | 163.9533 | 163.8992 | 163.845 | 163.7908 | 163.7367 | 163.6825 | 163.6283 | 163.5742 | 163.52 | 163.4658 | 163.4117 | 163.3575 | 163.3033 | 163.2492 | 163.195 | 163.1408 | 163.0867 | 163.0325 | 162.9783 | 162.9242 | 162.87 | 162.8158 | 162.7617 | 162.7075 | 162.6533
12.8 | 0 | 5.184 | 10.368 | 15.552 | 20.736 | 25.92 | 31.104 | 36.288 | 41.472 | 46.656 | 51.84 | 59.7077 | 67.5755 | 75.4432 | 83.3109 | 91.1787 | 91.2597 | 91.3408 | 91.4219 | 91.5029 | 91.584 | 93.6043 | 95.6245 | 97.6448 | 99.6651 | 101.6853 | 103.7056 | 105.7259 | 107.7461 | 109.7664 | 111.7867 | 113.1335 | 114.4804 | 115.8272 | 117.174 | 118.5209 | 119.8677 | 121.2146 | 122.5614 | 123.9083 | 125.2551 | 126.602 | 127.9488 | 129.2956 | 130.6425 | 131.9893 | 133.1854 | 134.3815 | 135.5776 | 136.7737 | 137.9698 | 139.1659 | 140.362 | 141.558 | 142.7541 | 143.9502 | 145.1463 | 146.3424 | 147.5385 | 148.7346 | 149.9307 | 150.2983 | 150.666 | 151.0336 | 151.4012 | 151.7689 | 152.1365 | 152.5042 | 152.8718 | 153.2395 | 153.6071 | 153.9748 | 154.3424 | 154.71 | 155.0777 | 155.4453 | 155.813 | 156.1806 | 156.5483 | 156.9159 | 157.2836 | 157.6512 | 158.0188 | 158.3865 | 158.7541 | 159.1218 | 159.4894 | 159.8571 | 160.2247 | 160.5924 | 160.96 | 161.115 | 161.27 | 161.4251 | 161.5801 | 161.7351 | 161.8901 | 162.0452 | 162.2002 | 162.3552 | 162.5102 | 162.6652 | 162.8203 | 162.9753 | 163.1303 | 163.2853 | 163.4404 | 163.5954 | 163.7504 | 163.9054 | 164.0604 | 164.2155 | 164.3705 | 164.5255 | 164.6805 | 164.8356 | 164.9906 | 165.1456 | 165.3006 | 165.4556 | 165.6107 | 165.6107 | 165.6107 | 165.6107 | 165.6107 | 165.6107 | 165.6107 | 165.6107 | 165.6107 | 165.6107 | 165.6107 | 165.6107 | 165.6107 | 165.6107 | 165.6107 | 165.6107 | 165.6107 | 165.6107 | 165.6107 | 165.6107 | 165.6107 | 165.6107 | 165.6107 | 165.6107 | 165.6107 | 165.6107 | 165.6107 | 165.6107 | 165.6107 | 165.6107 | 165.6107 | 165.5573 | 165.504 | 165.4507 | 165.3973 | 165.344 | 165.2907 | 165.2373 | 165.184 | 165.1307 | 165.0773 | 165.024 | 164.9707 | 164.9173 | 164.864 | 164.8107 | 164.7573 | 164.704 | 164.6507 | 164.5973 | 164.544 | 164.4907 | 164.4373 | 164.384 | 164.3307 | 164.2773 | 164.224 | 164.1707 | 164.1173 | 164.064 | 164.0107
12.85 | 0 | 5.223 | 10.446 | 15.669 | 20.892 | 26.115 | 31.338 | 36.561 | 41.784 | 47.007 | 52.23 | 60.1668 | 68.1036 | 76.0404 | 83.9772 | 91.914 | 91.9858 | 92.0576 | 92.1294 | 92.2012 | 92.273 | 94.3097 | 96.3464 | 98.3831 | 100.4198 | 102.4565 | 104.4932 | 106.5299 | 108.5666 | 110.6033 | 112.64 | 113.9978 | 115.3556 | 116.7134 | 118.0712 | 119.429 | 120.7868 | 122.1446 | 123.5024 | 124.8602 | 126.218 | 127.5758 | 128.9336 | 130.2914 | 131.6492 | 133.007 | 134.2137 | 135.4205 | 136.6272 | 137.8339 | 139.0407 | 140.2474 | 141.4541 | 142.6609 | 143.8676 | 145.0743 | 146.2811 | 147.4878 | 148.6945 | 149.9013 | 151.108 | 151.4792 | 151.8505 | 152.2217 | 152.5929 | 152.9642 | 153.3354 | 153.7066 | 154.0779 | 154.4491 | 154.8203 | 155.1916 | 155.5628 | 155.934 | 156.3053 | 156.6765 | 157.0477 | 157.419 | 157.7902 | 158.1614 | 158.5327 | 158.9039 | 159.2751 | 159.6464 | 160.0176 | 160.3888 | 160.7601 | 161.1313 | 161.5025 | 161.8738 | 162.245 | 162.4016 | 162.5582 | 162.7148 | 162.8714 | 163.028 | 163.1846 | 163.3412 | 163.4978 | 163.6544 | 163.811 | 163.9676 | 164.1242 | 164.2808 | 164.4374 | 164.594 | 164.7506 | 164.9072 | 165.0638 | 165.2204 | 165.377 | 165.5336 | 165.6902 | 165.8468 | 166.0034 | 166.16 | 166.3166 | 166.4732 | 166.6298 | 166.7864 | 166.943 | 166.943 | 166.943 | 166.943 | 166.943 | 166.943 | 166.943 | 166.943 | 166.943 | 166.943 | 166.943 | 166.943 | 166.943 | 166.943 | 166.943 | 166.943 | 166.943 | 166.943 | 166.943 | 166.943 | 166.943 | 166.943 | 166.943 | 166.943 | 166.943 | 166.943 | 166.943 | 166.943 | 166.943 | 166.943 | 166.943 | 166.8905 | 166.838 | 166.7855 | 166.733 | 166.6805 | 166.628 | 166.5755 | 166.523 | 166.4705 | 166.418 | 166.3655 | 166.313 | 166.2605 | 166.208 | 166.1555 | 166.103 | 166.0505 | 165.998 | 165.9455 | 165.893 | 165.8405 | 165.788 | 165.7355 | 165.683 | 165.6305 | 165.578 | 165.5255 | 165.473 | 165.4205 | 165.368
12.9 | 0 | 5.262 | 10.524 | 15.786 | 21.048 | 26.31 | 31.572 | 36.834 | 42.096 | 47.358 | 52.62 | 60.6259 | 68.6317 | 76.6376 | 84.6435 | 92.6493 | 92.7119 | 92.7744 | 92.8369 | 92.8995 | 92.962 | 95.0151 | 97.0683 | 99.1214 | 101.1745 | 103.2277 | 105.2808 | 107.3339 | 109.3871 | 111.4402 | 113.4933 | 114.8621 | 116.2308 | 117.5996 | 118.9684 | 120.3371 | 121.7059 | 123.0746 | 124.4434 | 125.8121 | 127.1809 | 128.5496 | 129.9184 | 131.2872 | 132.6559 | 134.0247 | 135.242 | 136.4594 | 137.6768 | 138.8942 | 140.1116 | 141.3289 | 142.5463 | 143.7637 | 144.9811 | 146.1984 | 147.4158 | 148.6332 | 149.8506 | 151.068 | 152.2853 | 152.6602 | 153.035 | 153.4098 | 153.7846 | 154.1594 | 154.5343 | 154.9091 | 155.2839 | 155.6587 | 156.0336 | 156.4084 | 156.7832 | 157.158 | 157.5328 | 157.9077 | 158.2825 | 158.6573 | 159.0321 | 159.407 | 159.7818 | 160.1566 | 160.5314 | 160.9062 | 161.2811 | 161.6559 | 162.0307 | 162.4055 | 162.7804 | 163.1552 | 163.53 | 163.6882 | 163.8464 | 164.0045 | 164.1627 | 164.3209 | 164.4791 | 164.6372 | 164.7954 | 164.9536 | 165.1118 | 165.27 | 165.4281 | 165.5863 | 165.7445 | 165.9027 | 166.0608 | 166.219 | 166.3772 | 166.5354 | 166.6936 | 166.8517 | 167.0099 | 167.1681 | 167.3263 | 167.4844 | 167.6426 | 167.8008 | 167.959 | 168.1172 | 168.2753 | 168.2753 | 168.2753 | 168.2753 | 168.2753 | 168.2753 | 168.2753 | 168.2753 | 168.2753 | 168.2753 | 168.2753 | 168.2753 | 168.2753 | 168.2753 | 168.2753 | 168.2753 | 168.2753 | 168.2753 | 168.2753 | 168.2753 | 168.2753 | 168.2753 | 168.2753 | 168.2753 | 168.2753 | 168.2753 | 168.2753 | 168.2753 | 168.2753 | 168.2753 | 168.2753 | 168.2237 | 168.172 | 168.1203 | 168.0687 | 168.017 | 167.9653 | 167.9137 | 167.862 | 167.8103 | 167.7587 | 167.707 | 167.6553 | 167.6037 | 167.552 | 167.5003 | 167.4487 | 167.397 | 167.3453 | 167.2937 | 167.242 | 167.1903 | 167.1387 | 167.087 | 167.0353 | 166.9837 | 166.932 | 166.8803 | 166.8287 | 166.777 | 166.7253
12.95 | 0 | 5.301 | 10.602 | 15.903 | 21.204 | 26.505 | 31.806 | 37.107 | 42.408 | 47.709 | 53.01 | 61.0849 | 69.1599 | 77.2348 | 85.3097 | 93.3847 | 93.4379 | 93.4912 | 93.5445 | 93.5977 | 93.651 | 95.7206 | 97.7901 | 99.8597 | 101.9293 | 103.9988 | 106.0684 | 108.138 | 110.2075 | 112.2771 | 114.3467 | 115.7264 | 117.1061 | 118.4858 | 119.8655 | 121.2452 | 122.6249 | 124.0046 | 125.3844 | 126.7641 | 128.1438 | 129.5235 | 130.9032 | 132.2829 | 133.6626 | 135.0423 | 136.2704 | 137.4984 | 138.7264 | 139.9544 | 141.1824 | 142.4105 | 143.6385 | 144.8665 | 146.0945 | 147.3226 | 148.5506 | 149.7786 | 151.0066 | 152.2346 | 153.4627 | 153.8411 | 154.2195 | 154.5979 | 154.9763 | 155.3547 | 155.7331 | 156.1115 | 156.49 | 156.8684 | 157.2468 | 157.6252 | 158.0036 | 158.382 | 158.7604 | 159.1388 | 159.5172 | 159.8957 | 160.2741 | 160.6525 | 161.0309 | 161.4093 | 161.7877 | 162.1661 | 162.5445 | 162.9229 | 163.3014 | 163.6798 | 164.0582 | 164.4366 | 164.815 | 164.9748 | 165.1345 | 165.2943 | 165.454 | 165.6138 | 165.7735 | 165.9333 | 166.093 | 166.2528 | 166.4126 | 166.5723 | 166.7321 | 166.8918 | 167.0516 | 167.2113 | 167.3711 | 167.5308 | 167.6906 | 167.8504 | 168.0101 | 168.1699 | 168.3296 | 168.4894 | 168.6491 | 168.8089 | 168.9686 | 169.1284 | 169.2882 | 169.4479 | 169.6077 | 169.6077 | 169.6077 | 169.6077 | 169.6077 | 169.6077 | 169.6077 | 169.6077 | 169.6077 | 169.6077 | 169.6077 | 169.6077 | 169.6077 | 169.6077 | 169.6077 | 169.6077 | 169.6077 | 169.6077 | 169.6077 | 169.6077 | 169.6077 | 169.6077 | 169.6077 | 169.6077 | 169.6077 | 169.6077 | 169.6077 | 169.6077 | 169.6077 | 169.6077 | 169.6077 | 169.5568 | 169.506 | 169.4552 | 169.4043 | 169.3535 | 169.3027 | 169.2518 | 169.201 | 169.1502 | 169.0993 | 169.0485 | 168.9977 | 168.9468 | 168.896 | 168.8452 | 168.7943 | 168.7435 | 168.6927 | 168.6418 | 168.591 | 168.5402 | 168.4893 | 168.4385 | 168.3877 | 168.3368 | 168.286 | 168.2352 | 168.1843 | 168.1335 | 168.0827
13 | 0 | 5.34 | 10.68 | 16.02 | 21.36 | 26.7 | 32.04 | 37.38 | 42.72 | 48.06 | 53.4 | 61.544 | 69.688 | 77.832 | 85.976 | 94.12 | 94.164 | 94.208 | 94.252 | 94.296 | 94.34 | 96.426 | 98.512 | 100.598 | 102.684 | 104.77 | 106.856 | 108.942 | 111.028 | 113.114 | 115.2 | 116.5907 | 117.9813 | 119.372 | 120.7627 | 122.1533 | 123.544 | 124.9347 | 126.3253 | 127.716 | 129.1067 | 130.4973 | 131.888 | 133.2787 | 134.6693 | 136.06 | 137.2987 | 138.5373 | 139.776 | 141.0147 | 142.2533 | 143.492 | 144.7307 | 145.9693 | 147.208 | 148.4467 | 149.6853 | 150.924 | 152.1627 | 153.4013 | 154.64 | 155.022 | 155.404 | 155.786 | 156.168 | 156.55 | 156.932 | 157.314 | 157.696 | 158.078 | 158.46 | 158.842 | 159.224 | 159.606 | 159.988 | 160.37 | 160.752 | 161.134 | 161.516 | 161.898 | 162.28 | 162.662 | 163.044 | 163.426 | 163.808 | 164.19 | 164.572 | 164.954 | 165.336 | 165.718 | 166.1 | 166.2613 | 166.4227 | 166.584 | 166.7453 | 166.9067 | 167.068 | 167.2293 | 167.3907 | 167.552 | 167.7133 | 167.8747 | 168.036 | 168.1973 | 168.3587 | 168.52 | 168.6813 | 168.8427 | 169.004 | 169.1653 | 169.3267 | 169.488 | 169.6493 | 169.8107 | 169.972 | 170.1333 | 170.2947 | 170.456 | 170.6173 | 170.7787 | 170.94 | 170.94 | 170.94 | 170.94 | 170.94 | 170.94 | 170.94 | 170.94 | 170.94 | 170.94 | 170.94 | 170.94 | 170.94 | 170.94 | 170.94 | 170.94 | 170.94 | 170.94 | 170.94 | 170.94 | 170.94 | 170.94 | 170.94 | 170.94 | 170.94 | 170.94 | 170.94 | 170.94 | 170.94 | 170.94 | 170.94 | 170.89 | 170.84 | 170.79 | 170.74 | 170.69 | 170.64 | 170.59 | 170.54 | 170.49 | 170.44 | 170.39 | 170.34 | 170.29 | 170.24 | 170.19 | 170.14 | 170.09 | 170.04 | 169.99 | 169.94 | 169.89 | 169.84 | 169.79 | 169.74 | 169.69 | 169.64 | 169.59 | 169.54 | 169.49 | 169.44
13.05 | 0 | 5.379 | 10.758 | 16.137 | 21.516 | 26.895 | 32.274 | 37.653 | 43.032 | 48.411 | 53.79 | 62.0031 | 70.2161 | 78.4292 | 86.6423 | 94.8553 | 94.8901 | 94.9248 | 94.9595 | 94.9943 | 95.029 | 97.1314 | 99.2339 | 101.3363 | 103.4387 | 105.5412 | 107.6436 | 109.746 | 111.8485 | 113.9509 | 116.0533 | 117.455 | 118.8566 | 120.2582 | 121.6598 | 123.0614 | 124.4631 | 125.8647 | 127.2663 | 128.6679 | 130.0696 | 131.4712 | 132.8728 | 134.2744 | 135.676 | 137.0777 | 138.327 | 139.5763 | 140.8256 | 142.0749 | 143.3242 | 144.5735 | 145.8228 | 147.0722 | 148.3215 | 149.5708 | 150.8201 | 152.0694 | 153.3187 | 154.568 | 155.8173 | 156.2029 | 156.5885 | 156.9741 | 157.3597 | 157.7453 | 158.1309 | 158.5165 | 158.902 | 159.2876 | 159.6732 | 160.0588 | 160.4444 | 160.83 | 161.2156 | 161.6012 | 161.9868 | 162.3723 | 162.7579 | 163.1435 | 163.5291 | 163.9147 | 164.3003 | 164.6859 | 165.0715 | 165.4571 | 165.8426 | 166.2282 | 166.6138 | 166.9994 | 167.385 | 167.5479 | 167.7108 | 167.8737 | 168.0366 | 168.1996 | 168.3625 | 168.5254 | 168.6883 | 168.8512 | 169.0141 | 169.177 | 169.3399 | 169.5028 | 169.6658 | 169.8287 | 169.9916 | 170.1545 | 170.3174 | 170.4803 | 170.6432 | 170.8061 | 170.969 | 171.132 | 171.2949 | 171.4578 | 171.6207 | 171.7836 | 171.9465 | 172.1094 | 172.2723 | 172.2723 | 172.2723 | 172.2723 | 172.2723 | 172.2723 | 172.2723 | 172.2723 | 172.2723 | 172.2723 | 172.2723 | 172.2723 | 172.2723 | 172.2723 | 172.2723 | 172.2723 | 172.2723 | 172.2723 | 172.2723 | 172.2723 | 172.2723 | 172.2723 | 172.2723 | 172.2723 | 172.2723 | 172.2723 | 172.2723 | 172.2723 | 172.2723 | 172.2723 | 172.2723 | 172.2232 | 172.174 | 172.1248 | 172.0757 | 172.0265 | 171.9773 | 171.9282 | 171.879 | 171.8298 | 171.7807 | 171.7315 | 171.6823 | 171.6332 | 171.584 | 171.5348 | 171.4857 | 171.4365 | 171.3873 | 171.3382 | 171.289 | 171.2398 | 171.1907 | 171.1415 | 171.0923 | 171.0432 | 170.994 | 170.9448 | 170.8957 | 170.8465 | 170.7973
13.1 | 0 | 5.418 | 10.836 | 16.254 | 21.672 | 27.09 | 32.508 | 37.926 | 43.344 | 48.762 | 54.18 | 62.4621 | 70.7443 | 79.0264 | 87.3085 | 95.5907 | 95.6161 | 95.6416 | 95.6671 | 95.6925 | 95.718 | 97.8369 | 99.9557 | 102.0746 | 104.1935 | 106.3123 | 108.4312 | 110.5501 | 112.6689 | 114.7878 | 116.9067 | 118.3192 | 119.7318 | 121.1444 | 122.557 | 123.9696 | 125.3821 | 126.7947 | 128.2073 | 129.6199 | 131.0324 | 132.445 | 133.8576 | 135.2702 | 136.6828 | 138.0953 | 139.3553 | 140.6152 | 141.8752 | 143.1352 | 144.3951 | 145.6551 | 146.915 | 148.175 | 149.4349 | 150.6949 | 151.9548 | 153.2148 | 154.4748 | 155.7347 | 156.9947 | 157.3838 | 157.773 | 158.1622 | 158.5514 | 158.9406 | 159.3297 | 159.7189 | 160.1081 | 160.4973 | 160.8864 | 161.2756 | 161.6648 | 162.054 | 162.4432 | 162.8323 | 163.2215 | 163.6107 | 163.9999 | 164.389 | 164.7782 | 165.1674 | 165.5566 | 165.9458 | 166.3349 | 166.7241 | 167.1133 | 167.5025 | 167.8916 | 168.2808 | 168.67 | 168.8345 | 168.999 | 169.1635 | 169.328 | 169.4924 | 169.6569 | 169.8214 | 169.9859 | 170.1504 | 170.3149 | 170.4794 | 170.6439 | 170.8084 | 170.9728 | 171.1373 | 171.3018 | 171.4663 | 171.6308 | 171.7953 | 171.9598 | 172.1243 | 172.2888 | 172.4532 | 172.6177 | 172.7822 | 172.9467 | 173.1112 | 173.2757 | 173.4402 | 173.6047 | 173.6047 | 173.6047 | 173.6047 | 173.6047 | 173.6047 | 173.6047 | 173.6047 | 173.6047 | 173.6047 | 173.6047 | 173.6047 | 173.6047 | 173.6047 | 173.6047 | 173.6047 | 173.6047 | 173.6047 | 173.6047 | 173.6047 | 173.6047 | 173.6047 | 173.6047 | 173.6047 | 173.6047 | 173.6047 | 173.6047 | 173.6047 | 173.6047 | 173.6047 | 173.6047 | 173.5563 | 173.508 | 173.4597 | 173.4113 | 173.363 | 173.3147 | 173.2663 | 173.218 | 173.1697 | 173.1213 | 173.073 | 173.0247 | 172.9763 | 172.928 | 172.8797 | 172.8313 | 172.783 | 172.7347 | 172.6863 | 172.638 | 172.5897 | 172.5413 | 172.493 | 172.4447 | 172.3963 | 172.348 | 172.2997 | 172.2513 | 172.203 | 172.1547
13.15 | 0 | 5.457 | 10.914 | 16.371 | 21.828 | 27.285 | 32.742 | 38.199 | 43.656 | 49.113 | 54.57 | 62.9212 | 71.2724 | 79.6236 | 87.9748 | 96.326 | 96.3422 | 96.3584 | 96.3746 | 96.3908 | 96.407 | 98.5423 | 100.6776 | 102.8129 | 104.9482 | 107.0835 | 109.2188 | 111.3541 | 113.4894 | 115.6247 | 117.76 | 119.1835 | 120.6071 | 122.0306 | 123.4541 | 124.8777 | 126.3012 | 127.7247 | 129.1483 | 130.5718 | 131.9953 | 133.4189 | 134.8424 | 136.2659 | 137.6895 | 139.113 | 140.3836 | 141.6542 | 142.9248 | 144.1954 | 145.466 | 146.7366 | 148.0072 | 149.2778 | 150.5484 | 151.819 | 153.0896 | 154.3602 | 155.6308 | 156.9014 | 158.172 | 158.5648 | 158.9575 | 159.3503 | 159.7431 | 160.1358 | 160.5286 | 160.9214 | 161.3141 | 161.7069 | 162.0997 | 162.4924 | 162.8852 | 163.278 | 163.6707 | 164.0635 | 164.4563 | 164.849 | 165.2418 | 165.6346 | 166.0273 | 166.4201 | 166.8129 | 167.2056 | 167.5984 | 167.9912 | 168.3839 | 168.7767 | 169.1695 | 169.5622 | 169.955 | 170.1211 | 170.2871 | 170.4532 | 170.6193 | 170.7853 | 170.9514 | 171.1175 | 171.2835 | 171.4496 | 171.6157 | 171.7817 | 171.9478 | 172.1139 | 172.2799 | 172.446 | 172.6121 | 172.7781 | 172.9442 | 173.1103 | 173.2763 | 173.4424 | 173.6085 | 173.7745 | 173.9406 | 174.1067 | 174.2727 | 174.4388 | 174.6049 | 174.7709 | 174.937 | 174.937 | 174.937 | 174.937 | 174.937 | 174.937 | 174.937 | 174.937 | 174.937 | 174.937 | 174.937 | 174.937 | 174.937 | 174.937 | 174.937 | 174.937 | 174.937 | 174.937 | 174.937 | 174.937 | 174.937 | 174.937 | 174.937 | 174.937 | 174.937 | 174.937 | 174.937 | 174.937 | 174.937 | 174.937 | 174.937 | 174.8895 | 174.842 | 174.7945 | 174.747 | 174.6995 | 174.652 | 174.6045 | 174.557 | 174.5095 | 174.462 | 174.4145 | 174.367 | 174.3195 | 174.272 | 174.2245 | 174.177 | 174.1295 | 174.082 | 174.0345 | 173.987 | 173.9395 | 173.892 | 173.8445 | 173.797 | 173.7495 | 173.702 | 173.6545 | 173.607 | 173.5595 | 173.512
13.2 | 0 | 5.496 | 10.992 | 16.488 | 21.984 | 27.48 | 32.976 | 38.472 | 43.968 | 49.464 | 54.96 | 63.3803 | 71.8005 | 80.2208 | 88.6411 | 97.0613 | 97.0683 | 97.0752 | 97.0821 | 97.0891 | 97.096 | 99.2477 | 101.3995 | 103.5512 | 105.7029 | 107.8547 | 110.0064 | 112.1581 | 114.3099 | 116.4616 | 118.6133 | 120.0478 | 121.4823 | 122.9168 | 124.3513 | 125.7858 | 127.2203 | 128.6548 | 130.0892 | 131.5237 | 132.9582 | 134.3927 | 135.8272 | 137.2617 | 138.6962 | 140.1307 | 141.4119 | 142.6932 | 143.9744 | 145.2556 | 146.5369 | 147.8181 | 149.0994 | 150.3806 | 151.6619 | 152.9431 | 154.2244 | 155.5056 | 156.7868 | 158.0681 | 159.3493 | 159.7457 | 160.142 | 160.5384 | 160.9348 | 161.3311 | 161.7275 | 162.1238 | 162.5202 | 162.9165 | 163.3129 | 163.7092 | 164.1056 | 164.502 | 164.8983 | 165.2947 | 165.691 | 166.0874 | 166.4837 | 166.8801 | 167.2764 | 167.6728 | 168.0692 | 168.4655 | 168.8619 | 169.2582 | 169.6546 | 170.0509 | 170.4473 | 170.8436 | 171.24 | 171.4076 | 171.5753 | 171.7429 | 171.9106 | 172.0782 | 172.2459 | 172.4135 | 172.5812 | 172.7488 | 172.9164 | 173.0841 | 173.2517 | 173.4194 | 173.587 | 173.7547 | 173.9223 | 174.09 | 174.2576 | 174.4252 | 174.5929 | 174.7605 | 174.9282 | 175.0958 | 175.2635 | 175.4311 | 175.5988 | 175.7664 | 175.934 | 176.1017 | 176.2693 | 176.2693 | 176.2693 | 176.2693 | 176.2693 | 176.2693 | 176.2693 | 176.2693 | 176.2693 | 176.2693 | 176.2693 | 176.2693 | 176.2693 | 176.2693 | 176.2693 | 176.2693 | 176.2693 | 176.2693 | 176.2693 | 176.2693 | 176.2693 | 176.2693 | 176.2693 | 176.2693 | 176.2693 | 176.2693 | 176.2693 | 176.2693 | 176.2693 | 176.2693 | 176.2693 | 176.2227 | 176.176 | 176.1293 | 176.0827 | 176.036 | 175.9893 | 175.9427 | 175.896 | 175.8493 | 175.8027 | 175.756 | 175.7093 | 175.6627 | 175.616 | 175.5693 | 175.5227 | 175.476 | 175.4293 | 175.3827 | 175.336 | 175.2893 | 175.2427 | 175.196 | 175.1493 | 175.1027 | 175.056 | 175.0093 | 174.9627 | 174.916 | 174.8693
13.25 | 0 | 5.535 | 11.07 | 16.605 | 22.14 | 27.675 | 33.21 | 38.745 | 44.28 | 49.815 | 55.35 | 63.8393 | 72.3287 | 80.818 | 89.3073 | 97.7967 | 97.7943 | 97.792 | 97.7897 | 97.7873 | 97.785 | 99.9532 | 102.1213 | 104.2895 | 106.4577 | 108.6258 | 110.794 | 112.9622 | 115.1303 | 117.2985 | 119.4667 | 120.9121 | 122.3576 | 123.803 | 125.2484 | 126.6939 | 128.1393 | 129.5848 | 131.0302 | 132.4757 | 133.9211 | 135.3666 | 136.812 | 138.2574 | 139.7029 | 141.1483 | 142.4402 | 143.7321 | 145.024 | 146.3159 | 147.6078 | 148.8997 | 150.1916 | 151.4834 | 152.7753 | 154.0672 | 155.3591 | 156.651 | 157.9429 | 159.2348 | 160.5267 | 160.9266 | 161.3266 | 161.7265 | 162.1264 | 162.5264 | 162.9263 | 163.3263 | 163.7262 | 164.1262 | 164.5261 | 164.9261 | 165.326 | 165.7259 | 166.1259 | 166.5258 | 166.9258 | 167.3257 | 167.7257 | 168.1256 | 168.5256 | 168.9255 | 169.3254 | 169.7254 | 170.1253 | 170.5253 | 170.9252 | 171.3252 | 171.7251 | 172.1251 | 172.525 | 172.6942 | 172.8634 | 173.0327 | 173.2019 | 173.3711 | 173.5403 | 173.7096 | 173.8788 | 174.048 | 174.2172 | 174.3864 | 174.5557 | 174.7249 | 174.8941 | 175.0633 | 175.2326 | 175.4018 | 175.571 | 175.7402 | 175.9094 | 176.0787 | 176.2479 | 176.4171 | 176.5863 | 176.7556 | 176.9248 | 177.094 | 177.2632 | 177.4324 | 177.6017 | 177.6017 | 177.6017 | 177.6017 | 177.6017 | 177.6017 | 177.6017 | 177.6017 | 177.6017 | 177.6017 | 177.6017 | 177.6017 | 177.6017 | 177.6017 | 177.6017 | 177.6017 | 177.6017 | 177.6017 | 177.6017 | 177.6017 | 177.6017 | 177.6017 | 177.6017 | 177.6017 | 177.6017 | 177.6017 | 177.6017 | 177.6017 | 177.6017 | 177.6017 | 177.6017 | 177.5558 | 177.51 | 177.4642 | 177.4183 | 177.3725 | 177.3267 | 177.2808 | 177.235 | 177.1892 | 177.1433 | 177.0975 | 177.0517 | 177.0058 | 176.96 | 176.9142 | 176.8683 | 176.8225 | 176.7767 | 176.7308 | 176.685 | 176.6392 | 176.5933 | 176.5475 | 176.5017 | 176.4558 | 176.41 | 176.3642 | 176.3183 | 176.2725 | 176.2267
13.3 | 0 | 5.574 | 11.148 | 16.722 | 22.296 | 27.87 | 33.444 | 39.018 | 44.592 | 50.166 | 55.74 | 64.2984 | 72.8568 | 81.4152 | 89.9736 | 98.532 | 98.5204 | 98.5088 | 98.4972 | 98.4856 | 98.474 | 100.6586 | 102.8432 | 105.0278 | 107.2124 | 109.397 | 111.5816 | 113.7662 | 115.9508 | 118.1354 | 120.32 | 121.7764 | 123.2328 | 124.6892 | 126.1456 | 127.602 | 129.0584 | 130.5148 | 131.9712 | 133.4276 | 134.884 | 136.3404 | 137.7968 | 139.2532 | 140.7096 | 142.166 | 143.4685 | 144.7711 | 146.0736 | 147.3761 | 148.6787 | 149.9812 | 151.2837 | 152.5863 | 153.8888 | 155.1913 | 156.4939 | 157.7964 | 159.0989 | 160.4015 | 161.704 | 162.1075 | 162.5111 | 162.9146 | 163.3181 | 163.7217 | 164.1252 | 164.5287 | 164.9323 | 165.3358 | 165.7393 | 166.1429 | 166.5464 | 166.9499 | 167.3535 | 167.757 | 168.1605 | 168.5641 | 168.9676 | 169.3711 | 169.7747 | 170.1782 | 170.5817 | 170.9853 | 171.3888 | 171.7923 | 172.1959 | 172.5994 | 173.0029 | 173.4065 | 173.81 | 173.9808 | 174.1516 | 174.3224 | 174.4932 | 174.664 | 174.8348 | 175.0056 | 175.1764 | 175.3472 | 175.518 | 175.6888 | 175.8596 | 176.0304 | 176.2012 | 176.372 | 176.5428 | 176.7136 | 176.8844 | 177.0552 | 177.226 | 177.3968 | 177.5676 | 177.7384 | 177.9092 | 178.08 | 178.2508 | 178.4216 | 178.5924 | 178.7632 | 178.934 | 178.934 | 178.934 | 178.934 | 178.934 | 178.934 | 178.934 | 178.934 | 178.934 | 178.934 | 178.934 | 178.934 | 178.934 | 178.934 | 178.934 | 178.934 | 178.934 | 178.934 | 178.934 | 178.934 | 178.934 | 178.934 | 178.934 | 178.934 | 178.934 | 178.934 | 178.934 | 178.934 | 178.934 | 178.934 | 178.934 | 178.889 | 178.844 | 178.799 | 178.754 | 178.709 | 178.664 | 178.619 | 178.574 | 178.529 | 178.484 | 178.439 | 178.394 | 178.349 | 178.304 | 178.259 | 178.214 | 178.169 | 178.124 | 178.079 | 178.034 | 177.989 | 177.944 | 177.899 | 177.854 | 177.809 | 177.764 | 177.719 | 177.674 | 177.629 | 177.584
13.35 | 0 | 5.613 | 11.226 | 16.839 | 22.452 | 28.065 | 33.678 | 39.291 | 44.904 | 50.517 | 56.13 | 64.7575 | 73.3849 | 82.0124 | 90.6399 | 99.2673 | 99.2465 | 99.2256 | 99.2047 | 99.1839 | 99.163 | 101.364 | 103.5651 | 105.7661 | 107.9671 | 110.1682 | 112.3692 | 114.5702 | 116.7713 | 118.9723 | 121.1733 | 122.6407 | 124.108 | 125.5754 | 127.0428 | 128.5101 | 129.9775 | 131.4448 | 132.9122 | 134.3795 | 135.8469 | 137.3142 | 138.7816 | 140.249 | 141.7163 | 143.1837 | 144.4968 | 145.81 | 147.1232 | 148.4364 | 149.7496 | 151.0627 | 152.3759 | 153.6891 | 155.0023 | 156.3154 | 157.6286 | 158.9418 | 160.255 | 161.5682 | 162.8813 | 163.2885 | 163.6956 | 164.1027 | 164.5098 | 164.9169 | 165.3241 | 165.7312 | 166.1383 | 166.5454 | 166.9526 | 167.3597 | 167.7668 | 168.1739 | 168.581 | 168.9882 | 169.3953 | 169.8024 | 170.2095 | 170.6167 | 171.0238 | 171.4309 | 171.838 | 172.2451 | 172.6523 | 173.0594 | 173.4665 | 173.8736 | 174.2808 | 174.6879 | 175.095 | 175.2674 | 175.4398 | 175.6121 | 175.7845 | 175.9569 | 176.1293 | 176.3016 | 176.474 | 176.6464 | 176.8188 | 176.9912 | 177.1635 | 177.3359 | 177.5083 | 177.6807 | 177.853 | 178.0254 | 178.1978 | 178.3702 | 178.5426 | 178.7149 | 178.8873 | 179.0597 | 179.2321 | 179.4044 | 179.5768 | 179.7492 | 179.9216 | 180.094 | 180.2663 | 180.2663 | 180.2663 | 180.2663 | 180.2663 | 180.2663 | 180.2663 | 180.2663 | 180.2663 | 180.2663 | 180.2663 | 180.2663 | 180.2663 | 180.2663 | 180.2663 | 180.2663 | 180.2663 | 180.2663 | 180.2663 | 180.2663 | 180.2663 | 180.2663 | 180.2663 | 180.2663 | 180.2663 | 180.2663 | 180.2663 | 180.2663 | 180.2663 | 180.2663 | 180.2663 | 180.2222 | 180.178 | 180.1338 | 180.0897 | 180.0455 | 180.0013 | 179.9572 | 179.913 | 179.8688 | 179.8247 | 179.7805 | 179.7363 | 179.6922 | 179.648 | 179.6038 | 179.5597 | 179.5155 | 179.4713 | 179.4272 | 179.383 | 179.3388 | 179.2947 | 179.2505 | 179.2063 | 179.1622 | 179.118 | 179.0738 | 179.0297 | 178.9855 | 178.9413
13.4 | 0 | 5.652 | 11.304 | 16.956 | 22.608 | 28.26 | 33.912 | 39.564 | 45.216 | 50.868 | 56.52 | 65.2165 | 73.9131 | 82.6096 | 91.3061 | 100.0027 | 99.9725 | 99.9424 | 99.9123 | 99.8821 | 99.852 | 102.0695 | 104.2869 | 106.5044 | 108.7219 | 110.9393 | 113.1568 | 115.3743 | 117.5917 | 119.8092 | 122.0267 | 123.505 | 124.9833 | 126.4616 | 127.9399 | 129.4182 | 130.8965 | 132.3748 | 133.8532 | 135.3315 | 136.8098 | 138.2881 | 139.7664 | 141.2447 | 142.723 | 144.2013 | 145.5252 | 146.849 | 148.1728 | 149.4966 | 150.8204 | 152.1443 | 153.4681 | 154.7919 | 156.1157 | 157.4396 | 158.7634 | 160.0872 | 161.411 | 162.7348 | 164.0587 | 164.4694 | 164.8801 | 165.2908 | 165.7015 | 166.1122 | 166.5229 | 166.9336 | 167.3444 | 167.7551 | 168.1658 | 168.5765 | 168.9872 | 169.3979 | 169.8086 | 170.2193 | 170.63 | 171.0408 | 171.4515 | 171.8622 | 172.2729 | 172.6836 | 173.0943 | 173.505 | 173.9157 | 174.3264 | 174.7372 | 175.1479 | 175.5586 | 175.9693 | 176.38 | 176.554 | 176.7279 | 176.9019 | 177.0758 | 177.2498 | 177.4237 | 177.5977 | 177.7716 | 177.9456 | 178.1196 | 178.2935 | 178.4675 | 178.6414 | 178.8154 | 178.9893 | 179.1633 | 179.3372 | 179.5112 | 179.6852 | 179.8591 | 180.0331 | 180.207 | 180.381 | 180.5549 | 180.7289 | 180.9028 | 181.0768 | 181.2508 | 181.4247 | 181.5987 | 181.5987 | 181.5987 | 181.5987 | 181.5987 | 181.5987 | 181.5987 | 181.5987 | 181.5987 | 181.5987 | 181.5987 | 181.5987 | 181.5987 | 181.5987 | 181.5987 | 181.5987 | 181.5987 | 181.5987 | 181.5987 | 181.5987 | 181.5987 | 181.5987 | 181.5987 | 181.5987 | 181.5987 | 181.5987 | 181.5987 | 181.5987 | 181.5987 | 181.5987 | 181.5987 | 181.5553 | 181.512 | 181.4687 | 181.4253 | 181.382 | 181.3387 | 181.2953 | 181.252 | 181.2087 | 181.1653 | 181.122 | 181.0787 | 181.0353 | 180.992 | 180.9487 | 180.9053 | 180.862 | 180.8187 | 180.7753 | 180.732 | 180.6887 | 180.6453 | 180.602 | 180.5587 | 180.5153 | 180.472 | 180.4287 | 180.3853 | 180.342 | 180.2987
13.45 | 0 | 5.691 | 11.382 | 17.073 | 22.764 | 28.455 | 34.146 | 39.837 | 45.528 | 51.219 | 56.91 | 65.6756 | 74.4412 | 83.2068 | 91.9724 | 100.738 | 100.6986 | 100.6592 | 100.6198 | 100.5804 | 100.541 | 102.7749 | 105.0088 | 107.2427 | 109.4766 | 111.7105 | 113.9444 | 116.1783 | 118.4122 | 120.6461 | 122.88 | 124.3693 | 125.8585 | 127.3478 | 128.8371 | 130.3263 | 131.8156 | 133.3049 | 134.7941 | 136.2834 | 137.7727 | 139.2619 | 140.7512 | 142.2405 | 143.7297 | 145.219 | 146.5535 | 147.8879 | 149.2224 | 150.5569 | 151.8913 | 153.2258 | 154.5603 | 155.8947 | 157.2292 | 158.5637 | 159.8981 | 161.2326 | 162.5671 | 163.9015 | 165.236 | 165.6503 | 166.0646 | 166.4789 | 166.8932 | 167.3075 | 167.7218 | 168.1361 | 168.5504 | 168.9647 | 169.379 | 169.7933 | 170.2076 | 170.6219 | 171.0362 | 171.4505 | 171.8648 | 172.2791 | 172.6934 | 173.1077 | 173.522 | 173.9363 | 174.3506 | 174.7649 | 175.1792 | 175.5935 | 176.0078 | 176.4221 | 176.8364 | 177.2507 | 177.665 | 177.8405 | 178.0161 | 178.1916 | 178.3671 | 178.5427 | 178.7182 | 178.8937 | 179.0693 | 179.2448 | 179.4203 | 179.5959 | 179.7714 | 179.9469 | 180.1225 | 180.298 | 180.4735 | 180.6491 | 180.8246 | 181.0001 | 181.1757 | 181.3512 | 181.5267 | 181.7023 | 181.8778 | 182.0533 | 182.2289 | 182.4044 | 182.5799 | 182.7555 | 182.931 | 182.931 | 182.931 | 182.931 | 182.931 | 182.931 | 182.931 | 182.931 | 182.931 | 182.931 | 182.931 | 182.931 | 182.931 | 182.931 | 182.931 | 182.931 | 182.931 | 182.931 | 182.931 | 182.931 | 182.931 | 182.931 | 182.931 | 182.931 | 182.931 | 182.931 | 182.931 | 182.931 | 182.931 | 182.931 | 182.931 | 182.8885 | 182.846 | 182.8035 | 182.761 | 182.7185 | 182.676 | 182.6335 | 182.591 | 182.5485 | 182.506 | 182.4635 | 182.421 | 182.3785 | 182.336 | 182.2935 | 182.251 | 182.2085 | 182.166 | 182.1235 | 182.081 | 182.0385 | 181.996 | 181.9535 | 181.911 | 181.8685 | 181.826 | 181.7835 | 181.741 | 181.6985 | 181.656
13.5 | 0 | 5.73 | 11.46 | 17.19 | 22.92 | 28.65 | 34.38 | 40.11 | 45.84 | 51.57 | 57.3 | 66.1347 | 74.9693 | 83.804 | 92.6387 | 101.4733 | 101.4247 | 101.376 | 101.3273 | 101.2787 | 101.23 | 103.4803 | 105.7307 | 107.981 | 110.2313 | 112.4817 | 114.732 | 116.9823 | 119.2327 | 121.483 | 123.7333 | 125.2336 | 126.7338 | 128.234 | 129.7342 | 131.2344 | 132.7347 | 134.2349 | 135.7351 | 137.2353 | 138.7356 | 140.2358 | 141.736 | 143.2362 | 144.7364 | 146.2367 | 147.5818 | 148.9269 | 150.272 | 151.6171 | 152.9622 | 154.3073 | 155.6524 | 156.9976 | 158.3427 | 159.6878 | 161.0329 | 162.378 | 163.7231 | 165.0682 | 166.4133 | 166.8312 | 167.2491 | 167.667 | 168.0849 | 168.5028 | 168.9207 | 169.3386 | 169.7564 | 170.1743 | 170.5922 | 171.0101 | 171.428 | 171.8459 | 172.2638 | 172.6817 | 173.0996 | 173.5174 | 173.9353 | 174.3532 | 174.7711 | 175.189 | 175.6069 | 176.0248 | 176.4427 | 176.8606 | 177.2784 | 177.6963 | 178.1142 | 178.5321 | 178.95 | 179.1271 | 179.3042 | 179.4813 | 179.6584 | 179.8356 | 180.0127 | 180.1898 | 180.3669 | 180.544 | 180.7211 | 180.8982 | 181.0753 | 181.2524 | 181.4296 | 181.6067 | 181.7838 | 181.9609 | 182.138 | 182.3151 | 182.4922 | 182.6693 | 182.8464 | 183.0236 | 183.2007 | 183.3778 | 183.5549 | 183.732 | 183.9091 | 184.0862 | 184.2633 | 184.2633 | 184.2633 | 184.2633 | 184.2633 | 184.2633 | 184.2633 | 184.2633 | 184.2633 | 184.2633 | 184.2633 | 184.2633 | 184.2633 | 184.2633 | 184.2633 | 184.2633 | 184.2633 | 184.2633 | 184.2633 | 184.2633 | 184.2633 | 184.2633 | 184.2633 | 184.2633 | 184.2633 | 184.2633 | 184.2633 | 184.2633 | 184.2633 | 184.2633 | 184.2633 | 184.2217 | 184.18 | 184.1383 | 184.0967 | 184.055 | 184.0133 | 183.9717 | 183.93 | 183.8883 | 183.8467 | 183.805 | 183.7633 | 183.7217 | 183.68 | 183.6383 | 183.5967 | 183.555 | 183.5133 | 183.4717 | 183.43 | 183.3883 | 183.3467 | 183.305 | 183.2633 | 183.2217 | 183.18 | 183.1383 | 183.0967 | 183.055 | 183.0133
13.55 | 0 | 5.769 | 11.538 | 17.307 | 23.076 | 28.845 | 34.614 | 40.383 | 46.152 | 51.921 | 57.69 | 66.5937 | 75.4975 | 84.4012 | 93.3049 | 102.2087 | 102.1507 | 102.0928 | 102.0349 | 101.9769 | 101.919 | 104.1858 | 106.4525 | 108.7193 | 110.9861 | 113.2528 | 115.5196 | 117.7864 | 120.0531 | 122.3199 | 124.5867 | 126.0978 | 127.609 | 129.1202 | 130.6314 | 132.1426 | 133.6537 | 135.1649 | 136.6761 | 138.1873 | 139.6984 | 141.2096 | 142.7208 | 144.232 | 145.7432 | 147.2543 | 148.6101 | 149.9658 | 151.3216 | 152.6774 | 154.0331 | 155.3889 | 156.7446 | 158.1004 | 159.4561 | 160.8119 | 162.1676 | 163.5234 | 164.8792 | 166.2349 | 167.5907 | 168.0121 | 168.4336 | 168.8551 | 169.2766 | 169.6981 | 170.1195 | 170.541 | 170.9625 | 171.384 | 171.8054 | 172.2269 | 172.6484 | 173.0699 | 173.4914 | 173.9128 | 174.3343 | 174.7558 | 175.1773 | 175.5987 | 176.0202 | 176.4417 | 176.8632 | 177.2847 | 177.7061 | 178.1276 | 178.5491 | 178.9706 | 179.392 | 179.8135 | 180.235 | 180.4137 | 180.5924 | 180.7711 | 180.9498 | 181.1284 | 181.3071 | 181.4858 | 181.6645 | 181.8432 | 182.0219 | 182.2006 | 182.3793 | 182.558 | 182.7366 | 182.9153 | 183.094 | 183.2727 | 183.4514 | 183.6301 | 183.8088 | 183.9875 | 184.1662 | 184.3448 | 184.5235 | 184.7022 | 184.8809 | 185.0596 | 185.2383 | 185.417 | 185.5957 | 185.5957 | 185.5957 | 185.5957 | 185.5957 | 185.5957 | 185.5957 | 185.5957 | 185.5957 | 185.5957 | 185.5957 | 185.5957 | 185.5957 | 185.5957 | 185.5957 | 185.5957 | 185.5957 | 185.5957 | 185.5957 | 185.5957 | 185.5957 | 185.5957 | 185.5957 | 185.5957 | 185.5957 | 185.5957 | 185.5957 | 185.5957 | 185.5957 | 185.5957 | 185.5957 | 185.5548 | 185.514 | 185.4732 | 185.4323 | 185.3915 | 185.3507 | 185.3098 | 185.269 | 185.2282 | 185.1873 | 185.1465 | 185.1057 | 185.0648 | 185.024 | 184.9832 | 184.9423 | 184.9015 | 184.8607 | 184.8198 | 184.779 | 184.7382 | 184.6973 | 184.6565 | 184.6157 | 184.5748 | 184.534 | 184.4932 | 184.4523 | 184.4115 | 184.3707
13.6 | 0 | 5.808 | 11.616 | 17.424 | 23.232 | 29.04 | 34.848 | 40.656 | 46.464 | 52.272 | 58.08 | 67.0528 | 76.0256 | 84.9984 | 93.9712 | 102.944 | 102.8768 | 102.8096 | 102.7424 | 102.6752 | 102.608 | 104.8912 | 107.1744 | 109.4576 | 111.7408 | 114.024 | 116.3072 | 118.5904 | 120.8736 | 123.1568 | 125.44 | 126.9621 | 128.4843 | 130.0064 | 131.5285 | 133.0507 | 134.5728 | 136.0949 | 137.6171 | 139.1392 | 140.6613 | 142.1835 | 143.7056 | 145.2277 | 146.7499 | 148.272 | 149.6384 | 151.0048 | 152.3712 | 153.7376 | 155.104 | 156.4704 | 157.8368 | 159.2032 | 160.5696 | 161.936 | 163.3024 | 164.6688 | 166.0352 | 167.4016 | 168.768 | 169.1931 | 169.6181 | 170.0432 | 170.4683 | 170.8933 | 171.3184 | 171.7435 | 172.1685 | 172.5936 | 173.0187 | 173.4437 | 173.8688 | 174.2939 | 174.7189 | 175.144 | 175.5691 | 175.9941 | 176.4192 | 176.8443 | 177.2693 | 177.6944 | 178.1195 | 178.5445 | 178.9696 | 179.3947 | 179.8197 | 180.2448 | 180.6699 | 181.0949 | 181.52 | 181.7003 | 181.8805 | 182.0608 | 182.2411 | 182.4213 | 182.6016 | 182.7819 | 182.9621 | 183.1424 | 183.3227 | 183.5029 | 183.6832 | 183.8635 | 184.0437 | 184.224 | 184.4043 | 184.5845 | 184.7648 | 184.9451 | 185.1253 | 185.3056 | 185.4859 | 185.6661 | 185.8464 | 186.0267 | 186.2069 | 186.3872 | 186.5675 | 186.7477 | 186.928 | 186.928 | 186.928 | 186.928 | 186.928 | 186.928 | 186.928 | 186.928 | 186.928 | 186.928 | 186.928 | 186.928 | 186.928 | 186.928 | 186.928 | 186.928 | 186.928 | 186.928 | 186.928 | 186.928 | 186.928 | 186.928 | 186.928 | 186.928 | 186.928 | 186.928 | 186.928 | 186.928 | 186.928 | 186.928 | 186.928 | 186.888 | 186.848 | 186.808 | 186.768 | 186.728 | 186.688 | 186.648 | 186.608 | 186.568 | 186.528 | 186.488 | 186.448 | 186.408 | 186.368 | 186.328 | 186.288 | 186.248 | 186.208 | 186.168 | 186.128 | 186.088 | 186.048 | 186.008 | 185.968 | 185.928 | 185.888 | 185.848 | 185.808 | 185.768 | 185.728
13.65 | 0 | 5.847 | 11.694 | 17.541 | 23.388 | 29.235 | 35.082 | 40.929 | 46.776 | 52.623 | 58.47 | 67.5119 | 76.5537 | 85.5956 | 94.6375 | 103.6793 | 103.6029 | 103.5264 | 103.4499 | 103.3735 | 103.297 | 105.5966 | 107.8963 | 110.1959 | 112.4955 | 114.7952 | 117.0948 | 119.3944 | 121.6941 | 123.9937 | 126.2933 | 127.8264 | 129.3595 | 130.8926 | 132.4257 | 133.9588 | 135.4919 | 137.025 | 138.558 | 140.0911 | 141.6242 | 143.1573 | 144.6904 | 146.2235 | 147.7566 | 149.2897 | 150.6667 | 152.0438 | 153.4208 | 154.7978 | 156.1749 | 157.5519 | 158.929 | 160.306 | 161.6831 | 163.0601 | 164.4372 | 165.8142 | 167.1912 | 168.5683 | 169.9453 | 170.374 | 170.8026 | 171.2313 | 171.66 | 172.0886 | 172.5173 | 172.9459 | 173.3746 | 173.8032 | 174.2319 | 174.6605 | 175.0892 | 175.5179 | 175.9465 | 176.3752 | 176.8038 | 177.2325 | 177.6611 | 178.0898 | 178.5184 | 178.9471 | 179.3758 | 179.8044 | 180.2331 | 180.6617 | 181.0904 | 181.519 | 181.9477 | 182.3763 | 182.805 | 182.9868 | 183.1687 | 183.3505 | 183.5324 | 183.7142 | 183.8961 | 184.0779 | 184.2598 | 184.4416 | 184.6234 | 184.8053 | 184.9871 | 185.169 | 185.3508 | 185.5327 | 185.7145 | 185.8964 | 186.0782 | 186.26 | 186.4419 | 186.6237 | 186.8056 | 186.9874 | 187.1693 | 187.3511 | 187.533 | 187.7148 | 187.8966 | 188.0785 | 188.2603 | 188.2603 | 188.2603 | 188.2603 | 188.2603 | 188.2603 | 188.2603 | 188.2603 | 188.2603 | 188.2603 | 188.2603 | 188.2603 | 188.2603 | 188.2603 | 188.2603 | 188.2603 | 188.2603 | 188.2603 | 188.2603 | 188.2603 | 188.2603 | 188.2603 | 188.2603 | 188.2603 | 188.2603 | 188.2603 | 188.2603 | 188.2603 | 188.2603 | 188.2603 | 188.2603 | 188.2212 | 188.182 | 188.1428 | 188.1037 | 188.0645 | 188.0253 | 187.9862 | 187.947 | 187.9078 | 187.8687 | 187.8295 | 187.7903 | 187.7512 | 187.712 | 187.6728 | 187.6337 | 187.5945 | 187.5553 | 187.5162 | 187.477 | 187.4378 | 187.3987 | 187.3595 | 187.3203 | 187.2812 | 187.242 | 187.2028 | 187.1637 | 187.1245 | 187.0853
13.7 | 0 | 5.886 | 11.772 | 17.658 | 23.544 | 29.43 | 35.316 | 41.202 | 47.088 | 52.974 | 58.86 | 67.9709 | 77.0819 | 86.1928 | 95.3037 | 104.4147 | 104.3289 | 104.2432 | 104.1575 | 104.0717 | 103.986 | 106.3021 | 108.6181 | 110.9342 | 113.2503 | 115.5663 | 117.8824 | 120.1985 | 122.5145 | 124.8306 | 127.1467 | 128.6907 | 130.2348 | 131.7788 | 133.3228 | 134.8669 | 136.4109 | 137.955 | 139.499 | 141.0431 | 142.5871 | 144.1312 | 145.6752 | 147.2192 | 148.7633 | 150.3073 | 151.695 | 153.0827 | 154.4704 | 155.8581 | 157.2458 | 158.6335 | 160.0212 | 161.4088 | 162.7965 | 164.1842 | 165.5719 | 166.9596 | 168.3473 | 169.735 | 171.1227 | 171.5549 | 171.9872 | 172.4194 | 172.8516 | 173.2839 | 173.7161 | 174.1484 | 174.5806 | 175.0129 | 175.4451 | 175.8774 | 176.3096 | 176.7418 | 177.1741 | 177.6063 | 178.0386 | 178.4708 | 178.9031 | 179.3353 | 179.7676 | 180.1998 | 180.632 | 181.0643 | 181.4965 | 181.9288 | 182.361 | 182.7933 | 183.2255 | 183.6578 | 184.09 | 184.2734 | 184.4568 | 184.6403 | 184.8237 | 185.0071 | 185.1905 | 185.374 | 185.5574 | 185.7408 | 185.9242 | 186.1076 | 186.2911 | 186.4745 | 186.6579 | 186.8413 | 187.0248 | 187.2082 | 187.3916 | 187.575 | 187.7584 | 187.9419 | 188.1253 | 188.3087 | 188.4921 | 188.6756 | 188.859 | 189.0424 | 189.2258 | 189.4092 | 189.5927 | 189.5927 | 189.5927 | 189.5927 | 189.5927 | 189.5927 | 189.5927 | 189.5927 | 189.5927 | 189.5927 | 189.5927 | 189.5927 | 189.5927 | 189.5927 | 189.5927 | 189.5927 | 189.5927 | 189.5927 | 189.5927 | 189.5927 | 189.5927 | 189.5927 | 189.5927 | 189.5927 | 189.5927 | 189.5927 | 189.5927 | 189.5927 | 189.5927 | 189.5927 | 189.5927 | 189.5543 | 189.516 | 189.4777 | 189.4393 | 189.401 | 189.3627 | 189.3243 | 189.286 | 189.2477 | 189.2093 | 189.171 | 189.1327 | 189.0943 | 189.056 | 189.0177 | 188.9793 | 188.941 | 188.9027 | 188.8643 | 188.826 | 188.7877 | 188.7493 | 188.711 | 188.6727 | 188.6343 | 188.596 | 188.5577 | 188.5193 | 188.481 | 188.4427
13.75 | 0 | 5.925 | 11.85 | 17.775 | 23.7 | 29.625 | 35.55 | 41.475 | 47.4 | 53.325 | 59.25 | 68.43 | 77.61 | 86.79 | 95.97 | 105.15 | 105.055 | 104.96 | 104.865 | 104.77 | 104.675 | 107.0075 | 109.34 | 111.6725 | 114.005 | 116.3375 | 118.67 | 121.0025 | 123.335 | 125.6675 | 128 | 129.555 | 131.11 | 132.665 | 134.22 | 135.775 | 137.33 | 138.885 | 140.44 | 141.995 | 143.55 | 145.105 | 146.66 | 148.215 | 149.77 | 151.325 | 152.7233 | 154.1217 | 155.52 | 156.9183 | 158.3167 | 159.715 | 161.1133 | 162.5117 | 163.91 | 165.3083 | 166.7067 | 168.105 | 169.5033 | 170.9017 | 172.3 | 172.7358 | 173.1717 | 173.6075 | 174.0433 | 174.4792 | 174.915 | 175.3508 | 175.7867 | 176.2225 | 176.6583 | 177.0942 | 177.53 | 177.9658 | 178.4017 | 178.8375 | 179.2733 | 179.7092 | 180.145 | 180.5808 | 181.0167 | 181.4525 | 181.8883 | 182.3242 | 182.76 | 183.1958 | 183.6317 | 184.0675 | 184.5033 | 184.9392 | 185.375 | 185.56 | 185.745 | 185.93 | 186.115 | 186.3 | 186.485 | 186.67 | 186.855 | 187.04 | 187.225 | 187.41 | 187.595 | 187.78 | 187.965 | 188.15 | 188.335 | 188.52 | 188.705 | 188.89 | 189.075 | 189.26 | 189.445 | 189.63 | 189.815 | 190 | 190.185 | 190.37 | 190.555 | 190.74 | 190.925 | 190.925 | 190.925 | 190.925 | 190.925 | 190.925 | 190.925 | 190.925 | 190.925 | 190.925 | 190.925 | 190.925 | 190.925 | 190.925 | 190.925 | 190.925 | 190.925 | 190.925 | 190.925 | 190.925 | 190.925 | 190.925 | 190.925 | 190.925 | 190.925 | 190.925 | 190.925 | 190.925 | 190.925 | 190.925 | 190.925 | 190.8875 | 190.85 | 190.8125 | 190.775 | 190.7375 | 190.7 | 190.6625 | 190.625 | 190.5875 | 190.55 | 190.5125 | 190.475 | 190.4375 | 190.4 | 190.3625 | 190.325 | 190.2875 | 190.25 | 190.2125 | 190.175 | 190.1375 | 190.1 | 190.0625 | 190.025 | 189.9875 | 189.95 | 189.9125 | 189.875 | 189.8375 | 189.8
13.8 | 0 | 5.964 | 11.928 | 17.892 | 23.856 | 29.82 | 35.784 | 41.748 | 47.712 | 53.676 | 59.64 | 68.8891 | 78.1381 | 87.3872 | 96.6363 | 105.8853 | 105.7811 | 105.6768 | 105.5725 | 105.4683 | 105.364 | 107.7129 | 110.0619 | 112.4108 | 114.7597 | 117.1087 | 119.4576 | 121.8065 | 124.1555 | 126.5044 | 128.8533 | 130.4193 | 131.9852 | 133.5512 | 135.1172 | 136.6831 | 138.2491 | 139.815 | 141.381 | 142.9469 | 144.5129 | 146.0788 | 147.6448 | 149.2108 | 150.7767 | 152.3427 | 153.7516 | 155.1606 | 156.5696 | 157.9786 | 159.3876 | 160.7965 | 162.2055 | 163.6145 | 165.0235 | 166.4324 | 167.8414 | 169.2504 | 170.6594 | 172.0684 | 173.4773 | 173.9168 | 174.3562 | 174.7956 | 175.235 | 175.6744 | 176.1139 | 176.5533 | 176.9927 | 177.4321 | 177.8716 | 178.311 | 178.7504 | 179.1898 | 179.6292 | 180.0687 | 180.5081 | 180.9475 | 181.3869 | 181.8264 | 182.2658 | 182.7052 | 183.1446 | 183.584 | 184.0235 | 184.4629 | 184.9023 | 185.3417 | 185.7812 | 186.2206 | 186.66 | 186.8466 | 187.0332 | 187.2197 | 187.4063 | 187.5929 | 187.7795 | 187.966 | 188.1526 | 188.3392 | 188.5258 | 188.7124 | 188.8989 | 189.0855 | 189.2721 | 189.4587 | 189.6452 | 189.8318 | 190.0184 | 190.205 | 190.3916 | 190.5781 | 190.7647 | 190.9513 | 191.1379 | 191.3244 | 191.511 | 191.6976 | 191.8842 | 192.0708 | 192.2573 | 192.2573 | 192.2573 | 192.2573 | 192.2573 | 192.2573 | 192.2573 | 192.2573 | 192.2573 | 192.2573 | 192.2573 | 192.2573 | 192.2573 | 192.2573 | 192.2573 | 192.2573 | 192.2573 | 192.2573 | 192.2573 | 192.2573 | 192.2573 | 192.2573 | 192.2573 | 192.2573 | 192.2573 | 192.2573 | 192.2573 | 192.2573 | 192.2573 | 192.2573 | 192.2573 | 192.2207 | 192.184 | 192.1473 | 192.1107 | 192.074 | 192.0373 | 192.0007 | 191.964 | 191.9273 | 191.8907 | 191.854 | 191.8173 | 191.7807 | 191.744 | 191.7073 | 191.6707 | 191.634 | 191.5973 | 191.5607 | 191.524 | 191.4873 | 191.4507 | 191.414 | 191.3773 | 191.3407 | 191.304 | 191.2673 | 191.2307 | 191.194 | 191.1573
13.85 | 0 | 6.003 | 12.006 | 18.009 | 24.012 | 30.015 | 36.018 | 42.021 | 48.024 | 54.027 | 60.03 | 69.3481 | 78.6663 | 87.9844 | 97.3025 | 106.6207 | 106.5071 | 106.3936 | 106.2801 | 106.1665 | 106.053 | 108.4184 | 110.7837 | 113.1491 | 115.5145 | 117.8798 | 120.2452 | 122.6106 | 124.9759 | 127.3413 | 129.7067 | 131.2836 | 132.8605 | 134.4374 | 136.0143 | 137.5912 | 139.1681 | 140.745 | 142.322 | 143.8989 | 145.4758 | 147.0527 | 148.6296 | 150.2065 | 151.7834 | 153.3603 | 154.78 | 156.1996 | 157.6192 | 159.0388 | 160.4584 | 161.8781 | 163.2977 | 164.7173 | 166.1369 | 167.5566 | 168.9762 | 170.3958 | 171.8154 | 173.235 | 174.6547 | 175.0977 | 175.5407 | 175.9837 | 176.4267 | 176.8697 | 177.3127 | 177.7557 | 178.1988 | 178.6418 | 179.0848 | 179.5278 | 179.9708 | 180.4138 | 180.8568 | 181.2998 | 181.7428 | 182.1859 | 182.6289 | 183.0719 | 183.5149 | 183.9579 | 184.4009 | 184.8439 | 185.2869 | 185.7299 | 186.173 | 186.616 | 187.059 | 187.502 | 187.945 | 188.1332 | 188.3213 | 188.5095 | 188.6976 | 188.8858 | 189.0739 | 189.2621 | 189.4502 | 189.6384 | 189.8266 | 190.0147 | 190.2029 | 190.391 | 190.5792 | 190.7673 | 190.9555 | 191.1436 | 191.3318 | 191.52 | 191.7081 | 191.8963 | 192.0844 | 192.2726 | 192.4607 | 192.6489 | 192.837 | 193.0252 | 193.2134 | 193.4015 | 193.5897 | 193.5897 | 193.5897 | 193.5897 | 193.5897 | 193.5897 | 193.5897 | 193.5897 | 193.5897 | 193.5897 | 193.5897 | 193.5897 | 193.5897 | 193.5897 | 193.5897 | 193.5897 | 193.5897 | 193.5897 | 193.5897 | 193.5897 | 193.5897 | 193.5897 | 193.5897 | 193.5897 | 193.5897 | 193.5897 | 193.5897 | 193.5897 | 193.5897 | 193.5897 | 193.5897 | 193.5538 | 193.518 | 193.4822 | 193.4463 | 193.4105 | 193.3747 | 193.3388 | 193.303 | 193.2672 | 193.2313 | 193.1955 | 193.1597 | 193.1238 | 193.088 | 193.0522 | 193.0163 | 192.9805 | 192.9447 | 192.9088 | 192.873 | 192.8372 | 192.8013 | 192.7655 | 192.7297 | 192.6938 | 192.658 | 192.6222 | 192.5863 | 192.5505 | 192.5147
13.9 | 0 | 6.042 | 12.084 | 18.126 | 24.168 | 30.21 | 36.252 | 42.294 | 48.336 | 54.378 | 60.42 | 69.8072 | 79.1944 | 88.5816 | 97.9688 | 107.356 | 107.2332 | 107.1104 | 106.9876 | 106.8648 | 106.742 | 109.1238 | 111.5056 | 113.8874 | 116.2692 | 118.651 | 121.0328 | 123.4146 | 125.7964 | 128.1782 | 130.56 | 132.1479 | 133.7357 | 135.3236 | 136.9115 | 138.4993 | 140.0872 | 141.6751 | 143.2629 | 144.8508 | 146.4387 | 148.0265 | 149.6144 | 151.2023 | 152.7901 | 154.378 | 155.8083 | 157.2385 | 158.6688 | 160.0991 | 161.5293 | 162.9596 | 164.3899 | 165.8201 | 167.2504 | 168.6807 | 170.1109 | 171.5412 | 172.9715 | 174.4017 | 175.832 | 176.2786 | 176.7252 | 177.1718 | 177.6184 | 178.065 | 178.5116 | 178.9582 | 179.4048 | 179.8514 | 180.298 | 180.7446 | 181.1912 | 181.6378 | 182.0844 | 182.531 | 182.9776 | 183.4242 | 183.8708 | 184.3174 | 184.764 | 185.2106 | 185.6572 | 186.1038 | 186.5504 | 186.997 | 187.4436 | 187.8902 | 188.3368 | 188.7834 | 189.23 | 189.4197 | 189.6095 | 189.7992 | 189.9889 | 190.1787 | 190.3684 | 190.5581 | 190.7479 | 190.9376 | 191.1273 | 191.3171 | 191.5068 | 191.6965 | 191.8863 | 192.076 | 192.2657 | 192.4555 | 192.6452 | 192.8349 | 193.0247 | 193.2144 | 193.4041 | 193.5939 | 193.7836 | 193.9733 | 194.1631 | 194.3528 | 194.5425 | 194.7323 | 194.922 | 194.922 | 194.922 | 194.922 | 194.922 | 194.922 | 194.922 | 194.922 | 194.922 | 194.922 | 194.922 | 194.922 | 194.922 | 194.922 | 194.922 | 194.922 | 194.922 | 194.922 | 194.922 | 194.922 | 194.922 | 194.922 | 194.922 | 194.922 | 194.922 | 194.922 | 194.922 | 194.922 | 194.922 | 194.922 | 194.922 | 194.887 | 194.852 | 194.817 | 194.782 | 194.747 | 194.712 | 194.677 | 194.642 | 194.607 | 194.572 | 194.537 | 194.502 | 194.467 | 194.432 | 194.397 | 194.362 | 194.327 | 194.292 | 194.257 | 194.222 | 194.187 | 194.152 | 194.117 | 194.082 | 194.047 | 194.012 | 193.977 | 193.942 | 193.907 | 193.872
13.95 | 0 | 6.081 | 12.162 | 18.243 | 24.324 | 30.405 | 36.486 | 42.567 | 48.648 | 54.729 | 60.81 | 70.2663 | 79.7225 | 89.1788 | 98.6351 | 108.0913 | 107.9593 | 107.8272 | 107.6951 | 107.5631 | 107.431 | 109.8292 | 112.2275 | 114.6257 | 117.0239 | 119.4222 | 121.8204 | 124.2186 | 126.6169 | 129.0151 | 131.4133 | 133.0122 | 134.611 | 136.2098 | 137.8086 | 139.4074 | 141.0063 | 142.6051 | 144.2039 | 145.8027 | 147.4016 | 149.0004 | 150.5992 | 152.198 | 153.7968 | 155.3957 | 156.8366 | 158.2775 | 159.7184 | 161.1593 | 162.6002 | 164.0411 | 165.482 | 166.923 | 168.3639 | 169.8048 | 171.2457 | 172.6866 | 174.1275 | 175.5684 | 177.0093 | 177.4595 | 177.9097 | 178.3599 | 178.8101 | 179.2603 | 179.7105 | 180.1607 | 180.6108 | 181.061 | 181.5112 | 181.9614 | 182.4116 | 182.8618 | 183.312 | 183.7622 | 184.2124 | 184.6625 | 185.1127 | 185.5629 | 186.0131 | 186.4633 | 186.9135 | 187.3637 | 187.8139 | 188.2641 | 188.7142 | 189.1644 | 189.6146 | 190.0648 | 190.515 | 190.7063 | 190.8976 | 191.0889 | 191.2802 | 191.4716 | 191.6629 | 191.8542 | 192.0455 | 192.2368 | 192.4281 | 192.6194 | 192.8107 | 193.002 | 193.1934 | 193.3847 | 193.576 | 193.7673 | 193.9586 | 194.1499 | 194.3412 | 194.5325 | 194.7238 | 194.9152 | 195.1065 | 195.2978 | 195.4891 | 195.6804 | 195.8717 | 196.063 | 196.2543 | 196.2543 | 196.2543 | 196.2543 | 196.2543 | 196.2543 | 196.2543 | 196.2543 | 196.2543 | 196.2543 | 196.2543 | 196.2543 | 196.2543 | 196.2543 | 196.2543 | 196.2543 | 196.2543 | 196.2543 | 196.2543 | 196.2543 | 196.2543 | 196.2543 | 196.2543 | 196.2543 | 196.2543 | 196.2543 | 196.2543 | 196.2543 | 196.2543 | 196.2543 | 196.2543 | 196.2202 | 196.186 | 196.1518 | 196.1177 | 196.0835 | 196.0493 | 196.0152 | 195.981 | 195.9468 | 195.9127 | 195.8785 | 195.8443 | 195.8102 | 195.776 | 195.7418 | 195.7077 | 195.6735 | 195.6393 | 195.6052 | 195.571 | 195.5368 | 195.5027 | 195.4685 | 195.4343 | 195.4002 | 195.366 | 195.3318 | 195.2977 | 195.2635 | 195.2293
14 | 0 | 6.12 | 12.24 | 18.36 | 24.48 | 30.6 | 36.72 | 42.84 | 48.96 | 55.08 | 61.2 | 70.7253 | 80.2507 | 89.776 | 99.3013 | 108.8267 | 108.6853 | 108.544 | 108.4027 | 108.2613 | 108.12 | 110.5347 | 112.9493 | 115.364 | 117.7787 | 120.1933 | 122.608 | 125.0227 | 127.4373 | 129.852 | 132.2667 | 133.8764 | 135.4862 | 137.096 | 138.7058 | 140.3156 | 141.9253 | 143.5351 | 145.1449 | 146.7547 | 148.3644 | 149.9742 | 151.584 | 153.1938 | 154.8036 | 156.4133 | 157.8649 | 159.3164 | 160.768 | 162.2196 | 163.6711 | 165.1227 | 166.5742 | 168.0258 | 169.4773 | 170.9289 | 172.3804 | 173.832 | 175.2836 | 176.7351 | 178.1867 | 178.6404 | 179.0942 | 179.548 | 180.0018 | 180.4556 | 180.9093 | 181.3631 | 181.8169 | 182.2707 | 182.7244 | 183.1782 | 183.632 | 184.0858 | 184.5396 | 184.9933 | 185.4471 | 185.9009 | 186.3547 | 186.8084 | 187.2622 | 187.716 | 188.1698 | 188.6236 | 189.0773 | 189.5311 | 189.9849 | 190.4387 | 190.8924 | 191.3462 | 191.8 | 191.9929 | 192.1858 | 192.3787 | 192.5716 | 192.7644 | 192.9573 | 193.1502 | 193.3431 | 193.536 | 193.7289 | 193.9218 | 194.1147 | 194.3076 | 194.5004 | 194.6933 | 194.8862 | 195.0791 | 195.272 | 195.4649 | 195.6578 | 195.8507 | 196.0436 | 196.2364 | 196.4293 | 196.6222 | 196.8151 | 197.008 | 197.2009 | 197.3938 | 197.5867 | 197.5867 | 197.5867 | 197.5867 | 197.5867 | 197.5867 | 197.5867 | 197.5867 | 197.5867 | 197.5867 | 197.5867 | 197.5867 | 197.5867 | 197.5867 | 197.5867 | 197.5867 | 197.5867 | 197.5867 | 197.5867 | 197.5867 | 197.5867 | 197.5867 | 197.5867 | 197.5867 | 197.5867 | 197.5867 | 197.5867 | 197.5867 | 197.5867 | 197.5867 | 197.5867 | 197.5533 | 197.52 | 197.4867 | 197.4533 | 197.42 | 197.3867 | 197.3533 | 197.32 | 197.2867 | 197.2533 | 197.22 | 197.1867 | 197.1533 | 197.12 | 197.0867 | 197.0533 | 197.02 | 196.9867 | 196.9533 | 196.92 | 196.8867 | 196.8533 | 196.82 | 196.7867 | 196.7533 | 196.72 | 196.6867 | 196.6533 | 196.62 | 196.5867
14.05 | 0 | 6.159 | 12.318 | 18.477 | 24.636 | 30.795 | 36.954 | 43.113 | 49.272 | 55.431 | 61.59 | 71.1844 | 80.7788 | 90.3732 | 99.9676 | 109.562 | 109.4114 | 109.2608 | 109.1102 | 108.9596 | 108.809 | 111.2401 | 113.6712 | 116.1023 | 118.5334 | 120.9645 | 123.3956 | 125.8267 | 128.2578 | 130.6889 | 133.12 | 134.7407 | 136.3615 | 137.9822 | 139.6029 | 141.2237 | 142.8444 | 144.4651 | 146.0859 | 147.7066 | 149.3273 | 150.9481 | 152.5688 | 154.1895 | 155.8103 | 157.431 | 158.8932 | 160.3554 | 161.8176 | 163.2798 | 164.742 | 166.2042 | 167.6664 | 169.1286 | 170.5908 | 172.053 | 173.5152 | 174.9774 | 176.4396 | 177.9018 | 179.364 | 179.8214 | 180.2787 | 180.7361 | 181.1935 | 181.6508 | 182.1082 | 182.5656 | 183.0229 | 183.4803 | 183.9377 | 184.395 | 184.8524 | 185.3098 | 185.7671 | 186.2245 | 186.6819 | 187.1392 | 187.5966 | 188.054 | 188.5113 | 188.9687 | 189.4261 | 189.8834 | 190.3408 | 190.7982 | 191.2555 | 191.7129 | 192.1703 | 192.6276 | 193.085 | 193.2795 | 193.4739 | 193.6684 | 193.8629 | 194.0573 | 194.2518 | 194.4463 | 194.6407 | 194.8352 | 195.0297 | 195.2241 | 195.4186 | 195.6131 | 195.8075 | 196.002 | 196.1965 | 196.3909 | 196.5854 | 196.7799 | 196.9743 | 197.1688 | 197.3633 | 197.5577 | 197.7522 | 197.9467 | 198.1411 | 198.3356 | 198.5301 | 198.7245 | 198.919 | 198.919 | 198.919 | 198.919 | 198.919 | 198.919 | 198.919 | 198.919 | 198.919 | 198.919 | 198.919 | 198.919 | 198.919 | 198.919 | 198.919 | 198.919 | 198.919 | 198.919 | 198.919 | 198.919 | 198.919 | 198.919 | 198.919 | 198.919 | 198.919 | 198.919 | 198.919 | 198.919 | 198.919 | 198.919 | 198.919 | 198.8865 | 198.854 | 198.8215 | 198.789 | 198.7565 | 198.724 | 198.6915 | 198.659 | 198.6265 | 198.594 | 198.5615 | 198.529 | 198.4965 | 198.464 | 198.4315 | 198.399 | 198.3665 | 198.334 | 198.3015 | 198.269 | 198.2365 | 198.204 | 198.1715 | 198.139 | 198.1065 | 198.074 | 198.0415 | 198.009 | 197.9765 | 197.944
14.1 | 0 | 6.198 | 12.396 | 18.594 | 24.792 | 30.99 | 37.188 | 43.386 | 49.584 | 55.782 | 61.98 | 71.6435 | 81.3069 | 90.9704 | 100.6339 | 110.2973 | 110.1375 | 109.9776 | 109.8177 | 109.6579 | 109.498 | 111.9455 | 114.3931 | 116.8406 | 119.2881 | 121.7357 | 124.1832 | 126.6307 | 129.0783 | 131.5258 | 133.9733 | 135.605 | 137.2367 | 138.8684 | 140.5001 | 142.1318 | 143.7635 | 145.3952 | 147.0268 | 148.6585 | 150.2902 | 151.9219 | 153.5536 | 155.1853 | 156.817 | 158.4487 | 159.9215 | 161.3944 | 162.8672 | 164.34 | 165.8129 | 167.2857 | 168.7586 | 170.2314 | 171.7043 | 173.1771 | 174.65 | 176.1228 | 177.5956 | 179.0685 | 180.5413 | 181.0023 | 181.4632 | 181.9242 | 182.3852 | 182.8461 | 183.3071 | 183.768 | 184.229 | 184.6899 | 185.1509 | 185.6118 | 186.0728 | 186.5338 | 186.9947 | 187.4557 | 187.9166 | 188.3776 | 188.8385 | 189.2995 | 189.7604 | 190.2214 | 190.6824 | 191.1433 | 191.6043 | 192.0652 | 192.5262 | 192.9871 | 193.4481 | 193.909 | 194.37 | 194.566 | 194.7621 | 194.9581 | 195.1542 | 195.3502 | 195.5463 | 195.7423 | 195.9384 | 196.1344 | 196.3304 | 196.5265 | 196.7225 | 196.9186 | 197.1146 | 197.3107 | 197.5067 | 197.7028 | 197.8988 | 198.0948 | 198.2909 | 198.4869 | 198.683 | 198.879 | 199.0751 | 199.2711 | 199.4672 | 199.6632 | 199.8592 | 200.0553 | 200.2513 | 200.2513 | 200.2513 | 200.2513 | 200.2513 | 200.2513 | 200.2513 | 200.2513 | 200.2513 | 200.2513 | 200.2513 | 200.2513 | 200.2513 | 200.2513 | 200.2513 | 200.2513 | 200.2513 | 200.2513 | 200.2513 | 200.2513 | 200.2513 | 200.2513 | 200.2513 | 200.2513 | 200.2513 | 200.2513 | 200.2513 | 200.2513 | 200.2513 | 200.2513 | 200.2513 | 200.2197 | 200.188 | 200.1563 | 200.1247 | 200.093 | 200.0613 | 200.0297 | 199.998 | 199.9663 | 199.9347 | 199.903 | 199.8713 | 199.8397 | 199.808 | 199.7763 | 199.7447 | 199.713 | 199.6813 | 199.6497 | 199.618 | 199.5863 | 199.5547 | 199.523 | 199.4913 | 199.4597 | 199.428 | 199.3963 | 199.3647 | 199.333 | 199.3013
14.15 | 0 | 6.237 | 12.474 | 18.711 | 24.948 | 31.185 | 37.422 | 43.659 | 49.896 | 56.133 | 62.37 | 72.1025 | 81.8351 | 91.5676 | 101.3001 | 111.0327 | 110.8635 | 110.6944 | 110.5253 | 110.3561 | 110.187 | 112.651 | 115.1149 | 117.5789 | 120.0429 | 122.5068 | 124.9708 | 127.4348 | 129.8987 | 132.3627 | 134.8267 | 136.4693 | 138.112 | 139.7546 | 141.3972 | 143.0399 | 144.6825 | 146.3252 | 147.9678 | 149.6105 | 151.2531 | 152.8958 | 154.5384 | 156.181 | 157.8237 | 159.4663 | 160.9498 | 162.4333 | 163.9168 | 165.4003 | 166.8838 | 168.3673 | 169.8508 | 171.3342 | 172.8177 | 174.3012 | 175.7847 | 177.2682 | 178.7517 | 180.2352 | 181.7187 | 182.1832 | 182.6478 | 183.1123 | 183.5768 | 184.0414 | 184.5059 | 184.9705 | 185.435 | 185.8996 | 186.3641 | 186.8287 | 187.2932 | 187.7577 | 188.2223 | 188.6868 | 189.1514 | 189.6159 | 190.0805 | 190.545 | 191.0096 | 191.4741 | 191.9386 | 192.4032 | 192.8677 | 193.3323 | 193.7968 | 194.2614 | 194.7259 | 195.1905 | 195.655 | 195.8526 | 196.0502 | 196.2479 | 196.4455 | 196.6431 | 196.8407 | 197.0384 | 197.236 | 197.4336 | 197.6312 | 197.8288 | 198.0265 | 198.2241 | 198.4217 | 198.6193 | 198.817 | 199.0146 | 199.2122 | 199.4098 | 199.6074 | 199.8051 | 200.0027 | 200.2003 | 200.3979 | 200.5956 | 200.7932 | 200.9908 | 201.1884 | 201.386 | 201.5837 | 201.5837 | 201.5837 | 201.5837 | 201.5837 | 201.5837 | 201.5837 | 201.5837 | 201.5837 | 201.5837 | 201.5837 | 201.5837 | 201.5837 | 201.5837 | 201.5837 | 201.5837 | 201.5837 | 201.5837 | 201.5837 | 201.5837 | 201.5837 | 201.5837 | 201.5837 | 201.5837 | 201.5837 | 201.5837 | 201.5837 | 201.5837 | 201.5837 | 201.5837 | 201.5837 | 201.5528 | 201.522 | 201.4912 | 201.4603 | 201.4295 | 201.3987 | 201.3678 | 201.337 | 201.3062 | 201.2753 | 201.2445 | 201.2137 | 201.1828 | 201.152 | 201.1212 | 201.0903 | 201.0595 | 201.0287 | 200.9978 | 200.967 | 200.9362 | 200.9053 | 200.8745 | 200.8437 | 200.8128 | 200.782 | 200.7512 | 200.7203 | 200.6895 | 200.6587
14.2 | 0 | 6.276 | 12.552 | 18.828 | 25.104 | 31.38 | 37.656 | 43.932 | 50.208 | 56.484 | 62.76 | 72.5616 | 82.3632 | 92.1648 | 101.9664 | 111.768 | 111.5896 | 111.4112 | 111.2328 | 111.0544 | 110.876 | 113.3564 | 115.8368 | 118.3172 | 120.7976 | 123.278 | 125.7584 | 128.2388 | 130.7192 | 133.1996 | 135.68 | 137.3336 | 138.9872 | 140.6408 | 142.2944 | 143.948 | 145.6016 | 147.2552 | 148.9088 | 150.5624 | 152.216 | 153.8696 | 155.5232 | 157.1768 | 158.8304 | 160.484 | 161.9781 | 163.4723 | 164.9664 | 166.4605 | 167.9547 | 169.4488 | 170.9429 | 172.4371 | 173.9312 | 175.4253 | 176.9195 | 178.4136 | 179.9077 | 181.4019 | 182.896 | 183.3641 | 183.8323 | 184.3004 | 184.7685 | 185.2367 | 185.7048 | 186.1729 | 186.6411 | 187.1092 | 187.5773 | 188.0455 | 188.5136 | 188.9817 | 189.4499 | 189.918 | 190.3861 | 190.8543 | 191.3224 | 191.7905 | 192.2587 | 192.7268 | 193.1949 | 193.6631 | 194.1312 | 194.5993 | 195.0675 | 195.5356 | 196.0037 | 196.4719 | 196.94 | 197.1392 | 197.3384 | 197.5376 | 197.7368 | 197.936 | 198.1352 | 198.3344 | 198.5336 | 198.7328 | 198.932 | 199.1312 | 199.3304 | 199.5296 | 199.7288 | 199.928 | 200.1272 | 200.3264 | 200.5256 | 200.7248 | 200.924 | 201.1232 | 201.3224 | 201.5216 | 201.7208 | 201.92 | 202.1192 | 202.3184 | 202.5176 | 202.7168 | 202.916 | 202.916 | 202.916 | 202.916 | 202.916 | 202.916 | 202.916 | 202.916 | 202.916 | 202.916 | 202.916 | 202.916 | 202.916 | 202.916 | 202.916 | 202.916 | 202.916 | 202.916 | 202.916 | 202.916 | 202.916 | 202.916 | 202.916 | 202.916 | 202.916 | 202.916 | 202.916 | 202.916 | 202.916 | 202.916 | 202.916 | 202.886 | 202.856 | 202.826 | 202.796 | 202.766 | 202.736 | 202.706 | 202.676 | 202.646 | 202.616 | 202.586 | 202.556 | 202.526 | 202.496 | 202.466 | 202.436 | 202.406 | 202.376 | 202.346 | 202.316 | 202.286 | 202.256 | 202.226 | 202.196 | 202.166 | 202.136 | 202.106 | 202.076 | 202.046 | 202.016
14.25 | 0 | 6.315 | 12.63 | 18.945 | 25.26 | 31.575 | 37.89 | 44.205 | 50.52 | 56.835 | 63.15 | 73.0207 | 82.8913 | 92.762 | 102.6327 | 112.5033 | 112.3157 | 112.128 | 111.9403 | 111.7527 | 111.565 | 114.0618 | 116.5587 | 119.0555 | 121.5523 | 124.0492 | 126.546 | 129.0428 | 131.5397 | 134.0365 | 136.5333 | 138.1979 | 139.8624 | 141.527 | 143.1916 | 144.8561 | 146.5207 | 148.1852 | 149.8498 | 151.5143 | 153.1789 | 154.8434 | 156.508 | 158.1726 | 159.8371 | 161.5017 | 163.0064 | 164.5112 | 166.016 | 167.5208 | 169.0256 | 170.5303 | 172.0351 | 173.5399 | 175.0447 | 176.5494 | 178.0542 | 179.559 | 181.0638 | 182.5686 | 184.0733 | 184.5451 | 185.0168 | 185.4885 | 185.9602 | 186.4319 | 186.9037 | 187.3754 | 187.8471 | 188.3188 | 188.7906 | 189.2623 | 189.734 | 190.2057 | 190.6774 | 191.1492 | 191.6209 | 192.0926 | 192.5643 | 193.0361 | 193.5078 | 193.9795 | 194.4512 | 194.9229 | 195.3947 | 195.8664 | 196.3381 | 196.8098 | 197.2816 | 197.7533 | 198.225 | 198.4258 | 198.6266 | 198.8273 | 199.0281 | 199.2289 | 199.4297 | 199.6304 | 199.8312 | 200.032 | 200.2328 | 200.4336 | 200.6343 | 200.8351 | 201.0359 | 201.2367 | 201.4374 | 201.6382 | 201.839 | 202.0398 | 202.2406 | 202.4413 | 202.6421 | 202.8429 | 203.0437 | 203.2444 | 203.4452 | 203.646 | 203.8468 | 204.0476 | 204.2483 | 204.2483 | 204.2483 | 204.2483 | 204.2483 | 204.2483 | 204.2483 | 204.2483 | 204.2483 | 204.2483 | 204.2483 | 204.2483 | 204.2483 | 204.2483 | 204.2483 | 204.2483 | 204.2483 | 204.2483 | 204.2483 | 204.2483 | 204.2483 | 204.2483 | 204.2483 | 204.2483 | 204.2483 | 204.2483 | 204.2483 | 204.2483 | 204.2483 | 204.2483 | 204.2483 | 204.2192 | 204.19 | 204.1608 | 204.1317 | 204.1025 | 204.0733 | 204.0442 | 204.015 | 203.9858 | 203.9567 | 203.9275 | 203.8983 | 203.8692 | 203.84 | 203.8108 | 203.7817 | 203.7525 | 203.7233 | 203.6942 | 203.665 | 203.6358 | 203.6067 | 203.5775 | 203.5483 | 203.5192 | 203.49 | 203.4608 | 203.4317 | 203.4025 | 203.3733
14.3 | 0 | 6.354 | 12.708 | 19.062 | 25.416 | 31.77 | 38.124 | 44.478 | 50.832 | 57.186 | 63.54 | 73.4797 | 83.4195 | 93.3592 | 103.2989 | 113.2387 | 113.0417 | 112.8448 | 112.6479 | 112.4509 | 112.254 | 114.7673 | 117.2805 | 119.7938 | 122.3071 | 124.8203 | 127.3336 | 129.8469 | 132.3601 | 134.8734 | 137.3867 | 139.0622 | 140.7377 | 142.4132 | 144.0887 | 145.7642 | 147.4397 | 149.1152 | 150.7908 | 152.4663 | 154.1418 | 155.8173 | 157.4928 | 159.1683 | 160.8438 | 162.5193 | 164.0348 | 165.5502 | 167.0656 | 168.581 | 170.0964 | 171.6119 | 173.1273 | 174.6427 | 176.1581 | 177.6736 | 179.189 | 180.7044 | 182.2198 | 183.7352 | 185.2507 | 185.726 | 186.2013 | 186.6766 | 187.1519 | 187.6272 | 188.1025 | 188.5778 | 189.0532 | 189.5285 | 190.0038 | 190.4791 | 190.9544 | 191.4297 | 191.905 | 192.3803 | 192.8556 | 193.331 | 193.8063 | 194.2816 | 194.7569 | 195.2322 | 195.7075 | 196.1828 | 196.6581 | 197.1334 | 197.6088 | 198.0841 | 198.5594 | 199.0347 | 199.51 | 199.7124 | 199.9147 | 200.1171 | 200.3194 | 200.5218 | 200.7241 | 200.9265 | 201.1288 | 201.3312 | 201.5336 | 201.7359 | 201.9383 | 202.1406 | 202.343 | 202.5453 | 202.7477 | 202.95 | 203.1524 | 203.3548 | 203.5571 | 203.7595 | 203.9618 | 204.1642 | 204.3665 | 204.5689 | 204.7712 | 204.9736 | 205.176 | 205.3783 | 205.5807 | 205.5807 | 205.5807 | 205.5807 | 205.5807 | 205.5807 | 205.5807 | 205.5807 | 205.5807 | 205.5807 | 205.5807 | 205.5807 | 205.5807 | 205.5807 | 205.5807 | 205.5807 | 205.5807 | 205.5807 | 205.5807 | 205.5807 | 205.5807 | 205.5807 | 205.5807 | 205.5807 | 205.5807 | 205.5807 | 205.5807 | 205.5807 | 205.5807 | 205.5807 | 205.5807 | 205.5523 | 205.524 | 205.4957 | 205.4673 | 205.439 | 205.4107 | 205.3823 | 205.354 | 205.3257 | 205.2973 | 205.269 | 205.2407 | 205.2123 | 205.184 | 205.1557 | 205.1273 | 205.099 | 205.0707 | 205.0423 | 205.014 | 204.9857 | 204.9573 | 204.929 | 204.9007 | 204.8723 | 204.844 | 204.8157 | 204.7873 | 204.759 | 204.7307
14.35 | 0 | 6.393 | 12.786 | 19.179 | 25.572 | 31.965 | 38.358 | 44.751 | 51.144 | 57.537 | 63.93 | 73.9388 | 83.9476 | 93.9564 | 103.9652 | 113.974 | 113.7678 | 113.5616 | 113.3554 | 113.1492 | 112.943 | 115.4727 | 118.0024 | 120.5321 | 123.0618 | 125.5915 | 128.1212 | 130.6509 | 133.1806 | 135.7103 | 138.24 | 139.9265 | 141.6129 | 143.2994 | 144.9859 | 146.6723 | 148.3588 | 150.0453 | 151.7317 | 153.4182 | 155.1047 | 156.7911 | 158.4776 | 160.1641 | 161.8505 | 163.537 | 165.0631 | 166.5891 | 168.1152 | 169.6413 | 171.1673 | 172.6934 | 174.2195 | 175.7455 | 177.2716 | 178.7977 | 180.3237 | 181.8498 | 183.3759 | 184.9019 | 186.428 | 186.9069 | 187.3858 | 187.8647 | 188.3436 | 188.8225 | 189.3014 | 189.7803 | 190.2592 | 190.7381 | 191.217 | 191.6959 | 192.1748 | 192.6537 | 193.1326 | 193.6115 | 194.0904 | 194.5693 | 195.0482 | 195.5271 | 196.006 | 196.4849 | 196.9638 | 197.4427 | 197.9216 | 198.4005 | 198.8794 | 199.3583 | 199.8372 | 200.3161 | 200.795 | 200.9989 | 201.2029 | 201.4068 | 201.6107 | 201.8147 | 202.0186 | 202.2225 | 202.4265 | 202.6304 | 202.8343 | 203.0383 | 203.2422 | 203.4461 | 203.6501 | 203.854 | 204.0579 | 204.2619 | 204.4658 | 204.6697 | 204.8737 | 205.0776 | 205.2815 | 205.4855 | 205.6894 | 205.8933 | 206.0973 | 206.3012 | 206.5051 | 206.7091 | 206.913 | 206.913 | 206.913 | 206.913 | 206.913 | 206.913 | 206.913 | 206.913 | 206.913 | 206.913 | 206.913 | 206.913 | 206.913 | 206.913 | 206.913 | 206.913 | 206.913 | 206.913 | 206.913 | 206.913 | 206.913 | 206.913 | 206.913 | 206.913 | 206.913 | 206.913 | 206.913 | 206.913 | 206.913 | 206.913 | 206.913 | 206.8855 | 206.858 | 206.8305 | 206.803 | 206.7755 | 206.748 | 206.7205 | 206.693 | 206.6655 | 206.638 | 206.6105 | 206.583 | 206.5555 | 206.528 | 206.5005 | 206.473 | 206.4455 | 206.418 | 206.3905 | 206.363 | 206.3355 | 206.308 | 206.2805 | 206.253 | 206.2255 | 206.198 | 206.1705 | 206.143 | 206.1155 | 206.088
14.4 | 0 | 6.432 | 12.864 | 19.296 | 25.728 | 32.16 | 38.592 | 45.024 | 51.456 | 57.888 | 64.32 | 74.3979 | 84.4757 | 94.5536 | 104.6315 | 114.7093 | 114.4939 | 114.2784 | 114.0629 | 113.8475 | 113.632 | 116.1781 | 118.7243 | 121.2704 | 123.8165 | 126.3627 | 128.9088 | 131.4549 | 134.0011 | 136.5472 | 139.0933 | 140.7908 | 142.4882 | 144.1856 | 145.883 | 147.5804 | 149.2779 | 150.9753 | 152.6727 | 154.3701 | 156.0676 | 157.765 | 159.4624 | 161.1598 | 162.8572 | 164.5547 | 166.0914 | 167.6281 | 169.1648 | 170.7015 | 172.2382 | 173.7749 | 175.3116 | 176.8484 | 178.3851 | 179.9218 | 181.4585 | 182.9952 | 184.5319 | 186.0686 | 187.6053 | 188.0878 | 188.5703 | 189.0528 | 189.5353 | 190.0178 | 190.5003 | 190.9828 | 191.4652 | 191.9477 | 192.4302 | 192.9127 | 193.3952 | 193.8777 | 194.3602 | 194.8427 | 195.3252 | 195.8076 | 196.2901 | 196.7726 | 197.2551 | 197.7376 | 198.2201 | 198.7026 | 199.1851 | 199.6676 | 200.15 | 200.6325 | 201.115 | 201.5975 | 202.08 | 202.2855 | 202.491 | 202.6965 | 202.902 | 203.1076 | 203.3131 | 203.5186 | 203.7241 | 203.9296 | 204.1351 | 204.3406 | 204.5461 | 204.7516 | 204.9572 | 205.1627 | 205.3682 | 205.5737 | 205.7792 | 205.9847 | 206.1902 | 206.3957 | 206.6012 | 206.8068 | 207.0123 | 207.2178 | 207.4233 | 207.6288 | 207.8343 | 208.0398 | 208.2453 | 208.2453 | 208.2453 | 208.2453 | 208.2453 | 208.2453 | 208.2453 | 208.2453 | 208.2453 | 208.2453 | 208.2453 | 208.2453 | 208.2453 | 208.2453 | 208.2453 | 208.2453 | 208.2453 | 208.2453 | 208.2453 | 208.2453 | 208.2453 | 208.2453 | 208.2453 | 208.2453 | 208.2453 | 208.2453 | 208.2453 | 208.2453 | 208.2453 | 208.2453 | 208.2453 | 208.2187 | 208.192 | 208.1653 | 208.1387 | 208.112 | 208.0853 | 208.0587 | 208.032 | 208.0053 | 207.9787 | 207.952 | 207.9253 | 207.8987 | 207.872 | 207.8453 | 207.8187 | 207.792 | 207.7653 | 207.7387 | 207.712 | 207.6853 | 207.6587 | 207.632 | 207.6053 | 207.5787 | 207.552 | 207.5253 | 207.4987 | 207.472 | 207.4453
14.45 | 0 | 6.471 | 12.942 | 19.413 | 25.884 | 32.355 | 38.826 | 45.297 | 51.768 | 58.239 | 64.71 | 74.8569 | 85.0039 | 95.1508 | 105.2977 | 115.4447 | 115.2199 | 114.9952 | 114.7705 | 114.5457 | 114.321 | 116.8836 | 119.4461 | 122.0087 | 124.5713 | 127.1338 | 129.6964 | 132.259 | 134.8215 | 137.3841 | 139.9467 | 141.655 | 143.3634 | 145.0718 | 146.7802 | 148.4886 | 150.1969 | 151.9053 | 153.6137 | 155.3221 | 157.0304 | 158.7388 | 160.4472 | 162.1556 | 163.864 | 165.5723 | 167.1197 | 168.667 | 170.2144 | 171.7618 | 173.3091 | 174.8565 | 176.4038 | 177.9512 | 179.4985 | 181.0459 | 182.5932 | 184.1406 | 185.688 | 187.2353 | 188.7827 | 189.2687 | 189.7548 | 190.2409 | 190.727 | 191.2131 | 191.6991 | 192.1852 | 192.6713 | 193.1574 | 193.6434 | 194.1295 | 194.6156 | 195.1017 | 195.5878 | 196.0738 | 196.5599 | 197.046 | 197.5321 | 198.0181 | 198.5042 | 198.9903 | 199.4764 | 199.9625 | 200.4485 | 200.9346 | 201.4207 | 201.9068 | 202.3928 | 202.8789 | 203.365 | 203.5721 | 203.7792 | 203.9863 | 204.1934 | 204.4004 | 204.6075 | 204.8146 | 205.0217 | 205.2288 | 205.4359 | 205.643 | 205.8501 | 206.0572 | 206.2642 | 206.4713 | 206.6784 | 206.8855 | 207.0926 | 207.2997 | 207.5068 | 207.7139 | 207.921 | 208.128 | 208.3351 | 208.5422 | 208.7493 | 208.9564 | 209.1635 | 209.3706 | 209.5777 | 209.5777 | 209.5777 | 209.5777 | 209.5777 | 209.5777 | 209.5777 | 209.5777 | 209.5777 | 209.5777 | 209.5777 | 209.5777 | 209.5777 | 209.5777 | 209.5777 | 209.5777 | 209.5777 | 209.5777 | 209.5777 | 209.5777 | 209.5777 | 209.5777 | 209.5777 | 209.5777 | 209.5777 | 209.5777 | 209.5777 | 209.5777 | 209.5777 | 209.5777 | 209.5777 | 209.5518 | 209.526 | 209.5002 | 209.4743 | 209.4485 | 209.4227 | 209.3968 | 209.371 | 209.3452 | 209.3193 | 209.2935 | 209.2677 | 209.2418 | 209.216 | 209.1902 | 209.1643 | 209.1385 | 209.1127 | 209.0868 | 209.061 | 209.0352 | 209.0093 | 208.9835 | 208.9577 | 208.9318 | 208.906 | 208.8802 | 208.8543 | 208.8285 | 208.8027
14.5 | 0 | 6.51 | 13.02 | 19.53 | 26.04 | 32.55 | 39.06 | 45.57 | 52.08 | 58.59 | 65.1 | 75.316 | 85.532 | 95.748 | 105.964 | 116.18 | 115.946 | 115.712 | 115.478 | 115.244 | 115.01 | 117.589 | 120.168 | 122.747 | 125.326 | 127.905 | 130.484 | 133.063 | 135.642 | 138.221 | 140.8 | 142.5193 | 144.2387 | 145.958 | 147.6773 | 149.3967 | 151.116 | 152.8353 | 154.5547 | 156.274 | 157.9933 | 159.7127 | 161.432 | 163.1513 | 164.8707 | 166.59 | 168.148 | 169.706 | 171.264 | 172.822 | 174.38 | 175.938 | 177.496 | 179.054 | 180.612 | 182.17 | 183.728 | 185.286 | 186.844 | 188.402 | 189.96 | 190.4497 | 190.9393 | 191.429 | 191.9187 | 192.4083 | 192.898 | 193.3877 | 193.8773 | 194.367 | 194.8567 | 195.3463 | 195.836 | 196.3257 | 196.8153 | 197.305 | 197.7947 | 198.2843 | 198.774 | 199.2637 | 199.7533 | 200.243 | 200.7327 | 201.2223 | 201.712 | 202.2017 | 202.6913 | 203.181 | 203.6707 | 204.1603 | 204.65 | 204.8587 | 205.0673 | 205.276 | 205.4847 | 205.6933 | 205.902 | 206.1107 | 206.3193 | 206.528 | 206.7367 | 206.9453 | 207.154 | 207.3627 | 207.5713 | 207.78 | 207.9887 | 208.1973 | 208.406 | 208.6147 | 208.8233 | 209.032 | 209.2407 | 209.4493 | 209.658 | 209.8667 | 210.0753 | 210.284 | 210.4927 | 210.7013 | 210.91 | 210.91 | 210.91 | 210.91 | 210.91 | 210.91 | 210.91 | 210.91 | 210.91 | 210.91 | 210.91 | 210.91 | 210.91 | 210.91 | 210.91 | 210.91 | 210.91 | 210.91 | 210.91 | 210.91 | 210.91 | 210.91 | 210.91 | 210.91 | 210.91 | 210.91 | 210.91 | 210.91 | 210.91 | 210.91 | 210.91 | 210.885 | 210.86 | 210.835 | 210.81 | 210.785 | 210.76 | 210.735 | 210.71 | 210.685 | 210.66 | 210.635 | 210.61 | 210.585 | 210.56 | 210.535 | 210.51 | 210.485 | 210.46 | 210.435 | 210.41 | 210.385 | 210.36 | 210.335 | 210.31 | 210.285 | 210.26 | 210.235 | 210.21 | 210.185 | 210.16
14.55 | 0 | 6.549 | 13.098 | 19.647 | 26.196 | 32.745 | 39.294 | 45.843 | 52.392 | 58.941 | 65.49 | 75.7751 | 86.0601 | 96.3452 | 106.6303 | 116.9153 | 116.6721 | 116.4288 | 116.1855 | 115.9423 | 115.699 | 118.2944 | 120.8899 | 123.4853 | 126.0807 | 128.6762 | 131.2716 | 133.867 | 136.4625 | 139.0579 | 141.6533 | 143.3836 | 145.1139 | 146.8442 | 148.5745 | 150.3048 | 152.0351 | 153.7654 | 155.4956 | 157.2259 | 158.9562 | 160.6865 | 162.4168 | 164.1471 | 165.8774 | 167.6077 | 169.1763 | 170.745 | 172.3136 | 173.8822 | 175.4509 | 177.0195 | 178.5882 | 180.1568 | 181.7255 | 183.2941 | 184.8628 | 186.4314 | 188 | 189.5687 | 191.1373 | 191.6306 | 192.1238 | 192.6171 | 193.1104 | 193.6036 | 194.0969 | 194.5901 | 195.0834 | 195.5766 | 196.0699 | 196.5631 | 197.0564 | 197.5497 | 198.0429 | 198.5362 | 199.0294 | 199.5227 | 200.0159 | 200.5092 | 201.0024 | 201.4957 | 201.989 | 202.4822 | 202.9755 | 203.4687 | 203.962 | 204.4552 | 204.9485 | 205.4417 | 205.935 | 206.1452 | 206.3555 | 206.5657 | 206.776 | 206.9862 | 207.1965 | 207.4067 | 207.617 | 207.8272 | 208.0374 | 208.2477 | 208.4579 | 208.6682 | 208.8784 | 209.0887 | 209.2989 | 209.5092 | 209.7194 | 209.9296 | 210.1399 | 210.3501 | 210.5604 | 210.7706 | 210.9809 | 211.1911 | 211.4014 | 211.6116 | 211.8218 | 212.0321 | 212.2423 | 212.2423 | 212.2423 | 212.2423 | 212.2423 | 212.2423 | 212.2423 | 212.2423 | 212.2423 | 212.2423 | 212.2423 | 212.2423 | 212.2423 | 212.2423 | 212.2423 | 212.2423 | 212.2423 | 212.2423 | 212.2423 | 212.2423 | 212.2423 | 212.2423 | 212.2423 | 212.2423 | 212.2423 | 212.2423 | 212.2423 | 212.2423 | 212.2423 | 212.2423 | 212.2423 | 212.2182 | 212.194 | 212.1698 | 212.1457 | 212.1215 | 212.0973 | 212.0732 | 212.049 | 212.0248 | 212.0007 | 211.9765 | 211.9523 | 211.9282 | 211.904 | 211.8798 | 211.8557 | 211.8315 | 211.8073 | 211.7832 | 211.759 | 211.7348 | 211.7107 | 211.6865 | 211.6623 | 211.6382 | 211.614 | 211.5898 | 211.5657 | 211.5415 | 211.5173
14.6 | 0 | 6.588 | 13.176 | 19.764 | 26.352 | 32.94 | 39.528 | 46.116 | 52.704 | 59.292 | 65.88 | 76.2341 | 86.5883 | 96.9424 | 107.2965 | 117.6507 | 117.3981 | 117.1456 | 116.8931 | 116.6405 | 116.388 | 118.9999 | 121.6117 | 124.2236 | 126.8355 | 129.4473 | 132.0592 | 134.6711 | 137.2829 | 139.8948 | 142.5067 | 144.2479 | 145.9892 | 147.7304 | 149.4716 | 151.2129 | 152.9541 | 154.6954 | 156.4366 | 158.1779 | 159.9191 | 161.6604 | 163.4016 | 165.1428 | 166.8841 | 168.6253 | 170.2046 | 171.7839 | 173.3632 | 174.9425 | 176.5218 | 178.1011 | 179.6804 | 181.2596 | 182.8389 | 184.4182 | 185.9975 | 187.5768 | 189.1561 | 190.7354 | 192.3147 | 192.8115 | 193.3084 | 193.8052 | 194.302 | 194.7989 | 195.2957 | 195.7926 | 196.2894 | 196.7863 | 197.2831 | 197.78 | 198.2768 | 198.7736 | 199.2705 | 199.7673 | 200.2642 | 200.761 | 201.2579 | 201.7547 | 202.2516 | 202.7484 | 203.2452 | 203.7421 | 204.2389 | 204.7358 | 205.2326 | 205.7295 | 206.2263 | 206.7232 | 207.22 | 207.4318 | 207.6436 | 207.8555 | 208.0673 | 208.2791 | 208.4909 | 208.7028 | 208.9146 | 209.1264 | 209.3382 | 209.55 | 209.7619 | 209.9737 | 210.1855 | 210.3973 | 210.6092 | 210.821 | 211.0328 | 211.2446 | 211.4564 | 211.6683 | 211.8801 | 212.0919 | 212.3037 | 212.5156 | 212.7274 | 212.9392 | 213.151 | 213.3628 | 213.5747 | 213.5747 | 213.5747 | 213.5747 | 213.5747 | 213.5747 | 213.5747 | 213.5747 | 213.5747 | 213.5747 | 213.5747 | 213.5747 | 213.5747 | 213.5747 | 213.5747 | 213.5747 | 213.5747 | 213.5747 | 213.5747 | 213.5747 | 213.5747 | 213.5747 | 213.5747 | 213.5747 | 213.5747 | 213.5747 | 213.5747 | 213.5747 | 213.5747 | 213.5747 | 213.5747 | 213.5513 | 213.528 | 213.5047 | 213.4813 | 213.458 | 213.4347 | 213.4113 | 213.388 | 213.3647 | 213.3413 | 213.318 | 213.2947 | 213.2713 | 213.248 | 213.2247 | 213.2013 | 213.178 | 213.1547 | 213.1313 | 213.108 | 213.0847 | 213.0613 | 213.038 | 213.0147 | 212.9913 | 212.968 | 212.9447 | 212.9213 | 212.898 | 212.8747
14.65 | 0 | 6.627 | 13.254 | 19.881 | 26.508 | 33.135 | 39.762 | 46.389 | 53.016 | 59.643 | 66.27 | 76.6932 | 87.1164 | 97.5396 | 107.9628 | 118.386 | 118.1242 | 117.8624 | 117.6006 | 117.3388 | 117.077 | 119.7053 | 122.3336 | 124.9619 | 127.5902 | 130.2185 | 132.8468 | 135.4751 | 138.1034 | 140.7317 | 143.36 | 145.1122 | 146.8644 | 148.6166 | 150.3688 | 152.121 | 153.8732 | 155.6254 | 157.3776 | 159.1298 | 160.882 | 162.6342 | 164.3864 | 166.1386 | 167.8908 | 169.643 | 171.2329 | 172.8229 | 174.4128 | 176.0027 | 177.5927 | 179.1826 | 180.7725 | 182.3625 | 183.9524 | 185.5423 | 187.1323 | 188.7222 | 190.3121 | 191.9021 | 193.492 | 193.9924 | 194.4929 | 194.9933 | 195.4937 | 195.9942 | 196.4946 | 196.995 | 197.4955 | 197.9959 | 198.4963 | 198.9968 | 199.4972 | 199.9976 | 200.4981 | 200.9985 | 201.4989 | 201.9994 | 202.4998 | 203.0002 | 203.5007 | 204.0011 | 204.5015 | 205.002 | 205.5024 | 206.0028 | 206.5033 | 207.0037 | 207.5041 | 208.0046 | 208.505 | 208.7184 | 208.9318 | 209.1452 | 209.3586 | 209.572 | 209.7854 | 209.9988 | 210.2122 | 210.4256 | 210.639 | 210.8524 | 211.0658 | 211.2792 | 211.4926 | 211.706 | 211.9194 | 212.1328 | 212.3462 | 212.5596 | 212.773 | 212.9864 | 213.1998 | 213.4132 | 213.6266 | 213.84 | 214.0534 | 214.2668 | 214.4802 | 214.6936 | 214.907 | 214.907 | 214.907 | 214.907 | 214.907 | 214.907 | 214.907 | 214.907 | 214.907 | 214.907 | 214.907 | 214.907 | 214.907 | 214.907 | 214.907 | 214.907 | 214.907 | 214.907 | 214.907 | 214.907 | 214.907 | 214.907 | 214.907 | 214.907 | 214.907 | 214.907 | 214.907 | 214.907 | 214.907 | 214.907 | 214.907 | 214.8845 | 214.862 | 214.8395 | 214.817 | 214.7945 | 214.772 | 214.7495 | 214.727 | 214.7045 | 214.682 | 214.6595 | 214.637 | 214.6145 | 214.592 | 214.5695 | 214.547 | 214.5245 | 214.502 | 214.4795 | 214.457 | 214.4345 | 214.412 | 214.3895 | 214.367 | 214.3445 | 214.322 | 214.2995 | 214.277 | 214.2545 | 214.232
14.7 | 0 | 6.666 | 13.332 | 19.998 | 26.664 | 33.33 | 39.996 | 46.662 | 53.328 | 59.994 | 66.66 | 77.1523 | 87.6445 | 98.1368 | 108.6291 | 119.1213 | 118.8503 | 118.5792 | 118.3081 | 118.0371 | 117.766 | 120.4107 | 123.0555 | 125.7002 | 128.3449 | 130.9897 | 133.6344 | 136.2791 | 138.9239 | 141.5686 | 144.2133 | 145.9765 | 147.7396 | 149.5028 | 151.266 | 153.0291 | 154.7923 | 156.5554 | 158.3186 | 160.0817 | 161.8449 | 163.608 | 165.3712 | 167.1344 | 168.8975 | 170.6607 | 172.2612 | 173.8618 | 175.4624 | 177.063 | 178.6636 | 180.2641 | 181.8647 | 183.4653 | 185.0659 | 186.6664 | 188.267 | 189.8676 | 191.4682 | 193.0688 | 194.6693 | 195.1734 | 195.6774 | 196.1814 | 196.6854 | 197.1894 | 197.6935 | 198.1975 | 198.7015 | 199.2055 | 199.7096 | 200.2136 | 200.7176 | 201.2216 | 201.7256 | 202.2297 | 202.7337 | 203.2377 | 203.7417 | 204.2458 | 204.7498 | 205.2538 | 205.7578 | 206.2618 | 206.7659 | 207.2699 | 207.7739 | 208.2779 | 208.782 | 209.286 | 209.79 | 210.005 | 210.22 | 210.4349 | 210.6499 | 210.8649 | 211.0799 | 211.2948 | 211.5098 | 211.7248 | 211.9398 | 212.1548 | 212.3697 | 212.5847 | 212.7997 | 213.0147 | 213.2296 | 213.4446 | 213.6596 | 213.8746 | 214.0896 | 214.3045 | 214.5195 | 214.7345 | 214.9495 | 215.1644 | 215.3794 | 215.5944 | 215.8094 | 216.0244 | 216.2393 | 216.2393 | 216.2393 | 216.2393 | 216.2393 | 216.2393 | 216.2393 | 216.2393 | 216.2393 | 216.2393 | 216.2393 | 216.2393 | 216.2393 | 216.2393 | 216.2393 | 216.2393 | 216.2393 | 216.2393 | 216.2393 | 216.2393 | 216.2393 | 216.2393 | 216.2393 | 216.2393 | 216.2393 | 216.2393 | 216.2393 | 216.2393 | 216.2393 | 216.2393 | 216.2393 | 216.2177 | 216.196 | 216.1743 | 216.1527 | 216.131 | 216.1093 | 216.0877 | 216.066 | 216.0443 | 216.0227 | 216.001 | 215.9793 | 215.9577 | 215.936 | 215.9143 | 215.8927 | 215.871 | 215.8493 | 215.8277 | 215.806 | 215.7843 | 215.7627 | 215.741 | 215.7193 | 215.6977 | 215.676 | 215.6543 | 215.6327 | 215.611 | 215.5893
14.75 | 0 | 6.705 | 13.41 | 20.115 | 26.82 | 33.525 | 40.23 | 46.935 | 53.64 | 60.345 | 67.05 | 77.6113 | 88.1727 | 98.734 | 109.2953 | 119.8567 | 119.5763 | 119.296 | 119.0157 | 118.7353 | 118.455 | 121.1162 | 123.7773 | 126.4385 | 129.0997 | 131.7608 | 134.422 | 137.0832 | 139.7443 | 142.4055 | 145.0667 | 146.8408 | 148.6149 | 150.389 | 152.1631 | 153.9372 | 155.7113 | 157.4854 | 159.2596 | 161.0337 | 162.8078 | 164.5819 | 166.356 | 168.1301 | 169.9042 | 171.6783 | 173.2896 | 174.9008 | 176.512 | 178.1232 | 179.7344 | 181.3457 | 182.9569 | 184.5681 | 186.1793 | 187.7906 | 189.4018 | 191.013 | 192.6242 | 194.2354 | 195.8467 | 196.3543 | 196.8619 | 197.3695 | 197.8771 | 198.3847 | 198.8923 | 199.3999 | 199.9076 | 200.4152 | 200.9228 | 201.4304 | 201.938 | 202.4456 | 202.9532 | 203.4608 | 203.9684 | 204.4761 | 204.9837 | 205.4913 | 205.9989 | 206.5065 | 207.0141 | 207.5217 | 208.0293 | 208.5369 | 209.0446 | 209.5522 | 210.0598 | 210.5674 | 211.075 | 211.2916 | 211.5081 | 211.7247 | 211.9412 | 212.1578 | 212.3743 | 212.5909 | 212.8074 | 213.024 | 213.2406 | 213.4571 | 213.6737 | 213.8902 | 214.1068 | 214.3233 | 214.5399 | 214.7564 | 214.973 | 215.1896 | 215.4061 | 215.6227 | 215.8392 | 216.0558 | 216.2723 | 216.4889 | 216.7054 | 216.922 | 217.1386 | 217.3551 | 217.5717 | 217.5717 | 217.5717 | 217.5717 | 217.5717 | 217.5717 | 217.5717 | 217.5717 | 217.5717 | 217.5717 | 217.5717 | 217.5717 | 217.5717 | 217.5717 | 217.5717 | 217.5717 | 217.5717 | 217.5717 | 217.5717 | 217.5717 | 217.5717 | 217.5717 | 217.5717 | 217.5717 | 217.5717 | 217.5717 | 217.5717 | 217.5717 | 217.5717 | 217.5717 | 217.5717 | 217.5508 | 217.53 | 217.5092 | 217.4883 | 217.4675 | 217.4467 | 217.4258 | 217.405 | 217.3842 | 217.3633 | 217.3425 | 217.3217 | 217.3008 | 217.28 | 217.2592 | 217.2383 | 217.2175 | 217.1967 | 217.1758 | 217.155 | 217.1342 | 217.1133 | 217.0925 | 217.0717 | 217.0508 | 217.03 | 217.0092 | 216.9883 | 216.9675 | 216.9467
14.8 | 0 | 6.744 | 13.488 | 20.232 | 26.976 | 33.72 | 40.464 | 47.208 | 53.952 | 60.696 | 67.44 | 78.0704 | 88.7008 | 99.3312 | 109.9616 | 120.592 | 120.3024 | 120.0128 | 119.7232 | 119.4336 | 119.144 | 121.8216 | 124.4992 | 127.1768 | 129.8544 | 132.532 | 135.2096 | 137.8872 | 140.5648 | 143.2424 | 145.92 | 147.7051 | 149.4901 | 151.2752 | 153.0603 | 154.8453 | 156.6304 | 158.4155 | 160.2005 | 161.9856 | 163.7707 | 165.5557 | 167.3408 | 169.1259 | 170.9109 | 172.696 | 174.3179 | 175.9397 | 177.5616 | 179.1835 | 180.8053 | 182.4272 | 184.0491 | 185.6709 | 187.2928 | 188.9147 | 190.5365 | 192.1584 | 193.7803 | 195.4021 | 197.024 | 197.5352 | 198.0464 | 198.5576 | 199.0688 | 199.58 | 200.0912 | 200.6024 | 201.1136 | 201.6248 | 202.136 | 202.6472 | 203.1584 | 203.6696 | 204.1808 | 204.692 | 205.2032 | 205.7144 | 206.2256 | 206.7368 | 207.248 | 207.7592 | 208.2704 | 208.7816 | 209.2928 | 209.804 | 210.3152 | 210.8264 | 211.3376 | 211.8488 | 212.36 | 212.5781 | 212.7963 | 213.0144 | 213.2325 | 213.4507 | 213.6688 | 213.8869 | 214.1051 | 214.3232 | 214.5413 | 214.7595 | 214.9776 | 215.1957 | 215.4139 | 215.632 | 215.8501 | 216.0683 | 216.2864 | 216.5045 | 216.7227 | 216.9408 | 217.1589 | 217.3771 | 217.5952 | 217.8133 | 218.0315 | 218.2496 | 218.4677 | 218.6859 | 218.904 | 218.904 | 218.904 | 218.904 | 218.904 | 218.904 | 218.904 | 218.904 | 218.904 | 218.904 | 218.904 | 218.904 | 218.904 | 218.904 | 218.904 | 218.904 | 218.904 | 218.904 | 218.904 | 218.904 | 218.904 | 218.904 | 218.904 | 218.904 | 218.904 | 218.904 | 218.904 | 218.904 | 218.904 | 218.904 | 218.904 | 218.884 | 218.864 | 218.844 | 218.824 | 218.804 | 218.784 | 218.764 | 218.744 | 218.724 | 218.704 | 218.684 | 218.664 | 218.644 | 218.624 | 218.604 | 218.584 | 218.564 | 218.544 | 218.524 | 218.504 | 218.484 | 218.464 | 218.444 | 218.424 | 218.404 | 218.384 | 218.364 | 218.344 | 218.324 | 218.304
14.85 | 0 | 6.783 | 13.566 | 20.349 | 27.132 | 33.915 | 40.698 | 47.481 | 54.264 | 61.047 | 67.83 | 78.5295 | 89.2289 | 99.9284 | 110.6279 | 121.3273 | 121.0285 | 120.7296 | 120.4307 | 120.1319 | 119.833 | 122.527 | 125.2211 | 127.9151 | 130.6091 | 133.3032 | 135.9972 | 138.6912 | 141.3853 | 144.0793 | 146.7733 | 148.5694 | 150.3654 | 152.1614 | 153.9574 | 155.7534 | 157.5495 | 159.3455 | 161.1415 | 162.9375 | 164.7336 | 166.5296 | 168.3256 | 170.1216 | 171.9176 | 173.7137 | 175.3462 | 176.9787 | 178.6112 | 180.2437 | 181.8762 | 183.5087 | 185.1412 | 186.7738 | 188.4063 | 190.0388 | 191.6713 | 193.3038 | 194.9363 | 196.5688 | 198.2013 | 198.7161 | 199.2309 | 199.7457 | 200.2605 | 200.7753 | 201.2901 | 201.8049 | 202.3196 | 202.8344 | 203.3492 | 203.864 | 204.3788 | 204.8936 | 205.4084 | 205.9232 | 206.438 | 206.9527 | 207.4675 | 207.9823 | 208.4971 | 209.0119 | 209.5267 | 210.0415 | 210.5563 | 211.0711 | 211.5858 | 212.1006 | 212.6154 | 213.1302 | 213.645 | 213.8647 | 214.0844 | 214.3041 | 214.5238 | 214.7436 | 214.9633 | 215.183 | 215.4027 | 215.6224 | 215.8421 | 216.0618 | 216.2815 | 216.5012 | 216.721 | 216.9407 | 217.1604 | 217.3801 | 217.5998 | 217.8195 | 218.0392 | 218.2589 | 218.4786 | 218.6984 | 218.9181 | 219.1378 | 219.3575 | 219.5772 | 219.7969 | 220.0166 | 220.2363 | 220.2363 | 220.2363 | 220.2363 | 220.2363 | 220.2363 | 220.2363 | 220.2363 | 220.2363 | 220.2363 | 220.2363 | 220.2363 | 220.2363 | 220.2363 | 220.2363 | 220.2363 | 220.2363 | 220.2363 | 220.2363 | 220.2363 | 220.2363 | 220.2363 | 220.2363 | 220.2363 | 220.2363 | 220.2363 | 220.2363 | 220.2363 | 220.2363 | 220.2363 | 220.2363 | 220.2172 | 220.198 | 220.1788 | 220.1597 | 220.1405 | 220.1213 | 220.1022 | 220.083 | 220.0638 | 220.0447 | 220.0255 | 220.0063 | 219.9872 | 219.968 | 219.9488 | 219.9297 | 219.9105 | 219.8913 | 219.8722 | 219.853 | 219.8338 | 219.8147 | 219.7955 | 219.7763 | 219.7572 | 219.738 | 219.7188 | 219.6997 | 219.6805 | 219.6613
14.9 | 0 | 6.822 | 13.644 | 20.466 | 27.288 | 34.11 | 40.932 | 47.754 | 54.576 | 61.398 | 68.22 | 78.9885 | 89.7571 | 100.5256 | 111.2941 | 122.0627 | 121.7545 | 121.4464 | 121.1383 | 120.8301 | 120.522 | 123.2325 | 125.9429 | 128.6534 | 131.3639 | 134.0743 | 136.7848 | 139.4953 | 142.2057 | 144.9162 | 147.6267 | 149.4336 | 151.2406 | 153.0476 | 154.8546 | 156.6616 | 158.4685 | 160.2755 | 162.0825 | 163.8895 | 165.6964 | 167.5034 | 169.3104 | 171.1174 | 172.9244 | 174.7313 | 176.3745 | 178.0176 | 179.6608 | 181.304 | 182.9471 | 184.5903 | 186.2334 | 187.8766 | 189.5197 | 191.1629 | 192.806 | 194.4492 | 196.0924 | 197.7355 | 199.3787 | 199.897 | 200.4154 | 200.9338 | 201.4522 | 201.9706 | 202.4889 | 203.0073 | 203.5257 | 204.0441 | 204.5624 | 205.0808 | 205.5992 | 206.1176 | 206.636 | 207.1543 | 207.6727 | 208.1911 | 208.7095 | 209.2278 | 209.7462 | 210.2646 | 210.783 | 211.3014 | 211.8197 | 212.3381 | 212.8565 | 213.3749 | 213.8932 | 214.4116 | 214.93 | 215.1513 | 215.3726 | 215.5939 | 215.8152 | 216.0364 | 216.2577 | 216.479 | 216.7003 | 216.9216 | 217.1429 | 217.3642 | 217.5855 | 217.8068 | 218.028 | 218.2493 | 218.4706 | 218.6919 | 218.9132 | 219.1345 | 219.3558 | 219.5771 | 219.7984 | 220.0196 | 220.2409 | 220.4622 | 220.6835 | 220.9048 | 221.1261 | 221.3474 | 221.5687 | 221.5687 | 221.5687 | 221.5687 | 221.5687 | 221.5687 | 221.5687 | 221.5687 | 221.5687 | 221.5687 | 221.5687 | 221.5687 | 221.5687 | 221.5687 | 221.5687 | 221.5687 | 221.5687 | 221.5687 | 221.5687 | 221.5687 | 221.5687 | 221.5687 | 221.5687 | 221.5687 | 221.5687 | 221.5687 | 221.5687 | 221.5687 | 221.5687 | 221.5687 | 221.5687 | 221.5503 | 221.532 | 221.5137 | 221.4953 | 221.477 | 221.4587 | 221.4403 | 221.422 | 221.4037 | 221.3853 | 221.367 | 221.3487 | 221.3303 | 221.312 | 221.2937 | 221.2753 | 221.257 | 221.2387 | 221.2203 | 221.202 | 221.1837 | 221.1653 | 221.147 | 221.1287 | 221.1103 | 221.092 | 221.0737 | 221.0553 | 221.037 | 221.0187
14.95 | 0 | 6.861 | 13.722 | 20.583 | 27.444 | 34.305 | 41.166 | 48.027 | 54.888 | 61.749 | 68.61 | 79.4476 | 90.2852 | 101.1228 | 111.9604 | 122.798 | 122.4806 | 122.1632 | 121.8458 | 121.5284 | 121.211 | 123.9379 | 126.6648 | 129.3917 | 132.1186 | 134.8455 | 137.5724 | 140.2993 | 143.0262 | 145.7531 | 148.48 | 150.2979 | 152.1159 | 153.9338 | 155.7517 | 157.5697 | 159.3876 | 161.2055 | 163.0235 | 164.8414 | 166.6593 | 168.4773 | 170.2952 | 172.1131 | 173.9311 | 175.749 | 177.4028 | 179.0566 | 180.7104 | 182.3642 | 184.018 | 185.6718 | 187.3256 | 188.9794 | 190.6332 | 192.287 | 193.9408 | 195.5946 | 197.2484 | 198.9022 | 200.556 | 201.078 | 201.5999 | 202.1219 | 202.6439 | 203.1658 | 203.6878 | 204.2098 | 204.7317 | 205.2537 | 205.7757 | 206.2976 | 206.8196 | 207.3416 | 207.8635 | 208.3855 | 208.9075 | 209.4294 | 209.9514 | 210.4734 | 210.9953 | 211.5173 | 212.0393 | 212.5612 | 213.0832 | 213.6052 | 214.1271 | 214.6491 | 215.1711 | 215.693 | 216.215 | 216.4379 | 216.6607 | 216.8836 | 217.1065 | 217.3293 | 217.5522 | 217.7751 | 217.9979 | 218.2208 | 218.4437 | 218.6665 | 218.8894 | 219.1123 | 219.3351 | 219.558 | 219.7809 | 220.0037 | 220.2266 | 220.4495 | 220.6723 | 220.8952 | 221.1181 | 221.3409 | 221.5638 | 221.7867 | 222.0095 | 222.2324 | 222.4553 | 222.6781 | 222.901 | 222.901 | 222.901 | 222.901 | 222.901 | 222.901 | 222.901 | 222.901 | 222.901 | 222.901 | 222.901 | 222.901 | 222.901 | 222.901 | 222.901 | 222.901 | 222.901 | 222.901 | 222.901 | 222.901 | 222.901 | 222.901 | 222.901 | 222.901 | 222.901 | 222.901 | 222.901 | 222.901 | 222.901 | 222.901 | 222.901 | 222.8835 | 222.866 | 222.8485 | 222.831 | 222.8135 | 222.796 | 222.7785 | 222.761 | 222.7435 | 222.726 | 222.7085 | 222.691 | 222.6735 | 222.656 | 222.6385 | 222.621 | 222.6035 | 222.586 | 222.5685 | 222.551 | 222.5335 | 222.516 | 222.4985 | 222.481 | 222.4635 | 222.446 | 222.4285 | 222.411 | 222.3935 | 222.376
15 | 0 | 6.9 | 13.8 | 20.7 | 27.6 | 34.5 | 41.4 | 48.3 | 55.2 | 62.1 | 69 | 79.9067 | 90.8133 | 101.72 | 112.6267 | 123.5333 | 123.2067 | 122.88 | 122.5533 | 122.2267 | 121.9 | 124.6433 | 127.3867 | 130.13 | 132.8733 | 135.6167 | 138.36 | 141.1033 | 143.8467 | 146.59 | 149.3333 | 151.1622 | 152.9911 | 154.82 | 156.6489 | 158.4778 | 160.3067 | 162.1356 | 163.9644 | 165.7933 | 167.6222 | 169.4511 | 171.28 | 173.1089 | 174.9378 | 176.7667 | 178.4311 | 180.0956 | 181.76 | 183.4244 | 185.0889 | 186.7533 | 188.4178 | 190.0822 | 191.7467 | 193.4111 | 195.0756 | 196.74 | 198.4044 | 200.0689 | 201.7333 | 202.2589 | 202.7844 | 203.31 | 203.8356 | 204.3611 | 204.8867 | 205.4122 | 205.9378 | 206.4633 | 206.9889 | 207.5144 | 208.04 | 208.5656 | 209.0911 | 209.6167 | 210.1422 | 210.6678 | 211.1933 | 211.7189 | 212.2444 | 212.77 | 213.2956 | 213.8211 | 214.3467 | 214.8722 | 215.3978 | 215.9233 | 216.4489 | 216.9744 | 217.5 | 217.7244 | 217.9489 | 218.1733 | 218.3978 | 218.6222 | 218.8467 | 219.0711 | 219.2956 | 219.52 | 219.7444 | 219.9689 | 220.1933 | 220.4178 | 220.6422 | 220.8667 | 221.0911 | 221.3156 | 221.54 | 221.7644 | 221.9889 | 222.2133 | 222.4378 | 222.6622 | 222.8867 | 223.1111 | 223.3356 | 223.56 | 223.7844 | 224.0089 | 224.2333 | 224.2333 | 224.2333 | 224.2333 | 224.2333 | 224.2333 | 224.2333 | 224.2333 | 224.2333 | 224.2333 | 224.2333 | 224.2333 | 224.2333 | 224.2333 | 224.2333 | 224.2333 | 224.2333 | 224.2333 | 224.2333 | 224.2333 | 224.2333 | 224.2333 | 224.2333 | 224.2333 | 224.2333 | 224.2333 | 224.2333 | 224.2333 | 224.2333 | 224.2333 | 224.2333 | 224.2167 | 224.2 | 224.1833 | 224.1667 | 224.15 | 224.1333 | 224.1167 | 224.1 | 224.0833 | 224.0667 | 224.05 | 224.0333 | 224.0167 | 224 | 223.9833 | 223.9667 | 223.95 | 223.9333 | 223.9167 | 223.9 | 223.8833 | 223.8667 | 223.85 | 223.8333 | 223.8167 | 223.8 | 223.7833 | 223.7667 | 223.75 | 223.7333
15.05 | 0 | 6.939 | 13.878 | 20.817 | 27.756 | 34.695 | 41.634 | 48.573 | 55.512 | 62.451 | 69.39 | 80.3657 | 91.3415 | 102.3172 | 113.2929 | 124.2687 | 123.9327 | 123.5968 | 123.2609 | 122.9249 | 122.589 | 125.3488 | 128.1085 | 130.8683 | 133.6281 | 136.3878 | 139.1476 | 141.9074 | 144.6671 | 147.4269 | 150.1867 | 152.0265 | 153.8664 | 155.7062 | 157.546 | 159.3859 | 161.2257 | 163.0656 | 164.9054 | 166.7453 | 168.5851 | 170.425 | 172.2648 | 174.1046 | 175.9445 | 177.7843 | 179.4594 | 181.1345 | 182.8096 | 184.4847 | 186.1598 | 187.8349 | 189.51 | 191.185 | 192.8601 | 194.5352 | 196.2103 | 197.8854 | 199.5605 | 201.2356 | 202.9107 | 203.4398 | 203.969 | 204.4981 | 205.0272 | 205.5564 | 206.0855 | 206.6147 | 207.1438 | 207.673 | 208.2021 | 208.7313 | 209.2604 | 209.7895 | 210.3187 | 210.8478 | 211.377 | 211.9061 | 212.4353 | 212.9644 | 213.4936 | 214.0227 | 214.5518 | 215.081 | 215.6101 | 216.1393 | 216.6684 | 217.1976 | 217.7267 | 218.2559 | 218.785 | 219.011 | 219.237 | 219.4631 | 219.6891 | 219.9151 | 220.1411 | 220.3672 | 220.5932 | 220.8192 | 221.0452 | 221.2712 | 221.4973 | 221.7233 | 221.9493 | 222.1753 | 222.4014 | 222.6274 | 222.8534 | 223.0794 | 223.3054 | 223.5315 | 223.7575 | 223.9835 | 224.2095 | 224.4356 | 224.6616 | 224.8876 | 225.1136 | 225.3396 | 225.5657 | 225.5657 | 225.5657 | 225.5657 | 225.5657 | 225.5657 | 225.5657 | 225.5657 | 225.5657 | 225.5657 | 225.5657 | 225.5657 | 225.5657 | 225.5657 | 225.5657 | 225.5657 | 225.5657 | 225.5657 | 225.5657 | 225.5657 | 225.5657 | 225.5657 | 225.5657 | 225.5657 | 225.5657 | 225.5657 | 225.5657 | 225.5657 | 225.5657 | 225.5657 | 225.5657 | 225.5498 | 225.534 | 225.5182 | 225.5023 | 225.4865 | 225.4707 | 225.4548 | 225.439 | 225.4232 | 225.4073 | 225.3915 | 225.3757 | 225.3598 | 225.344 | 225.3282 | 225.3123 | 225.2965 | 225.2807 | 225.2648 | 225.249 | 225.2332 | 225.2173 | 225.2015 | 225.1857 | 225.1698 | 225.154 | 225.1382 | 225.1223 | 225.1065 | 225.0907
15.1 | 0 | 6.978 | 13.956 | 20.934 | 27.912 | 34.89 | 41.868 | 48.846 | 55.824 | 62.802 | 69.78 | 80.8248 | 91.8696 | 102.9144 | 113.9592 | 125.004 | 124.6588 | 124.3136 | 123.9684 | 123.6232 | 123.278 | 126.0542 | 128.8304 | 131.6066 | 134.3828 | 137.159 | 139.9352 | 142.7114 | 145.4876 | 148.2638 | 151.04 | 152.8908 | 154.7416 | 156.5924 | 158.4432 | 160.294 | 162.1448 | 163.9956 | 165.8464 | 167.6972 | 169.548 | 171.3988 | 173.2496 | 175.1004 | 176.9512 | 178.802 | 180.4877 | 182.1735 | 183.8592 | 185.5449 | 187.2307 | 188.9164 | 190.6021 | 192.2879 | 193.9736 | 195.6593 | 197.3451 | 199.0308 | 200.7165 | 202.4023 | 204.088 | 204.6207 | 205.1535 | 205.6862 | 206.2189 | 206.7517 | 207.2844 | 207.8171 | 208.3499 | 208.8826 | 209.4153 | 209.9481 | 210.4808 | 211.0135 | 211.5463 | 212.079 | 212.6117 | 213.1445 | 213.6772 | 214.2099 | 214.7427 | 215.2754 | 215.8081 | 216.3409 | 216.8736 | 217.4063 | 217.9391 | 218.4718 | 219.0045 | 219.5373 | 220.07 | 220.2976 | 220.5252 | 220.7528 | 220.9804 | 221.208 | 221.4356 | 221.6632 | 221.8908 | 222.1184 | 222.346 | 222.5736 | 222.8012 | 223.0288 | 223.2564 | 223.484 | 223.7116 | 223.9392 | 224.1668 | 224.3944 | 224.622 | 224.8496 | 225.0772 | 225.3048 | 225.5324 | 225.76 | 225.9876 | 226.2152 | 226.4428 | 226.6704 | 226.898 | 226.898 | 226.898 | 226.898 | 226.898 | 226.898 | 226.898 | 226.898 | 226.898 | 226.898 | 226.898 | 226.898 | 226.898 | 226.898 | 226.898 | 226.898 | 226.898 | 226.898 | 226.898 | 226.898 | 226.898 | 226.898 | 226.898 | 226.898 | 226.898 | 226.898 | 226.898 | 226.898 | 226.898 | 226.898 | 226.898 | 226.883 | 226.868 | 226.853 | 226.838 | 226.823 | 226.808 | 226.793 | 226.778 | 226.763 | 226.748 | 226.733 | 226.718 | 226.703 | 226.688 | 226.673 | 226.658 | 226.643 | 226.628 | 226.613 | 226.598 | 226.583 | 226.568 | 226.553 | 226.538 | 226.523 | 226.508 | 226.493 | 226.478 | 226.463 | 226.448
15.15 | 0 | 7.017 | 14.034 | 21.051 | 28.068 | 35.085 | 42.102 | 49.119 | 56.136 | 63.153 | 70.17 | 81.2839 | 92.3977 | 103.5116 | 114.6255 | 125.7393 | 125.3849 | 125.0304 | 124.6759 | 124.3215 | 123.967 | 126.7596 | 129.5523 | 132.3449 | 135.1375 | 137.9302 | 140.7228 | 143.5154 | 146.3081 | 149.1007 | 151.8933 | 153.7551 | 155.6168 | 157.4786 | 159.3404 | 161.2021 | 163.0639 | 164.9256 | 166.7874 | 168.6491 | 170.5109 | 172.3726 | 174.2344 | 176.0962 | 177.9579 | 179.8197 | 181.516 | 183.2124 | 184.9088 | 186.6052 | 188.3016 | 189.9979 | 191.6943 | 193.3907 | 195.0871 | 196.7834 | 198.4798 | 200.1762 | 201.8726 | 203.569 | 205.2653 | 205.8017 | 206.338 | 206.8743 | 207.4106 | 207.9469 | 208.4833 | 209.0196 | 209.5559 | 210.0922 | 210.6286 | 211.1649 | 211.7012 | 212.2375 | 212.7738 | 213.3102 | 213.8465 | 214.3828 | 214.9191 | 215.4555 | 215.9918 | 216.5281 | 217.0644 | 217.6007 | 218.1371 | 218.6734 | 219.2097 | 219.746 | 220.2824 | 220.8187 | 221.355 | 221.5842 | 221.8134 | 222.0425 | 222.2717 | 222.5009 | 222.7301 | 222.9592 | 223.1884 | 223.4176 | 223.6468 | 223.876 | 224.1051 | 224.3343 | 224.5635 | 224.7927 | 225.0218 | 225.251 | 225.4802 | 225.7094 | 225.9386 | 226.1677 | 226.3969 | 226.6261 | 226.8553 | 227.0844 | 227.3136 | 227.5428 | 227.772 | 228.0012 | 228.2303 | 228.2303 | 228.2303 | 228.2303 | 228.2303 | 228.2303 | 228.2303 | 228.2303 | 228.2303 | 228.2303 | 228.2303 | 228.2303 | 228.2303 | 228.2303 | 228.2303 | 228.2303 | 228.2303 | 228.2303 | 228.2303 | 228.2303 | 228.2303 | 228.2303 | 228.2303 | 228.2303 | 228.2303 | 228.2303 | 228.2303 | 228.2303 | 228.2303 | 228.2303 | 228.2303 | 228.2162 | 228.202 | 228.1878 | 228.1737 | 228.1595 | 228.1453 | 228.1312 | 228.117 | 228.1028 | 228.0887 | 228.0745 | 228.0603 | 228.0462 | 228.032 | 228.0178 | 228.0037 | 227.9895 | 227.9753 | 227.9612 | 227.947 | 227.9328 | 227.9187 | 227.9045 | 227.8903 | 227.8762 | 227.862 | 227.8478 | 227.8337 | 227.8195 | 227.8053
15.2 | 0 | 7.056 | 14.112 | 21.168 | 28.224 | 35.28 | 42.336 | 49.392 | 56.448 | 63.504 | 70.56 | 81.7429 | 92.9259 | 104.1088 | 115.2917 | 126.4747 | 126.1109 | 125.7472 | 125.3835 | 125.0197 | 124.656 | 127.4651 | 130.2741 | 133.0832 | 135.8923 | 138.7013 | 141.5104 | 144.3195 | 147.1285 | 149.9376 | 152.7467 | 154.6194 | 156.4921 | 158.3648 | 160.2375 | 162.1102 | 163.9829 | 165.8556 | 167.7284 | 169.6011 | 171.4738 | 173.3465 | 175.2192 | 177.0919 | 178.9646 | 180.8373 | 182.5444 | 184.2514 | 185.9584 | 187.6654 | 189.3724 | 191.0795 | 192.7865 | 194.4935 | 196.2005 | 197.9076 | 199.6146 | 201.3216 | 203.0286 | 204.7356 | 206.4427 | 206.9826 | 207.5225 | 208.0624 | 208.6023 | 209.1422 | 209.6821 | 210.222 | 210.762 | 211.3019 | 211.8418 | 212.3817 | 212.9216 | 213.4615 | 214.0014 | 214.5413 | 215.0812 | 215.6212 | 216.1611 | 216.701 | 217.2409 | 217.7808 | 218.3207 | 218.8606 | 219.4005 | 219.9404 | 220.4804 | 221.0203 | 221.5602 | 222.1001 | 222.64 | 222.8708 | 223.1015 | 223.3323 | 223.563 | 223.7938 | 224.0245 | 224.2553 | 224.486 | 224.7168 | 224.9476 | 225.1783 | 225.4091 | 225.6398 | 225.8706 | 226.1013 | 226.3321 | 226.5628 | 226.7936 | 227.0244 | 227.2551 | 227.4859 | 227.7166 | 227.9474 | 228.1781 | 228.4089 | 228.6396 | 228.8704 | 229.1012 | 229.3319 | 229.5627 | 229.5627 | 229.5627 | 229.5627 | 229.5627 | 229.5627 | 229.5627 | 229.5627 | 229.5627 | 229.5627 | 229.5627 | 229.5627 | 229.5627 | 229.5627 | 229.5627 | 229.5627 | 229.5627 | 229.5627 | 229.5627 | 229.5627 | 229.5627 | 229.5627 | 229.5627 | 229.5627 | 229.5627 | 229.5627 | 229.5627 | 229.5627 | 229.5627 | 229.5627 | 229.5627 | 229.5493 | 229.536 | 229.5227 | 229.5093 | 229.496 | 229.4827 | 229.4693 | 229.456 | 229.4427 | 229.4293 | 229.416 | 229.4027 | 229.3893 | 229.376 | 229.3627 | 229.3493 | 229.336 | 229.3227 | 229.3093 | 229.296 | 229.2827 | 229.2693 | 229.256 | 229.2427 | 229.2293 | 229.216 | 229.2027 | 229.1893 | 229.176 | 229.1627
15.25 | 0 | 7.095 | 14.19 | 21.285 | 28.38 | 35.475 | 42.57 | 49.665 | 56.76 | 63.855 | 70.95 | 82.202 | 93.454 | 104.706 | 115.958 | 127.21 | 126.837 | 126.464 | 126.091 | 125.718 | 125.345 | 128.1705 | 130.996 | 133.8215 | 136.647 | 139.4725 | 142.298 | 145.1235 | 147.949 | 150.7745 | 153.6 | 155.4837 | 157.3673 | 159.251 | 161.1347 | 163.0183 | 164.902 | 166.7857 | 168.6693 | 170.553 | 172.4367 | 174.3203 | 176.204 | 178.0877 | 179.9713 | 181.855 | 183.5727 | 185.2903 | 187.008 | 188.7257 | 190.4433 | 192.161 | 193.8787 | 195.5963 | 197.314 | 199.0317 | 200.7493 | 202.467 | 204.1847 | 205.9023 | 207.62 | 208.1635 | 208.707 | 209.2505 | 209.794 | 210.3375 | 210.881 | 211.4245 | 211.968 | 212.5115 | 213.055 | 213.5985 | 214.142 | 214.6855 | 215.229 | 215.7725 | 216.316 | 216.8595 | 217.403 | 217.9465 | 218.49 | 219.0335 | 219.577 | 220.1205 | 220.664 | 221.2075 | 221.751 | 222.2945 | 222.838 | 223.3815 | 223.925 | 224.1573 | 224.3897 | 224.622 | 224.8543 | 225.0867 | 225.319 | 225.5513 | 225.7837 | 226.016 | 226.2483 | 226.4807 | 226.713 | 226.9453 | 227.1777 | 227.41 | 227.6423 | 227.8747 | 228.107 | 228.3393 | 228.5717 | 228.804 | 229.0363 | 229.2687 | 229.501 | 229.7333 | 229.9657 | 230.198 | 230.4303 | 230.6627 | 230.895 | 230.895 | 230.895 | 230.895 | 230.895 | 230.895 | 230.895 | 230.895 | 230.895 | 230.895 | 230.895 | 230.895 | 230.895 | 230.895 | 230.895 | 230.895 | 230.895 | 230.895 | 230.895 | 230.895 | 230.895 | 230.895 | 230.895 | 230.895 | 230.895 | 230.895 | 230.895 | 230.895 | 230.895 | 230.895 | 230.895 | 230.8825 | 230.87 | 230.8575 | 230.845 | 230.8325 | 230.82 | 230.8075 | 230.795 | 230.7825 | 230.77 | 230.7575 | 230.745 | 230.7325 | 230.72 | 230.7075 | 230.695 | 230.6825 | 230.67 | 230.6575 | 230.645 | 230.6325 | 230.62 | 230.6075 | 230.595 | 230.5825 | 230.57 | 230.5575 | 230.545 | 230.5325 | 230.52
15.3 | 0 | 7.134 | 14.268 | 21.402 | 28.536 | 35.67 | 42.804 | 49.938 | 57.072 | 64.206 | 71.34 | 82.6611 | 93.9821 | 105.3032 | 116.6243 | 127.9453 | 127.5631 | 127.1808 | 126.7985 | 126.4163 | 126.034 | 128.8759 | 131.7179 | 134.5598 | 137.4017 | 140.2437 | 143.0856 | 145.9275 | 148.7695 | 151.6114 | 154.4533 | 156.348 | 158.2426 | 160.1372 | 162.0318 | 163.9264 | 165.8211 | 167.7157 | 169.6103 | 171.5049 | 173.3996 | 175.2942 | 177.1888 | 179.0834 | 180.978 | 182.8727 | 184.601 | 186.3293 | 188.0576 | 189.7859 | 191.5142 | 193.2425 | 194.9708 | 196.6992 | 198.4275 | 200.1558 | 201.8841 | 203.6124 | 205.3407 | 207.069 | 208.7973 | 209.3444 | 209.8915 | 210.4386 | 210.9857 | 211.5328 | 212.0799 | 212.627 | 213.174 | 213.7211 | 214.2682 | 214.8153 | 215.3624 | 215.9095 | 216.4566 | 217.0037 | 217.5508 | 218.0978 | 218.6449 | 219.192 | 219.7391 | 220.2862 | 220.8333 | 221.3804 | 221.9275 | 222.4746 | 223.0216 | 223.5687 | 224.1158 | 224.6629 | 225.21 | 225.4439 | 225.6778 | 225.9117 | 226.1456 | 226.3796 | 226.6135 | 226.8474 | 227.0813 | 227.3152 | 227.5491 | 227.783 | 228.0169 | 228.2508 | 228.4848 | 228.7187 | 228.9526 | 229.1865 | 229.4204 | 229.6543 | 229.8882 | 230.1221 | 230.356 | 230.59 | 230.8239 | 231.0578 | 231.2917 | 231.5256 | 231.7595 | 231.9934 | 232.2273 | 232.2273 | 232.2273 | 232.2273 | 232.2273 | 232.2273 | 232.2273 | 232.2273 | 232.2273 | 232.2273 | 232.2273 | 232.2273 | 232.2273 | 232.2273 | 232.2273 | 232.2273 | 232.2273 | 232.2273 | 232.2273 | 232.2273 | 232.2273 | 232.2273 | 232.2273 | 232.2273 | 232.2273 | 232.2273 | 232.2273 | 232.2273 | 232.2273 | 232.2273 | 232.2273 | 232.2157 | 232.204 | 232.1923 | 232.1807 | 232.169 | 232.1573 | 232.1457 | 232.134 | 232.1223 | 232.1107 | 232.099 | 232.0873 | 232.0757 | 232.064 | 232.0523 | 232.0407 | 232.029 | 232.0173 | 232.0057 | 231.994 | 231.9823 | 231.9707 | 231.959 | 231.9473 | 231.9357 | 231.924 | 231.9123 | 231.9007 | 231.889 | 231.8773
15.35 | 0 | 7.173 | 14.346 | 21.519 | 28.692 | 35.865 | 43.038 | 50.211 | 57.384 | 64.557 | 71.73 | 83.1201 | 94.5103 | 105.9004 | 117.2905 | 128.6807 | 128.2891 | 127.8976 | 127.5061 | 127.1145 | 126.723 | 129.5814 | 132.4397 | 135.2981 | 138.1565 | 141.0148 | 143.8732 | 146.7316 | 149.5899 | 152.4483 | 155.3067 | 157.2122 | 159.1178 | 161.0234 | 162.929 | 164.8346 | 166.7401 | 168.6457 | 170.5513 | 172.4569 | 174.3624 | 176.268 | 178.1736 | 180.0792 | 181.9848 | 183.8903 | 185.6293 | 187.3682 | 189.1072 | 190.8462 | 192.5851 | 194.3241 | 196.063 | 197.802 | 199.5409 | 201.2799 | 203.0188 | 204.7578 | 206.4968 | 208.2357 | 209.9747 | 210.5253 | 211.076 | 211.6267 | 212.1774 | 212.7281 | 213.2787 | 213.8294 | 214.3801 | 214.9308 | 215.4814 | 216.0321 | 216.5828 | 217.1335 | 217.6842 | 218.2348 | 218.7855 | 219.3362 | 219.8869 | 220.4375 | 220.9882 | 221.5389 | 222.0896 | 222.6403 | 223.1909 | 223.7416 | 224.2923 | 224.843 | 225.3936 | 225.9443 | 226.495 | 226.7305 | 226.966 | 227.2015 | 227.437 | 227.6724 | 227.9079 | 228.1434 | 228.3789 | 228.6144 | 228.8499 | 229.0854 | 229.3209 | 229.5564 | 229.7918 | 230.0273 | 230.2628 | 230.4983 | 230.7338 | 230.9693 | 231.2048 | 231.4403 | 231.6758 | 231.9112 | 232.1467 | 232.3822 | 232.6177 | 232.8532 | 233.0887 | 233.3242 | 233.5597 | 233.5597 | 233.5597 | 233.5597 | 233.5597 | 233.5597 | 233.5597 | 233.5597 | 233.5597 | 233.5597 | 233.5597 | 233.5597 | 233.5597 | 233.5597 | 233.5597 | 233.5597 | 233.5597 | 233.5597 | 233.5597 | 233.5597 | 233.5597 | 233.5597 | 233.5597 | 233.5597 | 233.5597 | 233.5597 | 233.5597 | 233.5597 | 233.5597 | 233.5597 | 233.5597 | 233.5488 | 233.538 | 233.5272 | 233.5163 | 233.5055 | 233.4947 | 233.4838 | 233.473 | 233.4622 | 233.4513 | 233.4405 | 233.4297 | 233.4188 | 233.408 | 233.3972 | 233.3863 | 233.3755 | 233.3647 | 233.3538 | 233.343 | 233.3322 | 233.3213 | 233.3105 | 233.2997 | 233.2888 | 233.278 | 233.2672 | 233.2563 | 233.2455 | 233.2347
15.4 | 0 | 7.212 | 14.424 | 21.636 | 28.848 | 36.06 | 43.272 | 50.484 | 57.696 | 64.908 | 72.12 | 83.5792 | 95.0384 | 106.4976 | 117.9568 | 129.416 | 129.0152 | 128.6144 | 128.2136 | 127.8128 | 127.412 | 130.2868 | 133.1616 | 136.0364 | 138.9112 | 141.786 | 144.6608 | 147.5356 | 150.4104 | 153.2852 | 156.16 | 158.0765 | 159.9931 | 161.9096 | 163.8261 | 165.7427 | 167.6592 | 169.5757 | 171.4923 | 173.4088 | 175.3253 | 177.2419 | 179.1584 | 181.0749 | 182.9915 | 184.908 | 186.6576 | 188.4072 | 190.1568 | 191.9064 | 193.656 | 195.4056 | 197.1552 | 198.9048 | 200.6544 | 202.404 | 204.1536 | 205.9032 | 207.6528 | 209.4024 | 211.152 | 211.7063 | 212.2605 | 212.8148 | 213.3691 | 213.9233 | 214.4776 | 215.0319 | 215.5861 | 216.1404 | 216.6947 | 217.2489 | 217.8032 | 218.3575 | 218.9117 | 219.466 | 220.0203 | 220.5745 | 221.1288 | 221.6831 | 222.2373 | 222.7916 | 223.3459 | 223.9001 | 224.4544 | 225.0087 | 225.5629 | 226.1172 | 226.6715 | 227.2257 | 227.78 | 228.0171 | 228.2541 | 228.4912 | 228.7283 | 228.9653 | 229.2024 | 229.4395 | 229.6765 | 229.9136 | 230.1507 | 230.3877 | 230.6248 | 230.8619 | 231.0989 | 231.336 | 231.5731 | 231.8101 | 232.0472 | 232.2843 | 232.5213 | 232.7584 | 232.9955 | 233.2325 | 233.4696 | 233.7067 | 233.9437 | 234.1808 | 234.4179 | 234.6549 | 234.892 | 234.892 | 234.892 | 234.892 | 234.892 | 234.892 | 234.892 | 234.892 | 234.892 | 234.892 | 234.892 | 234.892 | 234.892 | 234.892 | 234.892 | 234.892 | 234.892 | 234.892 | 234.892 | 234.892 | 234.892 | 234.892 | 234.892 | 234.892 | 234.892 | 234.892 | 234.892 | 234.892 | 234.892 | 234.892 | 234.892 | 234.882 | 234.872 | 234.862 | 234.852 | 234.842 | 234.832 | 234.822 | 234.812 | 234.802 | 234.792 | 234.782 | 234.772 | 234.762 | 234.752 | 234.742 | 234.732 | 234.722 | 234.712 | 234.702 | 234.692 | 234.682 | 234.672 | 234.662 | 234.652 | 234.642 | 234.632 | 234.622 | 234.612 | 234.602 | 234.592
15.45 | 0 | 7.251 | 14.502 | 21.753 | 29.004 | 36.255 | 43.506 | 50.757 | 58.008 | 65.259 | 72.51 | 84.0383 | 95.5665 | 107.0948 | 118.6231 | 130.1513 | 129.7413 | 129.3312 | 128.9211 | 128.5111 | 128.101 | 130.9922 | 133.8835 | 136.7747 | 139.6659 | 142.5572 | 145.4484 | 148.3396 | 151.2309 | 154.1221 | 157.0133 | 158.9408 | 160.8683 | 162.7958 | 164.7233 | 166.6508 | 168.5783 | 170.5058 | 172.4332 | 174.3607 | 176.2882 | 178.2157 | 180.1432 | 182.0707 | 183.9982 | 185.9257 | 187.6859 | 189.4462 | 191.2064 | 192.9666 | 194.7269 | 196.4871 | 198.2474 | 200.0076 | 201.7679 | 203.5281 | 205.2884 | 207.0486 | 208.8088 | 210.5691 | 212.3293 | 212.8872 | 213.445 | 214.0029 | 214.5608 | 215.1186 | 215.6765 | 216.2343 | 216.7922 | 217.35 | 217.9079 | 218.4657 | 219.0236 | 219.5815 | 220.1393 | 220.6972 | 221.255 | 221.8129 | 222.3707 | 222.9286 | 223.4864 | 224.0443 | 224.6022 | 225.16 | 225.7179 | 226.2757 | 226.8336 | 227.3914 | 227.9493 | 228.5071 | 229.065 | 229.3036 | 229.5423 | 229.7809 | 230.0196 | 230.2582 | 230.4969 | 230.7355 | 230.9742 | 231.2128 | 231.4514 | 231.6901 | 231.9287 | 232.1674 | 232.406 | 232.6447 | 232.8833 | 233.122 | 233.3606 | 233.5992 | 233.8379 | 234.0765 | 234.3152 | 234.5538 | 234.7925 | 235.0311 | 235.2698 | 235.5084 | 235.747 | 235.9857 | 236.2243 | 236.2243 | 236.2243 | 236.2243 | 236.2243 | 236.2243 | 236.2243 | 236.2243 | 236.2243 | 236.2243 | 236.2243 | 236.2243 | 236.2243 | 236.2243 | 236.2243 | 236.2243 | 236.2243 | 236.2243 | 236.2243 | 236.2243 | 236.2243 | 236.2243 | 236.2243 | 236.2243 | 236.2243 | 236.2243 | 236.2243 | 236.2243 | 236.2243 | 236.2243 | 236.2243 | 236.2152 | 236.206 | 236.1968 | 236.1877 | 236.1785 | 236.1693 | 236.1602 | 236.151 | 236.1418 | 236.1327 | 236.1235 | 236.1143 | 236.1052 | 236.096 | 236.0868 | 236.0777 | 236.0685 | 236.0593 | 236.0502 | 236.041 | 236.0318 | 236.0227 | 236.0135 | 236.0043 | 235.9952 | 235.986 | 235.9768 | 235.9677 | 235.9585 | 235.9493
15.5 | 0 | 7.29 | 14.58 | 21.87 | 29.16 | 36.45 | 43.74 | 51.03 | 58.32 | 65.61 | 72.9 | 84.4973 | 96.0947 | 107.692 | 119.2893 | 130.8867 | 130.4673 | 130.048 | 129.6287 | 129.2093 | 128.79 | 131.6977 | 134.6053 | 137.513 | 140.4207 | 143.3283 | 146.236 | 149.1437 | 152.0513 | 154.959 | 157.8667 | 159.8051 | 161.7436 | 163.682 | 165.6204 | 167.5589 | 169.4973 | 171.4358 | 173.3742 | 175.3127 | 177.2511 | 179.1896 | 181.128 | 183.0664 | 185.0049 | 186.9433 | 188.7142 | 190.4851 | 192.256 | 194.0269 | 195.7978 | 197.5687 | 199.3396 | 201.1104 | 202.8813 | 204.6522 | 206.4231 | 208.194 | 209.9649 | 211.7358 | 213.5067 | 214.0681 | 214.6296 | 215.191 | 215.7524 | 216.3139 | 216.8753 | 217.4368 | 217.9982 | 218.5597 | 219.1211 | 219.6826 | 220.244 | 220.8054 | 221.3669 | 221.9283 | 222.4898 | 223.0512 | 223.6127 | 224.1741 | 224.7356 | 225.297 | 225.8584 | 226.4199 | 226.9813 | 227.5428 | 228.1042 | 228.6657 | 229.2271 | 229.7886 | 230.35 | 230.5902 | 230.8304 | 231.0707 | 231.3109 | 231.5511 | 231.7913 | 232.0316 | 232.2718 | 232.512 | 232.7522 | 232.9924 | 233.2327 | 233.4729 | 233.7131 | 233.9533 | 234.1936 | 234.4338 | 234.674 | 234.9142 | 235.1544 | 235.3947 | 235.6349 | 235.8751 | 236.1153 | 236.3556 | 236.5958 | 236.836 | 237.0762 | 237.3164 | 237.5567 | 237.5567 | 237.5567 | 237.5567 | 237.5567 | 237.5567 | 237.5567 | 237.5567 | 237.5567 | 237.5567 | 237.5567 | 237.5567 | 237.5567 | 237.5567 | 237.5567 | 237.5567 | 237.5567 | 237.5567 | 237.5567 | 237.5567 | 237.5567 | 237.5567 | 237.5567 | 237.5567 | 237.5567 | 237.5567 | 237.5567 | 237.5567 | 237.5567 | 237.5567 | 237.5567 | 237.5483 | 237.54 | 237.5317 | 237.5233 | 237.515 | 237.5067 | 237.4983 | 237.49 | 237.4817 | 237.4733 | 237.465 | 237.4567 | 237.4483 | 237.44 | 237.4317 | 237.4233 | 237.415 | 237.4067 | 237.3983 | 237.39 | 237.3817 | 237.3733 | 237.365 | 237.3567 | 237.3483 | 237.34 | 237.3317 | 237.3233 | 237.315 | 237.3067
15.55 | 0 | 7.329 | 14.658 | 21.987 | 29.316 | 36.645 | 43.974 | 51.303 | 58.632 | 65.961 | 73.29 | 84.9564 | 96.6228 | 108.2892 | 119.9556 | 131.622 | 131.1934 | 130.7648 | 130.3362 | 129.9076 | 129.479 | 132.4031 | 135.3272 | 138.2513 | 141.1754 | 144.0995 | 147.0236 | 149.9477 | 152.8718 | 155.7959 | 158.72 | 160.6694 | 162.6188 | 164.5682 | 166.5176 | 168.467 | 170.4164 | 172.3658 | 174.3152 | 176.2646 | 178.214 | 180.1634 | 182.1128 | 184.0622 | 186.0116 | 187.961 | 189.7425 | 191.5241 | 193.3056 | 195.0871 | 196.8687 | 198.6502 | 200.4317 | 202.2133 | 203.9948 | 205.7763 | 207.5579 | 209.3394 | 211.1209 | 212.9025 | 214.684 | 215.249 | 215.8141 | 216.3791 | 216.9441 | 217.5092 | 218.0742 | 218.6392 | 219.2043 | 219.7693 | 220.3343 | 220.8994 | 221.4644 | 222.0294 | 222.5945 | 223.1595 | 223.7245 | 224.2896 | 224.8546 | 225.4196 | 225.9847 | 226.5497 | 227.1147 | 227.6798 | 228.2448 | 228.8098 | 229.3749 | 229.9399 | 230.5049 | 231.07 | 231.635 | 231.8768 | 232.1186 | 232.3604 | 232.6022 | 232.844 | 233.0858 | 233.3276 | 233.5694 | 233.8112 | 234.053 | 234.2948 | 234.5366 | 234.7784 | 235.0202 | 235.262 | 235.5038 | 235.7456 | 235.9874 | 236.2292 | 236.471 | 236.7128 | 236.9546 | 237.1964 | 237.4382 | 237.68 | 237.9218 | 238.1636 | 238.4054 | 238.6472 | 238.889 | 238.889 | 238.889 | 238.889 | 238.889 | 238.889 | 238.889 | 238.889 | 238.889 | 238.889 | 238.889 | 238.889 | 238.889 | 238.889 | 238.889 | 238.889 | 238.889 | 238.889 | 238.889 | 238.889 | 238.889 | 238.889 | 238.889 | 238.889 | 238.889 | 238.889 | 238.889 | 238.889 | 238.889 | 238.889 | 238.889 | 238.8815 | 238.874 | 238.8665 | 238.859 | 238.8515 | 238.844 | 238.8365 | 238.829 | 238.8215 | 238.814 | 238.8065 | 238.799 | 238.7915 | 238.784 | 238.7765 | 238.769 | 238.7615 | 238.754 | 238.7465 | 238.739 | 238.7315 | 238.724 | 238.7165 | 238.709 | 238.7015 | 238.694 | 238.6865 | 238.679 | 238.6715 | 238.664
15.6 | 0 | 7.368 | 14.736 | 22.104 | 29.472 | 36.84 | 44.208 | 51.576 | 58.944 | 66.312 | 73.68 | 85.4155 | 97.1509 | 108.8864 | 120.6219 | 132.3573 | 131.9195 | 131.4816 | 131.0437 | 130.6059 | 130.168 | 133.1085 | 136.0491 | 138.9896 | 141.9301 | 144.8707 | 147.8112 | 150.7517 | 153.6923 | 156.6328 | 159.5733 | 161.5337 | 163.494 | 165.4544 | 167.4148 | 169.3751 | 171.3355 | 173.2958 | 175.2562 | 177.2165 | 179.1769 | 181.1372 | 183.0976 | 185.058 | 187.0183 | 188.9787 | 190.7708 | 192.563 | 194.3552 | 196.1474 | 197.9396 | 199.7317 | 201.5239 | 203.3161 | 205.1083 | 206.9004 | 208.6926 | 210.4848 | 212.277 | 214.0692 | 215.8613 | 216.43 | 216.9986 | 217.5672 | 218.1358 | 218.7044 | 219.2731 | 219.8417 | 220.4103 | 220.9789 | 221.5476 | 222.1162 | 222.6848 | 223.2534 | 223.822 | 224.3907 | 224.9593 | 225.5279 | 226.0965 | 226.6652 | 227.2338 | 227.8024 | 228.371 | 228.9396 | 229.5083 | 230.0769 | 230.6455 | 231.2141 | 231.7828 | 232.3514 | 232.92 | 233.1634 | 233.4068 | 233.6501 | 233.8935 | 234.1369 | 234.3803 | 234.6236 | 234.867 | 235.1104 | 235.3538 | 235.5972 | 235.8405 | 236.0839 | 236.3273 | 236.5707 | 236.814 | 237.0574 | 237.3008 | 237.5442 | 237.7876 | 238.0309 | 238.2743 | 238.5177 | 238.7611 | 239.0044 | 239.2478 | 239.4912 | 239.7346 | 239.978 | 240.2213 | 240.2213 | 240.2213 | 240.2213 | 240.2213 | 240.2213 | 240.2213 | 240.2213 | 240.2213 | 240.2213 | 240.2213 | 240.2213 | 240.2213 | 240.2213 | 240.2213 | 240.2213 | 240.2213 | 240.2213 | 240.2213 | 240.2213 | 240.2213 | 240.2213 | 240.2213 | 240.2213 | 240.2213 | 240.2213 | 240.2213 | 240.2213 | 240.2213 | 240.2213 | 240.2213 | 240.2147 | 240.208 | 240.2013 | 240.1947 | 240.188 | 240.1813 | 240.1747 | 240.168 | 240.1613 | 240.1547 | 240.148 | 240.1413 | 240.1347 | 240.128 | 240.1213 | 240.1147 | 240.108 | 240.1013 | 240.0947 | 240.088 | 240.0813 | 240.0747 | 240.068 | 240.0613 | 240.0547 | 240.048 | 240.0413 | 240.0347 | 240.028 | 240.0213
15.65 | 0 | 7.407 | 14.814 | 22.221 | 29.628 | 37.035 | 44.442 | 51.849 | 59.256 | 66.663 | 74.07 | 85.8745 | 97.6791 | 109.4836 | 121.2881 | 133.0927 | 132.6455 | 132.1984 | 131.7513 | 131.3041 | 130.857 | 133.814 | 136.7709 | 139.7279 | 142.6849 | 145.6418 | 148.5988 | 151.5558 | 154.5127 | 157.4697 | 160.4267 | 162.398 | 164.3693 | 166.3406 | 168.3119 | 170.2832 | 172.2545 | 174.2258 | 176.1972 | 178.1685 | 180.1398 | 182.1111 | 184.0824 | 186.0537 | 188.025 | 189.9963 | 191.7992 | 193.602 | 195.4048 | 197.2076 | 199.0104 | 200.8133 | 202.6161 | 204.4189 | 206.2217 | 208.0246 | 209.8274 | 211.6302 | 213.433 | 215.2358 | 217.0387 | 217.6109 | 218.1831 | 218.7553 | 219.3275 | 219.8997 | 220.4719 | 221.0441 | 221.6164 | 222.1886 | 222.7608 | 223.333 | 223.9052 | 224.4774 | 225.0496 | 225.6218 | 226.194 | 226.7663 | 227.3385 | 227.9107 | 228.4829 | 229.0551 | 229.6273 | 230.1995 | 230.7717 | 231.3439 | 231.9162 | 232.4884 | 233.0606 | 233.6328 | 234.205 | 234.45 | 234.6949 | 234.9399 | 235.1848 | 235.4298 | 235.6747 | 235.9197 | 236.1646 | 236.4096 | 236.6546 | 236.8995 | 237.1445 | 237.3894 | 237.6344 | 237.8793 | 238.1243 | 238.3692 | 238.6142 | 238.8592 | 239.1041 | 239.3491 | 239.594 | 239.839 | 240.0839 | 240.3289 | 240.5738 | 240.8188 | 241.0638 | 241.3087 | 241.5537 | 241.5537 | 241.5537 | 241.5537 | 241.5537 | 241.5537 | 241.5537 | 241.5537 | 241.5537 | 241.5537 | 241.5537 | 241.5537 | 241.5537 | 241.5537 | 241.5537 | 241.5537 | 241.5537 | 241.5537 | 241.5537 | 241.5537 | 241.5537 | 241.5537 | 241.5537 | 241.5537 | 241.5537 | 241.5537 | 241.5537 | 241.5537 | 241.5537 | 241.5537 | 241.5537 | 241.5478 | 241.542 | 241.5362 | 241.5303 | 241.5245 | 241.5187 | 241.5128 | 241.507 | 241.5012 | 241.4953 | 241.4895 | 241.4837 | 241.4778 | 241.472 | 241.4662 | 241.4603 | 241.4545 | 241.4487 | 241.4428 | 241.437 | 241.4312 | 241.4253 | 241.4195 | 241.4137 | 241.4078 | 241.402 | 241.3962 | 241.3903 | 241.3845 | 241.3787
15.7 | 0 | 7.446 | 14.892 | 22.338 | 29.784 | 37.23 | 44.676 | 52.122 | 59.568 | 67.014 | 74.46 | 86.3336 | 98.2072 | 110.0808 | 121.9544 | 133.828 | 133.3716 | 132.9152 | 132.4588 | 132.0024 | 131.546 | 134.5194 | 137.4928 | 140.4662 | 143.4396 | 146.413 | 149.3864 | 152.3598 | 155.3332 | 158.3066 | 161.28 | 163.2623 | 165.2445 | 167.2268 | 169.2091 | 171.1913 | 173.1736 | 175.1559 | 177.1381 | 179.1204 | 181.1027 | 183.0849 | 185.0672 | 187.0495 | 189.0317 | 191.014 | 192.8275 | 194.6409 | 196.4544 | 198.2679 | 200.0813 | 201.8948 | 203.7083 | 205.5217 | 207.3352 | 209.1487 | 210.9621 | 212.7756 | 214.5891 | 216.4025 | 218.216 | 218.7918 | 219.3676 | 219.9434 | 220.5192 | 221.095 | 221.6708 | 222.2466 | 222.8224 | 223.3982 | 223.974 | 224.5498 | 225.1256 | 225.7014 | 226.2772 | 226.853 | 227.4288 | 228.0046 | 228.5804 | 229.1562 | 229.732 | 230.3078 | 230.8836 | 231.4594 | 232.0352 | 232.611 | 233.1868 | 233.7626 | 234.3384 | 234.9142 | 235.49 | 235.7365 | 235.9831 | 236.2296 | 236.4761 | 236.7227 | 236.9692 | 237.2157 | 237.4623 | 237.7088 | 237.9553 | 238.2019 | 238.4484 | 238.6949 | 238.9415 | 239.188 | 239.4345 | 239.6811 | 239.9276 | 240.1741 | 240.4207 | 240.6672 | 240.9137 | 241.1603 | 241.4068 | 241.6533 | 241.8999 | 242.1464 | 242.3929 | 242.6395 | 242.886 | 242.886 | 242.886 | 242.886 | 242.886 | 242.886 | 242.886 | 242.886 | 242.886 | 242.886 | 242.886 | 242.886 | 242.886 | 242.886 | 242.886 | 242.886 | 242.886 | 242.886 | 242.886 | 242.886 | 242.886 | 242.886 | 242.886 | 242.886 | 242.886 | 242.886 | 242.886 | 242.886 | 242.886 | 242.886 | 242.886 | 242.881 | 242.876 | 242.871 | 242.866 | 242.861 | 242.856 | 242.851 | 242.846 | 242.841 | 242.836 | 242.831 | 242.826 | 242.821 | 242.816 | 242.811 | 242.806 | 242.801 | 242.796 | 242.791 | 242.786 | 242.781 | 242.776 | 242.771 | 242.766 | 242.761 | 242.756 | 242.751 | 242.746 | 242.741 | 242.736
15.75 | 0 | 7.485 | 14.97 | 22.455 | 29.94 | 37.425 | 44.91 | 52.395 | 59.88 | 67.365 | 74.85 | 86.7927 | 98.7353 | 110.678 | 122.6207 | 134.5633 | 134.0977 | 133.632 | 133.1663 | 132.7007 | 132.235 | 135.2248 | 138.2147 | 141.2045 | 144.1943 | 147.1842 | 150.174 | 153.1638 | 156.1537 | 159.1435 | 162.1333 | 164.1266 | 166.1198 | 168.113 | 170.1062 | 172.0994 | 174.0927 | 176.0859 | 178.0791 | 180.0723 | 182.0656 | 184.0588 | 186.052 | 188.0452 | 190.0384 | 192.0317 | 193.8558 | 195.6799 | 197.504 | 199.3281 | 201.1522 | 202.9763 | 204.8004 | 206.6246 | 208.4487 | 210.2728 | 212.0969 | 213.921 | 215.7451 | 217.5692 | 219.3933 | 219.9727 | 220.5521 | 221.1315 | 221.7109 | 222.2903 | 222.8697 | 223.4491 | 224.0284 | 224.6078 | 225.1872 | 225.7666 | 226.346 | 226.9254 | 227.5048 | 228.0842 | 228.6636 | 229.2429 | 229.8223 | 230.4017 | 230.9811 | 231.5605 | 232.1399 | 232.7193 | 233.2987 | 233.8781 | 234.4574 | 235.0368 | 235.6162 | 236.1956 | 236.775 | 237.0231 | 237.2712 | 237.5193 | 237.7674 | 238.0156 | 238.2637 | 238.5118 | 238.7599 | 239.008 | 239.2561 | 239.5042 | 239.7523 | 240.0004 | 240.2486 | 240.4967 | 240.7448 | 240.9929 | 241.241 | 241.4891 | 241.7372 | 241.9853 | 242.2334 | 242.4816 | 242.7297 | 242.9778 | 243.2259 | 243.474 | 243.7221 | 243.9702 | 244.2183 | 244.2183 | 244.2183 | 244.2183 | 244.2183 | 244.2183 | 244.2183 | 244.2183 | 244.2183 | 244.2183 | 244.2183 | 244.2183 | 244.2183 | 244.2183 | 244.2183 | 244.2183 | 244.2183 | 244.2183 | 244.2183 | 244.2183 | 244.2183 | 244.2183 | 244.2183 | 244.2183 | 244.2183 | 244.2183 | 244.2183 | 244.2183 | 244.2183 | 244.2183 | 244.2183 | 244.2142 | 244.21 | 244.2058 | 244.2017 | 244.1975 | 244.1933 | 244.1892 | 244.185 | 244.1808 | 244.1767 | 244.1725 | 244.1683 | 244.1642 | 244.16 | 244.1558 | 244.1517 | 244.1475 | 244.1433 | 244.1392 | 244.135 | 244.1308 | 244.1267 | 244.1225 | 244.1183 | 244.1142 | 244.11 | 244.1058 | 244.1017 | 244.0975 | 244.0933
15.8 | 0 | 7.524 | 15.048 | 22.572 | 30.096 | 37.62 | 45.144 | 52.668 | 60.192 | 67.716 | 75.24 | 87.2517 | 99.2635 | 111.2752 | 123.2869 | 135.2987 | 134.8237 | 134.3488 | 133.8739 | 133.3989 | 132.924 | 135.9303 | 138.9365 | 141.9428 | 144.9491 | 147.9553 | 150.9616 | 153.9679 | 156.9741 | 159.9804 | 162.9867 | 164.9908 | 166.995 | 168.9992 | 171.0034 | 173.0076 | 175.0117 | 177.0159 | 179.0201 | 181.0243 | 183.0284 | 185.0326 | 187.0368 | 189.041 | 191.0452 | 193.0493 | 194.8841 | 196.7188 | 198.5536 | 200.3884 | 202.2231 | 204.0579 | 205.8926 | 207.7274 | 209.5621 | 211.3969 | 213.2316 | 215.0664 | 216.9012 | 218.7359 | 220.5707 | 221.1536 | 221.7366 | 222.3196 | 222.9026 | 223.4856 | 224.0685 | 224.6515 | 225.2345 | 225.8175 | 226.4004 | 226.9834 | 227.5664 | 228.1494 | 228.7324 | 229.3153 | 229.8983 | 230.4813 | 231.0643 | 231.6472 | 232.2302 | 232.8132 | 233.3962 | 233.9792 | 234.5621 | 235.1451 | 235.7281 | 236.3111 | 236.894 | 237.477 | 238.06 | 238.3097 | 238.5594 | 238.8091 | 239.0588 | 239.3084 | 239.5581 | 239.8078 | 240.0575 | 240.3072 | 240.5569 | 240.8066 | 241.0563 | 241.306 | 241.5556 | 241.8053 | 242.055 | 242.3047 | 242.5544 | 242.8041 | 243.0538 | 243.3035 | 243.5532 | 243.8028 | 244.0525 | 244.3022 | 244.5519 | 244.8016 | 245.0513 | 245.301 | 245.5507 | 245.5507 | 245.5507 | 245.5507 | 245.5507 | 245.5507 | 245.5507 | 245.5507 | 245.5507 | 245.5507 | 245.5507 | 245.5507 | 245.5507 | 245.5507 | 245.5507 | 245.5507 | 245.5507 | 245.5507 | 245.5507 | 245.5507 | 245.5507 | 245.5507 | 245.5507 | 245.5507 | 245.5507 | 245.5507 | 245.5507 | 245.5507 | 245.5507 | 245.5507 | 245.5507 | 245.5473 | 245.544 | 245.5407 | 245.5373 | 245.534 | 245.5307 | 245.5273 | 245.524 | 245.5207 | 245.5173 | 245.514 | 245.5107 | 245.5073 | 245.504 | 245.5007 | 245.4973 | 245.494 | 245.4907 | 245.4873 | 245.484 | 245.4807 | 245.4773 | 245.474 | 245.4707 | 245.4673 | 245.464 | 245.4607 | 245.4573 | 245.454 | 245.4507
15.85 | 0 | 7.563 | 15.126 | 22.689 | 30.252 | 37.815 | 45.378 | 52.941 | 60.504 | 68.067 | 75.63 | 87.7108 | 99.7916 | 111.8724 | 123.9532 | 136.034 | 135.5498 | 135.0656 | 134.5814 | 134.0972 | 133.613 | 136.6357 | 139.6584 | 142.6811 | 145.7038 | 148.7265 | 151.7492 | 154.7719 | 157.7946 | 160.8173 | 163.84 | 165.8551 | 167.8703 | 169.8854 | 171.9005 | 173.9157 | 175.9308 | 177.9459 | 179.9611 | 181.9762 | 183.9913 | 186.0065 | 188.0216 | 190.0367 | 192.0519 | 194.067 | 195.9124 | 197.7578 | 199.6032 | 201.4486 | 203.294 | 205.1394 | 206.9848 | 208.8302 | 210.6756 | 212.521 | 214.3664 | 216.2118 | 218.0572 | 219.9026 | 221.748 | 222.3346 | 222.9211 | 223.5077 | 224.0943 | 224.6808 | 225.2674 | 225.854 | 226.4405 | 227.0271 | 227.6137 | 228.2002 | 228.7868 | 229.3734 | 229.9599 | 230.5465 | 231.1331 | 231.7196 | 232.3062 | 232.8928 | 233.4793 | 234.0659 | 234.6525 | 235.239 | 235.8256 | 236.4122 | 236.9987 | 237.5853 | 238.1719 | 238.7584 | 239.345 | 239.5963 | 239.8475 | 240.0988 | 240.3501 | 240.6013 | 240.8526 | 241.1039 | 241.3551 | 241.6064 | 241.8577 | 242.1089 | 242.3602 | 242.6115 | 242.8627 | 243.114 | 243.3653 | 243.6165 | 243.8678 | 244.1191 | 244.3703 | 244.6216 | 244.8729 | 245.1241 | 245.3754 | 245.6267 | 245.8779 | 246.1292 | 246.3805 | 246.6317 | 246.883 | 246.883 | 246.883 | 246.883 | 246.883 | 246.883 | 246.883 | 246.883 | 246.883 | 246.883 | 246.883 | 246.883 | 246.883 | 246.883 | 246.883 | 246.883 | 246.883 | 246.883 | 246.883 | 246.883 | 246.883 | 246.883 | 246.883 | 246.883 | 246.883 | 246.883 | 246.883 | 246.883 | 246.883 | 246.883 | 246.883 | 246.8805 | 246.878 | 246.8755 | 246.873 | 246.8705 | 246.868 | 246.8655 | 246.863 | 246.8605 | 246.858 | 246.8555 | 246.853 | 246.8505 | 246.848 | 246.8455 | 246.843 | 246.8405 | 246.838 | 246.8355 | 246.833 | 246.8305 | 246.828 | 246.8255 | 246.823 | 246.8205 | 246.818 | 246.8155 | 246.813 | 246.8105 | 246.808
15.9 | 0 | 7.602 | 15.204 | 22.806 | 30.408 | 38.01 | 45.612 | 53.214 | 60.816 | 68.418 | 76.02 | 88.1699 | 100.3197 | 112.4696 | 124.6195 | 136.7693 | 136.2759 | 135.7824 | 135.2889 | 134.7955 | 134.302 | 137.3411 | 140.3803 | 143.4194 | 146.4585 | 149.4977 | 152.5368 | 155.5759 | 158.6151 | 161.6542 | 164.6933 | 166.7194 | 168.7455 | 170.7716 | 172.7977 | 174.8238 | 176.8499 | 178.876 | 180.902 | 182.9281 | 184.9542 | 186.9803 | 189.0064 | 191.0325 | 193.0586 | 195.0847 | 196.9407 | 198.7968 | 200.6528 | 202.5088 | 204.3649 | 206.2209 | 208.077 | 209.933 | 211.7891 | 213.6451 | 215.5012 | 217.3572 | 219.2132 | 221.0693 | 222.9253 | 223.5155 | 224.1056 | 224.6958 | 225.286 | 225.8761 | 226.4663 | 227.0564 | 227.6466 | 228.2367 | 228.8269 | 229.417 | 230.0072 | 230.5974 | 231.1875 | 231.7777 | 232.3678 | 232.958 | 233.5481 | 234.1383 | 234.7284 | 235.3186 | 235.9088 | 236.4989 | 237.0891 | 237.6792 | 238.2694 | 238.8595 | 239.4497 | 240.0398 | 240.63 | 240.8828 | 241.1357 | 241.3885 | 241.6414 | 241.8942 | 242.1471 | 242.3999 | 242.6528 | 242.9056 | 243.1584 | 243.4113 | 243.6641 | 243.917 | 244.1698 | 244.4227 | 244.6755 | 244.9284 | 245.1812 | 245.434 | 245.6869 | 245.9397 | 246.1926 | 246.4454 | 246.6983 | 246.9511 | 247.204 | 247.4568 | 247.7096 | 247.9625 | 248.2153 | 248.2153 | 248.2153 | 248.2153 | 248.2153 | 248.2153 | 248.2153 | 248.2153 | 248.2153 | 248.2153 | 248.2153 | 248.2153 | 248.2153 | 248.2153 | 248.2153 | 248.2153 | 248.2153 | 248.2153 | 248.2153 | 248.2153 | 248.2153 | 248.2153 | 248.2153 | 248.2153 | 248.2153 | 248.2153 | 248.2153 | 248.2153 | 248.2153 | 248.2153 | 248.2153 | 248.2137 | 248.212 | 248.2103 | 248.2087 | 248.207 | 248.2053 | 248.2037 | 248.202 | 248.2003 | 248.1987 | 248.197 | 248.1953 | 248.1937 | 248.192 | 248.1903 | 248.1887 | 248.187 | 248.1853 | 248.1837 | 248.182 | 248.1803 | 248.1787 | 248.177 | 248.1753 | 248.1737 | 248.172 | 248.1703 | 248.1687 | 248.167 | 248.1653
15.95 | 0 | 7.641 | 15.282 | 22.923 | 30.564 | 38.205 | 45.846 | 53.487 | 61.128 | 68.769 | 76.41 | 88.6289 | 100.8479 | 113.0668 | 125.2857 | 137.5047 | 137.0019 | 136.4992 | 135.9965 | 135.4937 | 134.991 | 138.0466 | 141.1021 | 144.1577 | 147.2133 | 150.2688 | 153.3244 | 156.38 | 159.4355 | 162.4911 | 165.5467 | 167.5837 | 169.6208 | 171.6578 | 173.6948 | 175.7319 | 177.7689 | 179.806 | 181.843 | 183.8801 | 185.9171 | 187.9542 | 189.9912 | 192.0282 | 194.0653 | 196.1023 | 197.969 | 199.8357 | 201.7024 | 203.5691 | 205.4358 | 207.3025 | 209.1692 | 211.0358 | 212.9025 | 214.7692 | 216.6359 | 218.5026 | 220.3693 | 222.236 | 224.1027 | 224.6964 | 225.2902 | 225.8839 | 226.4776 | 227.0714 | 227.6651 | 228.2589 | 228.8526 | 229.4464 | 230.0401 | 230.6339 | 231.2276 | 231.8213 | 232.4151 | 233.0088 | 233.6026 | 234.1963 | 234.7901 | 235.3838 | 235.9776 | 236.5713 | 237.165 | 237.7588 | 238.3525 | 238.9463 | 239.54 | 240.1338 | 240.7275 | 241.3213 | 241.915 | 242.1694 | 242.4238 | 242.6783 | 242.9327 | 243.1871 | 243.4415 | 243.696 | 243.9504 | 244.2048 | 244.4592 | 244.7136 | 244.9681 | 245.2225 | 245.4769 | 245.7313 | 245.9858 | 246.2402 | 246.4946 | 246.749 | 247.0034 | 247.2579 | 247.5123 | 247.7667 | 248.0211 | 248.2756 | 248.53 | 248.7844 | 249.0388 | 249.2932 | 249.5477 | 249.5477 | 249.5477 | 249.5477 | 249.5477 | 249.5477 | 249.5477 | 249.5477 | 249.5477 | 249.5477 | 249.5477 | 249.5477 | 249.5477 | 249.5477 | 249.5477 | 249.5477 | 249.5477 | 249.5477 | 249.5477 | 249.5477 | 249.5477 | 249.5477 | 249.5477 | 249.5477 | 249.5477 | 249.5477 | 249.5477 | 249.5477 | 249.5477 | 249.5477 | 249.5477 | 249.5468 | 249.546 | 249.5452 | 249.5443 | 249.5435 | 249.5427 | 249.5418 | 249.541 | 249.5402 | 249.5393 | 249.5385 | 249.5377 | 249.5368 | 249.536 | 249.5352 | 249.5343 | 249.5335 | 249.5327 | 249.5318 | 249.531 | 249.5302 | 249.5293 | 249.5285 | 249.5277 | 249.5268 | 249.526 | 249.5252 | 249.5243 | 249.5235 | 249.5227
16 | 0 | 7.68 | 15.36 | 23.04 | 30.72 | 38.4 | 46.08 | 53.76 | 61.44 | 69.12 | 76.8 | 89.088 | 101.376 | 113.664 | 125.952 | 138.24 | 137.728 | 137.216 | 136.704 | 136.192 | 135.68 | 138.752 | 141.824 | 144.896 | 147.968 | 151.04 | 154.112 | 157.184 | 160.256 | 163.328 | 166.4 | 168.448 | 170.496 | 172.544 | 174.592 | 176.64 | 178.688 | 180.736 | 182.784 | 184.832 | 186.88 | 188.928 | 190.976 | 193.024 | 195.072 | 197.12 | 198.9973 | 200.8747 | 202.752 | 204.6293 | 206.5067 | 208.384 | 210.2613 | 212.1387 | 214.016 | 215.8933 | 217.7707 | 219.648 | 221.5253 | 223.4027 | 225.28 | 225.8773 | 226.4747 | 227.072 | 227.6693 | 228.2667 | 228.864 | 229.4613 | 230.0587 | 230.656 | 231.2533 | 231.8507 | 232.448 | 233.0453 | 233.6427 | 234.24 | 234.8373 | 235.4347 | 236.032 | 236.6293 | 237.2267 | 237.824 | 238.4213 | 239.0187 | 239.616 | 240.2133 | 240.8107 | 241.408 | 242.0053 | 242.6027 | 243.2 | 243.456 | 243.712 | 243.968 | 244.224 | 244.48 | 244.736 | 244.992 | 245.248 | 245.504 | 245.76 | 246.016 | 246.272 | 246.528 | 246.784 | 247.04 | 247.296 | 247.552 | 247.808 | 248.064 | 248.32 | 248.576 | 248.832 | 249.088 | 249.344 | 249.6 | 249.856 | 250.112 | 250.368 | 250.624 | 250.88 | 250.88 | 250.88 | 250.88 | 250.88 | 250.88 | 250.88 | 250.88 | 250.88 | 250.88 | 250.88 | 250.88 | 250.88 | 250.88 | 250.88 | 250.88 | 250.88 | 250.88 | 250.88 | 250.88 | 250.88 | 250.88 | 250.88 | 250.88 | 250.88 | 250.88 | 250.88 | 250.88 | 250.88 | 250.88 | 250.88 | 250.88 | 250.88 | 250.88 | 250.88 | 250.88 | 250.88 | 250.88 | 250.88 | 250.88 | 250.88 | 250.88 | 250.88 | 250.88 | 250.88 | 250.88 | 250.88 | 250.88 | 250.88 | 250.88 | 250.88 | 250.88 | 250.88 | 250.88 | 250.88 | 250.88 | 250.88 | 250.88 | 250.88 | 250.88 | 250.88