## Sheet1
Make-up Tank Volume Calculator
Flowrate of Cooling Tower | usgpm | 3600
| L/min | 13627.4824
| m3/h | 817.65
Evaporation loss | % of flow | 0.852
Drift loss | % of flow | 0.005
Cycle of Concentration | cycles | 6
No. of days of Storage | days | 2
Blowdown | % of flow | 0.1704
Make-up Tank Volume Required | m3 | 403.2252
Highlighted - Data to Input