## CB & Cable Size
COPPER CONDUCTOR (In Conduit or Trunking)
Commonly used Circuit Breaker Size | Commonly used Cable Sizes (mm2) |  |  |  | Type/Application | No. of Phases
| Thermoplastic PVC (60°C) | CPC | Thermosetting (90°C) | CPC
10 | 1.5 | 1.5 | 1.5 | 1.5 | Lighting | Single Phase
20 | 2.5 | 2.5 | 2.5 | 2.5 | Switched Socket Outlet/Water Heater Point | Single Phase
20 | 4 | 4 | 4 | 4 | Isolator/Air-Conditioner | Single Phase/Three Phase
30 | 6 | 6 | 6 | 6 | Isolator/Air-Conditioner | Single Phase/Three Phase
30 | 10 | 10 | 6 | 6 | Mains | Three Phase
40 | 16 | 16 | 10 | 10 | Isolator/Mains | Three Phase
60 | 25 | 16 | 16 | 16 | Isolator/Mains | Three Phase
100 | 50 | 25 | 35 | 16 | Isolator/Mains | Three Phase
150 | 95 | 50 | 70 | 35 | Isolator/Mains | Three Phase
200 | 150 | 70 | 120 | 70 | Isolator/Mains | Three Phase
250 | 240 | 95 | 185 | 95 | Isolator/Mains | Three Phase
300 | 300 | 95 | 240 | 95 | Isolator/Mains | Three Phase
400 | 400 | 120 | 300 | 95 | Isolator/Mains | Three Phase
500 | 500 | 120 | 400 | 120 | Isolator/Mains | Three Phase
600 | 630 | 120 | 500 | 120 | Isolator/Mains | Three Phase
> 600 A | Multiple Cores Cable to Manufacturer's Catalogue |  |  |  | Isolator/Mains | Three Phase
Input (Highlighted Field)
Power (kW) | 20
Voltage (V) | 400
Phase | Three Phase
Power Factor | 0.85
Current (Amps) | 33.9628
Conductor Operating Temp. (°C) | 60°C (Thermoplastic Insulation e.g. PVC)
Safety Factor (%) | 20%
Min. Breaker Size (Amps) | 40.7553
Selected Breaker Size (Amps)* | 60
Selected Cable Size** | 25
CPC | 16
Selected Cable*** | 4 x 1C 25 mm2 PVC/PVC Cable + 16 mm2 CPC
* Values greater than 600 A is not shown in this Calculator
** Cables of a specific size can be protected with various Circuit Breaker Sizes, for example, 30 Amps Breaker can be used to protect both 10mm2 Cable (From MSB to DB) or 6mm2 Cable (For Isolator/AC)
*** Different Configurations of Cable may be applicable