## Sheet1
Airchange (ACH) to Airflow (CFM) Calculator
Room Width (m) | 10
Room Length (m) | 10
Room Height (m) | 5
Room Volume (m3) | 500
Room Air Change (ACH) | 10
Air volume flow, CFM | 2943
Air volume flow, m3/h | 5000
Recommended ACH based on Types of Areas
Building / Room | Recommended ACH
Common Areas/Corridors/Hallways | 6-10
Assembly Halls | 6-10
Attic Spaces for Cooling | 12-15
Auditoriums | 10-15
Bathrooms | 6-8
Bakeries | 20-30
Banks | 6-10
Barber Shops | 6-10
Bars | 20-30
Beauty Shops | 6-10
Bedrooms | 6
Boiler Rooms | 15-20
Bowling Alleys | 10-15
Cafeterias | 12-15
Churches | 8-15
Classrooms | 6-10
Club Rooms | 12-15
Clubhouses | 20-30
Cocktail Lounges | 20-30
Computer/Photocopier Rooms | 10-15
Court Houses | 6-10
Dance Halls | 6-10
Dental Centers | 8-12
Department Stores | 6-10
Dining Halls | 8-15
Dining Rooms (Restaurants) | 12
Dress Shops | 6-10
Drug Shops | 6-10
Engine Rooms | 4-6
Factory Buildings, Ordinary | 2-4
Factory Buildings, with Fumes or Moisture | 10-15
Fire Stations | 4-10
Foundries | 15-20
Galvanizing Plants | 20-30
Garages Repair | 20-30
Garages Storage | 6
Homes, Night Cooling | 10-18
Hospital Rooms | 6-10
Hospital Isolation rooms | 15-20
Jewelry shops | 6-10
Kitchens (General) | 15-60
Commercial Kitchens | 25
Private Kitchens | 20
Living Room | 6-8
Launderettes | 18
Laundries | 10-15
Libraries, public | 6-10
Lunch Rooms | 12-15
Luncheonettes | 12-15
Nightclubs | 20-30
Machine shops | 6-12
Malls | 6-10
Medical Centers | 8-12
Medical Clinics | 8-12
Medical Procedures/Offices | 8-12
Mills, Paper | 15-20
Mills, Textile General Buildings | 6
Mills, Textile Dye Houses | 15-20
Municipal Buildings | 6-10
Museums | 12-15
Offices, Public | 6-8
Offices, Private | 6-8
Paint Shops | 10-15
Paper Mills | 15-20
Photo Dark Rooms | 10-15
Pig Houses | 6-10
Police Stations | 6-10
Post Offices | 6-10
Poultry Houses | 6-10
Precision Manufacturing | 10-50
Pump Rooms | 6
Residences | 1-2
Restaurants | 8-12
Retail | 6-10
School Classrooms | 6-12
Shoe Shops | 6-10
Shopping Centers | 6-10
Shops, Machine | 6
Shops, Paint | 15-20
Shops, Woodworking | 6
Smoking Area | 15-20
Substation, Electric | 5-10
Supermarkets | 6-10
Swimming Pools | 20-30
Textile Mills | 6
Textile Mills Dye Houses | 15-20
Town Halls | 6-10
Taverns | 20-30
Theaters | 8-15
Transformer Rooms | 10-30
Turbine rooms, Electric | 6-10
Warehouses | 6
Waiting rooms, Public | 6
Warehouses | 6-30
Wood-working Shops | 8
Smoke Spill System | 10
Smoke Spill Fresh Air Make-Up | 5-7
Toilets | 6-12
Showers | 6-12
Offices | 6-10
Restaurants | 12
Canteens | 12
Classrooms | 6
Conference Facilities | 8-12
Multi-purpose Halls | 6-10
Gyms | 6-10
Waiting Rooms | 6
Hotel Rooms | 6-10
Public Garages | 6
Swimming Pools (Private) | 6-10
Workshops | 10