## Sheet1
SR4-2 Transition, Pyramidal, Supply Air Systems
Transition Length, L |  | 500 | mm
Incoming (Pre-Transition)
Duct Width |  | 600 | mm
Duct Height |  | 550 | mm
Air Flow (CFM) |  | 4083
Duct Velocity (FPM) |  | 1149.8817
VP |  | 0.082433
Outgoing (Post-Transition)
Duct Width |  | 550 | mm
Duct Height |  | 500 | mm
Air Flow (CFM) |  | 4083
Duct Velocity (FPM) |  | 1379.8581
VP |  | 0.1187
θ1 (Side) |  | 5.7241 | °
θ2 (Top) |  | 5.7241 | °
A1/A |  | 1.2
θ (Max) |  | 5.7241 | °
C |  | 0.38352
Frictional Loss |  | 0.045525 | " WG
Table 14-12A Coefficient C (See Note 7)
A0 /A1 |  | θ
| 0 | 10 | 15 | 20 | 30 | 45 | 60 | 90 | 120 | 150 | 180 | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 41 | 42 | 43 | 44 | 45 | 46 | 47 | 48 | 49 | 50 | 51 | 52 | 53 | 54 | 55 | 56 | 57 | 58 | 59 | 60 | 61 | 62 | 63 | 64 | 65 | 66 | 67 | 68 | 69 | 70 | 71 | 72 | 73 | 74 | 75 | 76 | 77 | 78 | 79 | 80 | 81 | 82 | 83 | 84 | 85 | 86 | 87 | 88 | 89 | 90 | 91 | 92 | 93 | 94 | 95 | 96 | 97 | 98 | 99 | 100 | 101 | 102 | 103 | 104 | 105 | 106 | 107 | 108 | 109 | 110 | 111 | 112 | 113 | 114 | 115 | 116 | 117 | 118 | 119 | 120 | 121 | 122 | 123 | 124 | 125 | 126 | 127 | 128 | 129 | 130 | 131 | 132 | 133 | 134 | 135 | 136 | 137 | 138 | 139 | 140 | 141 | 142 | 143 | 144 | 145 | 146 | 147 | 148 | 149 | 150 | 151 | 152 | 153 | 154 | 155 | 156 | 157 | 158 | 159 | 160 | 161 | 162 | 163 | 164 | 165 | 166 | 167 | 168 | 169 | 170 | 171 | 172 | 173 | 174 | 175 | 176 | 177 | 178 | 179 | 180
0.06 | 0 | 0.3 | 0.54 | 0.53 | 0.65 | 0.77 | 0.88 | 0.95 | 0.98 | 0.98 | 0.93
0.1 | 0 | 0.3 | 0.5 | 0.53 | 0.64 | 0.75 | 0.84 | 0.89 | 0.91 | 0.91 | 0.88
0.25 | 0 | 0.25 | 0.36 | 0.45 | 0.52 | 0.58 | 0.62 | 0.64 | 0.64 | 0.64 | 0.64
0.5 | 0 | 0.15 | 0.21 | 0.25 | 0.3 | 0.33 | 0.33 | 0.33 | 0.32 | 0.31 | 0.3
1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 0 | 0.24 | 0.28 | 0.26 | 0.2 | 0.22 | 0.24 | 0.49 | 0.73 | 0.97 | 1.04
4 | 0 | 0.89 | 0.78 | 0.79 | 0.7 | 0.88 | 1.12 | 2.72 | 4.33 | 5.62 | 6.58
6 | 0 | 1.89 | 1.67 | 1.59 | 1.49 | 1.98 | 2.52 | 6.51 | 10.14 | 13.05 | 15.14
10 | 0 | 5.09 | 5.32 | 5.15 | 5.05 | 6.5 | 8.05 | 19.06 | 29.07 | 37.08 | 43.05
0.06 | 0 | 0.3 | 0.54 | 0.53 | 0.65 | 0.77 | 0.88 | 0.95 | 0.98 | 0.98 | 0.93 | 0 | 0.03 | 0.06 | 0.09 | 0.12 | 0.15 | 0.18 | 0.21 | 0.24 | 0.27 | 0.3 | 0.348 | 0.396 | 0.444 | 0.492 | 0.54 | 0.538 | 0.536 | 0.534 | 0.532 | 0.53 | 0.542 | 0.554 | 0.566 | 0.578 | 0.59 | 0.602 | 0.614 | 0.626 | 0.638 | 0.65 | 0.658 | 0.666 | 0.674 | 0.682 | 0.69 | 0.698 | 0.706 | 0.714 | 0.722 | 0.73 | 0.738 | 0.746 | 0.754 | 0.762 | 0.77 | 0.77733 | 0.78467 | 0.792 | 0.79933 | 0.80667 | 0.814 | 0.82133 | 0.82867 | 0.836 | 0.84333 | 0.85067 | 0.858 | 0.86533 | 0.87267 | 0.88 | 0.88233 | 0.88467 | 0.887 | 0.88933 | 0.89167 | 0.894 | 0.89633 | 0.89867 | 0.901 | 0.90333 | 0.90567 | 0.908 | 0.91033 | 0.91267 | 0.915 | 0.91733 | 0.91967 | 0.922 | 0.92433 | 0.92667 | 0.929 | 0.93133 | 0.93367 | 0.936 | 0.93833 | 0.94067 | 0.943 | 0.94533 | 0.94767 | 0.95 | 0.951 | 0.952 | 0.953 | 0.954 | 0.955 | 0.956 | 0.957 | 0.958 | 0.959 | 0.96 | 0.961 | 0.962 | 0.963 | 0.964 | 0.965 | 0.966 | 0.967 | 0.968 | 0.969 | 0.97 | 0.971 | 0.972 | 0.973 | 0.974 | 0.975 | 0.976 | 0.977 | 0.978 | 0.979 | 0.98 | 0.98 | 0.98 | 0.98 | 0.98 | 0.98 | 0.98 | 0.98 | 0.98 | 0.98 | 0.98 | 0.98 | 0.98 | 0.98 | 0.98 | 0.98 | 0.98 | 0.98 | 0.98 | 0.98 | 0.98 | 0.98 | 0.98 | 0.98 | 0.98 | 0.98 | 0.98 | 0.98 | 0.98 | 0.98 | 0.98 | 0.97833 | 0.97667 | 0.975 | 0.97333 | 0.97167 | 0.97 | 0.96833 | 0.96667 | 0.965 | 0.96333 | 0.96167 | 0.96 | 0.95833 | 0.95667 | 0.955 | 0.95333 | 0.95167 | 0.95 | 0.94833 | 0.94667 | 0.945 | 0.94333 | 0.94167 | 0.94 | 0.93833 | 0.93667 | 0.935 | 0.93333 | 0.93167 | 0.93
0.1 | 0 | 0.3 | 0.5 | 0.53 | 0.64 | 0.75 | 0.84 | 0.89 | 0.91 | 0.91 | 0.88 | 0 | 0.03 | 0.06 | 0.09 | 0.12 | 0.15 | 0.18 | 0.21 | 0.24 | 0.27 | 0.3 | 0.34 | 0.38 | 0.42 | 0.46 | 0.5 | 0.506 | 0.512 | 0.518 | 0.524 | 0.53 | 0.541 | 0.552 | 0.563 | 0.574 | 0.585 | 0.596 | 0.607 | 0.618 | 0.629 | 0.64 | 0.64733 | 0.65467 | 0.662 | 0.66933 | 0.67667 | 0.684 | 0.69133 | 0.69867 | 0.706 | 0.71333 | 0.72067 | 0.728 | 0.73533 | 0.74267 | 0.75 | 0.756 | 0.762 | 0.768 | 0.774 | 0.78 | 0.786 | 0.792 | 0.798 | 0.804 | 0.81 | 0.816 | 0.822 | 0.828 | 0.834 | 0.84 | 0.84167 | 0.84333 | 0.845 | 0.84667 | 0.84833 | 0.85 | 0.85167 | 0.85333 | 0.855 | 0.85667 | 0.85833 | 0.86 | 0.86167 | 0.86333 | 0.865 | 0.86667 | 0.86833 | 0.87 | 0.87167 | 0.87333 | 0.875 | 0.87667 | 0.87833 | 0.88 | 0.88167 | 0.88333 | 0.885 | 0.88667 | 0.88833 | 0.89 | 0.89067 | 0.89133 | 0.892 | 0.89267 | 0.89333 | 0.894 | 0.89467 | 0.89533 | 0.896 | 0.89667 | 0.89733 | 0.898 | 0.89867 | 0.89933 | 0.9 | 0.90067 | 0.90133 | 0.902 | 0.90267 | 0.90333 | 0.904 | 0.90467 | 0.90533 | 0.906 | 0.90667 | 0.90733 | 0.908 | 0.90867 | 0.90933 | 0.91 | 0.91 | 0.91 | 0.91 | 0.91 | 0.91 | 0.91 | 0.91 | 0.91 | 0.91 | 0.91 | 0.91 | 0.91 | 0.91 | 0.91 | 0.91 | 0.91 | 0.91 | 0.91 | 0.91 | 0.91 | 0.91 | 0.91 | 0.91 | 0.91 | 0.91 | 0.91 | 0.91 | 0.91 | 0.91 | 0.91 | 0.909 | 0.908 | 0.907 | 0.906 | 0.905 | 0.904 | 0.903 | 0.902 | 0.901 | 0.9 | 0.899 | 0.898 | 0.897 | 0.896 | 0.895 | 0.894 | 0.893 | 0.892 | 0.891 | 0.89 | 0.889 | 0.888 | 0.887 | 0.886 | 0.885 | 0.884 | 0.883 | 0.882 | 0.881 | 0.88
0.15 | 0 | 0.28333 | 0.45333 | 0.50333 | 0.6 | 0.69333 | 0.76667 | 0.80667 | 0.82 | 0.82 | 0.8 | 0 | 0.028333 | 0.056667 | 0.085 | 0.11333 | 0.14167 | 0.17 | 0.19833 | 0.22667 | 0.255 | 0.28333 | 0.31733 | 0.35133 | 0.38533 | 0.41933 | 0.45333 | 0.46333 | 0.47333 | 0.48333 | 0.49333 | 0.50333 | 0.513 | 0.52267 | 0.53233 | 0.542 | 0.55167 | 0.56133 | 0.571 | 0.58067 | 0.59033 | 0.6 | 0.60622 | 0.61244 | 0.61867 | 0.62489 | 0.63111 | 0.63733 | 0.64356 | 0.64978 | 0.656 | 0.66222 | 0.66844 | 0.67467 | 0.68089 | 0.68711 | 0.69333 | 0.69822 | 0.70311 | 0.708 | 0.71289 | 0.71778 | 0.72267 | 0.72756 | 0.73244 | 0.73733 | 0.74222 | 0.74711 | 0.752 | 0.75689 | 0.76178 | 0.76667 | 0.768 | 0.76933 | 0.77067 | 0.772 | 0.77333 | 0.77467 | 0.776 | 0.77733 | 0.77867 | 0.78 | 0.78133 | 0.78267 | 0.784 | 0.78533 | 0.78667 | 0.788 | 0.78933 | 0.79067 | 0.792 | 0.79333 | 0.79467 | 0.796 | 0.79733 | 0.79867 | 0.8 | 0.80133 | 0.80267 | 0.804 | 0.80533 | 0.80667 | 0.80711 | 0.80756 | 0.808 | 0.80844 | 0.80889 | 0.80933 | 0.80978 | 0.81022 | 0.81067 | 0.81111 | 0.81156 | 0.812 | 0.81244 | 0.81289 | 0.81333 | 0.81378 | 0.81422 | 0.81467 | 0.81511 | 0.81556 | 0.816 | 0.81644 | 0.81689 | 0.81733 | 0.81778 | 0.81822 | 0.81867 | 0.81911 | 0.81956 | 0.82 | 0.82 | 0.82 | 0.82 | 0.82 | 0.82 | 0.82 | 0.82 | 0.82 | 0.82 | 0.82 | 0.82 | 0.82 | 0.82 | 0.82 | 0.82 | 0.82 | 0.82 | 0.82 | 0.82 | 0.82 | 0.82 | 0.82 | 0.82 | 0.82 | 0.82 | 0.82 | 0.82 | 0.82 | 0.82 | 0.82 | 0.81933 | 0.81867 | 0.818 | 0.81733 | 0.81667 | 0.816 | 0.81533 | 0.81467 | 0.814 | 0.81333 | 0.81267 | 0.812 | 0.81133 | 0.81067 | 0.81 | 0.80933 | 0.80867 | 0.808 | 0.80733 | 0.80667 | 0.806 | 0.80533 | 0.80467 | 0.804 | 0.80333 | 0.80267 | 0.802 | 0.80133 | 0.80067 | 0.8
0.17 | 0 | 0.27667 | 0.43467 | 0.49267 | 0.584 | 0.67067 | 0.73733 | 0.77333 | 0.784 | 0.784 | 0.768 | 0 | 0.027667 | 0.055333 | 0.083 | 0.11067 | 0.13833 | 0.166 | 0.19367 | 0.22133 | 0.249 | 0.27667 | 0.30827 | 0.33987 | 0.37147 | 0.40307 | 0.43467 | 0.44627 | 0.45787 | 0.46947 | 0.48107 | 0.49267 | 0.5018 | 0.51093 | 0.52007 | 0.5292 | 0.53833 | 0.54747 | 0.5566 | 0.56573 | 0.57487 | 0.584 | 0.58978 | 0.59556 | 0.60133 | 0.60711 | 0.61289 | 0.61867 | 0.62444 | 0.63022 | 0.636 | 0.64178 | 0.64756 | 0.65333 | 0.65911 | 0.66489 | 0.67067 | 0.67511 | 0.67956 | 0.684 | 0.68844 | 0.69289 | 0.69733 | 0.70178 | 0.70622 | 0.71067 | 0.71511 | 0.71956 | 0.724 | 0.72844 | 0.73289 | 0.73733 | 0.73853 | 0.73973 | 0.74093 | 0.74213 | 0.74333 | 0.74453 | 0.74573 | 0.74693 | 0.74813 | 0.74933 | 0.75053 | 0.75173 | 0.75293 | 0.75413 | 0.75533 | 0.75653 | 0.75773 | 0.75893 | 0.76013 | 0.76133 | 0.76253 | 0.76373 | 0.76493 | 0.76613 | 0.76733 | 0.76853 | 0.76973 | 0.77093 | 0.77213 | 0.77333 | 0.77369 | 0.77404 | 0.7744 | 0.77476 | 0.77511 | 0.77547 | 0.77582 | 0.77618 | 0.77653 | 0.77689 | 0.77724 | 0.7776 | 0.77796 | 0.77831 | 0.77867 | 0.77902 | 0.77938 | 0.77973 | 0.78009 | 0.78044 | 0.7808 | 0.78116 | 0.78151 | 0.78187 | 0.78222 | 0.78258 | 0.78293 | 0.78329 | 0.78364 | 0.784 | 0.784 | 0.784 | 0.784 | 0.784 | 0.784 | 0.784 | 0.784 | 0.784 | 0.784 | 0.784 | 0.784 | 0.784 | 0.784 | 0.784 | 0.784 | 0.784 | 0.784 | 0.784 | 0.784 | 0.784 | 0.784 | 0.784 | 0.784 | 0.784 | 0.784 | 0.784 | 0.784 | 0.784 | 0.784 | 0.784 | 0.78347 | 0.78293 | 0.7824 | 0.78187 | 0.78133 | 0.7808 | 0.78027 | 0.77973 | 0.7792 | 0.77867 | 0.77813 | 0.7776 | 0.77707 | 0.77653 | 0.776 | 0.77547 | 0.77493 | 0.7744 | 0.77387 | 0.77333 | 0.7728 | 0.77227 | 0.77173 | 0.7712 | 0.77067 | 0.77013 | 0.7696 | 0.76907 | 0.76853 | 0.768
0.2 | 0 | 0.26667 | 0.40667 | 0.47667 | 0.56 | 0.63667 | 0.69333 | 0.72333 | 0.73 | 0.73 | 0.72 | 0 | 0.026667 | 0.053333 | 0.08 | 0.10667 | 0.13333 | 0.16 | 0.18667 | 0.21333 | 0.24 | 0.26667 | 0.29467 | 0.32267 | 0.35067 | 0.37867 | 0.40667 | 0.42067 | 0.43467 | 0.44867 | 0.46267 | 0.47667 | 0.485 | 0.49333 | 0.50167 | 0.51 | 0.51833 | 0.52667 | 0.535 | 0.54333 | 0.55167 | 0.56 | 0.56511 | 0.57022 | 0.57533 | 0.58044 | 0.58556 | 0.59067 | 0.59578 | 0.60089 | 0.606 | 0.61111 | 0.61622 | 0.62133 | 0.62644 | 0.63156 | 0.63667 | 0.64044 | 0.64422 | 0.648 | 0.65178 | 0.65556 | 0.65933 | 0.66311 | 0.66689 | 0.67067 | 0.67444 | 0.67822 | 0.682 | 0.68578 | 0.68956 | 0.69333 | 0.69433 | 0.69533 | 0.69633 | 0.69733 | 0.69833 | 0.69933 | 0.70033 | 0.70133 | 0.70233 | 0.70333 | 0.70433 | 0.70533 | 0.70633 | 0.70733 | 0.70833 | 0.70933 | 0.71033 | 0.71133 | 0.71233 | 0.71333 | 0.71433 | 0.71533 | 0.71633 | 0.71733 | 0.71833 | 0.71933 | 0.72033 | 0.72133 | 0.72233 | 0.72333 | 0.72356 | 0.72378 | 0.724 | 0.72422 | 0.72444 | 0.72467 | 0.72489 | 0.72511 | 0.72533 | 0.72556 | 0.72578 | 0.726 | 0.72622 | 0.72644 | 0.72667 | 0.72689 | 0.72711 | 0.72733 | 0.72756 | 0.72778 | 0.728 | 0.72822 | 0.72844 | 0.72867 | 0.72889 | 0.72911 | 0.72933 | 0.72956 | 0.72978 | 0.73 | 0.73 | 0.73 | 0.73 | 0.73 | 0.73 | 0.73 | 0.73 | 0.73 | 0.73 | 0.73 | 0.73 | 0.73 | 0.73 | 0.73 | 0.73 | 0.73 | 0.73 | 0.73 | 0.73 | 0.73 | 0.73 | 0.73 | 0.73 | 0.73 | 0.73 | 0.73 | 0.73 | 0.73 | 0.73 | 0.73 | 0.72967 | 0.72933 | 0.729 | 0.72867 | 0.72833 | 0.728 | 0.72767 | 0.72733 | 0.727 | 0.72667 | 0.72633 | 0.726 | 0.72567 | 0.72533 | 0.725 | 0.72467 | 0.72433 | 0.724 | 0.72367 | 0.72333 | 0.723 | 0.72267 | 0.72233 | 0.722 | 0.72167 | 0.72133 | 0.721 | 0.72067 | 0.72033 | 0.72
0.25 | 0 | 0.25 | 0.36 | 0.45 | 0.52 | 0.58 | 0.62 | 0.64 | 0.64 | 0.64 | 0.64 | 0 | 0.025 | 0.05 | 0.075 | 0.1 | 0.125 | 0.15 | 0.175 | 0.2 | 0.225 | 0.25 | 0.272 | 0.294 | 0.316 | 0.338 | 0.36 | 0.378 | 0.396 | 0.414 | 0.432 | 0.45 | 0.457 | 0.464 | 0.471 | 0.478 | 0.485 | 0.492 | 0.499 | 0.506 | 0.513 | 0.52 | 0.524 | 0.528 | 0.532 | 0.536 | 0.54 | 0.544 | 0.548 | 0.552 | 0.556 | 0.56 | 0.564 | 0.568 | 0.572 | 0.576 | 0.58 | 0.58267 | 0.58533 | 0.588 | 0.59067 | 0.59333 | 0.596 | 0.59867 | 0.60133 | 0.604 | 0.60667 | 0.60933 | 0.612 | 0.61467 | 0.61733 | 0.62 | 0.62067 | 0.62133 | 0.622 | 0.62267 | 0.62333 | 0.624 | 0.62467 | 0.62533 | 0.626 | 0.62667 | 0.62733 | 0.628 | 0.62867 | 0.62933 | 0.63 | 0.63067 | 0.63133 | 0.632 | 0.63267 | 0.63333 | 0.634 | 0.63467 | 0.63533 | 0.636 | 0.63667 | 0.63733 | 0.638 | 0.63867 | 0.63933 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64
0.3 | 0 | 0.23 | 0.33 | 0.41 | 0.476 | 0.53 | 0.562 | 0.578 | 0.576 | 0.574 | 0.572 | 0 | 0.023 | 0.046 | 0.069 | 0.092 | 0.115 | 0.138 | 0.161 | 0.184 | 0.207 | 0.23 | 0.25 | 0.27 | 0.29 | 0.31 | 0.33 | 0.346 | 0.362 | 0.378 | 0.394 | 0.41 | 0.4166 | 0.4232 | 0.4298 | 0.4364 | 0.443 | 0.4496 | 0.4562 | 0.4628 | 0.4694 | 0.476 | 0.4796 | 0.4832 | 0.4868 | 0.4904 | 0.494 | 0.4976 | 0.5012 | 0.5048 | 0.5084 | 0.512 | 0.5156 | 0.5192 | 0.5228 | 0.5264 | 0.53 | 0.53213 | 0.53427 | 0.5364 | 0.53853 | 0.54067 | 0.5428 | 0.54493 | 0.54707 | 0.5492 | 0.55133 | 0.55347 | 0.5556 | 0.55773 | 0.55987 | 0.562 | 0.56253 | 0.56307 | 0.5636 | 0.56413 | 0.56467 | 0.5652 | 0.56573 | 0.56627 | 0.5668 | 0.56733 | 0.56787 | 0.5684 | 0.56893 | 0.56947 | 0.57 | 0.57053 | 0.57107 | 0.5716 | 0.57213 | 0.57267 | 0.5732 | 0.57373 | 0.57427 | 0.5748 | 0.57533 | 0.57587 | 0.5764 | 0.57693 | 0.57747 | 0.578 | 0.57793 | 0.57787 | 0.5778 | 0.57773 | 0.57767 | 0.5776 | 0.57753 | 0.57747 | 0.5774 | 0.57733 | 0.57727 | 0.5772 | 0.57713 | 0.57707 | 0.577 | 0.57693 | 0.57687 | 0.5768 | 0.57673 | 0.57667 | 0.5766 | 0.57653 | 0.57647 | 0.5764 | 0.57633 | 0.57627 | 0.5762 | 0.57613 | 0.57607 | 0.576 | 0.57593 | 0.57587 | 0.5758 | 0.57573 | 0.57567 | 0.5756 | 0.57553 | 0.57547 | 0.5754 | 0.57533 | 0.57527 | 0.5752 | 0.57513 | 0.57507 | 0.575 | 0.57493 | 0.57487 | 0.5748 | 0.57473 | 0.57467 | 0.5746 | 0.57453 | 0.57447 | 0.5744 | 0.57433 | 0.57427 | 0.5742 | 0.57413 | 0.57407 | 0.574 | 0.57393 | 0.57387 | 0.5738 | 0.57373 | 0.57367 | 0.5736 | 0.57353 | 0.57347 | 0.5734 | 0.57333 | 0.57327 | 0.5732 | 0.57313 | 0.57307 | 0.573 | 0.57293 | 0.57287 | 0.5728 | 0.57273 | 0.57267 | 0.5726 | 0.57253 | 0.57247 | 0.5724 | 0.57233 | 0.57227 | 0.5722 | 0.57213 | 0.57207 | 0.572
0.35 | 0 | 0.21 | 0.3 | 0.37 | 0.432 | 0.48 | 0.504 | 0.516 | 0.512 | 0.508 | 0.504 | 0 | 0.021 | 0.042 | 0.063 | 0.084 | 0.105 | 0.126 | 0.147 | 0.168 | 0.189 | 0.21 | 0.228 | 0.246 | 0.264 | 0.282 | 0.3 | 0.314 | 0.328 | 0.342 | 0.356 | 0.37 | 0.3762 | 0.3824 | 0.3886 | 0.3948 | 0.401 | 0.4072 | 0.4134 | 0.4196 | 0.4258 | 0.432 | 0.4352 | 0.4384 | 0.4416 | 0.4448 | 0.448 | 0.4512 | 0.4544 | 0.4576 | 0.4608 | 0.464 | 0.4672 | 0.4704 | 0.4736 | 0.4768 | 0.48 | 0.4816 | 0.4832 | 0.4848 | 0.4864 | 0.488 | 0.4896 | 0.4912 | 0.4928 | 0.4944 | 0.496 | 0.4976 | 0.4992 | 0.5008 | 0.5024 | 0.504 | 0.5044 | 0.5048 | 0.5052 | 0.5056 | 0.506 | 0.5064 | 0.5068 | 0.5072 | 0.5076 | 0.508 | 0.5084 | 0.5088 | 0.5092 | 0.5096 | 0.51 | 0.5104 | 0.5108 | 0.5112 | 0.5116 | 0.512 | 0.5124 | 0.5128 | 0.5132 | 0.5136 | 0.514 | 0.5144 | 0.5148 | 0.5152 | 0.5156 | 0.516 | 0.51587 | 0.51573 | 0.5156 | 0.51547 | 0.51533 | 0.5152 | 0.51507 | 0.51493 | 0.5148 | 0.51467 | 0.51453 | 0.5144 | 0.51427 | 0.51413 | 0.514 | 0.51387 | 0.51373 | 0.5136 | 0.51347 | 0.51333 | 0.5132 | 0.51307 | 0.51293 | 0.5128 | 0.51267 | 0.51253 | 0.5124 | 0.51227 | 0.51213 | 0.512 | 0.51187 | 0.51173 | 0.5116 | 0.51147 | 0.51133 | 0.5112 | 0.51107 | 0.51093 | 0.5108 | 0.51067 | 0.51053 | 0.5104 | 0.51027 | 0.51013 | 0.51 | 0.50987 | 0.50973 | 0.5096 | 0.50947 | 0.50933 | 0.5092 | 0.50907 | 0.50893 | 0.5088 | 0.50867 | 0.50853 | 0.5084 | 0.50827 | 0.50813 | 0.508 | 0.50787 | 0.50773 | 0.5076 | 0.50747 | 0.50733 | 0.5072 | 0.50707 | 0.50693 | 0.5068 | 0.50667 | 0.50653 | 0.5064 | 0.50627 | 0.50613 | 0.506 | 0.50587 | 0.50573 | 0.5056 | 0.50547 | 0.50533 | 0.5052 | 0.50507 | 0.50493 | 0.5048 | 0.50467 | 0.50453 | 0.5044 | 0.50427 | 0.50413 | 0.504
0.4 | 0 | 0.19 | 0.27 | 0.33 | 0.388 | 0.43 | 0.446 | 0.454 | 0.448 | 0.442 | 0.436 | 0 | 0.019 | 0.038 | 0.057 | 0.076 | 0.095 | 0.114 | 0.133 | 0.152 | 0.171 | 0.19 | 0.206 | 0.222 | 0.238 | 0.254 | 0.27 | 0.282 | 0.294 | 0.306 | 0.318 | 0.33 | 0.3358 | 0.3416 | 0.3474 | 0.3532 | 0.359 | 0.3648 | 0.3706 | 0.3764 | 0.3822 | 0.388 | 0.3908 | 0.3936 | 0.3964 | 0.3992 | 0.402 | 0.4048 | 0.4076 | 0.4104 | 0.4132 | 0.416 | 0.4188 | 0.4216 | 0.4244 | 0.4272 | 0.43 | 0.43107 | 0.43213 | 0.4332 | 0.43427 | 0.43533 | 0.4364 | 0.43747 | 0.43853 | 0.4396 | 0.44067 | 0.44173 | 0.4428 | 0.44387 | 0.44493 | 0.446 | 0.44627 | 0.44653 | 0.4468 | 0.44707 | 0.44733 | 0.4476 | 0.44787 | 0.44813 | 0.4484 | 0.44867 | 0.44893 | 0.4492 | 0.44947 | 0.44973 | 0.45 | 0.45027 | 0.45053 | 0.4508 | 0.45107 | 0.45133 | 0.4516 | 0.45187 | 0.45213 | 0.4524 | 0.45267 | 0.45293 | 0.4532 | 0.45347 | 0.45373 | 0.454 | 0.4538 | 0.4536 | 0.4534 | 0.4532 | 0.453 | 0.4528 | 0.4526 | 0.4524 | 0.4522 | 0.452 | 0.4518 | 0.4516 | 0.4514 | 0.4512 | 0.451 | 0.4508 | 0.4506 | 0.4504 | 0.4502 | 0.45 | 0.4498 | 0.4496 | 0.4494 | 0.4492 | 0.449 | 0.4488 | 0.4486 | 0.4484 | 0.4482 | 0.448 | 0.4478 | 0.4476 | 0.4474 | 0.4472 | 0.447 | 0.4468 | 0.4466 | 0.4464 | 0.4462 | 0.446 | 0.4458 | 0.4456 | 0.4454 | 0.4452 | 0.445 | 0.4448 | 0.4446 | 0.4444 | 0.4442 | 0.444 | 0.4438 | 0.4436 | 0.4434 | 0.4432 | 0.443 | 0.4428 | 0.4426 | 0.4424 | 0.4422 | 0.442 | 0.4418 | 0.4416 | 0.4414 | 0.4412 | 0.441 | 0.4408 | 0.4406 | 0.4404 | 0.4402 | 0.44 | 0.4398 | 0.4396 | 0.4394 | 0.4392 | 0.439 | 0.4388 | 0.4386 | 0.4384 | 0.4382 | 0.438 | 0.4378 | 0.4376 | 0.4374 | 0.4372 | 0.437 | 0.4368 | 0.4366 | 0.4364 | 0.4362 | 0.436
0.45 | 0 | 0.17 | 0.24 | 0.29 | 0.344 | 0.38 | 0.388 | 0.392 | 0.384 | 0.376 | 0.368 | 0 | 0.017 | 0.034 | 0.051 | 0.068 | 0.085 | 0.102 | 0.119 | 0.136 | 0.153 | 0.17 | 0.184 | 0.198 | 0.212 | 0.226 | 0.24 | 0.25 | 0.26 | 0.27 | 0.28 | 0.29 | 0.2954 | 0.3008 | 0.3062 | 0.3116 | 0.317 | 0.3224 | 0.3278 | 0.3332 | 0.3386 | 0.344 | 0.3464 | 0.3488 | 0.3512 | 0.3536 | 0.356 | 0.3584 | 0.3608 | 0.3632 | 0.3656 | 0.368 | 0.3704 | 0.3728 | 0.3752 | 0.3776 | 0.38 | 0.38053 | 0.38107 | 0.3816 | 0.38213 | 0.38267 | 0.3832 | 0.38373 | 0.38427 | 0.3848 | 0.38533 | 0.38587 | 0.3864 | 0.38693 | 0.38747 | 0.388 | 0.38813 | 0.38827 | 0.3884 | 0.38853 | 0.38867 | 0.3888 | 0.38893 | 0.38907 | 0.3892 | 0.38933 | 0.38947 | 0.3896 | 0.38973 | 0.38987 | 0.39 | 0.39013 | 0.39027 | 0.3904 | 0.39053 | 0.39067 | 0.3908 | 0.39093 | 0.39107 | 0.3912 | 0.39133 | 0.39147 | 0.3916 | 0.39173 | 0.39187 | 0.392 | 0.39173 | 0.39147 | 0.3912 | 0.39093 | 0.39067 | 0.3904 | 0.39013 | 0.38987 | 0.3896 | 0.38933 | 0.38907 | 0.3888 | 0.38853 | 0.38827 | 0.388 | 0.38773 | 0.38747 | 0.3872 | 0.38693 | 0.38667 | 0.3864 | 0.38613 | 0.38587 | 0.3856 | 0.38533 | 0.38507 | 0.3848 | 0.38453 | 0.38427 | 0.384 | 0.38373 | 0.38347 | 0.3832 | 0.38293 | 0.38267 | 0.3824 | 0.38213 | 0.38187 | 0.3816 | 0.38133 | 0.38107 | 0.3808 | 0.38053 | 0.38027 | 0.38 | 0.37973 | 0.37947 | 0.3792 | 0.37893 | 0.37867 | 0.3784 | 0.37813 | 0.37787 | 0.3776 | 0.37733 | 0.37707 | 0.3768 | 0.37653 | 0.37627 | 0.376 | 0.37573 | 0.37547 | 0.3752 | 0.37493 | 0.37467 | 0.3744 | 0.37413 | 0.37387 | 0.3736 | 0.37333 | 0.37307 | 0.3728 | 0.37253 | 0.37227 | 0.372 | 0.37173 | 0.37147 | 0.3712 | 0.37093 | 0.37067 | 0.3704 | 0.37013 | 0.36987 | 0.3696 | 0.36933 | 0.36907 | 0.3688 | 0.36853 | 0.36827 | 0.368
0.5 | 0 | 0.15 | 0.21 | 0.25 | 0.3 | 0.33 | 0.33 | 0.33 | 0.32 | 0.31 | 0.3 | 0 | 0.015 | 0.03 | 0.045 | 0.06 | 0.075 | 0.09 | 0.105 | 0.12 | 0.135 | 0.15 | 0.162 | 0.174 | 0.186 | 0.198 | 0.21 | 0.218 | 0.226 | 0.234 | 0.242 | 0.25 | 0.255 | 0.26 | 0.265 | 0.27 | 0.275 | 0.28 | 0.285 | 0.29 | 0.295 | 0.3 | 0.302 | 0.304 | 0.306 | 0.308 | 0.31 | 0.312 | 0.314 | 0.316 | 0.318 | 0.32 | 0.322 | 0.324 | 0.326 | 0.328 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.32967 | 0.32933 | 0.329 | 0.32867 | 0.32833 | 0.328 | 0.32767 | 0.32733 | 0.327 | 0.32667 | 0.32633 | 0.326 | 0.32567 | 0.32533 | 0.325 | 0.32467 | 0.32433 | 0.324 | 0.32367 | 0.32333 | 0.323 | 0.32267 | 0.32233 | 0.322 | 0.32167 | 0.32133 | 0.321 | 0.32067 | 0.32033 | 0.32 | 0.31967 | 0.31933 | 0.319 | 0.31867 | 0.31833 | 0.318 | 0.31767 | 0.31733 | 0.317 | 0.31667 | 0.31633 | 0.316 | 0.31567 | 0.31533 | 0.315 | 0.31467 | 0.31433 | 0.314 | 0.31367 | 0.31333 | 0.313 | 0.31267 | 0.31233 | 0.312 | 0.31167 | 0.31133 | 0.311 | 0.31067 | 0.31033 | 0.31 | 0.30967 | 0.30933 | 0.309 | 0.30867 | 0.30833 | 0.308 | 0.30767 | 0.30733 | 0.307 | 0.30667 | 0.30633 | 0.306 | 0.30567 | 0.30533 | 0.305 | 0.30467 | 0.30433 | 0.304 | 0.30367 | 0.30333 | 0.303 | 0.30267 | 0.30233 | 0.302 | 0.30167 | 0.30133 | 0.301 | 0.30067 | 0.30033 | 0.3
0.55 | 0 | 0.135 | 0.189 | 0.225 | 0.27 | 0.297 | 0.297 | 0.297 | 0.288 | 0.279 | 0.27 | 0 | 0.0135 | 0.027 | 0.0405 | 0.054 | 0.0675 | 0.081 | 0.0945 | 0.108 | 0.1215 | 0.135 | 0.1458 | 0.1566 | 0.1674 | 0.1782 | 0.189 | 0.1962 | 0.2034 | 0.2106 | 0.2178 | 0.225 | 0.2295 | 0.234 | 0.2385 | 0.243 | 0.2475 | 0.252 | 0.2565 | 0.261 | 0.2655 | 0.27 | 0.2718 | 0.2736 | 0.2754 | 0.2772 | 0.279 | 0.2808 | 0.2826 | 0.2844 | 0.2862 | 0.288 | 0.2898 | 0.2916 | 0.2934 | 0.2952 | 0.297 | 0.297 | 0.297 | 0.297 | 0.297 | 0.297 | 0.297 | 0.297 | 0.297 | 0.297 | 0.297 | 0.297 | 0.297 | 0.297 | 0.297 | 0.297 | 0.297 | 0.297 | 0.297 | 0.297 | 0.297 | 0.297 | 0.297 | 0.297 | 0.297 | 0.297 | 0.297 | 0.297 | 0.297 | 0.297 | 0.297 | 0.297 | 0.297 | 0.297 | 0.297 | 0.297 | 0.297 | 0.297 | 0.297 | 0.297 | 0.297 | 0.297 | 0.297 | 0.297 | 0.297 | 0.297 | 0.2967 | 0.2964 | 0.2961 | 0.2958 | 0.2955 | 0.2952 | 0.2949 | 0.2946 | 0.2943 | 0.294 | 0.2937 | 0.2934 | 0.2931 | 0.2928 | 0.2925 | 0.2922 | 0.2919 | 0.2916 | 0.2913 | 0.291 | 0.2907 | 0.2904 | 0.2901 | 0.2898 | 0.2895 | 0.2892 | 0.2889 | 0.2886 | 0.2883 | 0.288 | 0.2877 | 0.2874 | 0.2871 | 0.2868 | 0.2865 | 0.2862 | 0.2859 | 0.2856 | 0.2853 | 0.285 | 0.2847 | 0.2844 | 0.2841 | 0.2838 | 0.2835 | 0.2832 | 0.2829 | 0.2826 | 0.2823 | 0.282 | 0.2817 | 0.2814 | 0.2811 | 0.2808 | 0.2805 | 0.2802 | 0.2799 | 0.2796 | 0.2793 | 0.279 | 0.2787 | 0.2784 | 0.2781 | 0.2778 | 0.2775 | 0.2772 | 0.2769 | 0.2766 | 0.2763 | 0.276 | 0.2757 | 0.2754 | 0.2751 | 0.2748 | 0.2745 | 0.2742 | 0.2739 | 0.2736 | 0.2733 | 0.273 | 0.2727 | 0.2724 | 0.2721 | 0.2718 | 0.2715 | 0.2712 | 0.2709 | 0.2706 | 0.2703 | 0.27
0.6 | 0 | 0.12 | 0.168 | 0.2 | 0.24 | 0.264 | 0.264 | 0.264 | 0.256 | 0.248 | 0.24 | 0 | 0.012 | 0.024 | 0.036 | 0.048 | 0.06 | 0.072 | 0.084 | 0.096 | 0.108 | 0.12 | 0.1296 | 0.1392 | 0.1488 | 0.1584 | 0.168 | 0.1744 | 0.1808 | 0.1872 | 0.1936 | 0.2 | 0.204 | 0.208 | 0.212 | 0.216 | 0.22 | 0.224 | 0.228 | 0.232 | 0.236 | 0.24 | 0.2416 | 0.2432 | 0.2448 | 0.2464 | 0.248 | 0.2496 | 0.2512 | 0.2528 | 0.2544 | 0.256 | 0.2576 | 0.2592 | 0.2608 | 0.2624 | 0.264 | 0.264 | 0.264 | 0.264 | 0.264 | 0.264 | 0.264 | 0.264 | 0.264 | 0.264 | 0.264 | 0.264 | 0.264 | 0.264 | 0.264 | 0.264 | 0.264 | 0.264 | 0.264 | 0.264 | 0.264 | 0.264 | 0.264 | 0.264 | 0.264 | 0.264 | 0.264 | 0.264 | 0.264 | 0.264 | 0.264 | 0.264 | 0.264 | 0.264 | 0.264 | 0.264 | 0.264 | 0.264 | 0.264 | 0.264 | 0.264 | 0.264 | 0.264 | 0.264 | 0.264 | 0.264 | 0.26373 | 0.26347 | 0.2632 | 0.26293 | 0.26267 | 0.2624 | 0.26213 | 0.26187 | 0.2616 | 0.26133 | 0.26107 | 0.2608 | 0.26053 | 0.26027 | 0.26 | 0.25973 | 0.25947 | 0.2592 | 0.25893 | 0.25867 | 0.2584 | 0.25813 | 0.25787 | 0.2576 | 0.25733 | 0.25707 | 0.2568 | 0.25653 | 0.25627 | 0.256 | 0.25573 | 0.25547 | 0.2552 | 0.25493 | 0.25467 | 0.2544 | 0.25413 | 0.25387 | 0.2536 | 0.25333 | 0.25307 | 0.2528 | 0.25253 | 0.25227 | 0.252 | 0.25173 | 0.25147 | 0.2512 | 0.25093 | 0.25067 | 0.2504 | 0.25013 | 0.24987 | 0.2496 | 0.24933 | 0.24907 | 0.2488 | 0.24853 | 0.24827 | 0.248 | 0.24773 | 0.24747 | 0.2472 | 0.24693 | 0.24667 | 0.2464 | 0.24613 | 0.24587 | 0.2456 | 0.24533 | 0.24507 | 0.2448 | 0.24453 | 0.24427 | 0.244 | 0.24373 | 0.24347 | 0.2432 | 0.24293 | 0.24267 | 0.2424 | 0.24213 | 0.24187 | 0.2416 | 0.24133 | 0.24107 | 0.2408 | 0.24053 | 0.24027 | 0.24
0.65 | 0 | 0.105 | 0.147 | 0.175 | 0.21 | 0.231 | 0.231 | 0.231 | 0.224 | 0.217 | 0.21 | 0 | 0.0105 | 0.021 | 0.0315 | 0.042 | 0.0525 | 0.063 | 0.0735 | 0.084 | 0.0945 | 0.105 | 0.1134 | 0.1218 | 0.1302 | 0.1386 | 0.147 | 0.1526 | 0.1582 | 0.1638 | 0.1694 | 0.175 | 0.1785 | 0.182 | 0.1855 | 0.189 | 0.1925 | 0.196 | 0.1995 | 0.203 | 0.2065 | 0.21 | 0.2114 | 0.2128 | 0.2142 | 0.2156 | 0.217 | 0.2184 | 0.2198 | 0.2212 | 0.2226 | 0.224 | 0.2254 | 0.2268 | 0.2282 | 0.2296 | 0.231 | 0.231 | 0.231 | 0.231 | 0.231 | 0.231 | 0.231 | 0.231 | 0.231 | 0.231 | 0.231 | 0.231 | 0.231 | 0.231 | 0.231 | 0.231 | 0.231 | 0.231 | 0.231 | 0.231 | 0.231 | 0.231 | 0.231 | 0.231 | 0.231 | 0.231 | 0.231 | 0.231 | 0.231 | 0.231 | 0.231 | 0.231 | 0.231 | 0.231 | 0.231 | 0.231 | 0.231 | 0.231 | 0.231 | 0.231 | 0.231 | 0.231 | 0.231 | 0.231 | 0.231 | 0.231 | 0.23077 | 0.23053 | 0.2303 | 0.23007 | 0.22983 | 0.2296 | 0.22937 | 0.22913 | 0.2289 | 0.22867 | 0.22843 | 0.2282 | 0.22797 | 0.22773 | 0.2275 | 0.22727 | 0.22703 | 0.2268 | 0.22657 | 0.22633 | 0.2261 | 0.22587 | 0.22563 | 0.2254 | 0.22517 | 0.22493 | 0.2247 | 0.22447 | 0.22423 | 0.224 | 0.22377 | 0.22353 | 0.2233 | 0.22307 | 0.22283 | 0.2226 | 0.22237 | 0.22213 | 0.2219 | 0.22167 | 0.22143 | 0.2212 | 0.22097 | 0.22073 | 0.2205 | 0.22027 | 0.22003 | 0.2198 | 0.21957 | 0.21933 | 0.2191 | 0.21887 | 0.21863 | 0.2184 | 0.21817 | 0.21793 | 0.2177 | 0.21747 | 0.21723 | 0.217 | 0.21677 | 0.21653 | 0.2163 | 0.21607 | 0.21583 | 0.2156 | 0.21537 | 0.21513 | 0.2149 | 0.21467 | 0.21443 | 0.2142 | 0.21397 | 0.21373 | 0.2135 | 0.21327 | 0.21303 | 0.2128 | 0.21257 | 0.21233 | 0.2121 | 0.21187 | 0.21163 | 0.2114 | 0.21117 | 0.21093 | 0.2107 | 0.21047 | 0.21023 | 0.21
0.7 | 0 | 0.09 | 0.126 | 0.15 | 0.18 | 0.198 | 0.198 | 0.198 | 0.192 | 0.186 | 0.18 | 0 | 0.009 | 0.018 | 0.027 | 0.036 | 0.045 | 0.054 | 0.063 | 0.072 | 0.081 | 0.09 | 0.0972 | 0.1044 | 0.1116 | 0.1188 | 0.126 | 0.1308 | 0.1356 | 0.1404 | 0.1452 | 0.15 | 0.153 | 0.156 | 0.159 | 0.162 | 0.165 | 0.168 | 0.171 | 0.174 | 0.177 | 0.18 | 0.1812 | 0.1824 | 0.1836 | 0.1848 | 0.186 | 0.1872 | 0.1884 | 0.1896 | 0.1908 | 0.192 | 0.1932 | 0.1944 | 0.1956 | 0.1968 | 0.198 | 0.198 | 0.198 | 0.198 | 0.198 | 0.198 | 0.198 | 0.198 | 0.198 | 0.198 | 0.198 | 0.198 | 0.198 | 0.198 | 0.198 | 0.198 | 0.198 | 0.198 | 0.198 | 0.198 | 0.198 | 0.198 | 0.198 | 0.198 | 0.198 | 0.198 | 0.198 | 0.198 | 0.198 | 0.198 | 0.198 | 0.198 | 0.198 | 0.198 | 0.198 | 0.198 | 0.198 | 0.198 | 0.198 | 0.198 | 0.198 | 0.198 | 0.198 | 0.198 | 0.198 | 0.198 | 0.1978 | 0.1976 | 0.1974 | 0.1972 | 0.197 | 0.1968 | 0.1966 | 0.1964 | 0.1962 | 0.196 | 0.1958 | 0.1956 | 0.1954 | 0.1952 | 0.195 | 0.1948 | 0.1946 | 0.1944 | 0.1942 | 0.194 | 0.1938 | 0.1936 | 0.1934 | 0.1932 | 0.193 | 0.1928 | 0.1926 | 0.1924 | 0.1922 | 0.192 | 0.1918 | 0.1916 | 0.1914 | 0.1912 | 0.191 | 0.1908 | 0.1906 | 0.1904 | 0.1902 | 0.19 | 0.1898 | 0.1896 | 0.1894 | 0.1892 | 0.189 | 0.1888 | 0.1886 | 0.1884 | 0.1882 | 0.188 | 0.1878 | 0.1876 | 0.1874 | 0.1872 | 0.187 | 0.1868 | 0.1866 | 0.1864 | 0.1862 | 0.186 | 0.1858 | 0.1856 | 0.1854 | 0.1852 | 0.185 | 0.1848 | 0.1846 | 0.1844 | 0.1842 | 0.184 | 0.1838 | 0.1836 | 0.1834 | 0.1832 | 0.183 | 0.1828 | 0.1826 | 0.1824 | 0.1822 | 0.182 | 0.1818 | 0.1816 | 0.1814 | 0.1812 | 0.181 | 0.1808 | 0.1806 | 0.1804 | 0.1802 | 0.18
0.75 | 0 | 0.075 | 0.105 | 0.125 | 0.15 | 0.165 | 0.165 | 0.165 | 0.16 | 0.155 | 0.15 | 0 | 0.0075 | 0.015 | 0.0225 | 0.03 | 0.0375 | 0.045 | 0.0525 | 0.06 | 0.0675 | 0.075 | 0.081 | 0.087 | 0.093 | 0.099 | 0.105 | 0.109 | 0.113 | 0.117 | 0.121 | 0.125 | 0.1275 | 0.13 | 0.1325 | 0.135 | 0.1375 | 0.14 | 0.1425 | 0.145 | 0.1475 | 0.15 | 0.151 | 0.152 | 0.153 | 0.154 | 0.155 | 0.156 | 0.157 | 0.158 | 0.159 | 0.16 | 0.161 | 0.162 | 0.163 | 0.164 | 0.165 | 0.165 | 0.165 | 0.165 | 0.165 | 0.165 | 0.165 | 0.165 | 0.165 | 0.165 | 0.165 | 0.165 | 0.165 | 0.165 | 0.165 | 0.165 | 0.165 | 0.165 | 0.165 | 0.165 | 0.165 | 0.165 | 0.165 | 0.165 | 0.165 | 0.165 | 0.165 | 0.165 | 0.165 | 0.165 | 0.165 | 0.165 | 0.165 | 0.165 | 0.165 | 0.165 | 0.165 | 0.165 | 0.165 | 0.165 | 0.165 | 0.165 | 0.165 | 0.165 | 0.165 | 0.165 | 0.16483 | 0.16467 | 0.1645 | 0.16433 | 0.16417 | 0.164 | 0.16383 | 0.16367 | 0.1635 | 0.16333 | 0.16317 | 0.163 | 0.16283 | 0.16267 | 0.1625 | 0.16233 | 0.16217 | 0.162 | 0.16183 | 0.16167 | 0.1615 | 0.16133 | 0.16117 | 0.161 | 0.16083 | 0.16067 | 0.1605 | 0.16033 | 0.16017 | 0.16 | 0.15983 | 0.15967 | 0.1595 | 0.15933 | 0.15917 | 0.159 | 0.15883 | 0.15867 | 0.1585 | 0.15833 | 0.15817 | 0.158 | 0.15783 | 0.15767 | 0.1575 | 0.15733 | 0.15717 | 0.157 | 0.15683 | 0.15667 | 0.1565 | 0.15633 | 0.15617 | 0.156 | 0.15583 | 0.15567 | 0.1555 | 0.15533 | 0.15517 | 0.155 | 0.15483 | 0.15467 | 0.1545 | 0.15433 | 0.15417 | 0.154 | 0.15383 | 0.15367 | 0.1535 | 0.15333 | 0.15317 | 0.153 | 0.15283 | 0.15267 | 0.1525 | 0.15233 | 0.15217 | 0.152 | 0.15183 | 0.15167 | 0.1515 | 0.15133 | 0.15117 | 0.151 | 0.15083 | 0.15067 | 0.1505 | 0.15033 | 0.15017 | 0.15
0.8 | 0 | 0.06 | 0.084 | 0.1 | 0.12 | 0.132 | 0.132 | 0.132 | 0.128 | 0.124 | 0.12 | 0 | 0.006 | 0.012 | 0.018 | 0.024 | 0.03 | 0.036 | 0.042 | 0.048 | 0.054 | 0.06 | 0.0648 | 0.0696 | 0.0744 | 0.0792 | 0.084 | 0.0872 | 0.0904 | 0.0936 | 0.0968 | 0.1 | 0.102 | 0.104 | 0.106 | 0.108 | 0.11 | 0.112 | 0.114 | 0.116 | 0.118 | 0.12 | 0.1208 | 0.1216 | 0.1224 | 0.1232 | 0.124 | 0.1248 | 0.1256 | 0.1264 | 0.1272 | 0.128 | 0.1288 | 0.1296 | 0.1304 | 0.1312 | 0.132 | 0.132 | 0.132 | 0.132 | 0.132 | 0.132 | 0.132 | 0.132 | 0.132 | 0.132 | 0.132 | 0.132 | 0.132 | 0.132 | 0.132 | 0.132 | 0.132 | 0.132 | 0.132 | 0.132 | 0.132 | 0.132 | 0.132 | 0.132 | 0.132 | 0.132 | 0.132 | 0.132 | 0.132 | 0.132 | 0.132 | 0.132 | 0.132 | 0.132 | 0.132 | 0.132 | 0.132 | 0.132 | 0.132 | 0.132 | 0.132 | 0.132 | 0.132 | 0.132 | 0.132 | 0.132 | 0.13187 | 0.13173 | 0.1316 | 0.13147 | 0.13133 | 0.1312 | 0.13107 | 0.13093 | 0.1308 | 0.13067 | 0.13053 | 0.1304 | 0.13027 | 0.13013 | 0.13 | 0.12987 | 0.12973 | 0.1296 | 0.12947 | 0.12933 | 0.1292 | 0.12907 | 0.12893 | 0.1288 | 0.12867 | 0.12853 | 0.1284 | 0.12827 | 0.12813 | 0.128 | 0.12787 | 0.12773 | 0.1276 | 0.12747 | 0.12733 | 0.1272 | 0.12707 | 0.12693 | 0.1268 | 0.12667 | 0.12653 | 0.1264 | 0.12627 | 0.12613 | 0.126 | 0.12587 | 0.12573 | 0.1256 | 0.12547 | 0.12533 | 0.1252 | 0.12507 | 0.12493 | 0.1248 | 0.12467 | 0.12453 | 0.1244 | 0.12427 | 0.12413 | 0.124 | 0.12387 | 0.12373 | 0.1236 | 0.12347 | 0.12333 | 0.1232 | 0.12307 | 0.12293 | 0.1228 | 0.12267 | 0.12253 | 0.1224 | 0.12227 | 0.12213 | 0.122 | 0.12187 | 0.12173 | 0.1216 | 0.12147 | 0.12133 | 0.1212 | 0.12107 | 0.12093 | 0.1208 | 0.12067 | 0.12053 | 0.1204 | 0.12027 | 0.12013 | 0.12
0.85 | 0 | 0.045 | 0.063 | 0.075 | 0.09 | 0.099 | 0.099 | 0.099 | 0.096 | 0.093 | 0.09 | 0 | 0.0045 | 0.009 | 0.0135 | 0.018 | 0.0225 | 0.027 | 0.0315 | 0.036 | 0.0405 | 0.045 | 0.0486 | 0.0522 | 0.0558 | 0.0594 | 0.063 | 0.0654 | 0.0678 | 0.0702 | 0.0726 | 0.075 | 0.0765 | 0.078 | 0.0795 | 0.081 | 0.0825 | 0.084 | 0.0855 | 0.087 | 0.0885 | 0.09 | 0.0906 | 0.0912 | 0.0918 | 0.0924 | 0.093 | 0.0936 | 0.0942 | 0.0948 | 0.0954 | 0.096 | 0.0966 | 0.0972 | 0.0978 | 0.0984 | 0.099 | 0.099 | 0.099 | 0.099 | 0.099 | 0.099 | 0.099 | 0.099 | 0.099 | 0.099 | 0.099 | 0.099 | 0.099 | 0.099 | 0.099 | 0.099 | 0.099 | 0.099 | 0.099 | 0.099 | 0.099 | 0.099 | 0.099 | 0.099 | 0.099 | 0.099 | 0.099 | 0.099 | 0.099 | 0.099 | 0.099 | 0.099 | 0.099 | 0.099 | 0.099 | 0.099 | 0.099 | 0.099 | 0.099 | 0.099 | 0.099 | 0.099 | 0.099 | 0.099 | 0.099 | 0.099 | 0.0989 | 0.0988 | 0.0987 | 0.0986 | 0.0985 | 0.0984 | 0.0983 | 0.0982 | 0.0981 | 0.098 | 0.0979 | 0.0978 | 0.0977 | 0.0976 | 0.0975 | 0.0974 | 0.0973 | 0.0972 | 0.0971 | 0.097 | 0.0969 | 0.0968 | 0.0967 | 0.0966 | 0.0965 | 0.0964 | 0.0963 | 0.0962 | 0.0961 | 0.096 | 0.0959 | 0.0958 | 0.0957 | 0.0956 | 0.0955 | 0.0954 | 0.0953 | 0.0952 | 0.0951 | 0.095 | 0.0949 | 0.0948 | 0.0947 | 0.0946 | 0.0945 | 0.0944 | 0.0943 | 0.0942 | 0.0941 | 0.094 | 0.0939 | 0.0938 | 0.0937 | 0.0936 | 0.0935 | 0.0934 | 0.0933 | 0.0932 | 0.0931 | 0.093 | 0.0929 | 0.0928 | 0.0927 | 0.0926 | 0.0925 | 0.0924 | 0.0923 | 0.0922 | 0.0921 | 0.092 | 0.0919 | 0.0918 | 0.0917 | 0.0916 | 0.0915 | 0.0914 | 0.0913 | 0.0912 | 0.0911 | 0.091 | 0.0909 | 0.0908 | 0.0907 | 0.0906 | 0.0905 | 0.0904 | 0.0903 | 0.0902 | 0.0901 | 0.09
0.9 | 0 | 0.03 | 0.042 | 0.05 | 0.06 | 0.066 | 0.066 | 0.066 | 0.064 | 0.062 | 0.06 | 0 | 0.003 | 0.006 | 0.009 | 0.012 | 0.015 | 0.018 | 0.021 | 0.024 | 0.027 | 0.03 | 0.0324 | 0.0348 | 0.0372 | 0.0396 | 0.042 | 0.0436 | 0.0452 | 0.0468 | 0.0484 | 0.05 | 0.051 | 0.052 | 0.053 | 0.054 | 0.055 | 0.056 | 0.057 | 0.058 | 0.059 | 0.06 | 0.0604 | 0.0608 | 0.0612 | 0.0616 | 0.062 | 0.0624 | 0.0628 | 0.0632 | 0.0636 | 0.064 | 0.0644 | 0.0648 | 0.0652 | 0.0656 | 0.066 | 0.066 | 0.066 | 0.066 | 0.066 | 0.066 | 0.066 | 0.066 | 0.066 | 0.066 | 0.066 | 0.066 | 0.066 | 0.066 | 0.066 | 0.066 | 0.066 | 0.066 | 0.066 | 0.066 | 0.066 | 0.066 | 0.066 | 0.066 | 0.066 | 0.066 | 0.066 | 0.066 | 0.066 | 0.066 | 0.066 | 0.066 | 0.066 | 0.066 | 0.066 | 0.066 | 0.066 | 0.066 | 0.066 | 0.066 | 0.066 | 0.066 | 0.066 | 0.066 | 0.066 | 0.066 | 0.065933 | 0.065867 | 0.0658 | 0.065733 | 0.065667 | 0.0656 | 0.065533 | 0.065467 | 0.0654 | 0.065333 | 0.065267 | 0.0652 | 0.065133 | 0.065067 | 0.065 | 0.064933 | 0.064867 | 0.0648 | 0.064733 | 0.064667 | 0.0646 | 0.064533 | 0.064467 | 0.0644 | 0.064333 | 0.064267 | 0.0642 | 0.064133 | 0.064067 | 0.064 | 0.063933 | 0.063867 | 0.0638 | 0.063733 | 0.063667 | 0.0636 | 0.063533 | 0.063467 | 0.0634 | 0.063333 | 0.063267 | 0.0632 | 0.063133 | 0.063067 | 0.063 | 0.062933 | 0.062867 | 0.0628 | 0.062733 | 0.062667 | 0.0626 | 0.062533 | 0.062467 | 0.0624 | 0.062333 | 0.062267 | 0.0622 | 0.062133 | 0.062067 | 0.062 | 0.061933 | 0.061867 | 0.0618 | 0.061733 | 0.061667 | 0.0616 | 0.061533 | 0.061467 | 0.0614 | 0.061333 | 0.061267 | 0.0612 | 0.061133 | 0.061067 | 0.061 | 0.060933 | 0.060867 | 0.0608 | 0.060733 | 0.060667 | 0.0606 | 0.060533 | 0.060467 | 0.0604 | 0.060333 | 0.060267 | 0.0602 | 0.060133 | 0.060067 | 0.06
0.95 | 0 | 0.015 | 0.021 | 0.025 | 0.03 | 0.033 | 0.033 | 0.033 | 0.032 | 0.031 | 0.03 | 0 | 0.0015 | 0.003 | 0.0045 | 0.006 | 0.0075 | 0.009 | 0.0105 | 0.012 | 0.0135 | 0.015 | 0.0162 | 0.0174 | 0.0186 | 0.0198 | 0.021 | 0.0218 | 0.0226 | 0.0234 | 0.0242 | 0.025 | 0.0255 | 0.026 | 0.0265 | 0.027 | 0.0275 | 0.028 | 0.0285 | 0.029 | 0.0295 | 0.03 | 0.0302 | 0.0304 | 0.0306 | 0.0308 | 0.031 | 0.0312 | 0.0314 | 0.0316 | 0.0318 | 0.032 | 0.0322 | 0.0324 | 0.0326 | 0.0328 | 0.033 | 0.033 | 0.033 | 0.033 | 0.033 | 0.033 | 0.033 | 0.033 | 0.033 | 0.033 | 0.033 | 0.033 | 0.033 | 0.033 | 0.033 | 0.033 | 0.033 | 0.033 | 0.033 | 0.033 | 0.033 | 0.033 | 0.033 | 0.033 | 0.033 | 0.033 | 0.033 | 0.033 | 0.033 | 0.033 | 0.033 | 0.033 | 0.033 | 0.033 | 0.033 | 0.033 | 0.033 | 0.033 | 0.033 | 0.033 | 0.033 | 0.033 | 0.033 | 0.033 | 0.033 | 0.033 | 0.032967 | 0.032933 | 0.0329 | 0.032867 | 0.032833 | 0.0328 | 0.032767 | 0.032733 | 0.0327 | 0.032667 | 0.032633 | 0.0326 | 0.032567 | 0.032533 | 0.0325 | 0.032467 | 0.032433 | 0.0324 | 0.032367 | 0.032333 | 0.0323 | 0.032267 | 0.032233 | 0.0322 | 0.032167 | 0.032133 | 0.0321 | 0.032067 | 0.032033 | 0.032 | 0.031967 | 0.031933 | 0.0319 | 0.031867 | 0.031833 | 0.0318 | 0.031767 | 0.031733 | 0.0317 | 0.031667 | 0.031633 | 0.0316 | 0.031567 | 0.031533 | 0.0315 | 0.031467 | 0.031433 | 0.0314 | 0.031367 | 0.031333 | 0.0313 | 0.031267 | 0.031233 | 0.0312 | 0.031167 | 0.031133 | 0.0311 | 0.031067 | 0.031033 | 0.031 | 0.030967 | 0.030933 | 0.0309 | 0.030867 | 0.030833 | 0.0308 | 0.030767 | 0.030733 | 0.0307 | 0.030667 | 0.030633 | 0.0306 | 0.030567 | 0.030533 | 0.0305 | 0.030467 | 0.030433 | 0.0304 | 0.030367 | 0.030333 | 0.0303 | 0.030267 | 0.030233 | 0.0302 | 0.030167 | 0.030133 | 0.0301 | 0.030067 | 0.030033 | 0.03
1 | 0 | 0 | 0 | 0 | -2.7756e-17 | -2.7756e-17 | 0 | 0 | 0 | -1.1102e-16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.7756e-18 | -5.5511e-18 | -8.3267e-18 | -1.1102e-17 | -1.3878e-17 | -1.6653e-17 | -1.9429e-17 | -2.2204e-17 | -2.498e-17 | -2.7756e-17 | -2.7756e-17 | -2.7756e-17 | -2.7756e-17 | -2.7756e-17 | -2.7756e-17 | -2.7756e-17 | -2.7756e-17 | -2.7756e-17 | -2.7756e-17 | -2.7756e-17 | -2.7756e-17 | -2.7756e-17 | -2.7756e-17 | -2.7756e-17 | -2.7756e-17 | -2.5905e-17 | -2.4055e-17 | -2.2204e-17 | -2.0354e-17 | -1.8504e-17 | -1.6653e-17 | -1.4803e-17 | -1.2953e-17 | -1.1102e-17 | -9.2519e-18 | -7.4015e-18 | -5.5511e-18 | -3.7007e-18 | -1.8504e-18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -3.7007e-18 | -7.4015e-18 | -1.1102e-17 | -1.4803e-17 | -1.8504e-17 | -2.2204e-17 | -2.5905e-17 | -2.9606e-17 | -3.3307e-17 | -3.7007e-17 | -4.0708e-17 | -4.4409e-17 | -4.811e-17 | -5.181e-17 | -5.5511e-17 | -5.9212e-17 | -6.2913e-17 | -6.6613e-17 | -7.0314e-17 | -7.4015e-17 | -7.7716e-17 | -8.1416e-17 | -8.5117e-17 | -8.8818e-17 | -9.2519e-17 | -9.6219e-17 | -9.992e-17 | -1.0362e-16 | -1.0732e-16 | -1.1102e-16 | -1.0732e-16 | -1.0362e-16 | -9.992e-17 | -9.6219e-17 | -9.2519e-17 | -8.8818e-17 | -8.5117e-17 | -8.1416e-17 | -7.7716e-17 | -7.4015e-17 | -7.0314e-17 | -6.6613e-17 | -6.2913e-17 | -5.9212e-17 | -5.5511e-17 | -5.181e-17 | -4.811e-17 | -4.4409e-17 | -4.0708e-17 | -3.7007e-17 | -3.3307e-17 | -2.9606e-17 | -2.5905e-17 | -2.2204e-17 | -1.8504e-17 | -1.4803e-17 | -1.1102e-17 | -7.4015e-18 | -3.7007e-18 | -3.7007e-23
1.05 | 0 | 0.012 | 0.014 | 0.013 | 0.01 | 0.011 | 0.012 | 0.0245 | 0.0365 | 0.0485 | 0.052 | 0 | 0.0012 | 0.0024 | 0.0036 | 0.0048 | 0.006 | 0.0072 | 0.0084 | 0.0096 | 0.0108 | 0.012 | 0.0124 | 0.0128 | 0.0132 | 0.0136 | 0.014 | 0.0138 | 0.0136 | 0.0134 | 0.0132 | 0.013 | 0.0127 | 0.0124 | 0.0121 | 0.0118 | 0.0115 | 0.0112 | 0.0109 | 0.0106 | 0.0103 | 0.01 | 0.010067 | 0.010133 | 0.0102 | 0.010267 | 0.010333 | 0.0104 | 0.010467 | 0.010533 | 0.0106 | 0.010667 | 0.010733 | 0.0108 | 0.010867 | 0.010933 | 0.011 | 0.011067 | 0.011133 | 0.0112 | 0.011267 | 0.011333 | 0.0114 | 0.011467 | 0.011533 | 0.0116 | 0.011667 | 0.011733 | 0.0118 | 0.011867 | 0.011933 | 0.012 | 0.012417 | 0.012833 | 0.01325 | 0.013667 | 0.014083 | 0.0145 | 0.014917 | 0.015333 | 0.01575 | 0.016167 | 0.016583 | 0.017 | 0.017417 | 0.017833 | 0.01825 | 0.018667 | 0.019083 | 0.0195 | 0.019917 | 0.020333 | 0.02075 | 0.021167 | 0.021583 | 0.022 | 0.022417 | 0.022833 | 0.02325 | 0.023667 | 0.024083 | 0.0245 | 0.0249 | 0.0253 | 0.0257 | 0.0261 | 0.0265 | 0.0269 | 0.0273 | 0.0277 | 0.0281 | 0.0285 | 0.0289 | 0.0293 | 0.0297 | 0.0301 | 0.0305 | 0.0309 | 0.0313 | 0.0317 | 0.0321 | 0.0325 | 0.0329 | 0.0333 | 0.0337 | 0.0341 | 0.0345 | 0.0349 | 0.0353 | 0.0357 | 0.0361 | 0.0365 | 0.0369 | 0.0373 | 0.0377 | 0.0381 | 0.0385 | 0.0389 | 0.0393 | 0.0397 | 0.0401 | 0.0405 | 0.0409 | 0.0413 | 0.0417 | 0.0421 | 0.0425 | 0.0429 | 0.0433 | 0.0437 | 0.0441 | 0.0445 | 0.0449 | 0.0453 | 0.0457 | 0.0461 | 0.0465 | 0.0469 | 0.0473 | 0.0477 | 0.0481 | 0.0485 | 0.048617 | 0.048733 | 0.04885 | 0.048967 | 0.049083 | 0.0492 | 0.049317 | 0.049433 | 0.04955 | 0.049667 | 0.049783 | 0.0499 | 0.050017 | 0.050133 | 0.05025 | 0.050367 | 0.050483 | 0.0506 | 0.050717 | 0.050833 | 0.05095 | 0.051067 | 0.051183 | 0.0513 | 0.051417 | 0.051533 | 0.05165 | 0.051767 | 0.051883 | 0.052
1.1 | 0 | 0.024 | 0.028 | 0.026 | 0.02 | 0.022 | 0.024 | 0.049 | 0.073 | 0.097 | 0.104 | 0 | 0.0024 | 0.0048 | 0.0072 | 0.0096 | 0.012 | 0.0144 | 0.0168 | 0.0192 | 0.0216 | 0.024 | 0.0248 | 0.0256 | 0.0264 | 0.0272 | 0.028 | 0.0276 | 0.0272 | 0.0268 | 0.0264 | 0.026 | 0.0254 | 0.0248 | 0.0242 | 0.0236 | 0.023 | 0.0224 | 0.0218 | 0.0212 | 0.0206 | 0.02 | 0.020133 | 0.020267 | 0.0204 | 0.020533 | 0.020667 | 0.0208 | 0.020933 | 0.021067 | 0.0212 | 0.021333 | 0.021467 | 0.0216 | 0.021733 | 0.021867 | 0.022 | 0.022133 | 0.022267 | 0.0224 | 0.022533 | 0.022667 | 0.0228 | 0.022933 | 0.023067 | 0.0232 | 0.023333 | 0.023467 | 0.0236 | 0.023733 | 0.023867 | 0.024 | 0.024833 | 0.025667 | 0.0265 | 0.027333 | 0.028167 | 0.029 | 0.029833 | 0.030667 | 0.0315 | 0.032333 | 0.033167 | 0.034 | 0.034833 | 0.035667 | 0.0365 | 0.037333 | 0.038167 | 0.039 | 0.039833 | 0.040667 | 0.0415 | 0.042333 | 0.043167 | 0.044 | 0.044833 | 0.045667 | 0.0465 | 0.047333 | 0.048167 | 0.049 | 0.0498 | 0.0506 | 0.0514 | 0.0522 | 0.053 | 0.0538 | 0.0546 | 0.0554 | 0.0562 | 0.057 | 0.0578 | 0.0586 | 0.0594 | 0.0602 | 0.061 | 0.0618 | 0.0626 | 0.0634 | 0.0642 | 0.065 | 0.0658 | 0.0666 | 0.0674 | 0.0682 | 0.069 | 0.0698 | 0.0706 | 0.0714 | 0.0722 | 0.073 | 0.0738 | 0.0746 | 0.0754 | 0.0762 | 0.077 | 0.0778 | 0.0786 | 0.0794 | 0.0802 | 0.081 | 0.0818 | 0.0826 | 0.0834 | 0.0842 | 0.085 | 0.0858 | 0.0866 | 0.0874 | 0.0882 | 0.089 | 0.0898 | 0.0906 | 0.0914 | 0.0922 | 0.093 | 0.0938 | 0.0946 | 0.0954 | 0.0962 | 0.097 | 0.097233 | 0.097467 | 0.0977 | 0.097933 | 0.098167 | 0.0984 | 0.098633 | 0.098867 | 0.0991 | 0.099333 | 0.099567 | 0.0998 | 0.10003 | 0.10027 | 0.1005 | 0.10073 | 0.10097 | 0.1012 | 0.10143 | 0.10167 | 0.1019 | 0.10213 | 0.10237 | 0.1026 | 0.10283 | 0.10307 | 0.1033 | 0.10353 | 0.10377 | 0.104
1.15 | 0 | 0.036 | 0.042 | 0.039 | 0.03 | 0.033 | 0.036 | 0.0735 | 0.1095 | 0.1455 | 0.156 | 0 | 0.0036 | 0.0072 | 0.0108 | 0.0144 | 0.018 | 0.0216 | 0.0252 | 0.0288 | 0.0324 | 0.036 | 0.0372 | 0.0384 | 0.0396 | 0.0408 | 0.042 | 0.0414 | 0.0408 | 0.0402 | 0.0396 | 0.039 | 0.0381 | 0.0372 | 0.0363 | 0.0354 | 0.0345 | 0.0336 | 0.0327 | 0.0318 | 0.0309 | 0.03 | 0.0302 | 0.0304 | 0.0306 | 0.0308 | 0.031 | 0.0312 | 0.0314 | 0.0316 | 0.0318 | 0.032 | 0.0322 | 0.0324 | 0.0326 | 0.0328 | 0.033 | 0.0332 | 0.0334 | 0.0336 | 0.0338 | 0.034 | 0.0342 | 0.0344 | 0.0346 | 0.0348 | 0.035 | 0.0352 | 0.0354 | 0.0356 | 0.0358 | 0.036 | 0.03725 | 0.0385 | 0.03975 | 0.041 | 0.04225 | 0.0435 | 0.04475 | 0.046 | 0.04725 | 0.0485 | 0.04975 | 0.051 | 0.05225 | 0.0535 | 0.05475 | 0.056 | 0.05725 | 0.0585 | 0.05975 | 0.061 | 0.06225 | 0.0635 | 0.06475 | 0.066 | 0.06725 | 0.0685 | 0.06975 | 0.071 | 0.07225 | 0.0735 | 0.0747 | 0.0759 | 0.0771 | 0.0783 | 0.0795 | 0.0807 | 0.0819 | 0.0831 | 0.0843 | 0.0855 | 0.0867 | 0.0879 | 0.0891 | 0.0903 | 0.0915 | 0.0927 | 0.0939 | 0.0951 | 0.0963 | 0.0975 | 0.0987 | 0.0999 | 0.1011 | 0.1023 | 0.1035 | 0.1047 | 0.1059 | 0.1071 | 0.1083 | 0.1095 | 0.1107 | 0.1119 | 0.1131 | 0.1143 | 0.1155 | 0.1167 | 0.1179 | 0.1191 | 0.1203 | 0.1215 | 0.1227 | 0.1239 | 0.1251 | 0.1263 | 0.1275 | 0.1287 | 0.1299 | 0.1311 | 0.1323 | 0.1335 | 0.1347 | 0.1359 | 0.1371 | 0.1383 | 0.1395 | 0.1407 | 0.1419 | 0.1431 | 0.1443 | 0.1455 | 0.14585 | 0.1462 | 0.14655 | 0.1469 | 0.14725 | 0.1476 | 0.14795 | 0.1483 | 0.14865 | 0.149 | 0.14935 | 0.1497 | 0.15005 | 0.1504 | 0.15075 | 0.1511 | 0.15145 | 0.1518 | 0.15215 | 0.1525 | 0.15285 | 0.1532 | 0.15355 | 0.1539 | 0.15425 | 0.1546 | 0.15495 | 0.1553 | 0.15565 | 0.156
1.2 | 0 | 0.048 | 0.056 | 0.052 | 0.04 | 0.044 | 0.048 | 0.098 | 0.146 | 0.194 | 0.208 | 0 | 0.0048 | 0.0096 | 0.0144 | 0.0192 | 0.024 | 0.0288 | 0.0336 | 0.0384 | 0.0432 | 0.048 | 0.0496 | 0.0512 | 0.0528 | 0.0544 | 0.056 | 0.0552 | 0.0544 | 0.0536 | 0.0528 | 0.052 | 0.0508 | 0.0496 | 0.0484 | 0.0472 | 0.046 | 0.0448 | 0.0436 | 0.0424 | 0.0412 | 0.04 | 0.040267 | 0.040533 | 0.0408 | 0.041067 | 0.041333 | 0.0416 | 0.041867 | 0.042133 | 0.0424 | 0.042667 | 0.042933 | 0.0432 | 0.043467 | 0.043733 | 0.044 | 0.044267 | 0.044533 | 0.0448 | 0.045067 | 0.045333 | 0.0456 | 0.045867 | 0.046133 | 0.0464 | 0.046667 | 0.046933 | 0.0472 | 0.047467 | 0.047733 | 0.048 | 0.049667 | 0.051333 | 0.053 | 0.054667 | 0.056333 | 0.058 | 0.059667 | 0.061333 | 0.063 | 0.064667 | 0.066333 | 0.068 | 0.069667 | 0.071333 | 0.073 | 0.074667 | 0.076333 | 0.078 | 0.079667 | 0.081333 | 0.083 | 0.084667 | 0.086333 | 0.088 | 0.089667 | 0.091333 | 0.093 | 0.094667 | 0.096333 | 0.098 | 0.0996 | 0.1012 | 0.1028 | 0.1044 | 0.106 | 0.1076 | 0.1092 | 0.1108 | 0.1124 | 0.114 | 0.1156 | 0.1172 | 0.1188 | 0.1204 | 0.122 | 0.1236 | 0.1252 | 0.1268 | 0.1284 | 0.13 | 0.1316 | 0.1332 | 0.1348 | 0.1364 | 0.138 | 0.1396 | 0.1412 | 0.1428 | 0.1444 | 0.146 | 0.1476 | 0.1492 | 0.1508 | 0.1524 | 0.154 | 0.1556 | 0.1572 | 0.1588 | 0.1604 | 0.162 | 0.1636 | 0.1652 | 0.1668 | 0.1684 | 0.17 | 0.1716 | 0.1732 | 0.1748 | 0.1764 | 0.178 | 0.1796 | 0.1812 | 0.1828 | 0.1844 | 0.186 | 0.1876 | 0.1892 | 0.1908 | 0.1924 | 0.194 | 0.19447 | 0.19493 | 0.1954 | 0.19587 | 0.19633 | 0.1968 | 0.19727 | 0.19773 | 0.1982 | 0.19867 | 0.19913 | 0.1996 | 0.20007 | 0.20053 | 0.201 | 0.20147 | 0.20193 | 0.2024 | 0.20287 | 0.20333 | 0.2038 | 0.20427 | 0.20473 | 0.2052 | 0.20567 | 0.20613 | 0.2066 | 0.20707 | 0.20753 | 0.208
1.25 | 0 | 0.06 | 0.07 | 0.065 | 0.05 | 0.055 | 0.06 | 0.1225 | 0.1825 | 0.2425 | 0.26 | 0 | 0.006 | 0.012 | 0.018 | 0.024 | 0.03 | 0.036 | 0.042 | 0.048 | 0.054 | 0.06 | 0.062 | 0.064 | 0.066 | 0.068 | 0.07 | 0.069 | 0.068 | 0.067 | 0.066 | 0.065 | 0.0635 | 0.062 | 0.0605 | 0.059 | 0.0575 | 0.056 | 0.0545 | 0.053 | 0.0515 | 0.05 | 0.050333 | 0.050667 | 0.051 | 0.051333 | 0.051667 | 0.052 | 0.052333 | 0.052667 | 0.053 | 0.053333 | 0.053667 | 0.054 | 0.054333 | 0.054667 | 0.055 | 0.055333 | 0.055667 | 0.056 | 0.056333 | 0.056667 | 0.057 | 0.057333 | 0.057667 | 0.058 | 0.058333 | 0.058667 | 0.059 | 0.059333 | 0.059667 | 0.06 | 0.062083 | 0.064167 | 0.06625 | 0.068333 | 0.070417 | 0.0725 | 0.074583 | 0.076667 | 0.07875 | 0.080833 | 0.082917 | 0.085 | 0.087083 | 0.089167 | 0.09125 | 0.093333 | 0.095417 | 0.0975 | 0.099583 | 0.10167 | 0.10375 | 0.10583 | 0.10792 | 0.11 | 0.11208 | 0.11417 | 0.11625 | 0.11833 | 0.12042 | 0.1225 | 0.1245 | 0.1265 | 0.1285 | 0.1305 | 0.1325 | 0.1345 | 0.1365 | 0.1385 | 0.1405 | 0.1425 | 0.1445 | 0.1465 | 0.1485 | 0.1505 | 0.1525 | 0.1545 | 0.1565 | 0.1585 | 0.1605 | 0.1625 | 0.1645 | 0.1665 | 0.1685 | 0.1705 | 0.1725 | 0.1745 | 0.1765 | 0.1785 | 0.1805 | 0.1825 | 0.1845 | 0.1865 | 0.1885 | 0.1905 | 0.1925 | 0.1945 | 0.1965 | 0.1985 | 0.2005 | 0.2025 | 0.2045 | 0.2065 | 0.2085 | 0.2105 | 0.2125 | 0.2145 | 0.2165 | 0.2185 | 0.2205 | 0.2225 | 0.2245 | 0.2265 | 0.2285 | 0.2305 | 0.2325 | 0.2345 | 0.2365 | 0.2385 | 0.2405 | 0.2425 | 0.24308 | 0.24367 | 0.24425 | 0.24483 | 0.24542 | 0.246 | 0.24658 | 0.24717 | 0.24775 | 0.24833 | 0.24892 | 0.2495 | 0.25008 | 0.25067 | 0.25125 | 0.25183 | 0.25242 | 0.253 | 0.25358 | 0.25417 | 0.25475 | 0.25533 | 0.25592 | 0.2565 | 0.25708 | 0.25767 | 0.25825 | 0.25883 | 0.25942 | 0.26
1.3 | 0 | 0.072 | 0.084 | 0.078 | 0.06 | 0.066 | 0.072 | 0.147 | 0.219 | 0.291 | 0.312 | 0 | 0.0072 | 0.0144 | 0.0216 | 0.0288 | 0.036 | 0.0432 | 0.0504 | 0.0576 | 0.0648 | 0.072 | 0.0744 | 0.0768 | 0.0792 | 0.0816 | 0.084 | 0.0828 | 0.0816 | 0.0804 | 0.0792 | 0.078 | 0.0762 | 0.0744 | 0.0726 | 0.0708 | 0.069 | 0.0672 | 0.0654 | 0.0636 | 0.0618 | 0.06 | 0.0604 | 0.0608 | 0.0612 | 0.0616 | 0.062 | 0.0624 | 0.0628 | 0.0632 | 0.0636 | 0.064 | 0.0644 | 0.0648 | 0.0652 | 0.0656 | 0.066 | 0.0664 | 0.0668 | 0.0672 | 0.0676 | 0.068 | 0.0684 | 0.0688 | 0.0692 | 0.0696 | 0.07 | 0.0704 | 0.0708 | 0.0712 | 0.0716 | 0.072 | 0.0745 | 0.077 | 0.0795 | 0.082 | 0.0845 | 0.087 | 0.0895 | 0.092 | 0.0945 | 0.097 | 0.0995 | 0.102 | 0.1045 | 0.107 | 0.1095 | 0.112 | 0.1145 | 0.117 | 0.1195 | 0.122 | 0.1245 | 0.127 | 0.1295 | 0.132 | 0.1345 | 0.137 | 0.1395 | 0.142 | 0.1445 | 0.147 | 0.1494 | 0.1518 | 0.1542 | 0.1566 | 0.159 | 0.1614 | 0.1638 | 0.1662 | 0.1686 | 0.171 | 0.1734 | 0.1758 | 0.1782 | 0.1806 | 0.183 | 0.1854 | 0.1878 | 0.1902 | 0.1926 | 0.195 | 0.1974 | 0.1998 | 0.2022 | 0.2046 | 0.207 | 0.2094 | 0.2118 | 0.2142 | 0.2166 | 0.219 | 0.2214 | 0.2238 | 0.2262 | 0.2286 | 0.231 | 0.2334 | 0.2358 | 0.2382 | 0.2406 | 0.243 | 0.2454 | 0.2478 | 0.2502 | 0.2526 | 0.255 | 0.2574 | 0.2598 | 0.2622 | 0.2646 | 0.267 | 0.2694 | 0.2718 | 0.2742 | 0.2766 | 0.279 | 0.2814 | 0.2838 | 0.2862 | 0.2886 | 0.291 | 0.2917 | 0.2924 | 0.2931 | 0.2938 | 0.2945 | 0.2952 | 0.2959 | 0.2966 | 0.2973 | 0.298 | 0.2987 | 0.2994 | 0.3001 | 0.3008 | 0.3015 | 0.3022 | 0.3029 | 0.3036 | 0.3043 | 0.305 | 0.3057 | 0.3064 | 0.3071 | 0.3078 | 0.3085 | 0.3092 | 0.3099 | 0.3106 | 0.3113 | 0.312
1.35 | 0 | 0.084 | 0.098 | 0.091 | 0.07 | 0.077 | 0.084 | 0.1715 | 0.2555 | 0.3395 | 0.364 | 0 | 0.0084 | 0.0168 | 0.0252 | 0.0336 | 0.042 | 0.0504 | 0.0588 | 0.0672 | 0.0756 | 0.084 | 0.0868 | 0.0896 | 0.0924 | 0.0952 | 0.098 | 0.0966 | 0.0952 | 0.0938 | 0.0924 | 0.091 | 0.0889 | 0.0868 | 0.0847 | 0.0826 | 0.0805 | 0.0784 | 0.0763 | 0.0742 | 0.0721 | 0.07 | 0.070467 | 0.070933 | 0.0714 | 0.071867 | 0.072333 | 0.0728 | 0.073267 | 0.073733 | 0.0742 | 0.074667 | 0.075133 | 0.0756 | 0.076067 | 0.076533 | 0.077 | 0.077467 | 0.077933 | 0.0784 | 0.078867 | 0.079333 | 0.0798 | 0.080267 | 0.080733 | 0.0812 | 0.081667 | 0.082133 | 0.0826 | 0.083067 | 0.083533 | 0.084 | 0.086917 | 0.089833 | 0.09275 | 0.095667 | 0.098583 | 0.1015 | 0.10442 | 0.10733 | 0.11025 | 0.11317 | 0.11608 | 0.119 | 0.12192 | 0.12483 | 0.12775 | 0.13067 | 0.13358 | 0.1365 | 0.13942 | 0.14233 | 0.14525 | 0.14817 | 0.15108 | 0.154 | 0.15692 | 0.15983 | 0.16275 | 0.16567 | 0.16858 | 0.1715 | 0.1743 | 0.1771 | 0.1799 | 0.1827 | 0.1855 | 0.1883 | 0.1911 | 0.1939 | 0.1967 | 0.1995 | 0.2023 | 0.2051 | 0.2079 | 0.2107 | 0.2135 | 0.2163 | 0.2191 | 0.2219 | 0.2247 | 0.2275 | 0.2303 | 0.2331 | 0.2359 | 0.2387 | 0.2415 | 0.2443 | 0.2471 | 0.2499 | 0.2527 | 0.2555 | 0.2583 | 0.2611 | 0.2639 | 0.2667 | 0.2695 | 0.2723 | 0.2751 | 0.2779 | 0.2807 | 0.2835 | 0.2863 | 0.2891 | 0.2919 | 0.2947 | 0.2975 | 0.3003 | 0.3031 | 0.3059 | 0.3087 | 0.3115 | 0.3143 | 0.3171 | 0.3199 | 0.3227 | 0.3255 | 0.3283 | 0.3311 | 0.3339 | 0.3367 | 0.3395 | 0.34032 | 0.34113 | 0.34195 | 0.34277 | 0.34358 | 0.3444 | 0.34522 | 0.34603 | 0.34685 | 0.34767 | 0.34848 | 0.3493 | 0.35012 | 0.35093 | 0.35175 | 0.35257 | 0.35338 | 0.3542 | 0.35502 | 0.35583 | 0.35665 | 0.35747 | 0.35828 | 0.3591 | 0.35992 | 0.36073 | 0.36155 | 0.36237 | 0.36318 | 0.364
1.4 | 0 | 0.096 | 0.112 | 0.104 | 0.08 | 0.088 | 0.096 | 0.196 | 0.292 | 0.388 | 0.416 | 0 | 0.0096 | 0.0192 | 0.0288 | 0.0384 | 0.048 | 0.0576 | 0.0672 | 0.0768 | 0.0864 | 0.096 | 0.0992 | 0.1024 | 0.1056 | 0.1088 | 0.112 | 0.1104 | 0.1088 | 0.1072 | 0.1056 | 0.104 | 0.1016 | 0.0992 | 0.0968 | 0.0944 | 0.092 | 0.0896 | 0.0872 | 0.0848 | 0.0824 | 0.08 | 0.080533 | 0.081067 | 0.0816 | 0.082133 | 0.082667 | 0.0832 | 0.083733 | 0.084267 | 0.0848 | 0.085333 | 0.085867 | 0.0864 | 0.086933 | 0.087467 | 0.088 | 0.088533 | 0.089067 | 0.0896 | 0.090133 | 0.090667 | 0.0912 | 0.091733 | 0.092267 | 0.0928 | 0.093333 | 0.093867 | 0.0944 | 0.094933 | 0.095467 | 0.096 | 0.099333 | 0.10267 | 0.106 | 0.10933 | 0.11267 | 0.116 | 0.11933 | 0.12267 | 0.126 | 0.12933 | 0.13267 | 0.136 | 0.13933 | 0.14267 | 0.146 | 0.14933 | 0.15267 | 0.156 | 0.15933 | 0.16267 | 0.166 | 0.16933 | 0.17267 | 0.176 | 0.17933 | 0.18267 | 0.186 | 0.18933 | 0.19267 | 0.196 | 0.1992 | 0.2024 | 0.2056 | 0.2088 | 0.212 | 0.2152 | 0.2184 | 0.2216 | 0.2248 | 0.228 | 0.2312 | 0.2344 | 0.2376 | 0.2408 | 0.244 | 0.2472 | 0.2504 | 0.2536 | 0.2568 | 0.26 | 0.2632 | 0.2664 | 0.2696 | 0.2728 | 0.276 | 0.2792 | 0.2824 | 0.2856 | 0.2888 | 0.292 | 0.2952 | 0.2984 | 0.3016 | 0.3048 | 0.308 | 0.3112 | 0.3144 | 0.3176 | 0.3208 | 0.324 | 0.3272 | 0.3304 | 0.3336 | 0.3368 | 0.34 | 0.3432 | 0.3464 | 0.3496 | 0.3528 | 0.356 | 0.3592 | 0.3624 | 0.3656 | 0.3688 | 0.372 | 0.3752 | 0.3784 | 0.3816 | 0.3848 | 0.388 | 0.38893 | 0.38987 | 0.3908 | 0.39173 | 0.39267 | 0.3936 | 0.39453 | 0.39547 | 0.3964 | 0.39733 | 0.39827 | 0.3992 | 0.40013 | 0.40107 | 0.402 | 0.40293 | 0.40387 | 0.4048 | 0.40573 | 0.40667 | 0.4076 | 0.40853 | 0.40947 | 0.4104 | 0.41133 | 0.41227 | 0.4132 | 0.41413 | 0.41507 | 0.416
1.45 | 0 | 0.108 | 0.126 | 0.117 | 0.09 | 0.099 | 0.108 | 0.2205 | 0.3285 | 0.4365 | 0.468 | 0 | 0.0108 | 0.0216 | 0.0324 | 0.0432 | 0.054 | 0.0648 | 0.0756 | 0.0864 | 0.0972 | 0.108 | 0.1116 | 0.1152 | 0.1188 | 0.1224 | 0.126 | 0.1242 | 0.1224 | 0.1206 | 0.1188 | 0.117 | 0.1143 | 0.1116 | 0.1089 | 0.1062 | 0.1035 | 0.1008 | 0.0981 | 0.0954 | 0.0927 | 0.09 | 0.0906 | 0.0912 | 0.0918 | 0.0924 | 0.093 | 0.0936 | 0.0942 | 0.0948 | 0.0954 | 0.096 | 0.0966 | 0.0972 | 0.0978 | 0.0984 | 0.099 | 0.0996 | 0.1002 | 0.1008 | 0.1014 | 0.102 | 0.1026 | 0.1032 | 0.1038 | 0.1044 | 0.105 | 0.1056 | 0.1062 | 0.1068 | 0.1074 | 0.108 | 0.11175 | 0.1155 | 0.11925 | 0.123 | 0.12675 | 0.1305 | 0.13425 | 0.138 | 0.14175 | 0.1455 | 0.14925 | 0.153 | 0.15675 | 0.1605 | 0.16425 | 0.168 | 0.17175 | 0.1755 | 0.17925 | 0.183 | 0.18675 | 0.1905 | 0.19425 | 0.198 | 0.20175 | 0.2055 | 0.20925 | 0.213 | 0.21675 | 0.2205 | 0.2241 | 0.2277 | 0.2313 | 0.2349 | 0.2385 | 0.2421 | 0.2457 | 0.2493 | 0.2529 | 0.2565 | 0.2601 | 0.2637 | 0.2673 | 0.2709 | 0.2745 | 0.2781 | 0.2817 | 0.2853 | 0.2889 | 0.2925 | 0.2961 | 0.2997 | 0.3033 | 0.3069 | 0.3105 | 0.3141 | 0.3177 | 0.3213 | 0.3249 | 0.3285 | 0.3321 | 0.3357 | 0.3393 | 0.3429 | 0.3465 | 0.3501 | 0.3537 | 0.3573 | 0.3609 | 0.3645 | 0.3681 | 0.3717 | 0.3753 | 0.3789 | 0.3825 | 0.3861 | 0.3897 | 0.3933 | 0.3969 | 0.4005 | 0.4041 | 0.4077 | 0.4113 | 0.4149 | 0.4185 | 0.4221 | 0.4257 | 0.4293 | 0.4329 | 0.4365 | 0.43755 | 0.4386 | 0.43965 | 0.4407 | 0.44175 | 0.4428 | 0.44385 | 0.4449 | 0.44595 | 0.447 | 0.44805 | 0.4491 | 0.45015 | 0.4512 | 0.45225 | 0.4533 | 0.45435 | 0.4554 | 0.45645 | 0.4575 | 0.45855 | 0.4596 | 0.46065 | 0.4617 | 0.46275 | 0.4638 | 0.46485 | 0.4659 | 0.46695 | 0.468
1.5 | 0 | 0.12 | 0.14 | 0.13 | 0.1 | 0.11 | 0.12 | 0.245 | 0.365 | 0.485 | 0.52 | 0 | 0.012 | 0.024 | 0.036 | 0.048 | 0.06 | 0.072 | 0.084 | 0.096 | 0.108 | 0.12 | 0.124 | 0.128 | 0.132 | 0.136 | 0.14 | 0.138 | 0.136 | 0.134 | 0.132 | 0.13 | 0.127 | 0.124 | 0.121 | 0.118 | 0.115 | 0.112 | 0.109 | 0.106 | 0.103 | 0.1 | 0.10067 | 0.10133 | 0.102 | 0.10267 | 0.10333 | 0.104 | 0.10467 | 0.10533 | 0.106 | 0.10667 | 0.10733 | 0.108 | 0.10867 | 0.10933 | 0.11 | 0.11067 | 0.11133 | 0.112 | 0.11267 | 0.11333 | 0.114 | 0.11467 | 0.11533 | 0.116 | 0.11667 | 0.11733 | 0.118 | 0.11867 | 0.11933 | 0.12 | 0.12417 | 0.12833 | 0.1325 | 0.13667 | 0.14083 | 0.145 | 0.14917 | 0.15333 | 0.1575 | 0.16167 | 0.16583 | 0.17 | 0.17417 | 0.17833 | 0.1825 | 0.18667 | 0.19083 | 0.195 | 0.19917 | 0.20333 | 0.2075 | 0.21167 | 0.21583 | 0.22 | 0.22417 | 0.22833 | 0.2325 | 0.23667 | 0.24083 | 0.245 | 0.249 | 0.253 | 0.257 | 0.261 | 0.265 | 0.269 | 0.273 | 0.277 | 0.281 | 0.285 | 0.289 | 0.293 | 0.297 | 0.301 | 0.305 | 0.309 | 0.313 | 0.317 | 0.321 | 0.325 | 0.329 | 0.333 | 0.337 | 0.341 | 0.345 | 0.349 | 0.353 | 0.357 | 0.361 | 0.365 | 0.369 | 0.373 | 0.377 | 0.381 | 0.385 | 0.389 | 0.393 | 0.397 | 0.401 | 0.405 | 0.409 | 0.413 | 0.417 | 0.421 | 0.425 | 0.429 | 0.433 | 0.437 | 0.441 | 0.445 | 0.449 | 0.453 | 0.457 | 0.461 | 0.465 | 0.469 | 0.473 | 0.477 | 0.481 | 0.485 | 0.48617 | 0.48733 | 0.4885 | 0.48967 | 0.49083 | 0.492 | 0.49317 | 0.49433 | 0.4955 | 0.49667 | 0.49783 | 0.499 | 0.50017 | 0.50133 | 0.5025 | 0.50367 | 0.50483 | 0.506 | 0.50717 | 0.50833 | 0.5095 | 0.51067 | 0.51183 | 0.513 | 0.51417 | 0.51533 | 0.5165 | 0.51767 | 0.51883 | 0.52
1.55 | 0 | 0.132 | 0.154 | 0.143 | 0.11 | 0.121 | 0.132 | 0.2695 | 0.4015 | 0.5335 | 0.572 | 0 | 0.0132 | 0.0264 | 0.0396 | 0.0528 | 0.066 | 0.0792 | 0.0924 | 0.1056 | 0.1188 | 0.132 | 0.1364 | 0.1408 | 0.1452 | 0.1496 | 0.154 | 0.1518 | 0.1496 | 0.1474 | 0.1452 | 0.143 | 0.1397 | 0.1364 | 0.1331 | 0.1298 | 0.1265 | 0.1232 | 0.1199 | 0.1166 | 0.1133 | 0.11 | 0.11073 | 0.11147 | 0.1122 | 0.11293 | 0.11367 | 0.1144 | 0.11513 | 0.11587 | 0.1166 | 0.11733 | 0.11807 | 0.1188 | 0.11953 | 0.12027 | 0.121 | 0.12173 | 0.12247 | 0.1232 | 0.12393 | 0.12467 | 0.1254 | 0.12613 | 0.12687 | 0.1276 | 0.12833 | 0.12907 | 0.1298 | 0.13053 | 0.13127 | 0.132 | 0.13658 | 0.14117 | 0.14575 | 0.15033 | 0.15492 | 0.1595 | 0.16408 | 0.16867 | 0.17325 | 0.17783 | 0.18242 | 0.187 | 0.19158 | 0.19617 | 0.20075 | 0.20533 | 0.20992 | 0.2145 | 0.21908 | 0.22367 | 0.22825 | 0.23283 | 0.23742 | 0.242 | 0.24658 | 0.25117 | 0.25575 | 0.26033 | 0.26492 | 0.2695 | 0.2739 | 0.2783 | 0.2827 | 0.2871 | 0.2915 | 0.2959 | 0.3003 | 0.3047 | 0.3091 | 0.3135 | 0.3179 | 0.3223 | 0.3267 | 0.3311 | 0.3355 | 0.3399 | 0.3443 | 0.3487 | 0.3531 | 0.3575 | 0.3619 | 0.3663 | 0.3707 | 0.3751 | 0.3795 | 0.3839 | 0.3883 | 0.3927 | 0.3971 | 0.4015 | 0.4059 | 0.4103 | 0.4147 | 0.4191 | 0.4235 | 0.4279 | 0.4323 | 0.4367 | 0.4411 | 0.4455 | 0.4499 | 0.4543 | 0.4587 | 0.4631 | 0.4675 | 0.4719 | 0.4763 | 0.4807 | 0.4851 | 0.4895 | 0.4939 | 0.4983 | 0.5027 | 0.5071 | 0.5115 | 0.5159 | 0.5203 | 0.5247 | 0.5291 | 0.5335 | 0.53478 | 0.53607 | 0.53735 | 0.53863 | 0.53992 | 0.5412 | 0.54248 | 0.54377 | 0.54505 | 0.54633 | 0.54762 | 0.5489 | 0.55018 | 0.55147 | 0.55275 | 0.55403 | 0.55532 | 0.5566 | 0.55788 | 0.55917 | 0.56045 | 0.56173 | 0.56302 | 0.5643 | 0.56558 | 0.56687 | 0.56815 | 0.56943 | 0.57072 | 0.572
1.6 | 0 | 0.144 | 0.168 | 0.156 | 0.12 | 0.132 | 0.144 | 0.294 | 0.438 | 0.582 | 0.624 | 0 | 0.0144 | 0.0288 | 0.0432 | 0.0576 | 0.072 | 0.0864 | 0.1008 | 0.1152 | 0.1296 | 0.144 | 0.1488 | 0.1536 | 0.1584 | 0.1632 | 0.168 | 0.1656 | 0.1632 | 0.1608 | 0.1584 | 0.156 | 0.1524 | 0.1488 | 0.1452 | 0.1416 | 0.138 | 0.1344 | 0.1308 | 0.1272 | 0.1236 | 0.12 | 0.1208 | 0.1216 | 0.1224 | 0.1232 | 0.124 | 0.1248 | 0.1256 | 0.1264 | 0.1272 | 0.128 | 0.1288 | 0.1296 | 0.1304 | 0.1312 | 0.132 | 0.1328 | 0.1336 | 0.1344 | 0.1352 | 0.136 | 0.1368 | 0.1376 | 0.1384 | 0.1392 | 0.14 | 0.1408 | 0.1416 | 0.1424 | 0.1432 | 0.144 | 0.149 | 0.154 | 0.159 | 0.164 | 0.169 | 0.174 | 0.179 | 0.184 | 0.189 | 0.194 | 0.199 | 0.204 | 0.209 | 0.214 | 0.219 | 0.224 | 0.229 | 0.234 | 0.239 | 0.244 | 0.249 | 0.254 | 0.259 | 0.264 | 0.269 | 0.274 | 0.279 | 0.284 | 0.289 | 0.294 | 0.2988 | 0.3036 | 0.3084 | 0.3132 | 0.318 | 0.3228 | 0.3276 | 0.3324 | 0.3372 | 0.342 | 0.3468 | 0.3516 | 0.3564 | 0.3612 | 0.366 | 0.3708 | 0.3756 | 0.3804 | 0.3852 | 0.39 | 0.3948 | 0.3996 | 0.4044 | 0.4092 | 0.414 | 0.4188 | 0.4236 | 0.4284 | 0.4332 | 0.438 | 0.4428 | 0.4476 | 0.4524 | 0.4572 | 0.462 | 0.4668 | 0.4716 | 0.4764 | 0.4812 | 0.486 | 0.4908 | 0.4956 | 0.5004 | 0.5052 | 0.51 | 0.5148 | 0.5196 | 0.5244 | 0.5292 | 0.534 | 0.5388 | 0.5436 | 0.5484 | 0.5532 | 0.558 | 0.5628 | 0.5676 | 0.5724 | 0.5772 | 0.582 | 0.5834 | 0.5848 | 0.5862 | 0.5876 | 0.589 | 0.5904 | 0.5918 | 0.5932 | 0.5946 | 0.596 | 0.5974 | 0.5988 | 0.6002 | 0.6016 | 0.603 | 0.6044 | 0.6058 | 0.6072 | 0.6086 | 0.61 | 0.6114 | 0.6128 | 0.6142 | 0.6156 | 0.617 | 0.6184 | 0.6198 | 0.6212 | 0.6226 | 0.624
1.65 | 0 | 0.156 | 0.182 | 0.169 | 0.13 | 0.143 | 0.156 | 0.3185 | 0.4745 | 0.6305 | 0.676 | 0 | 0.0156 | 0.0312 | 0.0468 | 0.0624 | 0.078 | 0.0936 | 0.1092 | 0.1248 | 0.1404 | 0.156 | 0.1612 | 0.1664 | 0.1716 | 0.1768 | 0.182 | 0.1794 | 0.1768 | 0.1742 | 0.1716 | 0.169 | 0.1651 | 0.1612 | 0.1573 | 0.1534 | 0.1495 | 0.1456 | 0.1417 | 0.1378 | 0.1339 | 0.13 | 0.13087 | 0.13173 | 0.1326 | 0.13347 | 0.13433 | 0.1352 | 0.13607 | 0.13693 | 0.1378 | 0.13867 | 0.13953 | 0.1404 | 0.14127 | 0.14213 | 0.143 | 0.14387 | 0.14473 | 0.1456 | 0.14647 | 0.14733 | 0.1482 | 0.14907 | 0.14993 | 0.1508 | 0.15167 | 0.15253 | 0.1534 | 0.15427 | 0.15513 | 0.156 | 0.16142 | 0.16683 | 0.17225 | 0.17767 | 0.18308 | 0.1885 | 0.19392 | 0.19933 | 0.20475 | 0.21017 | 0.21558 | 0.221 | 0.22642 | 0.23183 | 0.23725 | 0.24267 | 0.24808 | 0.2535 | 0.25892 | 0.26433 | 0.26975 | 0.27517 | 0.28058 | 0.286 | 0.29142 | 0.29683 | 0.30225 | 0.30767 | 0.31308 | 0.3185 | 0.3237 | 0.3289 | 0.3341 | 0.3393 | 0.3445 | 0.3497 | 0.3549 | 0.3601 | 0.3653 | 0.3705 | 0.3757 | 0.3809 | 0.3861 | 0.3913 | 0.3965 | 0.4017 | 0.4069 | 0.4121 | 0.4173 | 0.4225 | 0.4277 | 0.4329 | 0.4381 | 0.4433 | 0.4485 | 0.4537 | 0.4589 | 0.4641 | 0.4693 | 0.4745 | 0.4797 | 0.4849 | 0.4901 | 0.4953 | 0.5005 | 0.5057 | 0.5109 | 0.5161 | 0.5213 | 0.5265 | 0.5317 | 0.5369 | 0.5421 | 0.5473 | 0.5525 | 0.5577 | 0.5629 | 0.5681 | 0.5733 | 0.5785 | 0.5837 | 0.5889 | 0.5941 | 0.5993 | 0.6045 | 0.6097 | 0.6149 | 0.6201 | 0.6253 | 0.6305 | 0.63202 | 0.63353 | 0.63505 | 0.63657 | 0.63808 | 0.6396 | 0.64112 | 0.64263 | 0.64415 | 0.64567 | 0.64718 | 0.6487 | 0.65022 | 0.65173 | 0.65325 | 0.65477 | 0.65628 | 0.6578 | 0.65932 | 0.66083 | 0.66235 | 0.66387 | 0.66538 | 0.6669 | 0.66842 | 0.66993 | 0.67145 | 0.67297 | 0.67448 | 0.676
1.7 | 0 | 0.168 | 0.196 | 0.182 | 0.14 | 0.154 | 0.168 | 0.343 | 0.511 | 0.679 | 0.728 | 1.3878e-17 | 0.0168 | 0.0336 | 0.0504 | 0.0672 | 0.084 | 0.1008 | 0.1176 | 0.1344 | 0.1512 | 0.168 | 0.1736 | 0.1792 | 0.1848 | 0.1904 | 0.196 | 0.1932 | 0.1904 | 0.1876 | 0.1848 | 0.182 | 0.1778 | 0.1736 | 0.1694 | 0.1652 | 0.161 | 0.1568 | 0.1526 | 0.1484 | 0.1442 | 0.14 | 0.14093 | 0.14187 | 0.1428 | 0.14373 | 0.14467 | 0.1456 | 0.14653 | 0.14747 | 0.1484 | 0.14933 | 0.15027 | 0.1512 | 0.15213 | 0.15307 | 0.154 | 0.15493 | 0.15587 | 0.1568 | 0.15773 | 0.15867 | 0.1596 | 0.16053 | 0.16147 | 0.1624 | 0.16333 | 0.16427 | 0.1652 | 0.16613 | 0.16707 | 0.168 | 0.17383 | 0.17967 | 0.1855 | 0.19133 | 0.19717 | 0.203 | 0.20883 | 0.21467 | 0.2205 | 0.22633 | 0.23217 | 0.238 | 0.24383 | 0.24967 | 0.2555 | 0.26133 | 0.26717 | 0.273 | 0.27883 | 0.28467 | 0.2905 | 0.29633 | 0.30217 | 0.308 | 0.31383 | 0.31967 | 0.3255 | 0.33133 | 0.33717 | 0.343 | 0.3486 | 0.3542 | 0.3598 | 0.3654 | 0.371 | 0.3766 | 0.3822 | 0.3878 | 0.3934 | 0.399 | 0.4046 | 0.4102 | 0.4158 | 0.4214 | 0.427 | 0.4326 | 0.4382 | 0.4438 | 0.4494 | 0.455 | 0.4606 | 0.4662 | 0.4718 | 0.4774 | 0.483 | 0.4886 | 0.4942 | 0.4998 | 0.5054 | 0.511 | 0.5166 | 0.5222 | 0.5278 | 0.5334 | 0.539 | 0.5446 | 0.5502 | 0.5558 | 0.5614 | 0.567 | 0.5726 | 0.5782 | 0.5838 | 0.5894 | 0.595 | 0.6006 | 0.6062 | 0.6118 | 0.6174 | 0.623 | 0.6286 | 0.6342 | 0.6398 | 0.6454 | 0.651 | 0.6566 | 0.6622 | 0.6678 | 0.6734 | 0.679 | 0.68063 | 0.68227 | 0.6839 | 0.68553 | 0.68717 | 0.6888 | 0.69043 | 0.69207 | 0.6937 | 0.69533 | 0.69697 | 0.6986 | 0.70023 | 0.70187 | 0.7035 | 0.70513 | 0.70677 | 0.7084 | 0.71003 | 0.71167 | 0.7133 | 0.71493 | 0.71657 | 0.7182 | 0.71983 | 0.72147 | 0.7231 | 0.72473 | 0.72637 | 0.728
1.75 | 0 | 0.18 | 0.21 | 0.195 | 0.15 | 0.165 | 0.18 | 0.3675 | 0.5475 | 0.7275 | 0.78 | 0 | 0.018 | 0.036 | 0.054 | 0.072 | 0.09 | 0.108 | 0.126 | 0.144 | 0.162 | 0.18 | 0.186 | 0.192 | 0.198 | 0.204 | 0.21 | 0.207 | 0.204 | 0.201 | 0.198 | 0.195 | 0.1905 | 0.186 | 0.1815 | 0.177 | 0.1725 | 0.168 | 0.1635 | 0.159 | 0.1545 | 0.15 | 0.151 | 0.152 | 0.153 | 0.154 | 0.155 | 0.156 | 0.157 | 0.158 | 0.159 | 0.16 | 0.161 | 0.162 | 0.163 | 0.164 | 0.165 | 0.166 | 0.167 | 0.168 | 0.169 | 0.17 | 0.171 | 0.172 | 0.173 | 0.174 | 0.175 | 0.176 | 0.177 | 0.178 | 0.179 | 0.18 | 0.18625 | 0.1925 | 0.19875 | 0.205 | 0.21125 | 0.2175 | 0.22375 | 0.23 | 0.23625 | 0.2425 | 0.24875 | 0.255 | 0.26125 | 0.2675 | 0.27375 | 0.28 | 0.28625 | 0.2925 | 0.29875 | 0.305 | 0.31125 | 0.3175 | 0.32375 | 0.33 | 0.33625 | 0.3425 | 0.34875 | 0.355 | 0.36125 | 0.3675 | 0.3735 | 0.3795 | 0.3855 | 0.3915 | 0.3975 | 0.4035 | 0.4095 | 0.4155 | 0.4215 | 0.4275 | 0.4335 | 0.4395 | 0.4455 | 0.4515 | 0.4575 | 0.4635 | 0.4695 | 0.4755 | 0.4815 | 0.4875 | 0.4935 | 0.4995 | 0.5055 | 0.5115 | 0.5175 | 0.5235 | 0.5295 | 0.5355 | 0.5415 | 0.5475 | 0.5535 | 0.5595 | 0.5655 | 0.5715 | 0.5775 | 0.5835 | 0.5895 | 0.5955 | 0.6015 | 0.6075 | 0.6135 | 0.6195 | 0.6255 | 0.6315 | 0.6375 | 0.6435 | 0.6495 | 0.6555 | 0.6615 | 0.6675 | 0.6735 | 0.6795 | 0.6855 | 0.6915 | 0.6975 | 0.7035 | 0.7095 | 0.7155 | 0.7215 | 0.7275 | 0.72925 | 0.731 | 0.73275 | 0.7345 | 0.73625 | 0.738 | 0.73975 | 0.7415 | 0.74325 | 0.745 | 0.74675 | 0.7485 | 0.75025 | 0.752 | 0.75375 | 0.7555 | 0.75725 | 0.759 | 0.76075 | 0.7625 | 0.76425 | 0.766 | 0.76775 | 0.7695 | 0.77125 | 0.773 | 0.77475 | 0.7765 | 0.77825 | 0.78
1.8 | 0 | 0.192 | 0.224 | 0.208 | 0.16 | 0.176 | 0.192 | 0.392 | 0.584 | 0.776 | 0.832 | 1.3878e-17 | 0.0192 | 0.0384 | 0.0576 | 0.0768 | 0.096 | 0.1152 | 0.1344 | 0.1536 | 0.1728 | 0.192 | 0.1984 | 0.2048 | 0.2112 | 0.2176 | 0.224 | 0.2208 | 0.2176 | 0.2144 | 0.2112 | 0.208 | 0.2032 | 0.1984 | 0.1936 | 0.1888 | 0.184 | 0.1792 | 0.1744 | 0.1696 | 0.1648 | 0.16 | 0.16107 | 0.16213 | 0.1632 | 0.16427 | 0.16533 | 0.1664 | 0.16747 | 0.16853 | 0.1696 | 0.17067 | 0.17173 | 0.1728 | 0.17387 | 0.17493 | 0.176 | 0.17707 | 0.17813 | 0.1792 | 0.18027 | 0.18133 | 0.1824 | 0.18347 | 0.18453 | 0.1856 | 0.18667 | 0.18773 | 0.1888 | 0.18987 | 0.19093 | 0.192 | 0.19867 | 0.20533 | 0.212 | 0.21867 | 0.22533 | 0.232 | 0.23867 | 0.24533 | 0.252 | 0.25867 | 0.26533 | 0.272 | 0.27867 | 0.28533 | 0.292 | 0.29867 | 0.30533 | 0.312 | 0.31867 | 0.32533 | 0.332 | 0.33867 | 0.34533 | 0.352 | 0.35867 | 0.36533 | 0.372 | 0.37867 | 0.38533 | 0.392 | 0.3984 | 0.4048 | 0.4112 | 0.4176 | 0.424 | 0.4304 | 0.4368 | 0.4432 | 0.4496 | 0.456 | 0.4624 | 0.4688 | 0.4752 | 0.4816 | 0.488 | 0.4944 | 0.5008 | 0.5072 | 0.5136 | 0.52 | 0.5264 | 0.5328 | 0.5392 | 0.5456 | 0.552 | 0.5584 | 0.5648 | 0.5712 | 0.5776 | 0.584 | 0.5904 | 0.5968 | 0.6032 | 0.6096 | 0.616 | 0.6224 | 0.6288 | 0.6352 | 0.6416 | 0.648 | 0.6544 | 0.6608 | 0.6672 | 0.6736 | 0.68 | 0.6864 | 0.6928 | 0.6992 | 0.7056 | 0.712 | 0.7184 | 0.7248 | 0.7312 | 0.7376 | 0.744 | 0.7504 | 0.7568 | 0.7632 | 0.7696 | 0.776 | 0.77787 | 0.77973 | 0.7816 | 0.78347 | 0.78533 | 0.7872 | 0.78907 | 0.79093 | 0.7928 | 0.79467 | 0.79653 | 0.7984 | 0.80027 | 0.80213 | 0.804 | 0.80587 | 0.80773 | 0.8096 | 0.81147 | 0.81333 | 0.8152 | 0.81707 | 0.81893 | 0.8208 | 0.82267 | 0.82453 | 0.8264 | 0.82827 | 0.83013 | 0.832
1.85 | 0 | 0.204 | 0.238 | 0.221 | 0.17 | 0.187 | 0.204 | 0.4165 | 0.6205 | 0.8245 | 0.884 | 0 | 0.0204 | 0.0408 | 0.0612 | 0.0816 | 0.102 | 0.1224 | 0.1428 | 0.1632 | 0.1836 | 0.204 | 0.2108 | 0.2176 | 0.2244 | 0.2312 | 0.238 | 0.2346 | 0.2312 | 0.2278 | 0.2244 | 0.221 | 0.2159 | 0.2108 | 0.2057 | 0.2006 | 0.1955 | 0.1904 | 0.1853 | 0.1802 | 0.1751 | 0.17 | 0.17113 | 0.17227 | 0.1734 | 0.17453 | 0.17567 | 0.1768 | 0.17793 | 0.17907 | 0.1802 | 0.18133 | 0.18247 | 0.1836 | 0.18473 | 0.18587 | 0.187 | 0.18813 | 0.18927 | 0.1904 | 0.19153 | 0.19267 | 0.1938 | 0.19493 | 0.19607 | 0.1972 | 0.19833 | 0.19947 | 0.2006 | 0.20173 | 0.20287 | 0.204 | 0.21108 | 0.21817 | 0.22525 | 0.23233 | 0.23942 | 0.2465 | 0.25358 | 0.26067 | 0.26775 | 0.27483 | 0.28192 | 0.289 | 0.29608 | 0.30317 | 0.31025 | 0.31733 | 0.32442 | 0.3315 | 0.33858 | 0.34567 | 0.35275 | 0.35983 | 0.36692 | 0.374 | 0.38108 | 0.38817 | 0.39525 | 0.40233 | 0.40942 | 0.4165 | 0.4233 | 0.4301 | 0.4369 | 0.4437 | 0.4505 | 0.4573 | 0.4641 | 0.4709 | 0.4777 | 0.4845 | 0.4913 | 0.4981 | 0.5049 | 0.5117 | 0.5185 | 0.5253 | 0.5321 | 0.5389 | 0.5457 | 0.5525 | 0.5593 | 0.5661 | 0.5729 | 0.5797 | 0.5865 | 0.5933 | 0.6001 | 0.6069 | 0.6137 | 0.6205 | 0.6273 | 0.6341 | 0.6409 | 0.6477 | 0.6545 | 0.6613 | 0.6681 | 0.6749 | 0.6817 | 0.6885 | 0.6953 | 0.7021 | 0.7089 | 0.7157 | 0.7225 | 0.7293 | 0.7361 | 0.7429 | 0.7497 | 0.7565 | 0.7633 | 0.7701 | 0.7769 | 0.7837 | 0.7905 | 0.7973 | 0.8041 | 0.8109 | 0.8177 | 0.8245 | 0.82648 | 0.82847 | 0.83045 | 0.83243 | 0.83442 | 0.8364 | 0.83838 | 0.84037 | 0.84235 | 0.84433 | 0.84632 | 0.8483 | 0.85028 | 0.85227 | 0.85425 | 0.85623 | 0.85822 | 0.8602 | 0.86218 | 0.86417 | 0.86615 | 0.86813 | 0.87012 | 0.8721 | 0.87408 | 0.87607 | 0.87805 | 0.88003 | 0.88202 | 0.884
1.9 | 0 | 0.216 | 0.252 | 0.234 | 0.18 | 0.198 | 0.216 | 0.441 | 0.657 | 0.873 | 0.936 | 0 | 0.0216 | 0.0432 | 0.0648 | 0.0864 | 0.108 | 0.1296 | 0.1512 | 0.1728 | 0.1944 | 0.216 | 0.2232 | 0.2304 | 0.2376 | 0.2448 | 0.252 | 0.2484 | 0.2448 | 0.2412 | 0.2376 | 0.234 | 0.2286 | 0.2232 | 0.2178 | 0.2124 | 0.207 | 0.2016 | 0.1962 | 0.1908 | 0.1854 | 0.18 | 0.1812 | 0.1824 | 0.1836 | 0.1848 | 0.186 | 0.1872 | 0.1884 | 0.1896 | 0.1908 | 0.192 | 0.1932 | 0.1944 | 0.1956 | 0.1968 | 0.198 | 0.1992 | 0.2004 | 0.2016 | 0.2028 | 0.204 | 0.2052 | 0.2064 | 0.2076 | 0.2088 | 0.21 | 0.2112 | 0.2124 | 0.2136 | 0.2148 | 0.216 | 0.2235 | 0.231 | 0.2385 | 0.246 | 0.2535 | 0.261 | 0.2685 | 0.276 | 0.2835 | 0.291 | 0.2985 | 0.306 | 0.3135 | 0.321 | 0.3285 | 0.336 | 0.3435 | 0.351 | 0.3585 | 0.366 | 0.3735 | 0.381 | 0.3885 | 0.396 | 0.4035 | 0.411 | 0.4185 | 0.426 | 0.4335 | 0.441 | 0.4482 | 0.4554 | 0.4626 | 0.4698 | 0.477 | 0.4842 | 0.4914 | 0.4986 | 0.5058 | 0.513 | 0.5202 | 0.5274 | 0.5346 | 0.5418 | 0.549 | 0.5562 | 0.5634 | 0.5706 | 0.5778 | 0.585 | 0.5922 | 0.5994 | 0.6066 | 0.6138 | 0.621 | 0.6282 | 0.6354 | 0.6426 | 0.6498 | 0.657 | 0.6642 | 0.6714 | 0.6786 | 0.6858 | 0.693 | 0.7002 | 0.7074 | 0.7146 | 0.7218 | 0.729 | 0.7362 | 0.7434 | 0.7506 | 0.7578 | 0.765 | 0.7722 | 0.7794 | 0.7866 | 0.7938 | 0.801 | 0.8082 | 0.8154 | 0.8226 | 0.8298 | 0.837 | 0.8442 | 0.8514 | 0.8586 | 0.8658 | 0.873 | 0.8751 | 0.8772 | 0.8793 | 0.8814 | 0.8835 | 0.8856 | 0.8877 | 0.8898 | 0.8919 | 0.894 | 0.8961 | 0.8982 | 0.9003 | 0.9024 | 0.9045 | 0.9066 | 0.9087 | 0.9108 | 0.9129 | 0.915 | 0.9171 | 0.9192 | 0.9213 | 0.9234 | 0.9255 | 0.9276 | 0.9297 | 0.9318 | 0.9339 | 0.936
1.95 | 0 | 0.228 | 0.266 | 0.247 | 0.19 | 0.209 | 0.228 | 0.4655 | 0.6935 | 0.9215 | 0.988 | 0 | 0.0228 | 0.0456 | 0.0684 | 0.0912 | 0.114 | 0.1368 | 0.1596 | 0.1824 | 0.2052 | 0.228 | 0.2356 | 0.2432 | 0.2508 | 0.2584 | 0.266 | 0.2622 | 0.2584 | 0.2546 | 0.2508 | 0.247 | 0.2413 | 0.2356 | 0.2299 | 0.2242 | 0.2185 | 0.2128 | 0.2071 | 0.2014 | 0.1957 | 0.19 | 0.19127 | 0.19253 | 0.1938 | 0.19507 | 0.19633 | 0.1976 | 0.19887 | 0.20013 | 0.2014 | 0.20267 | 0.20393 | 0.2052 | 0.20647 | 0.20773 | 0.209 | 0.21027 | 0.21153 | 0.2128 | 0.21407 | 0.21533 | 0.2166 | 0.21787 | 0.21913 | 0.2204 | 0.22167 | 0.22293 | 0.2242 | 0.22547 | 0.22673 | 0.228 | 0.23592 | 0.24383 | 0.25175 | 0.25967 | 0.26758 | 0.2755 | 0.28342 | 0.29133 | 0.29925 | 0.30717 | 0.31508 | 0.323 | 0.33092 | 0.33883 | 0.34675 | 0.35467 | 0.36258 | 0.3705 | 0.37842 | 0.38633 | 0.39425 | 0.40217 | 0.41008 | 0.418 | 0.42592 | 0.43383 | 0.44175 | 0.44967 | 0.45758 | 0.4655 | 0.4731 | 0.4807 | 0.4883 | 0.4959 | 0.5035 | 0.5111 | 0.5187 | 0.5263 | 0.5339 | 0.5415 | 0.5491 | 0.5567 | 0.5643 | 0.5719 | 0.5795 | 0.5871 | 0.5947 | 0.6023 | 0.6099 | 0.6175 | 0.6251 | 0.6327 | 0.6403 | 0.6479 | 0.6555 | 0.6631 | 0.6707 | 0.6783 | 0.6859 | 0.6935 | 0.7011 | 0.7087 | 0.7163 | 0.7239 | 0.7315 | 0.7391 | 0.7467 | 0.7543 | 0.7619 | 0.7695 | 0.7771 | 0.7847 | 0.7923 | 0.7999 | 0.8075 | 0.8151 | 0.8227 | 0.8303 | 0.8379 | 0.8455 | 0.8531 | 0.8607 | 0.8683 | 0.8759 | 0.8835 | 0.8911 | 0.8987 | 0.9063 | 0.9139 | 0.9215 | 0.92372 | 0.92593 | 0.92815 | 0.93037 | 0.93258 | 0.9348 | 0.93702 | 0.93923 | 0.94145 | 0.94367 | 0.94588 | 0.9481 | 0.95032 | 0.95253 | 0.95475 | 0.95697 | 0.95918 | 0.9614 | 0.96362 | 0.96583 | 0.96805 | 0.97027 | 0.97248 | 0.9747 | 0.97692 | 0.97913 | 0.98135 | 0.98357 | 0.98578 | 0.988
2 | 0 | 0.24 | 0.28 | 0.26 | 0.2 | 0.22 | 0.24 | 0.49 | 0.73 | 0.97 | 1.04 | 0 | 0.024 | 0.048 | 0.072 | 0.096 | 0.12 | 0.144 | 0.168 | 0.192 | 0.216 | 0.24 | 0.248 | 0.256 | 0.264 | 0.272 | 0.28 | 0.276 | 0.272 | 0.268 | 0.264 | 0.26 | 0.254 | 0.248 | 0.242 | 0.236 | 0.23 | 0.224 | 0.218 | 0.212 | 0.206 | 0.2 | 0.20133 | 0.20267 | 0.204 | 0.20533 | 0.20667 | 0.208 | 0.20933 | 0.21067 | 0.212 | 0.21333 | 0.21467 | 0.216 | 0.21733 | 0.21867 | 0.22 | 0.22133 | 0.22267 | 0.224 | 0.22533 | 0.22667 | 0.228 | 0.22933 | 0.23067 | 0.232 | 0.23333 | 0.23467 | 0.236 | 0.23733 | 0.23867 | 0.24 | 0.24833 | 0.25667 | 0.265 | 0.27333 | 0.28167 | 0.29 | 0.29833 | 0.30667 | 0.315 | 0.32333 | 0.33167 | 0.34 | 0.34833 | 0.35667 | 0.365 | 0.37333 | 0.38167 | 0.39 | 0.39833 | 0.40667 | 0.415 | 0.42333 | 0.43167 | 0.44 | 0.44833 | 0.45667 | 0.465 | 0.47333 | 0.48167 | 0.49 | 0.498 | 0.506 | 0.514 | 0.522 | 0.53 | 0.538 | 0.546 | 0.554 | 0.562 | 0.57 | 0.578 | 0.586 | 0.594 | 0.602 | 0.61 | 0.618 | 0.626 | 0.634 | 0.642 | 0.65 | 0.658 | 0.666 | 0.674 | 0.682 | 0.69 | 0.698 | 0.706 | 0.714 | 0.722 | 0.73 | 0.738 | 0.746 | 0.754 | 0.762 | 0.77 | 0.778 | 0.786 | 0.794 | 0.802 | 0.81 | 0.818 | 0.826 | 0.834 | 0.842 | 0.85 | 0.858 | 0.866 | 0.874 | 0.882 | 0.89 | 0.898 | 0.906 | 0.914 | 0.922 | 0.93 | 0.938 | 0.946 | 0.954 | 0.962 | 0.97 | 0.97233 | 0.97467 | 0.977 | 0.97933 | 0.98167 | 0.984 | 0.98633 | 0.98867 | 0.991 | 0.99333 | 0.99567 | 0.998 | 1.0003 | 1.0027 | 1.005 | 1.0073 | 1.0097 | 1.012 | 1.0143 | 1.0167 | 1.019 | 1.0213 | 1.0237 | 1.026 | 1.0283 | 1.0307 | 1.033 | 1.0353 | 1.0377 | 1.04
2.05 | 0 | 0.25625 | 0.2925 | 0.27325 | 0.2125 | 0.2365 | 0.262 | 0.54575 | 0.82 | 1.0862 | 1.1785 | 0 | 0.025625 | 0.05125 | 0.076875 | 0.1025 | 0.12812 | 0.15375 | 0.17937 | 0.205 | 0.23062 | 0.25625 | 0.2635 | 0.27075 | 0.278 | 0.28525 | 0.2925 | 0.28865 | 0.2848 | 0.28095 | 0.2771 | 0.27325 | 0.26717 | 0.2611 | 0.25502 | 0.24895 | 0.24287 | 0.2368 | 0.23072 | 0.22465 | 0.21857 | 0.2125 | 0.2141 | 0.2157 | 0.2173 | 0.2189 | 0.2205 | 0.2221 | 0.2237 | 0.2253 | 0.2269 | 0.2285 | 0.2301 | 0.2317 | 0.2333 | 0.2349 | 0.2365 | 0.2382 | 0.2399 | 0.2416 | 0.2433 | 0.245 | 0.2467 | 0.2484 | 0.2501 | 0.2518 | 0.2535 | 0.2552 | 0.2569 | 0.2586 | 0.2603 | 0.262 | 0.27146 | 0.28092 | 0.29037 | 0.29983 | 0.30929 | 0.31875 | 0.32821 | 0.33767 | 0.34712 | 0.35658 | 0.36604 | 0.3755 | 0.38496 | 0.39442 | 0.40387 | 0.41333 | 0.42279 | 0.43225 | 0.44171 | 0.45117 | 0.46062 | 0.47008 | 0.47954 | 0.489 | 0.49846 | 0.50792 | 0.51737 | 0.52683 | 0.53629 | 0.54575 | 0.55489 | 0.56403 | 0.57317 | 0.58232 | 0.59146 | 0.6006 | 0.60974 | 0.61888 | 0.62802 | 0.63717 | 0.64631 | 0.65545 | 0.66459 | 0.67373 | 0.68287 | 0.69202 | 0.70116 | 0.7103 | 0.71944 | 0.72858 | 0.73772 | 0.74687 | 0.75601 | 0.76515 | 0.77429 | 0.78343 | 0.79257 | 0.80172 | 0.81086 | 0.82 | 0.82887 | 0.83775 | 0.84662 | 0.8555 | 0.86437 | 0.87325 | 0.88212 | 0.891 | 0.89987 | 0.90875 | 0.91762 | 0.9265 | 0.93537 | 0.94425 | 0.95312 | 0.962 | 0.97087 | 0.97975 | 0.98862 | 0.9975 | 1.0064 | 1.0152 | 1.0241 | 1.033 | 1.0419 | 1.0507 | 1.0596 | 1.0685 | 1.0774 | 1.0862 | 1.0893 | 1.0924 | 1.0955 | 1.0985 | 1.1016 | 1.1047 | 1.1078 | 1.1108 | 1.1139 | 1.117 | 1.1201 | 1.1231 | 1.1262 | 1.1293 | 1.1324 | 1.1354 | 1.1385 | 1.1416 | 1.1447 | 1.1477 | 1.1508 | 1.1539 | 1.157 | 1.16 | 1.1631 | 1.1662 | 1.1693 | 1.1723 | 1.1754 | 1.1785
2.1 | 0 | 0.2725 | 0.305 | 0.2865 | 0.225 | 0.253 | 0.284 | 0.6015 | 0.91 | 1.2025 | 1.317 | 0 | 0.02725 | 0.0545 | 0.08175 | 0.109 | 0.13625 | 0.1635 | 0.19075 | 0.218 | 0.24525 | 0.2725 | 0.279 | 0.2855 | 0.292 | 0.2985 | 0.305 | 0.3013 | 0.2976 | 0.2939 | 0.2902 | 0.2865 | 0.28035 | 0.2742 | 0.26805 | 0.2619 | 0.25575 | 0.2496 | 0.24345 | 0.2373 | 0.23115 | 0.225 | 0.22687 | 0.22873 | 0.2306 | 0.23247 | 0.23433 | 0.2362 | 0.23807 | 0.23993 | 0.2418 | 0.24367 | 0.24553 | 0.2474 | 0.24927 | 0.25113 | 0.253 | 0.25507 | 0.25713 | 0.2592 | 0.26127 | 0.26333 | 0.2654 | 0.26747 | 0.26953 | 0.2716 | 0.27367 | 0.27573 | 0.2778 | 0.27987 | 0.28193 | 0.284 | 0.29458 | 0.30517 | 0.31575 | 0.32633 | 0.33692 | 0.3475 | 0.35808 | 0.36867 | 0.37925 | 0.38983 | 0.40042 | 0.411 | 0.42158 | 0.43217 | 0.44275 | 0.45333 | 0.46392 | 0.4745 | 0.48508 | 0.49567 | 0.50625 | 0.51683 | 0.52742 | 0.538 | 0.54858 | 0.55917 | 0.56975 | 0.58033 | 0.59092 | 0.6015 | 0.61178 | 0.62207 | 0.63235 | 0.64263 | 0.65292 | 0.6632 | 0.67348 | 0.68377 | 0.69405 | 0.70433 | 0.71462 | 0.7249 | 0.73518 | 0.74547 | 0.75575 | 0.76603 | 0.77632 | 0.7866 | 0.79688 | 0.80717 | 0.81745 | 0.82773 | 0.83802 | 0.8483 | 0.85858 | 0.86887 | 0.87915 | 0.88943 | 0.89972 | 0.91 | 0.91975 | 0.9295 | 0.93925 | 0.949 | 0.95875 | 0.9685 | 0.97825 | 0.988 | 0.99775 | 1.0075 | 1.0172 | 1.027 | 1.0367 | 1.0465 | 1.0562 | 1.066 | 1.0757 | 1.0855 | 1.0952 | 1.105 | 1.1147 | 1.1245 | 1.1342 | 1.144 | 1.1537 | 1.1635 | 1.1732 | 1.183 | 1.1927 | 1.2025 | 1.2063 | 1.2101 | 1.2139 | 1.2178 | 1.2216 | 1.2254 | 1.2292 | 1.233 | 1.2368 | 1.2407 | 1.2445 | 1.2483 | 1.2521 | 1.2559 | 1.2597 | 1.2636 | 1.2674 | 1.2712 | 1.275 | 1.2788 | 1.2827 | 1.2865 | 1.2903 | 1.2941 | 1.2979 | 1.3017 | 1.3056 | 1.3094 | 1.3132 | 1.317
2.15 | 0 | 0.28875 | 0.3175 | 0.29975 | 0.2375 | 0.2695 | 0.306 | 0.65725 | 1 | 1.3187 | 1.4555 | 0 | 0.028875 | 0.05775 | 0.086625 | 0.1155 | 0.14437 | 0.17325 | 0.20212 | 0.231 | 0.25987 | 0.28875 | 0.2945 | 0.30025 | 0.306 | 0.31175 | 0.3175 | 0.31395 | 0.3104 | 0.30685 | 0.3033 | 0.29975 | 0.29352 | 0.2873 | 0.28107 | 0.27485 | 0.26862 | 0.2624 | 0.25617 | 0.24995 | 0.24372 | 0.2375 | 0.23963 | 0.24177 | 0.2439 | 0.24603 | 0.24817 | 0.2503 | 0.25243 | 0.25457 | 0.2567 | 0.25883 | 0.26097 | 0.2631 | 0.26523 | 0.26737 | 0.2695 | 0.27193 | 0.27437 | 0.2768 | 0.27923 | 0.28167 | 0.2841 | 0.28653 | 0.28897 | 0.2914 | 0.29383 | 0.29627 | 0.2987 | 0.30113 | 0.30357 | 0.306 | 0.31771 | 0.32942 | 0.34112 | 0.35283 | 0.36454 | 0.37625 | 0.38796 | 0.39967 | 0.41137 | 0.42308 | 0.43479 | 0.4465 | 0.45821 | 0.46992 | 0.48162 | 0.49333 | 0.50504 | 0.51675 | 0.52846 | 0.54017 | 0.55187 | 0.56358 | 0.57529 | 0.587 | 0.59871 | 0.61042 | 0.62212 | 0.63383 | 0.64554 | 0.65725 | 0.66867 | 0.6801 | 0.69152 | 0.70295 | 0.71437 | 0.7258 | 0.73722 | 0.74865 | 0.76007 | 0.7715 | 0.78292 | 0.79435 | 0.80577 | 0.8172 | 0.82862 | 0.84005 | 0.85147 | 0.8629 | 0.87432 | 0.88575 | 0.89717 | 0.9086 | 0.92002 | 0.93145 | 0.94287 | 0.9543 | 0.96572 | 0.97715 | 0.98857 | 1 | 1.0106 | 1.0212 | 1.0319 | 1.0425 | 1.0531 | 1.0637 | 1.0744 | 1.085 | 1.0956 | 1.1062 | 1.1169 | 1.1275 | 1.1381 | 1.1487 | 1.1594 | 1.17 | 1.1806 | 1.1912 | 1.2019 | 1.2125 | 1.2231 | 1.2337 | 1.2444 | 1.255 | 1.2656 | 1.2762 | 1.2869 | 1.2975 | 1.3081 | 1.3187 | 1.3233 | 1.3279 | 1.3324 | 1.337 | 1.3415 | 1.3461 | 1.3507 | 1.3552 | 1.3598 | 1.3643 | 1.3689 | 1.3734 | 1.378 | 1.3826 | 1.3871 | 1.3917 | 1.3962 | 1.4008 | 1.4054 | 1.4099 | 1.4145 | 1.419 | 1.4236 | 1.4281 | 1.4327 | 1.4373 | 1.4418 | 1.4464 | 1.4509 | 1.4555
2.2 | 0 | 0.305 | 0.33 | 0.313 | 0.25 | 0.286 | 0.328 | 0.713 | 1.09 | 1.435 | 1.594 | 0 | 0.0305 | 0.061 | 0.0915 | 0.122 | 0.1525 | 0.183 | 0.2135 | 0.244 | 0.2745 | 0.305 | 0.31 | 0.315 | 0.32 | 0.325 | 0.33 | 0.3266 | 0.3232 | 0.3198 | 0.3164 | 0.313 | 0.3067 | 0.3004 | 0.2941 | 0.2878 | 0.2815 | 0.2752 | 0.2689 | 0.2626 | 0.2563 | 0.25 | 0.2524 | 0.2548 | 0.2572 | 0.2596 | 0.262 | 0.2644 | 0.2668 | 0.2692 | 0.2716 | 0.274 | 0.2764 | 0.2788 | 0.2812 | 0.2836 | 0.286 | 0.2888 | 0.2916 | 0.2944 | 0.2972 | 0.3 | 0.3028 | 0.3056 | 0.3084 | 0.3112 | 0.314 | 0.3168 | 0.3196 | 0.3224 | 0.3252 | 0.328 | 0.34083 | 0.35367 | 0.3665 | 0.37933 | 0.39217 | 0.405 | 0.41783 | 0.43067 | 0.4435 | 0.45633 | 0.46917 | 0.482 | 0.49483 | 0.50767 | 0.5205 | 0.53333 | 0.54617 | 0.559 | 0.57183 | 0.58467 | 0.5975 | 0.61033 | 0.62317 | 0.636 | 0.64883 | 0.66167 | 0.6745 | 0.68733 | 0.70017 | 0.713 | 0.72557 | 0.73813 | 0.7507 | 0.76327 | 0.77583 | 0.7884 | 0.80097 | 0.81353 | 0.8261 | 0.83867 | 0.85123 | 0.8638 | 0.87637 | 0.88893 | 0.9015 | 0.91407 | 0.92663 | 0.9392 | 0.95177 | 0.96433 | 0.9769 | 0.98947 | 1.002 | 1.0146 | 1.0272 | 1.0397 | 1.0523 | 1.0649 | 1.0774 | 1.09 | 1.1015 | 1.113 | 1.1245 | 1.136 | 1.1475 | 1.159 | 1.1705 | 1.182 | 1.1935 | 1.205 | 1.2165 | 1.228 | 1.2395 | 1.251 | 1.2625 | 1.274 | 1.2855 | 1.297 | 1.3085 | 1.32 | 1.3315 | 1.343 | 1.3545 | 1.366 | 1.3775 | 1.389 | 1.4005 | 1.412 | 1.4235 | 1.435 | 1.4403 | 1.4456 | 1.4509 | 1.4562 | 1.4615 | 1.4668 | 1.4721 | 1.4774 | 1.4827 | 1.488 | 1.4933 | 1.4986 | 1.5039 | 1.5092 | 1.5145 | 1.5198 | 1.5251 | 1.5304 | 1.5357 | 1.541 | 1.5463 | 1.5516 | 1.5569 | 1.5622 | 1.5675 | 1.5728 | 1.5781 | 1.5834 | 1.5887 | 1.594
2.25 | 0 | 0.32125 | 0.3425 | 0.32625 | 0.2625 | 0.3025 | 0.35 | 0.76875 | 1.18 | 1.5512 | 1.7325 | 0 | 0.032125 | 0.06425 | 0.096375 | 0.1285 | 0.16062 | 0.19275 | 0.22487 | 0.257 | 0.28912 | 0.32125 | 0.3255 | 0.32975 | 0.334 | 0.33825 | 0.3425 | 0.33925 | 0.336 | 0.33275 | 0.3295 | 0.32625 | 0.31988 | 0.3135 | 0.30712 | 0.30075 | 0.29437 | 0.288 | 0.28163 | 0.27525 | 0.26887 | 0.2625 | 0.26517 | 0.26783 | 0.2705 | 0.27317 | 0.27583 | 0.2785 | 0.28117 | 0.28383 | 0.2865 | 0.28917 | 0.29183 | 0.2945 | 0.29717 | 0.29983 | 0.3025 | 0.30567 | 0.30883 | 0.312 | 0.31517 | 0.31833 | 0.3215 | 0.32467 | 0.32783 | 0.331 | 0.33417 | 0.33733 | 0.3405 | 0.34367 | 0.34683 | 0.35 | 0.36396 | 0.37792 | 0.39187 | 0.40583 | 0.41979 | 0.43375 | 0.44771 | 0.46167 | 0.47562 | 0.48958 | 0.50354 | 0.5175 | 0.53146 | 0.54542 | 0.55937 | 0.57333 | 0.58729 | 0.60125 | 0.61521 | 0.62917 | 0.64312 | 0.65708 | 0.67104 | 0.685 | 0.69896 | 0.71292 | 0.72687 | 0.74083 | 0.75479 | 0.76875 | 0.78246 | 0.79617 | 0.80987 | 0.82358 | 0.83729 | 0.851 | 0.86471 | 0.87842 | 0.89212 | 0.90583 | 0.91954 | 0.93325 | 0.94696 | 0.96067 | 0.97437 | 0.98808 | 1.0018 | 1.0155 | 1.0292 | 1.0429 | 1.0566 | 1.0703 | 1.084 | 1.0977 | 1.1115 | 1.1252 | 1.1389 | 1.1526 | 1.1663 | 1.18 | 1.1924 | 1.2047 | 1.2171 | 1.2295 | 1.2419 | 1.2542 | 1.2666 | 1.279 | 1.2914 | 1.3037 | 1.3161 | 1.3285 | 1.3409 | 1.3532 | 1.3656 | 1.378 | 1.3904 | 1.4027 | 1.4151 | 1.4275 | 1.4399 | 1.4522 | 1.4646 | 1.477 | 1.4894 | 1.5017 | 1.5141 | 1.5265 | 1.5389 | 1.5512 | 1.5573 | 1.5633 | 1.5694 | 1.5754 | 1.5815 | 1.5875 | 1.5935 | 1.5996 | 1.6056 | 1.6117 | 1.6177 | 1.6237 | 1.6298 | 1.6358 | 1.6419 | 1.6479 | 1.654 | 1.66 | 1.666 | 1.6721 | 1.6781 | 1.6842 | 1.6902 | 1.6962 | 1.7023 | 1.7083 | 1.7144 | 1.7204 | 1.7265 | 1.7325
2.3 | 0 | 0.3375 | 0.355 | 0.3395 | 0.275 | 0.319 | 0.372 | 0.8245 | 1.27 | 1.6675 | 1.871 | 0 | 0.03375 | 0.0675 | 0.10125 | 0.135 | 0.16875 | 0.2025 | 0.23625 | 0.27 | 0.30375 | 0.3375 | 0.341 | 0.3445 | 0.348 | 0.3515 | 0.355 | 0.3519 | 0.3488 | 0.3457 | 0.3426 | 0.3395 | 0.33305 | 0.3266 | 0.32015 | 0.3137 | 0.30725 | 0.3008 | 0.29435 | 0.2879 | 0.28145 | 0.275 | 0.27793 | 0.28087 | 0.2838 | 0.28673 | 0.28967 | 0.2926 | 0.29553 | 0.29847 | 0.3014 | 0.30433 | 0.30727 | 0.3102 | 0.31313 | 0.31607 | 0.319 | 0.32253 | 0.32607 | 0.3296 | 0.33313 | 0.33667 | 0.3402 | 0.34373 | 0.34727 | 0.3508 | 0.35433 | 0.35787 | 0.3614 | 0.36493 | 0.36847 | 0.372 | 0.38708 | 0.40217 | 0.41725 | 0.43233 | 0.44742 | 0.4625 | 0.47758 | 0.49267 | 0.50775 | 0.52283 | 0.53792 | 0.553 | 0.56808 | 0.58317 | 0.59825 | 0.61333 | 0.62842 | 0.6435 | 0.65858 | 0.67367 | 0.68875 | 0.70383 | 0.71892 | 0.734 | 0.74908 | 0.76417 | 0.77925 | 0.79433 | 0.80942 | 0.8245 | 0.83935 | 0.8542 | 0.86905 | 0.8839 | 0.89875 | 0.9136 | 0.92845 | 0.9433 | 0.95815 | 0.973 | 0.98785 | 1.0027 | 1.0175 | 1.0324 | 1.0472 | 1.0621 | 1.0769 | 1.0918 | 1.1066 | 1.1215 | 1.1363 | 1.1512 | 1.166 | 1.1809 | 1.1957 | 1.2106 | 1.2254 | 1.2403 | 1.2551 | 1.27 | 1.2832 | 1.2965 | 1.3097 | 1.323 | 1.3362 | 1.3495 | 1.3627 | 1.376 | 1.3892 | 1.4025 | 1.4157 | 1.429 | 1.4422 | 1.4555 | 1.4687 | 1.482 | 1.4952 | 1.5085 | 1.5217 | 1.535 | 1.5482 | 1.5615 | 1.5747 | 1.588 | 1.6012 | 1.6145 | 1.6277 | 1.641 | 1.6542 | 1.6675 | 1.6743 | 1.6811 | 1.6878 | 1.6946 | 1.7014 | 1.7082 | 1.715 | 1.7218 | 1.7285 | 1.7353 | 1.7421 | 1.7489 | 1.7557 | 1.7625 | 1.7692 | 1.776 | 1.7828 | 1.7896 | 1.7964 | 1.8032 | 1.8099 | 1.8167 | 1.8235 | 1.8303 | 1.8371 | 1.8439 | 1.8506 | 1.8574 | 1.8642 | 1.871
2.35 | 0 | 0.35375 | 0.3675 | 0.35275 | 0.2875 | 0.3355 | 0.394 | 0.88025 | 1.36 | 1.7838 | 2.0095 | 0 | 0.035375 | 0.07075 | 0.10612 | 0.1415 | 0.17687 | 0.21225 | 0.24762 | 0.283 | 0.31837 | 0.35375 | 0.3565 | 0.35925 | 0.362 | 0.36475 | 0.3675 | 0.36455 | 0.3616 | 0.35865 | 0.3557 | 0.35275 | 0.34623 | 0.3397 | 0.33317 | 0.32665 | 0.32012 | 0.3136 | 0.30707 | 0.30055 | 0.29402 | 0.2875 | 0.2907 | 0.2939 | 0.2971 | 0.3003 | 0.3035 | 0.3067 | 0.3099 | 0.3131 | 0.3163 | 0.3195 | 0.3227 | 0.3259 | 0.3291 | 0.3323 | 0.3355 | 0.3394 | 0.3433 | 0.3472 | 0.3511 | 0.355 | 0.3589 | 0.3628 | 0.3667 | 0.3706 | 0.3745 | 0.3784 | 0.3823 | 0.3862 | 0.3901 | 0.394 | 0.41021 | 0.42642 | 0.44263 | 0.45883 | 0.47504 | 0.49125 | 0.50746 | 0.52367 | 0.53988 | 0.55608 | 0.57229 | 0.5885 | 0.60471 | 0.62092 | 0.63712 | 0.65333 | 0.66954 | 0.68575 | 0.70196 | 0.71817 | 0.73438 | 0.75058 | 0.76679 | 0.783 | 0.79921 | 0.81542 | 0.83162 | 0.84783 | 0.86404 | 0.88025 | 0.89624 | 0.91223 | 0.92822 | 0.94422 | 0.96021 | 0.9762 | 0.99219 | 1.0082 | 1.0242 | 1.0402 | 1.0562 | 1.0721 | 1.0881 | 1.1041 | 1.1201 | 1.1361 | 1.1521 | 1.1681 | 1.1841 | 1.2001 | 1.2161 | 1.2321 | 1.2481 | 1.2641 | 1.28 | 1.296 | 1.312 | 1.328 | 1.344 | 1.36 | 1.3741 | 1.3883 | 1.4024 | 1.4165 | 1.4306 | 1.4448 | 1.4589 | 1.473 | 1.4871 | 1.5013 | 1.5154 | 1.5295 | 1.5436 | 1.5578 | 1.5719 | 1.586 | 1.6001 | 1.6143 | 1.6284 | 1.6425 | 1.6566 | 1.6708 | 1.6849 | 1.699 | 1.7131 | 1.7273 | 1.7414 | 1.7555 | 1.7696 | 1.7838 | 1.7913 | 1.7988 | 1.8063 | 1.8139 | 1.8214 | 1.8289 | 1.8364 | 1.844 | 1.8515 | 1.859 | 1.8665 | 1.8741 | 1.8816 | 1.8891 | 1.8966 | 1.9042 | 1.9117 | 1.9192 | 1.9267 | 1.9343 | 1.9418 | 1.9493 | 1.9568 | 1.9644 | 1.9719 | 1.9794 | 1.9869 | 1.9945 | 2.002 | 2.0095
2.4 | 0 | 0.37 | 0.38 | 0.366 | 0.3 | 0.352 | 0.416 | 0.936 | 1.45 | 1.9 | 2.148 | 0 | 0.037 | 0.074 | 0.111 | 0.148 | 0.185 | 0.222 | 0.259 | 0.296 | 0.333 | 0.37 | 0.372 | 0.374 | 0.376 | 0.378 | 0.38 | 0.3772 | 0.3744 | 0.3716 | 0.3688 | 0.366 | 0.3594 | 0.3528 | 0.3462 | 0.3396 | 0.333 | 0.3264 | 0.3198 | 0.3132 | 0.3066 | 0.3 | 0.30347 | 0.30693 | 0.3104 | 0.31387 | 0.31733 | 0.3208 | 0.32427 | 0.32773 | 0.3312 | 0.33467 | 0.33813 | 0.3416 | 0.34507 | 0.34853 | 0.352 | 0.35627 | 0.36053 | 0.3648 | 0.36907 | 0.37333 | 0.3776 | 0.38187 | 0.38613 | 0.3904 | 0.39467 | 0.39893 | 0.4032 | 0.40747 | 0.41173 | 0.416 | 0.43333 | 0.45067 | 0.468 | 0.48533 | 0.50267 | 0.52 | 0.53733 | 0.55467 | 0.572 | 0.58933 | 0.60667 | 0.624 | 0.64133 | 0.65867 | 0.676 | 0.69333 | 0.71067 | 0.728 | 0.74533 | 0.76267 | 0.78 | 0.79733 | 0.81467 | 0.832 | 0.84933 | 0.86667 | 0.884 | 0.90133 | 0.91867 | 0.936 | 0.95313 | 0.97027 | 0.9874 | 1.0045 | 1.0217 | 1.0388 | 1.0559 | 1.0731 | 1.0902 | 1.1073 | 1.1245 | 1.1416 | 1.1587 | 1.1759 | 1.193 | 1.2101 | 1.2273 | 1.2444 | 1.2615 | 1.2787 | 1.2958 | 1.3129 | 1.3301 | 1.3472 | 1.3643 | 1.3815 | 1.3986 | 1.4157 | 1.4329 | 1.45 | 1.465 | 1.48 | 1.495 | 1.51 | 1.525 | 1.54 | 1.555 | 1.57 | 1.585 | 1.6 | 1.615 | 1.63 | 1.645 | 1.66 | 1.675 | 1.69 | 1.705 | 1.72 | 1.735 | 1.75 | 1.765 | 1.78 | 1.795 | 1.81 | 1.825 | 1.84 | 1.855 | 1.87 | 1.885 | 1.9 | 1.9083 | 1.9165 | 1.9248 | 1.9331 | 1.9413 | 1.9496 | 1.9579 | 1.9661 | 1.9744 | 1.9827 | 1.9909 | 1.9992 | 2.0075 | 2.0157 | 2.024 | 2.0323 | 2.0405 | 2.0488 | 2.0571 | 2.0653 | 2.0736 | 2.0819 | 2.0901 | 2.0984 | 2.1067 | 2.1149 | 2.1232 | 2.1315 | 2.1397 | 2.148
2.45 | 0 | 0.38625 | 0.3925 | 0.37925 | 0.3125 | 0.3685 | 0.438 | 0.99175 | 1.54 | 2.0163 | 2.2865 | 0 | 0.038625 | 0.07725 | 0.11588 | 0.1545 | 0.19312 | 0.23175 | 0.27037 | 0.309 | 0.34763 | 0.38625 | 0.3875 | 0.38875 | 0.39 | 0.39125 | 0.3925 | 0.38985 | 0.3872 | 0.38455 | 0.3819 | 0.37925 | 0.37258 | 0.3659 | 0.35923 | 0.35255 | 0.34588 | 0.3392 | 0.33253 | 0.32585 | 0.31917 | 0.3125 | 0.31623 | 0.31997 | 0.3237 | 0.32743 | 0.33117 | 0.3349 | 0.33863 | 0.34237 | 0.3461 | 0.34983 | 0.35357 | 0.3573 | 0.36103 | 0.36477 | 0.3685 | 0.37313 | 0.37777 | 0.3824 | 0.38703 | 0.39167 | 0.3963 | 0.40093 | 0.40557 | 0.4102 | 0.41483 | 0.41947 | 0.4241 | 0.42873 | 0.43337 | 0.438 | 0.45646 | 0.47492 | 0.49338 | 0.51183 | 0.53029 | 0.54875 | 0.56721 | 0.58567 | 0.60413 | 0.62258 | 0.64104 | 0.6595 | 0.67796 | 0.69642 | 0.71488 | 0.73333 | 0.75179 | 0.77025 | 0.78871 | 0.80717 | 0.82563 | 0.84408 | 0.86254 | 0.881 | 0.89946 | 0.91792 | 0.93638 | 0.95483 | 0.97329 | 0.99175 | 1.01 | 1.0283 | 1.0466 | 1.0649 | 1.0831 | 1.1014 | 1.1197 | 1.138 | 1.1562 | 1.1745 | 1.1928 | 1.211 | 1.2293 | 1.2476 | 1.2659 | 1.2841 | 1.3024 | 1.3207 | 1.339 | 1.3573 | 1.3755 | 1.3938 | 1.4121 | 1.4303 | 1.4486 | 1.4669 | 1.4852 | 1.5034 | 1.5217 | 1.54 | 1.5559 | 1.5718 | 1.5876 | 1.6035 | 1.6194 | 1.6353 | 1.6511 | 1.667 | 1.6829 | 1.6988 | 1.7146 | 1.7305 | 1.7464 | 1.7623 | 1.7781 | 1.794 | 1.8099 | 1.8258 | 1.8416 | 1.8575 | 1.8734 | 1.8893 | 1.9051 | 1.921 | 1.9369 | 1.9528 | 1.9686 | 1.9845 | 2.0004 | 2.0163 | 2.0253 | 2.0343 | 2.0433 | 2.0523 | 2.0613 | 2.0703 | 2.0793 | 2.0883 | 2.0973 | 2.1063 | 2.1153 | 2.1244 | 2.1334 | 2.1424 | 2.1514 | 2.1604 | 2.1694 | 2.1784 | 2.1874 | 2.1964 | 2.2054 | 2.2144 | 2.2234 | 2.2325 | 2.2415 | 2.2505 | 2.2595 | 2.2685 | 2.2775 | 2.2865
2.5 | 0 | 0.4025 | 0.405 | 0.3925 | 0.325 | 0.385 | 0.46 | 1.0475 | 1.63 | 2.1325 | 2.425 | 0 | 0.04025 | 0.0805 | 0.12075 | 0.161 | 0.20125 | 0.2415 | 0.28175 | 0.322 | 0.36225 | 0.4025 | 0.403 | 0.4035 | 0.404 | 0.4045 | 0.405 | 0.4025 | 0.4 | 0.3975 | 0.395 | 0.3925 | 0.38575 | 0.379 | 0.37225 | 0.3655 | 0.35875 | 0.352 | 0.34525 | 0.3385 | 0.33175 | 0.325 | 0.329 | 0.333 | 0.337 | 0.341 | 0.345 | 0.349 | 0.353 | 0.357 | 0.361 | 0.365 | 0.369 | 0.373 | 0.377 | 0.381 | 0.385 | 0.39 | 0.395 | 0.4 | 0.405 | 0.41 | 0.415 | 0.42 | 0.425 | 0.43 | 0.435 | 0.44 | 0.445 | 0.45 | 0.455 | 0.46 | 0.47958 | 0.49917 | 0.51875 | 0.53833 | 0.55792 | 0.5775 | 0.59708 | 0.61667 | 0.63625 | 0.65583 | 0.67542 | 0.695 | 0.71458 | 0.73417 | 0.75375 | 0.77333 | 0.79292 | 0.8125 | 0.83208 | 0.85167 | 0.87125 | 0.89083 | 0.91042 | 0.93 | 0.94958 | 0.96917 | 0.98875 | 1.0083 | 1.0279 | 1.0475 | 1.0669 | 1.0863 | 1.1057 | 1.1252 | 1.1446 | 1.164 | 1.1834 | 1.2028 | 1.2222 | 1.2417 | 1.2611 | 1.2805 | 1.2999 | 1.3193 | 1.3387 | 1.3582 | 1.3776 | 1.397 | 1.4164 | 1.4358 | 1.4552 | 1.4747 | 1.4941 | 1.5135 | 1.5329 | 1.5523 | 1.5717 | 1.5912 | 1.6106 | 1.63 | 1.6467 | 1.6635 | 1.6803 | 1.697 | 1.7137 | 1.7305 | 1.7472 | 1.764 | 1.7807 | 1.7975 | 1.8142 | 1.831 | 1.8477 | 1.8645 | 1.8812 | 1.898 | 1.9147 | 1.9315 | 1.9482 | 1.965 | 1.9817 | 1.9985 | 2.0152 | 2.032 | 2.0487 | 2.0655 | 2.0822 | 2.099 | 2.1157 | 2.1325 | 2.1422 | 2.152 | 2.1617 | 2.1715 | 2.1812 | 2.191 | 2.2007 | 2.2105 | 2.2202 | 2.23 | 2.2397 | 2.2495 | 2.2592 | 2.269 | 2.2787 | 2.2885 | 2.2982 | 2.308 | 2.3177 | 2.3275 | 2.3372 | 2.347 | 2.3567 | 2.3665 | 2.3762 | 2.386 | 2.3957 | 2.4055 | 2.4152 | 2.425
2.55 | 0 | 0.41875 | 0.4175 | 0.40575 | 0.3375 | 0.4015 | 0.482 | 1.1032 | 1.72 | 2.2487 | 2.5635 | 0 | 0.041875 | 0.08375 | 0.12562 | 0.1675 | 0.20937 | 0.25125 | 0.29312 | 0.335 | 0.37687 | 0.41875 | 0.4185 | 0.41825 | 0.418 | 0.41775 | 0.4175 | 0.41515 | 0.4128 | 0.41045 | 0.4081 | 0.40575 | 0.39892 | 0.3921 | 0.38527 | 0.37845 | 0.37162 | 0.3648 | 0.35797 | 0.35115 | 0.34432 | 0.3375 | 0.34177 | 0.34603 | 0.3503 | 0.35457 | 0.35883 | 0.3631 | 0.36737 | 0.37163 | 0.3759 | 0.38017 | 0.38443 | 0.3887 | 0.39297 | 0.39723 | 0.4015 | 0.40687 | 0.41223 | 0.4176 | 0.42297 | 0.42833 | 0.4337 | 0.43907 | 0.44443 | 0.4498 | 0.45517 | 0.46053 | 0.4659 | 0.47127 | 0.47663 | 0.482 | 0.50271 | 0.52342 | 0.54412 | 0.56483 | 0.58554 | 0.60625 | 0.62696 | 0.64767 | 0.66837 | 0.68908 | 0.70979 | 0.7305 | 0.75121 | 0.77192 | 0.79262 | 0.81333 | 0.83404 | 0.85475 | 0.87546 | 0.89617 | 0.91687 | 0.93758 | 0.95829 | 0.979 | 0.99971 | 1.0204 | 1.0411 | 1.0618 | 1.0825 | 1.1032 | 1.1238 | 1.1444 | 1.1649 | 1.1855 | 1.206 | 1.2266 | 1.2472 | 1.2677 | 1.2883 | 1.3088 | 1.3294 | 1.3499 | 1.3705 | 1.3911 | 1.4116 | 1.4322 | 1.4527 | 1.4733 | 1.4939 | 1.5144 | 1.535 | 1.5555 | 1.5761 | 1.5966 | 1.6172 | 1.6378 | 1.6583 | 1.6789 | 1.6994 | 1.72 | 1.7376 | 1.7552 | 1.7729 | 1.7905 | 1.8081 | 1.8257 | 1.8434 | 1.861 | 1.8786 | 1.8962 | 1.9139 | 1.9315 | 1.9491 | 1.9667 | 1.9844 | 2.002 | 2.0196 | 2.0372 | 2.0549 | 2.0725 | 2.0901 | 2.1077 | 2.1254 | 2.143 | 2.1606 | 2.1782 | 2.1959 | 2.2135 | 2.2311 | 2.2487 | 2.2592 | 2.2697 | 2.2802 | 2.2907 | 2.3012 | 2.3117 | 2.3222 | 2.3327 | 2.3432 | 2.3537 | 2.3642 | 2.3746 | 2.3851 | 2.3956 | 2.4061 | 2.4166 | 2.4271 | 2.4376 | 2.4481 | 2.4586 | 2.4691 | 2.4796 | 2.4901 | 2.5005 | 2.511 | 2.5215 | 2.532 | 2.5425 | 2.553 | 2.5635
2.6 | 0 | 0.435 | 0.43 | 0.419 | 0.35 | 0.418 | 0.504 | 1.159 | 1.81 | 2.365 | 2.702 | 0 | 0.0435 | 0.087 | 0.1305 | 0.174 | 0.2175 | 0.261 | 0.3045 | 0.348 | 0.3915 | 0.435 | 0.434 | 0.433 | 0.432 | 0.431 | 0.43 | 0.4278 | 0.4256 | 0.4234 | 0.4212 | 0.419 | 0.4121 | 0.4052 | 0.3983 | 0.3914 | 0.3845 | 0.3776 | 0.3707 | 0.3638 | 0.3569 | 0.35 | 0.35453 | 0.35907 | 0.3636 | 0.36813 | 0.37267 | 0.3772 | 0.38173 | 0.38627 | 0.3908 | 0.39533 | 0.39987 | 0.4044 | 0.40893 | 0.41347 | 0.418 | 0.42373 | 0.42947 | 0.4352 | 0.44093 | 0.44667 | 0.4524 | 0.45813 | 0.46387 | 0.4696 | 0.47533 | 0.48107 | 0.4868 | 0.49253 | 0.49827 | 0.504 | 0.52583 | 0.54767 | 0.5695 | 0.59133 | 0.61317 | 0.635 | 0.65683 | 0.67867 | 0.7005 | 0.72233 | 0.74417 | 0.766 | 0.78783 | 0.80967 | 0.8315 | 0.85333 | 0.87517 | 0.897 | 0.91883 | 0.94067 | 0.9625 | 0.98433 | 1.0062 | 1.028 | 1.0498 | 1.0717 | 1.0935 | 1.1153 | 1.1372 | 1.159 | 1.1807 | 1.2024 | 1.2241 | 1.2458 | 1.2675 | 1.2892 | 1.3109 | 1.3326 | 1.3543 | 1.376 | 1.3977 | 1.4194 | 1.4411 | 1.4628 | 1.4845 | 1.5062 | 1.5279 | 1.5496 | 1.5713 | 1.593 | 1.6147 | 1.6364 | 1.6581 | 1.6798 | 1.7015 | 1.7232 | 1.7449 | 1.7666 | 1.7883 | 1.81 | 1.8285 | 1.847 | 1.8655 | 1.884 | 1.9025 | 1.921 | 1.9395 | 1.958 | 1.9765 | 1.995 | 2.0135 | 2.032 | 2.0505 | 2.069 | 2.0875 | 2.106 | 2.1245 | 2.143 | 2.1615 | 2.18 | 2.1985 | 2.217 | 2.2355 | 2.254 | 2.2725 | 2.291 | 2.3095 | 2.328 | 2.3465 | 2.365 | 2.3762 | 2.3875 | 2.3987 | 2.4099 | 2.4212 | 2.4324 | 2.4436 | 2.4549 | 2.4661 | 2.4773 | 2.4886 | 2.4998 | 2.511 | 2.5223 | 2.5335 | 2.5447 | 2.556 | 2.5672 | 2.5784 | 2.5897 | 2.6009 | 2.6121 | 2.6234 | 2.6346 | 2.6458 | 2.6571 | 2.6683 | 2.6795 | 2.6908 | 2.702
2.65 | 0 | 0.45125 | 0.4425 | 0.43225 | 0.3625 | 0.4345 | 0.526 | 1.2147 | 1.9 | 2.4812 | 2.8405 | 0 | 0.045125 | 0.09025 | 0.13537 | 0.1805 | 0.22562 | 0.27075 | 0.31587 | 0.361 | 0.40612 | 0.45125 | 0.4495 | 0.44775 | 0.446 | 0.44425 | 0.4425 | 0.44045 | 0.4384 | 0.43635 | 0.4343 | 0.43225 | 0.42528 | 0.4183 | 0.41132 | 0.40435 | 0.39737 | 0.3904 | 0.38342 | 0.37645 | 0.36947 | 0.3625 | 0.3673 | 0.3721 | 0.3769 | 0.3817 | 0.3865 | 0.3913 | 0.3961 | 0.4009 | 0.4057 | 0.4105 | 0.4153 | 0.4201 | 0.4249 | 0.4297 | 0.4345 | 0.4406 | 0.4467 | 0.4528 | 0.4589 | 0.465 | 0.4711 | 0.4772 | 0.4833 | 0.4894 | 0.4955 | 0.5016 | 0.5077 | 0.5138 | 0.5199 | 0.526 | 0.54896 | 0.57192 | 0.59487 | 0.61783 | 0.64079 | 0.66375 | 0.68671 | 0.70967 | 0.73262 | 0.75558 | 0.77854 | 0.8015 | 0.82446 | 0.84742 | 0.87037 | 0.89333 | 0.91629 | 0.93925 | 0.96221 | 0.98517 | 1.0081 | 1.0311 | 1.054 | 1.077 | 1.1 | 1.1229 | 1.1459 | 1.1688 | 1.1918 | 1.2148 | 1.2376 | 1.2604 | 1.2833 | 1.3061 | 1.329 | 1.3518 | 1.3746 | 1.3975 | 1.4203 | 1.4432 | 1.466 | 1.4889 | 1.5117 | 1.5345 | 1.5574 | 1.5802 | 1.6031 | 1.6259 | 1.6487 | 1.6716 | 1.6944 | 1.7173 | 1.7401 | 1.7629 | 1.7858 | 1.8086 | 1.8315 | 1.8543 | 1.8772 | 1.9 | 1.9194 | 1.9387 | 1.9581 | 1.9775 | 1.9969 | 2.0162 | 2.0356 | 2.055 | 2.0744 | 2.0937 | 2.1131 | 2.1325 | 2.1519 | 2.1712 | 2.1906 | 2.21 | 2.2294 | 2.2487 | 2.2681 | 2.2875 | 2.3069 | 2.3262 | 2.3456 | 2.365 | 2.3844 | 2.4037 | 2.4231 | 2.4425 | 2.4619 | 2.4812 | 2.4932 | 2.5052 | 2.5172 | 2.5291 | 2.5411 | 2.5531 | 2.5651 | 2.577 | 2.589 | 2.601 | 2.613 | 2.6249 | 2.6369 | 2.6489 | 2.6609 | 2.6728 | 2.6848 | 2.6968 | 2.7088 | 2.7207 | 2.7327 | 2.7447 | 2.7567 | 2.7686 | 2.7806 | 2.7926 | 2.8046 | 2.8165 | 2.8285 | 2.8405
2.7 | 0 | 0.4675 | 0.455 | 0.4455 | 0.375 | 0.451 | 0.548 | 1.2705 | 1.99 | 2.5975 | 2.979 | 2.7756e-17 | 0.04675 | 0.0935 | 0.14025 | 0.187 | 0.23375 | 0.2805 | 0.32725 | 0.374 | 0.42075 | 0.4675 | 0.465 | 0.4625 | 0.46 | 0.4575 | 0.455 | 0.4531 | 0.4512 | 0.4493 | 0.4474 | 0.4455 | 0.43845 | 0.4314 | 0.42435 | 0.4173 | 0.41025 | 0.4032 | 0.39615 | 0.3891 | 0.38205 | 0.375 | 0.38007 | 0.38513 | 0.3902 | 0.39527 | 0.40033 | 0.4054 | 0.41047 | 0.41553 | 0.4206 | 0.42567 | 0.43073 | 0.4358 | 0.44087 | 0.44593 | 0.451 | 0.45747 | 0.46393 | 0.4704 | 0.47687 | 0.48333 | 0.4898 | 0.49627 | 0.50273 | 0.5092 | 0.51567 | 0.52213 | 0.5286 | 0.53507 | 0.54153 | 0.548 | 0.57208 | 0.59617 | 0.62025 | 0.64433 | 0.66842 | 0.6925 | 0.71658 | 0.74067 | 0.76475 | 0.78883 | 0.81292 | 0.837 | 0.86108 | 0.88517 | 0.90925 | 0.93333 | 0.95742 | 0.9815 | 1.0056 | 1.0297 | 1.0538 | 1.0778 | 1.1019 | 1.126 | 1.1501 | 1.1742 | 1.1983 | 1.2223 | 1.2464 | 1.2705 | 1.2945 | 1.3185 | 1.3425 | 1.3664 | 1.3904 | 1.4144 | 1.4384 | 1.4624 | 1.4864 | 1.5103 | 1.5343 | 1.5583 | 1.5823 | 1.6063 | 1.6303 | 1.6542 | 1.6782 | 1.7022 | 1.7262 | 1.7502 | 1.7742 | 1.7981 | 1.8221 | 1.8461 | 1.8701 | 1.8941 | 1.9181 | 1.942 | 1.966 | 1.99 | 2.0103 | 2.0305 | 2.0508 | 2.071 | 2.0913 | 2.1115 | 2.1318 | 2.152 | 2.1723 | 2.1925 | 2.2128 | 2.233 | 2.2532 | 2.2735 | 2.2938 | 2.314 | 2.3342 | 2.3545 | 2.3748 | 2.395 | 2.4152 | 2.4355 | 2.4558 | 2.476 | 2.4963 | 2.5165 | 2.5368 | 2.557 | 2.5773 | 2.5975 | 2.6102 | 2.6229 | 2.6357 | 2.6484 | 2.6611 | 2.6738 | 2.6865 | 2.6992 | 2.712 | 2.7247 | 2.7374 | 2.7501 | 2.7628 | 2.7755 | 2.7883 | 2.801 | 2.8137 | 2.8264 | 2.8391 | 2.8518 | 2.8646 | 2.8773 | 2.89 | 2.9027 | 2.9154 | 2.9281 | 2.9409 | 2.9536 | 2.9663 | 2.979
2.75 | 0 | 0.48375 | 0.4675 | 0.45875 | 0.3875 | 0.4675 | 0.57 | 1.3262 | 2.08 | 2.7138 | 3.1175 | 0 | 0.048375 | 0.09675 | 0.14512 | 0.1935 | 0.24187 | 0.29025 | 0.33862 | 0.387 | 0.43537 | 0.48375 | 0.4805 | 0.47725 | 0.474 | 0.47075 | 0.4675 | 0.46575 | 0.464 | 0.46225 | 0.4605 | 0.45875 | 0.45162 | 0.4445 | 0.43737 | 0.43025 | 0.42312 | 0.416 | 0.40887 | 0.40175 | 0.39462 | 0.3875 | 0.39283 | 0.39817 | 0.4035 | 0.40883 | 0.41417 | 0.4195 | 0.42483 | 0.43017 | 0.4355 | 0.44083 | 0.44617 | 0.4515 | 0.45683 | 0.46217 | 0.4675 | 0.47433 | 0.48117 | 0.488 | 0.49483 | 0.50167 | 0.5085 | 0.51533 | 0.52217 | 0.529 | 0.53583 | 0.54267 | 0.5495 | 0.55633 | 0.56317 | 0.57 | 0.59521 | 0.62042 | 0.64562 | 0.67083 | 0.69604 | 0.72125 | 0.74646 | 0.77167 | 0.79687 | 0.82208 | 0.84729 | 0.8725 | 0.89771 | 0.92292 | 0.94812 | 0.97333 | 0.99854 | 1.0237 | 1.049 | 1.0742 | 1.0994 | 1.1246 | 1.1498 | 1.175 | 1.2002 | 1.2254 | 1.2506 | 1.2758 | 1.301 | 1.3262 | 1.3514 | 1.3765 | 1.4016 | 1.4268 | 1.4519 | 1.477 | 1.5021 | 1.5272 | 1.5524 | 1.5775 | 1.6026 | 1.6277 | 1.6529 | 1.678 | 1.7031 | 1.7283 | 1.7534 | 1.7785 | 1.8036 | 1.8287 | 1.8539 | 1.879 | 1.9041 | 1.9293 | 1.9544 | 1.9795 | 2.0046 | 2.0297 | 2.0549 | 2.08 | 2.1011 | 2.1223 | 2.1434 | 2.1645 | 2.1856 | 2.2067 | 2.2279 | 2.249 | 2.2701 | 2.2913 | 2.3124 | 2.3335 | 2.3546 | 2.3758 | 2.3969 | 2.418 | 2.4391 | 2.4603 | 2.4814 | 2.5025 | 2.5236 | 2.5448 | 2.5659 | 2.587 | 2.6081 | 2.6293 | 2.6504 | 2.6715 | 2.6926 | 2.7138 | 2.7272 | 2.7407 | 2.7541 | 2.7676 | 2.781 | 2.7945 | 2.808 | 2.8214 | 2.8349 | 2.8483 | 2.8618 | 2.8752 | 2.8887 | 2.9022 | 2.9156 | 2.9291 | 2.9425 | 2.956 | 2.9695 | 2.9829 | 2.9964 | 3.0098 | 3.0233 | 3.0367 | 3.0502 | 3.0637 | 3.0771 | 3.0906 | 3.104 | 3.1175
2.8 | 0 | 0.5 | 0.48 | 0.472 | 0.4 | 0.484 | 0.592 | 1.382 | 2.17 | 2.83 | 3.256 | -2.7756e-17 | 0.05 | 0.1 | 0.15 | 0.2 | 0.25 | 0.3 | 0.35 | 0.4 | 0.45 | 0.5 | 0.496 | 0.492 | 0.488 | 0.484 | 0.48 | 0.4784 | 0.4768 | 0.4752 | 0.4736 | 0.472 | 0.4648 | 0.4576 | 0.4504 | 0.4432 | 0.436 | 0.4288 | 0.4216 | 0.4144 | 0.4072 | 0.4 | 0.4056 | 0.4112 | 0.4168 | 0.4224 | 0.428 | 0.4336 | 0.4392 | 0.4448 | 0.4504 | 0.456 | 0.4616 | 0.4672 | 0.4728 | 0.4784 | 0.484 | 0.4912 | 0.4984 | 0.5056 | 0.5128 | 0.52 | 0.5272 | 0.5344 | 0.5416 | 0.5488 | 0.556 | 0.5632 | 0.5704 | 0.5776 | 0.5848 | 0.592 | 0.61833 | 0.64467 | 0.671 | 0.69733 | 0.72367 | 0.75 | 0.77633 | 0.80267 | 0.829 | 0.85533 | 0.88167 | 0.908 | 0.93433 | 0.96067 | 0.987 | 1.0133 | 1.0397 | 1.066 | 1.0923 | 1.1187 | 1.145 | 1.1713 | 1.1977 | 1.224 | 1.2503 | 1.2767 | 1.303 | 1.3293 | 1.3557 | 1.382 | 1.4083 | 1.4345 | 1.4608 | 1.4871 | 1.5133 | 1.5396 | 1.5659 | 1.5921 | 1.6184 | 1.6447 | 1.6709 | 1.6972 | 1.7235 | 1.7497 | 1.776 | 1.8023 | 1.8285 | 1.8548 | 1.8811 | 1.9073 | 1.9336 | 1.9599 | 1.9861 | 2.0124 | 2.0387 | 2.0649 | 2.0912 | 2.1175 | 2.1437 | 2.17 | 2.192 | 2.214 | 2.236 | 2.258 | 2.28 | 2.302 | 2.324 | 2.346 | 2.368 | 2.39 | 2.412 | 2.434 | 2.456 | 2.478 | 2.5 | 2.522 | 2.544 | 2.566 | 2.588 | 2.61 | 2.632 | 2.654 | 2.676 | 2.698 | 2.72 | 2.742 | 2.764 | 2.786 | 2.808 | 2.83 | 2.8442 | 2.8584 | 2.8726 | 2.8868 | 2.901 | 2.9152 | 2.9294 | 2.9436 | 2.9578 | 2.972 | 2.9862 | 3.0004 | 3.0146 | 3.0288 | 3.043 | 3.0572 | 3.0714 | 3.0856 | 3.0998 | 3.114 | 3.1282 | 3.1424 | 3.1566 | 3.1708 | 3.185 | 3.1992 | 3.2134 | 3.2276 | 3.2418 | 3.256
2.85 | 0 | 0.51625 | 0.4925 | 0.48525 | 0.4125 | 0.5005 | 0.614 | 1.4377 | 2.26 | 2.9463 | 3.3945 | 0 | 0.051625 | 0.10325 | 0.15487 | 0.2065 | 0.25812 | 0.30975 | 0.36137 | 0.413 | 0.46462 | 0.51625 | 0.5115 | 0.50675 | 0.502 | 0.49725 | 0.4925 | 0.49105 | 0.4896 | 0.48815 | 0.4867 | 0.48525 | 0.47798 | 0.4707 | 0.46343 | 0.45615 | 0.44888 | 0.4416 | 0.43433 | 0.42705 | 0.41978 | 0.4125 | 0.41837 | 0.42423 | 0.4301 | 0.43597 | 0.44183 | 0.4477 | 0.45357 | 0.45943 | 0.4653 | 0.47117 | 0.47703 | 0.4829 | 0.48877 | 0.49463 | 0.5005 | 0.50807 | 0.51563 | 0.5232 | 0.53077 | 0.53833 | 0.5459 | 0.55347 | 0.56103 | 0.5686 | 0.57617 | 0.58373 | 0.5913 | 0.59887 | 0.60643 | 0.614 | 0.64146 | 0.66892 | 0.69637 | 0.72383 | 0.75129 | 0.77875 | 0.80621 | 0.83367 | 0.86112 | 0.88858 | 0.91604 | 0.9435 | 0.97096 | 0.99842 | 1.0259 | 1.0533 | 1.0808 | 1.1082 | 1.1357 | 1.1632 | 1.1906 | 1.2181 | 1.2455 | 1.273 | 1.3005 | 1.3279 | 1.3554 | 1.3828 | 1.4103 | 1.4378 | 1.4652 | 1.4926 | 1.52 | 1.5474 | 1.5748 | 1.6022 | 1.6296 | 1.657 | 1.6844 | 1.7118 | 1.7392 | 1.7667 | 1.7941 | 1.8215 | 1.8489 | 1.8763 | 1.9037 | 1.9311 | 1.9585 | 1.9859 | 2.0133 | 2.0407 | 2.0681 | 2.0956 | 2.123 | 2.1504 | 2.1778 | 2.2052 | 2.2326 | 2.26 | 2.2829 | 2.3058 | 2.3286 | 2.3515 | 2.3744 | 2.3973 | 2.4201 | 2.443 | 2.4659 | 2.4888 | 2.5116 | 2.5345 | 2.5574 | 2.5802 | 2.6031 | 2.626 | 2.6489 | 2.6718 | 2.6946 | 2.7175 | 2.7404 | 2.7633 | 2.7861 | 2.809 | 2.8319 | 2.8548 | 2.8776 | 2.9005 | 2.9234 | 2.9463 | 2.9612 | 2.9761 | 2.9911 | 3.006 | 3.021 | 3.0359 | 3.0508 | 3.0658 | 3.0807 | 3.0957 | 3.1106 | 3.1256 | 3.1405 | 3.1554 | 3.1704 | 3.1853 | 3.2003 | 3.2152 | 3.2301 | 3.2451 | 3.26 | 3.275 | 3.2899 | 3.3049 | 3.3198 | 3.3347 | 3.3497 | 3.3646 | 3.3796 | 3.3945
2.9 | 0 | 0.5325 | 0.505 | 0.4985 | 0.425 | 0.517 | 0.636 | 1.4935 | 2.35 | 3.0625 | 3.533 | 0 | 0.05325 | 0.1065 | 0.15975 | 0.213 | 0.26625 | 0.3195 | 0.37275 | 0.426 | 0.47925 | 0.5325 | 0.527 | 0.5215 | 0.516 | 0.5105 | 0.505 | 0.5037 | 0.5024 | 0.5011 | 0.4998 | 0.4985 | 0.49115 | 0.4838 | 0.47645 | 0.4691 | 0.46175 | 0.4544 | 0.44705 | 0.4397 | 0.43235 | 0.425 | 0.43113 | 0.43727 | 0.4434 | 0.44953 | 0.45567 | 0.4618 | 0.46793 | 0.47407 | 0.4802 | 0.48633 | 0.49247 | 0.4986 | 0.50473 | 0.51087 | 0.517 | 0.52493 | 0.53287 | 0.5408 | 0.54873 | 0.55667 | 0.5646 | 0.57253 | 0.58047 | 0.5884 | 0.59633 | 0.60427 | 0.6122 | 0.62013 | 0.62807 | 0.636 | 0.66458 | 0.69317 | 0.72175 | 0.75033 | 0.77892 | 0.8075 | 0.83608 | 0.86467 | 0.89325 | 0.92183 | 0.95042 | 0.979 | 1.0076 | 1.0362 | 1.0647 | 1.0933 | 1.1219 | 1.1505 | 1.1791 | 1.2077 | 1.2362 | 1.2648 | 1.2934 | 1.322 | 1.3506 | 1.3792 | 1.4077 | 1.4363 | 1.4649 | 1.4935 | 1.5221 | 1.5506 | 1.5791 | 1.6077 | 1.6362 | 1.6648 | 1.6933 | 1.7219 | 1.7504 | 1.779 | 1.8075 | 1.8361 | 1.8646 | 1.8932 | 1.9217 | 1.9503 | 1.9788 | 2.0074 | 2.0359 | 2.0645 | 2.093 | 2.1216 | 2.1501 | 2.1787 | 2.2072 | 2.2358 | 2.2643 | 2.2929 | 2.3214 | 2.35 | 2.3737 | 2.3975 | 2.4212 | 2.445 | 2.4687 | 2.4925 | 2.5162 | 2.54 | 2.5637 | 2.5875 | 2.6112 | 2.635 | 2.6587 | 2.6825 | 2.7062 | 2.73 | 2.7537 | 2.7775 | 2.8012 | 2.825 | 2.8487 | 2.8725 | 2.8962 | 2.92 | 2.9437 | 2.9675 | 2.9912 | 3.015 | 3.0387 | 3.0625 | 3.0782 | 3.0939 | 3.1096 | 3.1252 | 3.1409 | 3.1566 | 3.1723 | 3.188 | 3.2037 | 3.2193 | 3.235 | 3.2507 | 3.2664 | 3.2821 | 3.2977 | 3.3134 | 3.3291 | 3.3448 | 3.3605 | 3.3762 | 3.3918 | 3.4075 | 3.4232 | 3.4389 | 3.4546 | 3.4703 | 3.4859 | 3.5016 | 3.5173 | 3.533
2.95 | 0 | 0.54875 | 0.5175 | 0.51175 | 0.4375 | 0.5335 | 0.658 | 1.5493 | 2.44 | 3.1787 | 3.6715 | 0 | 0.054875 | 0.10975 | 0.16462 | 0.2195 | 0.27437 | 0.32925 | 0.38412 | 0.439 | 0.49388 | 0.54875 | 0.5425 | 0.53625 | 0.53 | 0.52375 | 0.5175 | 0.51635 | 0.5152 | 0.51405 | 0.5129 | 0.51175 | 0.50433 | 0.4969 | 0.48947 | 0.48205 | 0.47463 | 0.4672 | 0.45978 | 0.45235 | 0.44493 | 0.4375 | 0.4439 | 0.4503 | 0.4567 | 0.4631 | 0.4695 | 0.4759 | 0.4823 | 0.4887 | 0.4951 | 0.5015 | 0.5079 | 0.5143 | 0.5207 | 0.5271 | 0.5335 | 0.5418 | 0.5501 | 0.5584 | 0.5667 | 0.575 | 0.5833 | 0.5916 | 0.5999 | 0.6082 | 0.6165 | 0.6248 | 0.6331 | 0.6414 | 0.6497 | 0.658 | 0.68771 | 0.71742 | 0.74712 | 0.77683 | 0.80654 | 0.83625 | 0.86596 | 0.89567 | 0.92537 | 0.95508 | 0.98479 | 1.0145 | 1.0442 | 1.0739 | 1.1036 | 1.1333 | 1.163 | 1.1928 | 1.2225 | 1.2522 | 1.2819 | 1.3116 | 1.3413 | 1.371 | 1.4007 | 1.4304 | 1.4601 | 1.4898 | 1.5195 | 1.5493 | 1.5789 | 1.6086 | 1.6383 | 1.668 | 1.6977 | 1.7274 | 1.7571 | 1.7868 | 1.8165 | 1.8462 | 1.8759 | 1.9056 | 1.9352 | 1.9649 | 1.9946 | 2.0243 | 2.054 | 2.0837 | 2.1134 | 2.1431 | 2.1728 | 2.2025 | 2.2322 | 2.2619 | 2.2915 | 2.3212 | 2.3509 | 2.3806 | 2.4103 | 2.44 | 2.4646 | 2.4893 | 2.5139 | 2.5385 | 2.5631 | 2.5878 | 2.6124 | 2.637 | 2.6616 | 2.6863 | 2.7109 | 2.7355 | 2.7601 | 2.7848 | 2.8094 | 2.834 | 2.8586 | 2.8833 | 2.9079 | 2.9325 | 2.9571 | 2.9818 | 3.0064 | 3.031 | 3.0556 | 3.0803 | 3.1049 | 3.1295 | 3.1541 | 3.1787 | 3.1952 | 3.2116 | 3.228 | 3.2444 | 3.2609 | 3.2773 | 3.2937 | 3.3101 | 3.3266 | 3.343 | 3.3594 | 3.3758 | 3.3923 | 3.4087 | 3.4251 | 3.4415 | 3.458 | 3.4744 | 3.4908 | 3.5072 | 3.5237 | 3.5401 | 3.5565 | 3.5729 | 3.5894 | 3.6058 | 3.6222 | 3.6386 | 3.6551 | 3.6715
3 | 0 | 0.565 | 0.53 | 0.525 | 0.45 | 0.55 | 0.68 | 1.605 | 2.53 | 3.295 | 3.81 | 0 | 0.0565 | 0.113 | 0.1695 | 0.226 | 0.2825 | 0.339 | 0.3955 | 0.452 | 0.5085 | 0.565 | 0.558 | 0.551 | 0.544 | 0.537 | 0.53 | 0.529 | 0.528 | 0.527 | 0.526 | 0.525 | 0.5175 | 0.51 | 0.5025 | 0.495 | 0.4875 | 0.48 | 0.4725 | 0.465 | 0.4575 | 0.45 | 0.45667 | 0.46333 | 0.47 | 0.47667 | 0.48333 | 0.49 | 0.49667 | 0.50333 | 0.51 | 0.51667 | 0.52333 | 0.53 | 0.53667 | 0.54333 | 0.55 | 0.55867 | 0.56733 | 0.576 | 0.58467 | 0.59333 | 0.602 | 0.61067 | 0.61933 | 0.628 | 0.63667 | 0.64533 | 0.654 | 0.66267 | 0.67133 | 0.68 | 0.71083 | 0.74167 | 0.7725 | 0.80333 | 0.83417 | 0.865 | 0.89583 | 0.92667 | 0.9575 | 0.98833 | 1.0192 | 1.05 | 1.0808 | 1.1117 | 1.1425 | 1.1733 | 1.2042 | 1.235 | 1.2658 | 1.2967 | 1.3275 | 1.3583 | 1.3892 | 1.42 | 1.4508 | 1.4817 | 1.5125 | 1.5433 | 1.5742 | 1.605 | 1.6358 | 1.6667 | 1.6975 | 1.7283 | 1.7592 | 1.79 | 1.8208 | 1.8517 | 1.8825 | 1.9133 | 1.9442 | 1.975 | 2.0058 | 2.0367 | 2.0675 | 2.0983 | 2.1292 | 2.16 | 2.1908 | 2.2217 | 2.2525 | 2.2833 | 2.3142 | 2.345 | 2.3758 | 2.4067 | 2.4375 | 2.4683 | 2.4992 | 2.53 | 2.5555 | 2.581 | 2.6065 | 2.632 | 2.6575 | 2.683 | 2.7085 | 2.734 | 2.7595 | 2.785 | 2.8105 | 2.836 | 2.8615 | 2.887 | 2.9125 | 2.938 | 2.9635 | 2.989 | 3.0145 | 3.04 | 3.0655 | 3.091 | 3.1165 | 3.142 | 3.1675 | 3.193 | 3.2185 | 3.244 | 3.2695 | 3.295 | 3.3122 | 3.3293 | 3.3465 | 3.3637 | 3.3808 | 3.398 | 3.4152 | 3.4323 | 3.4495 | 3.4667 | 3.4838 | 3.501 | 3.5182 | 3.5353 | 3.5525 | 3.5697 | 3.5868 | 3.604 | 3.6212 | 3.6383 | 3.6555 | 3.6727 | 3.6898 | 3.707 | 3.7242 | 3.7413 | 3.7585 | 3.7757 | 3.7928 | 3.81
3.05 | 0 | 0.58125 | 0.5425 | 0.53825 | 0.4625 | 0.5665 | 0.702 | 1.6607 | 2.62 | 3.4112 | 3.9485 | 0 | 0.058125 | 0.11625 | 0.17437 | 0.2325 | 0.29062 | 0.34875 | 0.40687 | 0.465 | 0.52312 | 0.58125 | 0.5735 | 0.56575 | 0.558 | 0.55025 | 0.5425 | 0.54165 | 0.5408 | 0.53995 | 0.5391 | 0.53825 | 0.53068 | 0.5231 | 0.51553 | 0.50795 | 0.50038 | 0.4928 | 0.48523 | 0.47765 | 0.47008 | 0.4625 | 0.46943 | 0.47637 | 0.4833 | 0.49023 | 0.49717 | 0.5041 | 0.51103 | 0.51797 | 0.5249 | 0.53183 | 0.53877 | 0.5457 | 0.55263 | 0.55957 | 0.5665 | 0.57553 | 0.58457 | 0.5936 | 0.60263 | 0.61167 | 0.6207 | 0.62973 | 0.63877 | 0.6478 | 0.65683 | 0.66587 | 0.6749 | 0.68393 | 0.69297 | 0.702 | 0.73396 | 0.76592 | 0.79787 | 0.82983 | 0.86179 | 0.89375 | 0.92571 | 0.95767 | 0.98962 | 1.0216 | 1.0535 | 1.0855 | 1.1175 | 1.1494 | 1.1814 | 1.2133 | 1.2453 | 1.2772 | 1.3092 | 1.3412 | 1.3731 | 1.4051 | 1.437 | 1.469 | 1.501 | 1.5329 | 1.5649 | 1.5968 | 1.6288 | 1.6607 | 1.6927 | 1.7247 | 1.7567 | 1.7886 | 1.8206 | 1.8526 | 1.8846 | 1.9165 | 1.9485 | 1.9805 | 2.0125 | 2.0444 | 2.0764 | 2.1084 | 2.1404 | 2.1723 | 2.2043 | 2.2363 | 2.2683 | 2.3002 | 2.3322 | 2.3642 | 2.3962 | 2.4281 | 2.4601 | 2.4921 | 2.5241 | 2.556 | 2.588 | 2.62 | 2.6464 | 2.6728 | 2.6991 | 2.7255 | 2.7519 | 2.7782 | 2.8046 | 2.831 | 2.8574 | 2.8838 | 2.9101 | 2.9365 | 2.9629 | 2.9892 | 3.0156 | 3.042 | 3.0684 | 3.0947 | 3.1211 | 3.1475 | 3.1739 | 3.2003 | 3.2266 | 3.253 | 3.2794 | 3.3057 | 3.3321 | 3.3585 | 3.3849 | 3.4112 | 3.4292 | 3.4471 | 3.465 | 3.4829 | 3.5008 | 3.5187 | 3.5366 | 3.5545 | 3.5724 | 3.5903 | 3.6082 | 3.6261 | 3.6441 | 3.662 | 3.6799 | 3.6978 | 3.7157 | 3.7336 | 3.7515 | 3.7694 | 3.7873 | 3.8052 | 3.8231 | 3.841 | 3.859 | 3.8769 | 3.8948 | 3.9127 | 3.9306 | 3.9485
3.1 | 0 | 0.5975 | 0.555 | 0.5515 | 0.475 | 0.583 | 0.724 | 1.7165 | 2.71 | 3.5275 | 4.087 | 0 | 0.05975 | 0.1195 | 0.17925 | 0.239 | 0.29875 | 0.3585 | 0.41825 | 0.478 | 0.53775 | 0.5975 | 0.589 | 0.5805 | 0.572 | 0.5635 | 0.555 | 0.5543 | 0.5536 | 0.5529 | 0.5522 | 0.5515 | 0.54385 | 0.5362 | 0.52855 | 0.5209 | 0.51325 | 0.5056 | 0.49795 | 0.4903 | 0.48265 | 0.475 | 0.4822 | 0.4894 | 0.4966 | 0.5038 | 0.511 | 0.5182 | 0.5254 | 0.5326 | 0.5398 | 0.547 | 0.5542 | 0.5614 | 0.5686 | 0.5758 | 0.583 | 0.5924 | 0.6018 | 0.6112 | 0.6206 | 0.63 | 0.6394 | 0.6488 | 0.6582 | 0.6676 | 0.677 | 0.6864 | 0.6958 | 0.7052 | 0.7146 | 0.724 | 0.75708 | 0.79017 | 0.82325 | 0.85633 | 0.88942 | 0.9225 | 0.95558 | 0.98867 | 1.0218 | 1.0548 | 1.0879 | 1.121 | 1.1541 | 1.1872 | 1.2203 | 1.2533 | 1.2864 | 1.3195 | 1.3526 | 1.3857 | 1.4188 | 1.4518 | 1.4849 | 1.518 | 1.5511 | 1.5842 | 1.6173 | 1.6503 | 1.6834 | 1.7165 | 1.7496 | 1.7827 | 1.8159 | 1.849 | 1.8821 | 1.9152 | 1.9483 | 1.9814 | 2.0145 | 2.0477 | 2.0808 | 2.1139 | 2.147 | 2.1801 | 2.2132 | 2.2464 | 2.2795 | 2.3126 | 2.3457 | 2.3788 | 2.412 | 2.4451 | 2.4782 | 2.5113 | 2.5444 | 2.5775 | 2.6107 | 2.6438 | 2.6769 | 2.71 | 2.7372 | 2.7645 | 2.7917 | 2.819 | 2.8462 | 2.8735 | 2.9007 | 2.928 | 2.9552 | 2.9825 | 3.0097 | 3.037 | 3.0642 | 3.0915 | 3.1187 | 3.146 | 3.1732 | 3.2005 | 3.2277 | 3.255 | 3.2822 | 3.3095 | 3.3367 | 3.364 | 3.3912 | 3.4185 | 3.4457 | 3.473 | 3.5002 | 3.5275 | 3.5461 | 3.5648 | 3.5835 | 3.6021 | 3.6207 | 3.6394 | 3.658 | 3.6767 | 3.6953 | 3.714 | 3.7327 | 3.7513 | 3.7699 | 3.7886 | 3.8072 | 3.8259 | 3.8445 | 3.8632 | 3.8819 | 3.9005 | 3.9191 | 3.9378 | 3.9564 | 3.9751 | 3.9937 | 4.0124 | 4.031 | 4.0497 | 4.0683 | 4.087
3.15 | 0 | 0.61375 | 0.5675 | 0.56475 | 0.4875 | 0.5995 | 0.746 | 1.7723 | 2.8 | 3.6437 | 4.2255 | 0 | 0.061375 | 0.12275 | 0.18412 | 0.2455 | 0.30687 | 0.36825 | 0.42962 | 0.491 | 0.55237 | 0.61375 | 0.6045 | 0.59525 | 0.586 | 0.57675 | 0.5675 | 0.56695 | 0.5664 | 0.56585 | 0.5653 | 0.56475 | 0.55702 | 0.5493 | 0.54157 | 0.53385 | 0.52612 | 0.5184 | 0.51067 | 0.50295 | 0.49522 | 0.4875 | 0.49497 | 0.50243 | 0.5099 | 0.51737 | 0.52483 | 0.5323 | 0.53977 | 0.54723 | 0.5547 | 0.56217 | 0.56963 | 0.5771 | 0.58457 | 0.59203 | 0.5995 | 0.60927 | 0.61903 | 0.6288 | 0.63857 | 0.64833 | 0.6581 | 0.66787 | 0.67763 | 0.6874 | 0.69717 | 0.70693 | 0.7167 | 0.72647 | 0.73623 | 0.746 | 0.78021 | 0.81442 | 0.84862 | 0.88283 | 0.91704 | 0.95125 | 0.98546 | 1.0197 | 1.0539 | 1.0881 | 1.1223 | 1.1565 | 1.1907 | 1.2249 | 1.2591 | 1.2933 | 1.3275 | 1.3617 | 1.396 | 1.4302 | 1.4644 | 1.4986 | 1.5328 | 1.567 | 1.6012 | 1.6354 | 1.6696 | 1.7038 | 1.738 | 1.7723 | 1.8065 | 1.8408 | 1.875 | 1.9093 | 1.9435 | 1.9778 | 2.0121 | 2.0463 | 2.0806 | 2.1148 | 2.1491 | 2.1834 | 2.2176 | 2.2519 | 2.2861 | 2.3204 | 2.3546 | 2.3889 | 2.4232 | 2.4574 | 2.4917 | 2.5259 | 2.5602 | 2.5945 | 2.6287 | 2.663 | 2.6972 | 2.7315 | 2.7657 | 2.8 | 2.8281 | 2.8562 | 2.8844 | 2.9125 | 2.9406 | 2.9688 | 2.9969 | 3.025 | 3.0531 | 3.0812 | 3.1094 | 3.1375 | 3.1656 | 3.1938 | 3.2219 | 3.25 | 3.2781 | 3.3062 | 3.3344 | 3.3625 | 3.3906 | 3.4187 | 3.4469 | 3.475 | 3.5031 | 3.5312 | 3.5594 | 3.5875 | 3.6156 | 3.6437 | 3.6631 | 3.6825 | 3.7019 | 3.7213 | 3.7407 | 3.7601 | 3.7795 | 3.7989 | 3.8183 | 3.8377 | 3.8571 | 3.8765 | 3.8958 | 3.9152 | 3.9346 | 3.954 | 3.9734 | 3.9928 | 4.0122 | 4.0316 | 4.051 | 4.0704 | 4.0898 | 4.1092 | 4.1285 | 4.1479 | 4.1673 | 4.1867 | 4.2061 | 4.2255
3.2 | 0 | 0.63 | 0.58 | 0.578 | 0.5 | 0.616 | 0.768 | 1.828 | 2.89 | 3.76 | 4.364 | 0 | 0.063 | 0.126 | 0.189 | 0.252 | 0.315 | 0.378 | 0.441 | 0.504 | 0.567 | 0.63 | 0.62 | 0.61 | 0.6 | 0.59 | 0.58 | 0.5796 | 0.5792 | 0.5788 | 0.5784 | 0.578 | 0.5702 | 0.5624 | 0.5546 | 0.5468 | 0.539 | 0.5312 | 0.5234 | 0.5156 | 0.5078 | 0.5 | 0.50773 | 0.51547 | 0.5232 | 0.53093 | 0.53867 | 0.5464 | 0.55413 | 0.56187 | 0.5696 | 0.57733 | 0.58507 | 0.5928 | 0.60053 | 0.60827 | 0.616 | 0.62613 | 0.63627 | 0.6464 | 0.65653 | 0.66667 | 0.6768 | 0.68693 | 0.69707 | 0.7072 | 0.71733 | 0.72747 | 0.7376 | 0.74773 | 0.75787 | 0.768 | 0.80333 | 0.83867 | 0.874 | 0.90933 | 0.94467 | 0.98 | 1.0153 | 1.0507 | 1.086 | 1.1213 | 1.1567 | 1.192 | 1.2273 | 1.2627 | 1.298 | 1.3333 | 1.3687 | 1.404 | 1.4393 | 1.4747 | 1.51 | 1.5453 | 1.5807 | 1.616 | 1.6513 | 1.6867 | 1.722 | 1.7573 | 1.7927 | 1.828 | 1.8634 | 1.8988 | 1.9342 | 1.9696 | 2.005 | 2.0404 | 2.0758 | 2.1112 | 2.1466 | 2.182 | 2.2174 | 2.2528 | 2.2882 | 2.3236 | 2.359 | 2.3944 | 2.4298 | 2.4652 | 2.5006 | 2.536 | 2.5714 | 2.6068 | 2.6422 | 2.6776 | 2.713 | 2.7484 | 2.7838 | 2.8192 | 2.8546 | 2.89 | 2.919 | 2.948 | 2.977 | 3.006 | 3.035 | 3.064 | 3.093 | 3.122 | 3.151 | 3.18 | 3.209 | 3.238 | 3.267 | 3.296 | 3.325 | 3.354 | 3.383 | 3.412 | 3.441 | 3.47 | 3.499 | 3.528 | 3.557 | 3.586 | 3.615 | 3.644 | 3.673 | 3.702 | 3.731 | 3.76 | 3.7801 | 3.8003 | 3.8204 | 3.8405 | 3.8607 | 3.8808 | 3.9009 | 3.9211 | 3.9412 | 3.9613 | 3.9815 | 4.0016 | 4.0217 | 4.0419 | 4.062 | 4.0821 | 4.1023 | 4.1224 | 4.1425 | 4.1627 | 4.1828 | 4.2029 | 4.2231 | 4.2432 | 4.2633 | 4.2835 | 4.3036 | 4.3237 | 4.3439 | 4.364
3.25 | 0 | 0.64625 | 0.5925 | 0.59125 | 0.5125 | 0.6325 | 0.79 | 1.8838 | 2.98 | 3.8762 | 4.5025 | 0 | 0.064625 | 0.12925 | 0.19388 | 0.2585 | 0.32312 | 0.38775 | 0.45238 | 0.517 | 0.58163 | 0.64625 | 0.6355 | 0.62475 | 0.614 | 0.60325 | 0.5925 | 0.59225 | 0.592 | 0.59175 | 0.5915 | 0.59125 | 0.58337 | 0.5755 | 0.56763 | 0.55975 | 0.55188 | 0.544 | 0.53612 | 0.52825 | 0.52037 | 0.5125 | 0.5205 | 0.5285 | 0.5365 | 0.5445 | 0.5525 | 0.5605 | 0.5685 | 0.5765 | 0.5845 | 0.5925 | 0.6005 | 0.6085 | 0.6165 | 0.6245 | 0.6325 | 0.643 | 0.6535 | 0.664 | 0.6745 | 0.685 | 0.6955 | 0.706 | 0.7165 | 0.727 | 0.7375 | 0.748 | 0.7585 | 0.769 | 0.7795 | 0.79 | 0.82646 | 0.86292 | 0.89938 | 0.93583 | 0.97229 | 1.0088 | 1.0452 | 1.0817 | 1.1181 | 1.1546 | 1.191 | 1.2275 | 1.264 | 1.3004 | 1.3369 | 1.3733 | 1.4098 | 1.4463 | 1.4827 | 1.5192 | 1.5556 | 1.5921 | 1.6285 | 1.665 | 1.7015 | 1.7379 | 1.7744 | 1.8108 | 1.8473 | 1.8838 | 1.9203 | 1.9568 | 1.9934 | 2.0299 | 2.0665 | 2.103 | 2.1395 | 2.1761 | 2.2126 | 2.2492 | 2.2857 | 2.3223 | 2.3588 | 2.3953 | 2.4319 | 2.4684 | 2.505 | 2.5415 | 2.578 | 2.6146 | 2.6511 | 2.6877 | 2.7242 | 2.7608 | 2.7973 | 2.8338 | 2.8704 | 2.9069 | 2.9435 | 2.98 | 3.0099 | 3.0398 | 3.0696 | 3.0995 | 3.1294 | 3.1593 | 3.1891 | 3.219 | 3.2489 | 3.2787 | 3.3086 | 3.3385 | 3.3684 | 3.3982 | 3.4281 | 3.458 | 3.4879 | 3.5177 | 3.5476 | 3.5775 | 3.6074 | 3.6372 | 3.6671 | 3.697 | 3.7269 | 3.7567 | 3.7866 | 3.8165 | 3.8464 | 3.8763 | 3.8971 | 3.918 | 3.9389 | 3.9598 | 3.9806 | 4.0015 | 4.0224 | 4.0433 | 4.0641 | 4.085 | 4.1059 | 4.1267 | 4.1476 | 4.1685 | 4.1894 | 4.2103 | 4.2311 | 4.252 | 4.2729 | 4.2938 | 4.3146 | 4.3355 | 4.3564 | 4.3773 | 4.3981 | 4.419 | 4.4399 | 4.4607 | 4.4816 | 4.5025
3.3 | 0 | 0.6625 | 0.605 | 0.6045 | 0.525 | 0.649 | 0.812 | 1.9395 | 3.07 | 3.9925 | 4.641 | 5.5511e-17 | 0.06625 | 0.1325 | 0.19875 | 0.265 | 0.33125 | 0.3975 | 0.46375 | 0.53 | 0.59625 | 0.6625 | 0.651 | 0.6395 | 0.628 | 0.6165 | 0.605 | 0.6049 | 0.6048 | 0.6047 | 0.6046 | 0.6045 | 0.59655 | 0.5886 | 0.58065 | 0.5727 | 0.56475 | 0.5568 | 0.54885 | 0.5409 | 0.53295 | 0.525 | 0.53327 | 0.54153 | 0.5498 | 0.55807 | 0.56633 | 0.5746 | 0.58287 | 0.59113 | 0.5994 | 0.60767 | 0.61593 | 0.6242 | 0.63247 | 0.64073 | 0.649 | 0.65987 | 0.67073 | 0.6816 | 0.69247 | 0.70333 | 0.7142 | 0.72507 | 0.73593 | 0.7468 | 0.75767 | 0.76853 | 0.7794 | 0.79027 | 0.80113 | 0.812 | 0.84958 | 0.88717 | 0.92475 | 0.96233 | 0.99992 | 1.0375 | 1.0751 | 1.1127 | 1.1502 | 1.1878 | 1.2254 | 1.263 | 1.3006 | 1.3382 | 1.3757 | 1.4133 | 1.4509 | 1.4885 | 1.5261 | 1.5637 | 1.6012 | 1.6388 | 1.6764 | 1.714 | 1.7516 | 1.7892 | 1.8267 | 1.8643 | 1.9019 | 1.9395 | 1.9772 | 2.0149 | 2.0525 | 2.0902 | 2.1279 | 2.1656 | 2.2033 | 2.241 | 2.2786 | 2.3163 | 2.354 | 2.3917 | 2.4294 | 2.4671 | 2.5047 | 2.5424 | 2.5801 | 2.6178 | 2.6555 | 2.6932 | 2.7308 | 2.7685 | 2.8062 | 2.8439 | 2.8816 | 2.9193 | 2.9569 | 2.9946 | 3.0323 | 3.07 | 3.1007 | 3.1315 | 3.1622 | 3.193 | 3.2237 | 3.2545 | 3.2852 | 3.316 | 3.3467 | 3.3775 | 3.4082 | 3.439 | 3.4697 | 3.5005 | 3.5312 | 3.562 | 3.5927 | 3.6235 | 3.6542 | 3.685 | 3.7157 | 3.7465 | 3.7772 | 3.808 | 3.8387 | 3.8695 | 3.9002 | 3.931 | 3.9617 | 3.9925 | 4.0141 | 4.0357 | 4.0573 | 4.079 | 4.1006 | 4.1222 | 4.1438 | 4.1654 | 4.187 | 4.2087 | 4.2303 | 4.2519 | 4.2735 | 4.2951 | 4.3167 | 4.3384 | 4.36 | 4.3816 | 4.4032 | 4.4248 | 4.4465 | 4.4681 | 4.4897 | 4.5113 | 4.5329 | 4.5545 | 4.5762 | 4.5978 | 4.6194 | 4.641
3.35 | 0 | 0.67875 | 0.6175 | 0.61775 | 0.5375 | 0.6655 | 0.834 | 1.9952 | 3.16 | 4.1088 | 4.7795 | 0 | 0.067875 | 0.13575 | 0.20362 | 0.2715 | 0.33937 | 0.40725 | 0.47512 | 0.543 | 0.61087 | 0.67875 | 0.6665 | 0.65425 | 0.642 | 0.62975 | 0.6175 | 0.61755 | 0.6176 | 0.61765 | 0.6177 | 0.61775 | 0.60973 | 0.6017 | 0.59367 | 0.58565 | 0.57763 | 0.5696 | 0.56157 | 0.55355 | 0.54553 | 0.5375 | 0.54603 | 0.55457 | 0.5631 | 0.57163 | 0.58017 | 0.5887 | 0.59723 | 0.60577 | 0.6143 | 0.62283 | 0.63137 | 0.6399 | 0.64843 | 0.65697 | 0.6655 | 0.67673 | 0.68797 | 0.6992 | 0.71043 | 0.72167 | 0.7329 | 0.74413 | 0.75537 | 0.7666 | 0.77783 | 0.78907 | 0.8003 | 0.81153 | 0.82277 | 0.834 | 0.87271 | 0.91142 | 0.95013 | 0.98883 | 1.0275 | 1.0663 | 1.105 | 1.1437 | 1.1824 | 1.2211 | 1.2598 | 1.2985 | 1.3372 | 1.3759 | 1.4146 | 1.4533 | 1.492 | 1.5308 | 1.5695 | 1.6082 | 1.6469 | 1.6856 | 1.7243 | 1.763 | 1.8017 | 1.8404 | 1.8791 | 1.9178 | 1.9565 | 1.9952 | 2.0341 | 2.0729 | 2.1117 | 2.1505 | 2.1894 | 2.2282 | 2.267 | 2.3058 | 2.3447 | 2.3835 | 2.4223 | 2.4611 | 2.5 | 2.5388 | 2.5776 | 2.6164 | 2.6553 | 2.6941 | 2.7329 | 2.7717 | 2.8106 | 2.8494 | 2.8882 | 2.9271 | 2.9659 | 3.0047 | 3.0435 | 3.0823 | 3.1212 | 3.16 | 3.1916 | 3.2233 | 3.2549 | 3.2865 | 3.3181 | 3.3498 | 3.3814 | 3.413 | 3.4446 | 3.4763 | 3.5079 | 3.5395 | 3.5711 | 3.6028 | 3.6344 | 3.666 | 3.6976 | 3.7293 | 3.7609 | 3.7925 | 3.8241 | 3.8558 | 3.8874 | 3.919 | 3.9506 | 3.9823 | 4.0139 | 4.0455 | 4.0771 | 4.1088 | 4.1311 | 4.1535 | 4.1758 | 4.1982 | 4.2205 | 4.2429 | 4.2653 | 4.2876 | 4.31 | 4.3323 | 4.3547 | 4.3771 | 4.3994 | 4.4218 | 4.4441 | 4.4665 | 4.4888 | 4.5112 | 4.5336 | 4.5559 | 4.5783 | 4.6006 | 4.623 | 4.6454 | 4.6677 | 4.6901 | 4.7124 | 4.7348 | 4.7571 | 4.7795
3.4 | 0 | 0.695 | 0.63 | 0.631 | 0.55 | 0.682 | 0.856 | 2.051 | 3.25 | 4.225 | 4.918 | 0 | 0.0695 | 0.139 | 0.2085 | 0.278 | 0.3475 | 0.417 | 0.4865 | 0.556 | 0.6255 | 0.695 | 0.682 | 0.669 | 0.656 | 0.643 | 0.63 | 0.6302 | 0.6304 | 0.6306 | 0.6308 | 0.631 | 0.6229 | 0.6148 | 0.6067 | 0.5986 | 0.5905 | 0.5824 | 0.5743 | 0.5662 | 0.5581 | 0.55 | 0.5588 | 0.5676 | 0.5764 | 0.5852 | 0.594 | 0.6028 | 0.6116 | 0.6204 | 0.6292 | 0.638 | 0.6468 | 0.6556 | 0.6644 | 0.6732 | 0.682 | 0.6936 | 0.7052 | 0.7168 | 0.7284 | 0.74 | 0.7516 | 0.7632 | 0.7748 | 0.7864 | 0.798 | 0.8096 | 0.8212 | 0.8328 | 0.8444 | 0.856 | 0.89583 | 0.93567 | 0.9755 | 1.0153 | 1.0552 | 1.095 | 1.1348 | 1.1747 | 1.2145 | 1.2543 | 1.2942 | 1.334 | 1.3738 | 1.4137 | 1.4535 | 1.4933 | 1.5332 | 1.573 | 1.6128 | 1.6527 | 1.6925 | 1.7323 | 1.7722 | 1.812 | 1.8518 | 1.8917 | 1.9315 | 1.9713 | 2.0112 | 2.051 | 2.091 | 2.1309 | 2.1709 | 2.2109 | 2.2508 | 2.2908 | 2.3308 | 2.3707 | 2.4107 | 2.4507 | 2.4906 | 2.5306 | 2.5706 | 2.6105 | 2.6505 | 2.6905 | 2.7304 | 2.7704 | 2.8104 | 2.8503 | 2.8903 | 2.9303 | 2.9702 | 3.0102 | 3.0502 | 3.0901 | 3.1301 | 3.1701 | 3.21 | 3.25 | 3.2825 | 3.315 | 3.3475 | 3.38 | 3.4125 | 3.445 | 3.4775 | 3.51 | 3.5425 | 3.575 | 3.6075 | 3.64 | 3.6725 | 3.705 | 3.7375 | 3.77 | 3.8025 | 3.835 | 3.8675 | 3.9 | 3.9325 | 3.965 | 3.9975 | 4.03 | 4.0625 | 4.095 | 4.1275 | 4.16 | 4.1925 | 4.225 | 4.2481 | 4.2712 | 4.2943 | 4.3174 | 4.3405 | 4.3636 | 4.3867 | 4.4098 | 4.4329 | 4.456 | 4.4791 | 4.5022 | 4.5253 | 4.5484 | 4.5715 | 4.5946 | 4.6177 | 4.6408 | 4.6639 | 4.687 | 4.7101 | 4.7332 | 4.7563 | 4.7794 | 4.8025 | 4.8256 | 4.8487 | 4.8718 | 4.8949 | 4.918
3.45 | 0 | 0.71125 | 0.6425 | 0.64425 | 0.5625 | 0.6985 | 0.878 | 2.1068 | 3.34 | 4.3412 | 5.0565 | 0 | 0.071125 | 0.14225 | 0.21337 | 0.2845 | 0.35562 | 0.42675 | 0.49787 | 0.569 | 0.64012 | 0.71125 | 0.6975 | 0.68375 | 0.67 | 0.65625 | 0.6425 | 0.64285 | 0.6432 | 0.64355 | 0.6439 | 0.64425 | 0.63607 | 0.6279 | 0.61972 | 0.61155 | 0.60337 | 0.5952 | 0.58702 | 0.57885 | 0.57067 | 0.5625 | 0.57157 | 0.58063 | 0.5897 | 0.59877 | 0.60783 | 0.6169 | 0.62597 | 0.63503 | 0.6441 | 0.65317 | 0.66223 | 0.6713 | 0.68037 | 0.68943 | 0.6985 | 0.71047 | 0.72243 | 0.7344 | 0.74637 | 0.75833 | 0.7703 | 0.78227 | 0.79423 | 0.8062 | 0.81817 | 0.83013 | 0.8421 | 0.85407 | 0.86603 | 0.878 | 0.91896 | 0.95992 | 1.0009 | 1.0418 | 1.0828 | 1.1238 | 1.1647 | 1.2057 | 1.2466 | 1.2876 | 1.3285 | 1.3695 | 1.4105 | 1.4514 | 1.4924 | 1.5333 | 1.5743 | 1.6153 | 1.6562 | 1.6972 | 1.7381 | 1.7791 | 1.82 | 1.861 | 1.902 | 1.9429 | 1.9839 | 2.0248 | 2.0658 | 2.1068 | 2.1479 | 2.189 | 2.2301 | 2.2712 | 2.3123 | 2.3534 | 2.3945 | 2.4356 | 2.4767 | 2.5178 | 2.5589 | 2.6001 | 2.6412 | 2.6823 | 2.7234 | 2.7645 | 2.8056 | 2.8467 | 2.8878 | 2.9289 | 2.97 | 3.0111 | 3.0522 | 3.0934 | 3.1345 | 3.1756 | 3.2167 | 3.2578 | 3.2989 | 3.34 | 3.3734 | 3.4068 | 3.4401 | 3.4735 | 3.5069 | 3.5403 | 3.5736 | 3.607 | 3.6404 | 3.6738 | 3.7071 | 3.7405 | 3.7739 | 3.8072 | 3.8406 | 3.874 | 3.9074 | 3.9407 | 3.9741 | 4.0075 | 4.0409 | 4.0742 | 4.1076 | 4.141 | 4.1744 | 4.2077 | 4.2411 | 4.2745 | 4.3079 | 4.3412 | 4.3651 | 4.3889 | 4.4128 | 4.4366 | 4.4605 | 4.4843 | 4.5081 | 4.532 | 4.5558 | 4.5797 | 4.6035 | 4.6273 | 4.6512 | 4.675 | 4.6989 | 4.7227 | 4.7466 | 4.7704 | 4.7942 | 4.8181 | 4.8419 | 4.8658 | 4.8896 | 4.9134 | 4.9373 | 4.9611 | 4.985 | 5.0088 | 5.0327 | 5.0565
3.5 | 0 | 0.7275 | 0.655 | 0.6575 | 0.575 | 0.715 | 0.9 | 2.1625 | 3.43 | 4.4575 | 5.195 | 0 | 0.07275 | 0.1455 | 0.21825 | 0.291 | 0.36375 | 0.4365 | 0.50925 | 0.582 | 0.65475 | 0.7275 | 0.713 | 0.6985 | 0.684 | 0.6695 | 0.655 | 0.6555 | 0.656 | 0.6565 | 0.657 | 0.6575 | 0.64925 | 0.641 | 0.63275 | 0.6245 | 0.61625 | 0.608 | 0.59975 | 0.5915 | 0.58325 | 0.575 | 0.58433 | 0.59367 | 0.603 | 0.61233 | 0.62167 | 0.631 | 0.64033 | 0.64967 | 0.659 | 0.66833 | 0.67767 | 0.687 | 0.69633 | 0.70567 | 0.715 | 0.72733 | 0.73967 | 0.752 | 0.76433 | 0.77667 | 0.789 | 0.80133 | 0.81367 | 0.826 | 0.83833 | 0.85067 | 0.863 | 0.87533 | 0.88767 | 0.9 | 0.94208 | 0.98417 | 1.0263 | 1.0683 | 1.1104 | 1.1525 | 1.1946 | 1.2367 | 1.2788 | 1.3208 | 1.3629 | 1.405 | 1.4471 | 1.4892 | 1.5312 | 1.5733 | 1.6154 | 1.6575 | 1.6996 | 1.7417 | 1.7837 | 1.8258 | 1.8679 | 1.91 | 1.9521 | 1.9942 | 2.0362 | 2.0783 | 2.1204 | 2.1625 | 2.2048 | 2.247 | 2.2893 | 2.3315 | 2.3738 | 2.416 | 2.4583 | 2.5005 | 2.5427 | 2.585 | 2.6273 | 2.6695 | 2.7118 | 2.754 | 2.7962 | 2.8385 | 2.8807 | 2.923 | 2.9653 | 3.0075 | 3.0498 | 3.092 | 3.1342 | 3.1765 | 3.2188 | 3.261 | 3.3033 | 3.3455 | 3.3877 | 3.43 | 3.4643 | 3.4985 | 3.5328 | 3.567 | 3.6012 | 3.6355 | 3.6698 | 3.704 | 3.7383 | 3.7725 | 3.8068 | 3.841 | 3.8752 | 3.9095 | 3.9438 | 3.978 | 4.0122 | 4.0465 | 4.0808 | 4.115 | 4.1493 | 4.1835 | 4.2178 | 4.252 | 4.2863 | 4.3205 | 4.3548 | 4.389 | 4.4233 | 4.4575 | 4.4821 | 4.5067 | 4.5312 | 4.5558 | 4.5804 | 4.605 | 4.6296 | 4.6542 | 4.6787 | 4.7033 | 4.7279 | 4.7525 | 4.7771 | 4.8017 | 4.8262 | 4.8508 | 4.8754 | 4.9 | 4.9246 | 4.9492 | 4.9737 | 4.9983 | 5.0229 | 5.0475 | 5.0721 | 5.0967 | 5.1212 | 5.1458 | 5.1704 | 5.195
3.55 | 0 | 0.74375 | 0.6675 | 0.67075 | 0.5875 | 0.7315 | 0.922 | 2.2182 | 3.52 | 4.5737 | 5.3335 | 0 | 0.074375 | 0.14875 | 0.22312 | 0.2975 | 0.37187 | 0.44625 | 0.52063 | 0.595 | 0.66937 | 0.74375 | 0.7285 | 0.71325 | 0.698 | 0.68275 | 0.6675 | 0.66815 | 0.6688 | 0.66945 | 0.6701 | 0.67075 | 0.66242 | 0.6541 | 0.64577 | 0.63745 | 0.62912 | 0.6208 | 0.61247 | 0.60415 | 0.59582 | 0.5875 | 0.5971 | 0.6067 | 0.6163 | 0.6259 | 0.6355 | 0.6451 | 0.6547 | 0.6643 | 0.6739 | 0.6835 | 0.6931 | 0.7027 | 0.7123 | 0.7219 | 0.7315 | 0.7442 | 0.7569 | 0.7696 | 0.7823 | 0.795 | 0.8077 | 0.8204 | 0.8331 | 0.8458 | 0.8585 | 0.8712 | 0.8839 | 0.8966 | 0.9093 | 0.922 | 0.96521 | 1.0084 | 1.0516 | 1.0948 | 1.138 | 1.1812 | 1.2245 | 1.2677 | 1.3109 | 1.3541 | 1.3973 | 1.4405 | 1.4837 | 1.5269 | 1.5701 | 1.6133 | 1.6565 | 1.6997 | 1.743 | 1.7862 | 1.8294 | 1.8726 | 1.9158 | 1.959 | 2.0022 | 2.0454 | 2.0886 | 2.1318 | 2.175 | 2.2182 | 2.2616 | 2.305 | 2.3484 | 2.3918 | 2.4352 | 2.4786 | 2.522 | 2.5654 | 2.6088 | 2.6522 | 2.6956 | 2.7389 | 2.7823 | 2.8257 | 2.8691 | 2.9125 | 2.9559 | 2.9993 | 3.0427 | 3.0861 | 3.1295 | 3.1729 | 3.2163 | 3.2596 | 3.303 | 3.3464 | 3.3898 | 3.4332 | 3.4766 | 3.52 | 3.5551 | 3.5903 | 3.6254 | 3.6605 | 3.6956 | 3.7308 | 3.7659 | 3.801 | 3.8361 | 3.8712 | 3.9064 | 3.9415 | 3.9766 | 4.0118 | 4.0469 | 4.082 | 4.1171 | 4.1523 | 4.1874 | 4.2225 | 4.2576 | 4.2927 | 4.3279 | 4.363 | 4.3981 | 4.4333 | 4.4684 | 4.5035 | 4.5386 | 4.5737 | 4.5991 | 4.6244 | 4.6497 | 4.675 | 4.7004 | 4.7257 | 4.751 | 4.7763 | 4.8017 | 4.827 | 4.8523 | 4.8776 | 4.903 | 4.9283 | 4.9536 | 4.9789 | 5.0043 | 5.0296 | 5.0549 | 5.0802 | 5.1056 | 5.1309 | 5.1562 | 5.1815 | 5.2069 | 5.2322 | 5.2575 | 5.2828 | 5.3082 | 5.3335
3.6 | 0 | 0.76 | 0.68 | 0.684 | 0.6 | 0.748 | 0.944 | 2.274 | 3.61 | 4.69 | 5.472 | 0 | 0.076 | 0.152 | 0.228 | 0.304 | 0.38 | 0.456 | 0.532 | 0.608 | 0.684 | 0.76 | 0.744 | 0.728 | 0.712 | 0.696 | 0.68 | 0.6808 | 0.6816 | 0.6824 | 0.6832 | 0.684 | 0.6756 | 0.6672 | 0.6588 | 0.6504 | 0.642 | 0.6336 | 0.6252 | 0.6168 | 0.6084 | 0.6 | 0.60987 | 0.61973 | 0.6296 | 0.63947 | 0.64933 | 0.6592 | 0.66907 | 0.67893 | 0.6888 | 0.69867 | 0.70853 | 0.7184 | 0.72827 | 0.73813 | 0.748 | 0.76107 | 0.77413 | 0.7872 | 0.80027 | 0.81333 | 0.8264 | 0.83947 | 0.85253 | 0.8656 | 0.87867 | 0.89173 | 0.9048 | 0.91787 | 0.93093 | 0.944 | 0.98833 | 1.0327 | 1.077 | 1.1213 | 1.1657 | 1.21 | 1.2543 | 1.2987 | 1.343 | 1.3873 | 1.4317 | 1.476 | 1.5203 | 1.5647 | 1.609 | 1.6533 | 1.6977 | 1.742 | 1.7863 | 1.8307 | 1.875 | 1.9193 | 1.9637 | 2.008 | 2.0523 | 2.0967 | 2.141 | 2.1853 | 2.2297 | 2.274 | 2.3185 | 2.3631 | 2.4076 | 2.4521 | 2.4967 | 2.5412 | 2.5857 | 2.6303 | 2.6748 | 2.7193 | 2.7639 | 2.8084 | 2.8529 | 2.8975 | 2.942 | 2.9865 | 3.0311 | 3.0756 | 3.1201 | 3.1647 | 3.2092 | 3.2537 | 3.2983 | 3.3428 | 3.3873 | 3.4319 | 3.4764 | 3.5209 | 3.5655 | 3.61 | 3.646 | 3.682 | 3.718 | 3.754 | 3.79 | 3.826 | 3.862 | 3.898 | 3.934 | 3.97 | 4.006 | 4.042 | 4.078 | 4.114 | 4.15 | 4.186 | 4.222 | 4.258 | 4.294 | 4.33 | 4.366 | 4.402 | 4.438 | 4.474 | 4.51 | 4.546 | 4.582 | 4.618 | 4.654 | 4.69 | 4.7161 | 4.7421 | 4.7682 | 4.7943 | 4.8203 | 4.8464 | 4.8725 | 4.8985 | 4.9246 | 4.9507 | 4.9767 | 5.0028 | 5.0289 | 5.0549 | 5.081 | 5.1071 | 5.1331 | 5.1592 | 5.1853 | 5.2113 | 5.2374 | 5.2635 | 5.2895 | 5.3156 | 5.3417 | 5.3677 | 5.3938 | 5.4199 | 5.4459 | 5.472
3.65 | 0 | 0.77625 | 0.6925 | 0.69725 | 0.6125 | 0.7645 | 0.966 | 2.3298 | 3.7 | 4.8062 | 5.6105 | -5.5511e-17 | 0.077625 | 0.15525 | 0.23287 | 0.3105 | 0.38812 | 0.46575 | 0.54337 | 0.621 | 0.69863 | 0.77625 | 0.7595 | 0.74275 | 0.726 | 0.70925 | 0.6925 | 0.69345 | 0.6944 | 0.69535 | 0.6963 | 0.69725 | 0.68878 | 0.6803 | 0.67183 | 0.66335 | 0.65487 | 0.6464 | 0.63792 | 0.62945 | 0.62097 | 0.6125 | 0.62263 | 0.63277 | 0.6429 | 0.65303 | 0.66317 | 0.6733 | 0.68343 | 0.69357 | 0.7037 | 0.71383 | 0.72397 | 0.7341 | 0.74423 | 0.75437 | 0.7645 | 0.77793 | 0.79137 | 0.8048 | 0.81823 | 0.83167 | 0.8451 | 0.85853 | 0.87197 | 0.8854 | 0.89883 | 0.91227 | 0.9257 | 0.93913 | 0.95257 | 0.966 | 1.0115 | 1.0569 | 1.1024 | 1.1478 | 1.1933 | 1.2388 | 1.2842 | 1.3297 | 1.3751 | 1.4206 | 1.466 | 1.5115 | 1.557 | 1.6024 | 1.6479 | 1.6933 | 1.7388 | 1.7843 | 1.8297 | 1.8752 | 1.9206 | 1.9661 | 2.0115 | 2.057 | 2.1025 | 2.1479 | 2.1934 | 2.2388 | 2.2843 | 2.3298 | 2.3754 | 2.4211 | 2.4668 | 2.5125 | 2.5581 | 2.6038 | 2.6495 | 2.6951 | 2.7408 | 2.7865 | 2.8322 | 2.8779 | 2.9235 | 2.9692 | 3.0149 | 3.0606 | 3.1062 | 3.1519 | 3.1976 | 3.2433 | 3.2889 | 3.3346 | 3.3803 | 3.426 | 3.4716 | 3.5173 | 3.563 | 3.6086 | 3.6543 | 3.7 | 3.7369 | 3.7738 | 3.8106 | 3.8475 | 3.8844 | 3.9213 | 3.9581 | 3.995 | 4.0319 | 4.0687 | 4.1056 | 4.1425 | 4.1794 | 4.2162 | 4.2531 | 4.29 | 4.3269 | 4.3637 | 4.4006 | 4.4375 | 4.4744 | 4.5112 | 4.5481 | 4.585 | 4.6219 | 4.6587 | 4.6956 | 4.7325 | 4.7694 | 4.8062 | 4.8331 | 4.8599 | 4.8867 | 4.9135 | 4.9403 | 4.9671 | 4.9939 | 5.0207 | 5.0475 | 5.0743 | 5.1011 | 5.128 | 5.1548 | 5.1816 | 5.2084 | 5.2352 | 5.262 | 5.2888 | 5.3156 | 5.3424 | 5.3692 | 5.396 | 5.4228 | 5.4497 | 5.4765 | 5.5033 | 5.5301 | 5.5569 | 5.5837 | 5.6105
3.7 | 0 | 0.7925 | 0.705 | 0.7105 | 0.625 | 0.781 | 0.988 | 2.3855 | 3.79 | 4.9225 | 5.749 | 0 | 0.07925 | 0.1585 | 0.23775 | 0.317 | 0.39625 | 0.4755 | 0.55475 | 0.634 | 0.71325 | 0.7925 | 0.775 | 0.7575 | 0.74 | 0.7225 | 0.705 | 0.7061 | 0.7072 | 0.7083 | 0.7094 | 0.7105 | 0.70195 | 0.6934 | 0.68485 | 0.6763 | 0.66775 | 0.6592 | 0.65065 | 0.6421 | 0.63355 | 0.625 | 0.6354 | 0.6458 | 0.6562 | 0.6666 | 0.677 | 0.6874 | 0.6978 | 0.7082 | 0.7186 | 0.729 | 0.7394 | 0.7498 | 0.7602 | 0.7706 | 0.781 | 0.7948 | 0.8086 | 0.8224 | 0.8362 | 0.85 | 0.8638 | 0.8776 | 0.8914 | 0.9052 | 0.919 | 0.9328 | 0.9466 | 0.9604 | 0.9742 | 0.988 | 1.0346 | 1.0812 | 1.1277 | 1.1743 | 1.2209 | 1.2675 | 1.3141 | 1.3607 | 1.4072 | 1.4538 | 1.5004 | 1.547 | 1.5936 | 1.6402 | 1.6867 | 1.7333 | 1.7799 | 1.8265 | 1.8731 | 1.9197 | 1.9663 | 2.0128 | 2.0594 | 2.106 | 2.1526 | 2.1992 | 2.2457 | 2.2923 | 2.3389 | 2.3855 | 2.4323 | 2.4791 | 2.5259 | 2.5728 | 2.6196 | 2.6664 | 2.7132 | 2.76 | 2.8068 | 2.8537 | 2.9005 | 2.9473 | 2.9941 | 3.0409 | 3.0877 | 3.1346 | 3.1814 | 3.2282 | 3.275 | 3.3218 | 3.3686 | 3.4155 | 3.4623 | 3.5091 | 3.5559 | 3.6027 | 3.6495 | 3.6964 | 3.7432 | 3.79 | 3.8278 | 3.8655 | 3.9033 | 3.941 | 3.9788 | 4.0165 | 4.0543 | 4.092 | 4.1298 | 4.1675 | 4.2053 | 4.243 | 4.2808 | 4.3185 | 4.3563 | 4.394 | 4.4318 | 4.4695 | 4.5073 | 4.545 | 4.5828 | 4.6205 | 4.6583 | 4.696 | 4.7338 | 4.7715 | 4.8093 | 4.847 | 4.8848 | 4.9225 | 4.9501 | 4.9776 | 5.0052 | 5.0327 | 5.0603 | 5.0878 | 5.1154 | 5.1429 | 5.1705 | 5.198 | 5.2256 | 5.2531 | 5.2807 | 5.3082 | 5.3358 | 5.3633 | 5.3909 | 5.4184 | 5.446 | 5.4735 | 5.5011 | 5.5286 | 5.5562 | 5.5837 | 5.6113 | 5.6388 | 5.6664 | 5.6939 | 5.7215 | 5.749
3.75 | 0 | 0.80875 | 0.7175 | 0.72375 | 0.6375 | 0.7975 | 1.01 | 2.4412 | 3.88 | 5.0387 | 5.8875 | 0 | 0.080875 | 0.16175 | 0.24262 | 0.3235 | 0.40437 | 0.48525 | 0.56612 | 0.647 | 0.72787 | 0.80875 | 0.7905 | 0.77225 | 0.754 | 0.73575 | 0.7175 | 0.71875 | 0.72 | 0.72125 | 0.7225 | 0.72375 | 0.71513 | 0.7065 | 0.69788 | 0.68925 | 0.68063 | 0.672 | 0.66338 | 0.65475 | 0.64613 | 0.6375 | 0.64817 | 0.65883 | 0.6695 | 0.68017 | 0.69083 | 0.7015 | 0.71217 | 0.72283 | 0.7335 | 0.74417 | 0.75483 | 0.7655 | 0.77617 | 0.78683 | 0.7975 | 0.81167 | 0.82583 | 0.84 | 0.85417 | 0.86833 | 0.8825 | 0.89667 | 0.91083 | 0.925 | 0.93917 | 0.95333 | 0.9675 | 0.98167 | 0.99583 | 1.01 | 1.0577 | 1.1054 | 1.1531 | 1.2008 | 1.2485 | 1.2962 | 1.344 | 1.3917 | 1.4394 | 1.4871 | 1.5348 | 1.5825 | 1.6302 | 1.6779 | 1.7256 | 1.7733 | 1.821 | 1.8687 | 1.9165 | 1.9642 | 2.0119 | 2.0596 | 2.1073 | 2.155 | 2.2027 | 2.2504 | 2.2981 | 2.3458 | 2.3935 | 2.4412 | 2.4892 | 2.5372 | 2.5851 | 2.6331 | 2.681 | 2.729 | 2.777 | 2.8249 | 2.8729 | 2.9208 | 2.9688 | 3.0167 | 3.0647 | 3.1127 | 3.1606 | 3.2086 | 3.2565 | 3.3045 | 3.3525 | 3.4004 | 3.4484 | 3.4963 | 3.5443 | 3.5922 | 3.6402 | 3.6882 | 3.7361 | 3.7841 | 3.832 | 3.88 | 3.9186 | 3.9573 | 3.9959 | 4.0345 | 4.0731 | 4.1117 | 4.1504 | 4.189 | 4.2276 | 4.2663 | 4.3049 | 4.3435 | 4.3821 | 4.4207 | 4.4594 | 4.498 | 4.5366 | 4.5752 | 4.6139 | 4.6525 | 4.6911 | 4.7298 | 4.7684 | 4.807 | 4.8456 | 4.8842 | 4.9229 | 4.9615 | 5.0001 | 5.0388 | 5.067 | 5.0953 | 5.1236 | 5.1519 | 5.1802 | 5.2085 | 5.2368 | 5.2651 | 5.2934 | 5.3217 | 5.35 | 5.3782 | 5.4065 | 5.4348 | 5.4631 | 5.4914 | 5.5197 | 5.548 | 5.5763 | 5.6046 | 5.6329 | 5.6612 | 5.6895 | 5.7177 | 5.746 | 5.7743 | 5.8026 | 5.8309 | 5.8592 | 5.8875
3.8 | 0 | 0.825 | 0.73 | 0.737 | 0.65 | 0.814 | 1.032 | 2.497 | 3.97 | 5.155 | 6.026 | 5.5511e-17 | 0.0825 | 0.165 | 0.2475 | 0.33 | 0.4125 | 0.495 | 0.5775 | 0.66 | 0.7425 | 0.825 | 0.806 | 0.787 | 0.768 | 0.749 | 0.73 | 0.7314 | 0.7328 | 0.7342 | 0.7356 | 0.737 | 0.7283 | 0.7196 | 0.7109 | 0.7022 | 0.6935 | 0.6848 | 0.6761 | 0.6674 | 0.6587 | 0.65 | 0.66093 | 0.67187 | 0.6828 | 0.69373 | 0.70467 | 0.7156 | 0.72653 | 0.73747 | 0.7484 | 0.75933 | 0.77027 | 0.7812 | 0.79213 | 0.80307 | 0.814 | 0.82853 | 0.84307 | 0.8576 | 0.87213 | 0.88667 | 0.9012 | 0.91573 | 0.93027 | 0.9448 | 0.95933 | 0.97387 | 0.9884 | 1.0029 | 1.0175 | 1.032 | 1.0808 | 1.1297 | 1.1785 | 1.2273 | 1.2762 | 1.325 | 1.3738 | 1.4227 | 1.4715 | 1.5203 | 1.5692 | 1.618 | 1.6668 | 1.7157 | 1.7645 | 1.8133 | 1.8622 | 1.911 | 1.9598 | 2.0087 | 2.0575 | 2.1063 | 2.1552 | 2.204 | 2.2528 | 2.3017 | 2.3505 | 2.3993 | 2.4482 | 2.497 | 2.5461 | 2.5952 | 2.6443 | 2.6934 | 2.7425 | 2.7916 | 2.8407 | 2.8898 | 2.9389 | 2.988 | 3.0371 | 3.0862 | 3.1353 | 3.1844 | 3.2335 | 3.2826 | 3.3317 | 3.3808 | 3.4299 | 3.479 | 3.5281 | 3.5772 | 3.6263 | 3.6754 | 3.7245 | 3.7736 | 3.8227 | 3.8718 | 3.9209 | 3.97 | 4.0095 | 4.049 | 4.0885 | 4.128 | 4.1675 | 4.207 | 4.2465 | 4.286 | 4.3255 | 4.365 | 4.4045 | 4.444 | 4.4835 | 4.523 | 4.5625 | 4.602 | 4.6415 | 4.681 | 4.7205 | 4.76 | 4.7995 | 4.839 | 4.8785 | 4.918 | 4.9575 | 4.997 | 5.0365 | 5.076 | 5.1155 | 5.155 | 5.184 | 5.2131 | 5.2421 | 5.2711 | 5.3002 | 5.3292 | 5.3582 | 5.3873 | 5.4163 | 5.4453 | 5.4744 | 5.5034 | 5.5324 | 5.5615 | 5.5905 | 5.6195 | 5.6486 | 5.6776 | 5.7066 | 5.7357 | 5.7647 | 5.7937 | 5.8228 | 5.8518 | 5.8808 | 5.9099 | 5.9389 | 5.9679 | 5.997 | 6.026
3.85 | 0 | 0.84125 | 0.7425 | 0.75025 | 0.6625 | 0.8305 | 1.054 | 2.5528 | 4.06 | 5.2713 | 6.1645 | 0 | 0.084125 | 0.16825 | 0.25237 | 0.3365 | 0.42062 | 0.50475 | 0.58887 | 0.673 | 0.75712 | 0.84125 | 0.8215 | 0.80175 | 0.782 | 0.76225 | 0.7425 | 0.74405 | 0.7456 | 0.74715 | 0.7487 | 0.75025 | 0.74148 | 0.7327 | 0.72393 | 0.71515 | 0.70637 | 0.6976 | 0.68883 | 0.68005 | 0.67128 | 0.6625 | 0.6737 | 0.6849 | 0.6961 | 0.7073 | 0.7185 | 0.7297 | 0.7409 | 0.7521 | 0.7633 | 0.7745 | 0.7857 | 0.7969 | 0.8081 | 0.8193 | 0.8305 | 0.8454 | 0.8603 | 0.8752 | 0.8901 | 0.905 | 0.9199 | 0.9348 | 0.9497 | 0.9646 | 0.9795 | 0.9944 | 1.0093 | 1.0242 | 1.0391 | 1.054 | 1.104 | 1.1539 | 1.2039 | 1.2538 | 1.3038 | 1.3537 | 1.4037 | 1.4537 | 1.5036 | 1.5536 | 1.6035 | 1.6535 | 1.7035 | 1.7534 | 1.8034 | 1.8533 | 1.9033 | 1.9532 | 2.0032 | 2.0532 | 2.1031 | 2.1531 | 2.203 | 2.253 | 2.303 | 2.3529 | 2.4029 | 2.4528 | 2.5028 | 2.5527 | 2.603 | 2.6532 | 2.7035 | 2.7537 | 2.804 | 2.8542 | 2.9044 | 2.9547 | 3.0049 | 3.0552 | 3.1054 | 3.1556 | 3.2059 | 3.2561 | 3.3064 | 3.3566 | 3.4069 | 3.4571 | 3.5073 | 3.5576 | 3.6078 | 3.6581 | 3.7083 | 3.7585 | 3.8088 | 3.859 | 3.9093 | 3.9595 | 4.0098 | 4.06 | 4.1004 | 4.1407 | 4.1811 | 4.2215 | 4.2619 | 4.3022 | 4.3426 | 4.383 | 4.4234 | 4.4638 | 4.5041 | 4.5445 | 4.5849 | 4.6253 | 4.6656 | 4.706 | 4.7464 | 4.7868 | 4.8271 | 4.8675 | 4.9079 | 4.9483 | 4.9886 | 5.029 | 5.0694 | 5.1098 | 5.1501 | 5.1905 | 5.2309 | 5.2713 | 5.301 | 5.3308 | 5.3606 | 5.3904 | 5.4201 | 5.4499 | 5.4797 | 5.5095 | 5.5392 | 5.569 | 5.5988 | 5.6286 | 5.6583 | 5.6881 | 5.7179 | 5.7477 | 5.7774 | 5.8072 | 5.837 | 5.8668 | 5.8965 | 5.9263 | 5.9561 | 5.9859 | 6.0156 | 6.0454 | 6.0752 | 6.105 | 6.1347 | 6.1645
3.9 | 0 | 0.8575 | 0.755 | 0.7635 | 0.675 | 0.847 | 1.076 | 2.6085 | 4.15 | 5.3875 | 6.303 | 0 | 0.08575 | 0.1715 | 0.25725 | 0.343 | 0.42875 | 0.5145 | 0.60025 | 0.686 | 0.77175 | 0.8575 | 0.837 | 0.8165 | 0.796 | 0.7755 | 0.755 | 0.7567 | 0.7584 | 0.7601 | 0.7618 | 0.7635 | 0.75465 | 0.7458 | 0.73695 | 0.7281 | 0.71925 | 0.7104 | 0.70155 | 0.6927 | 0.68385 | 0.675 | 0.68647 | 0.69793 | 0.7094 | 0.72087 | 0.73233 | 0.7438 | 0.75527 | 0.76673 | 0.7782 | 0.78967 | 0.80113 | 0.8126 | 0.82407 | 0.83553 | 0.847 | 0.86227 | 0.87753 | 0.8928 | 0.90807 | 0.92333 | 0.9386 | 0.95387 | 0.96913 | 0.9844 | 0.99967 | 1.0149 | 1.0302 | 1.0455 | 1.0607 | 1.076 | 1.1271 | 1.1782 | 1.2293 | 1.2803 | 1.3314 | 1.3825 | 1.4336 | 1.4847 | 1.5358 | 1.5868 | 1.6379 | 1.689 | 1.7401 | 1.7912 | 1.8422 | 1.8933 | 1.9444 | 1.9955 | 2.0466 | 2.0977 | 2.1488 | 2.1998 | 2.2509 | 2.302 | 2.3531 | 2.4042 | 2.4552 | 2.5063 | 2.5574 | 2.6085 | 2.6599 | 2.7113 | 2.7626 | 2.814 | 2.8654 | 2.9168 | 2.9682 | 3.0196 | 3.0709 | 3.1223 | 3.1737 | 3.2251 | 3.2765 | 3.3279 | 3.3792 | 3.4306 | 3.482 | 3.5334 | 3.5848 | 3.6362 | 3.6875 | 3.7389 | 3.7903 | 3.8417 | 3.8931 | 3.9445 | 3.9958 | 4.0472 | 4.0986 | 4.15 | 4.1912 | 4.2325 | 4.2737 | 4.315 | 4.3562 | 4.3975 | 4.4387 | 4.48 | 4.5212 | 4.5625 | 4.6037 | 4.645 | 4.6862 | 4.7275 | 4.7687 | 4.81 | 4.8512 | 4.8925 | 4.9337 | 4.975 | 5.0162 | 5.0575 | 5.0987 | 5.14 | 5.1813 | 5.2225 | 5.2637 | 5.305 | 5.3463 | 5.3875 | 5.418 | 5.4485 | 5.479 | 5.5096 | 5.5401 | 5.5706 | 5.6011 | 5.6316 | 5.6621 | 5.6927 | 5.7232 | 5.7537 | 5.7842 | 5.8147 | 5.8453 | 5.8758 | 5.9063 | 5.9368 | 5.9673 | 5.9978 | 6.0283 | 6.0589 | 6.0894 | 6.1199 | 6.1504 | 6.1809 | 6.2114 | 6.242 | 6.2725 | 6.303
3.95 | 0 | 0.87375 | 0.7675 | 0.77675 | 0.6875 | 0.8635 | 1.098 | 2.6643 | 4.24 | 5.5038 | 6.4415 | 0 | 0.087375 | 0.17475 | 0.26213 | 0.3495 | 0.43688 | 0.52425 | 0.61163 | 0.699 | 0.78638 | 0.87375 | 0.8525 | 0.83125 | 0.81 | 0.78875 | 0.7675 | 0.76935 | 0.7712 | 0.77305 | 0.7749 | 0.77675 | 0.76782 | 0.7589 | 0.74998 | 0.74105 | 0.73213 | 0.7232 | 0.71427 | 0.70535 | 0.69642 | 0.6875 | 0.69923 | 0.71097 | 0.7227 | 0.73443 | 0.74617 | 0.7579 | 0.76963 | 0.78137 | 0.7931 | 0.80483 | 0.81657 | 0.8283 | 0.84003 | 0.85177 | 0.8635 | 0.87913 | 0.89477 | 0.9104 | 0.92603 | 0.94167 | 0.9573 | 0.97293 | 0.98857 | 1.0042 | 1.0198 | 1.0355 | 1.0511 | 1.0667 | 1.0824 | 1.098 | 1.1502 | 1.2024 | 1.2546 | 1.3068 | 1.359 | 1.4113 | 1.4635 | 1.5157 | 1.5679 | 1.6201 | 1.6723 | 1.7245 | 1.7767 | 1.8289 | 1.8811 | 1.9333 | 1.9855 | 2.0378 | 2.09 | 2.1422 | 2.1944 | 2.2466 | 2.2988 | 2.351 | 2.4032 | 2.4554 | 2.5076 | 2.5598 | 2.612 | 2.6643 | 2.7168 | 2.7693 | 2.8218 | 2.8744 | 2.9269 | 2.9794 | 3.0319 | 3.0845 | 3.137 | 3.1895 | 3.242 | 3.2946 | 3.3471 | 3.3996 | 3.4521 | 3.5047 | 3.5572 | 3.6097 | 3.6622 | 3.7148 | 3.7673 | 3.8198 | 3.8723 | 3.9249 | 3.9774 | 4.0299 | 4.0824 | 4.135 | 4.1875 | 4.24 | 4.2821 | 4.3243 | 4.3664 | 4.4085 | 4.4506 | 4.4928 | 4.5349 | 4.577 | 4.6191 | 4.6613 | 4.7034 | 4.7455 | 4.7876 | 4.8298 | 4.8719 | 4.914 | 4.9561 | 4.9983 | 5.0404 | 5.0825 | 5.1246 | 5.1668 | 5.2089 | 5.251 | 5.2931 | 5.3353 | 5.3774 | 5.4195 | 5.4616 | 5.5038 | 5.535 | 5.5663 | 5.5975 | 5.6288 | 5.66 | 5.6913 | 5.7226 | 5.7538 | 5.7851 | 5.8163 | 5.8476 | 5.8789 | 5.9101 | 5.9414 | 5.9726 | 6.0039 | 6.0351 | 6.0664 | 6.0977 | 6.1289 | 6.1602 | 6.1914 | 6.2227 | 6.254 | 6.2852 | 6.3165 | 6.3477 | 6.379 | 6.4102 | 6.4415
4 | 0 | 0.89 | 0.78 | 0.79 | 0.7 | 0.88 | 1.12 | 2.72 | 4.33 | 5.62 | 6.58 | -5.5511e-17 | 0.089 | 0.178 | 0.267 | 0.356 | 0.445 | 0.534 | 0.623 | 0.712 | 0.801 | 0.89 | 0.868 | 0.846 | 0.824 | 0.802 | 0.78 | 0.782 | 0.784 | 0.786 | 0.788 | 0.79 | 0.781 | 0.772 | 0.763 | 0.754 | 0.745 | 0.736 | 0.727 | 0.718 | 0.709 | 0.7 | 0.712 | 0.724 | 0.736 | 0.748 | 0.76 | 0.772 | 0.784 | 0.796 | 0.808 | 0.82 | 0.832 | 0.844 | 0.856 | 0.868 | 0.88 | 0.896 | 0.912 | 0.928 | 0.944 | 0.96 | 0.976 | 0.992 | 1.008 | 1.024 | 1.04 | 1.056 | 1.072 | 1.088 | 1.104 | 1.12 | 1.1733 | 1.2267 | 1.28 | 1.3333 | 1.3867 | 1.44 | 1.4933 | 1.5467 | 1.6 | 1.6533 | 1.7067 | 1.76 | 1.8133 | 1.8667 | 1.92 | 1.9733 | 2.0267 | 2.08 | 2.1333 | 2.1867 | 2.24 | 2.2933 | 2.3467 | 2.4 | 2.4533 | 2.5067 | 2.56 | 2.6133 | 2.6667 | 2.72 | 2.7737 | 2.8273 | 2.881 | 2.9347 | 2.9883 | 3.042 | 3.0957 | 3.1493 | 3.203 | 3.2567 | 3.3103 | 3.364 | 3.4177 | 3.4713 | 3.525 | 3.5787 | 3.6323 | 3.686 | 3.7397 | 3.7933 | 3.847 | 3.9007 | 3.9543 | 4.008 | 4.0617 | 4.1153 | 4.169 | 4.2227 | 4.2763 | 4.33 | 4.373 | 4.416 | 4.459 | 4.502 | 4.545 | 4.588 | 4.631 | 4.674 | 4.717 | 4.76 | 4.803 | 4.846 | 4.889 | 4.932 | 4.975 | 5.018 | 5.061 | 5.104 | 5.147 | 5.19 | 5.233 | 5.276 | 5.319 | 5.362 | 5.405 | 5.448 | 5.491 | 5.534 | 5.577 | 5.62 | 5.652 | 5.684 | 5.716 | 5.748 | 5.78 | 5.812 | 5.844 | 5.876 | 5.908 | 5.94 | 5.972 | 6.004 | 6.036 | 6.068 | 6.1 | 6.132 | 6.164 | 6.196 | 6.228 | 6.26 | 6.292 | 6.324 | 6.356 | 6.388 | 6.42 | 6.452 | 6.484 | 6.516 | 6.548 | 6.58
4.05 | 0 | 0.915 | 0.80225 | 0.81 | 0.71975 | 0.9075 | 1.155 | 2.8147 | 4.4752 | 5.8057 | 6.794 | 0 | 0.0915 | 0.183 | 0.2745 | 0.366 | 0.4575 | 0.549 | 0.6405 | 0.732 | 0.8235 | 0.915 | 0.89245 | 0.8699 | 0.84735 | 0.8248 | 0.80225 | 0.8038 | 0.80535 | 0.8069 | 0.80845 | 0.81 | 0.80097 | 0.79195 | 0.78292 | 0.7739 | 0.76487 | 0.75585 | 0.74682 | 0.7378 | 0.72877 | 0.71975 | 0.73227 | 0.74478 | 0.7573 | 0.76982 | 0.78233 | 0.79485 | 0.80737 | 0.81988 | 0.8324 | 0.84492 | 0.85743 | 0.86995 | 0.88247 | 0.89498 | 0.9075 | 0.924 | 0.9405 | 0.957 | 0.9735 | 0.99 | 1.0065 | 1.023 | 1.0395 | 1.056 | 1.0725 | 1.089 | 1.1055 | 1.122 | 1.1385 | 1.155 | 1.2103 | 1.2656 | 1.321 | 1.3763 | 1.4316 | 1.4869 | 1.5423 | 1.5976 | 1.6529 | 1.7082 | 1.7636 | 1.8189 | 1.8742 | 1.9295 | 1.9849 | 2.0402 | 2.0955 | 2.1508 | 2.2062 | 2.2615 | 2.3168 | 2.3721 | 2.4275 | 2.4828 | 2.5381 | 2.5934 | 2.6488 | 2.7041 | 2.7594 | 2.8147 | 2.8701 | 2.9254 | 2.9808 | 3.0361 | 3.0915 | 3.1468 | 3.2022 | 3.2575 | 3.3129 | 3.3682 | 3.4236 | 3.4789 | 3.5343 | 3.5896 | 3.645 | 3.7003 | 3.7557 | 3.811 | 3.8664 | 3.9217 | 3.9771 | 4.0324 | 4.0878 | 4.1431 | 4.1985 | 4.2538 | 4.3092 | 4.3645 | 4.4199 | 4.4752 | 4.5196 | 4.5639 | 4.6083 | 4.6526 | 4.697 | 4.7413 | 4.7857 | 4.83 | 4.8744 | 4.9187 | 4.9631 | 5.0074 | 5.0518 | 5.0961 | 5.1405 | 5.1848 | 5.2292 | 5.2735 | 5.3179 | 5.3622 | 5.4066 | 5.4509 | 5.4953 | 5.5396 | 5.584 | 5.6283 | 5.6727 | 5.717 | 5.7614 | 5.8057 | 5.8387 | 5.8716 | 5.9046 | 5.9375 | 5.9705 | 6.0034 | 6.0363 | 6.0693 | 6.1022 | 6.1352 | 6.1681 | 6.201 | 6.234 | 6.2669 | 6.2999 | 6.3328 | 6.3658 | 6.3987 | 6.4316 | 6.4646 | 6.4975 | 6.5305 | 6.5634 | 6.5963 | 6.6293 | 6.6622 | 6.6952 | 6.7281 | 6.7611 | 6.794
4.1 | 0 | 0.94 | 0.8245 | 0.83 | 0.7395 | 0.935 | 1.19 | 2.9095 | 4.6205 | 5.9915 | 7.008 | 0 | 0.094 | 0.188 | 0.282 | 0.376 | 0.47 | 0.564 | 0.658 | 0.752 | 0.846 | 0.94 | 0.9169 | 0.8938 | 0.8707 | 0.8476 | 0.8245 | 0.8256 | 0.8267 | 0.8278 | 0.8289 | 0.83 | 0.82095 | 0.8119 | 0.80285 | 0.7938 | 0.78475 | 0.7757 | 0.76665 | 0.7576 | 0.74855 | 0.7395 | 0.75253 | 0.76557 | 0.7786 | 0.79163 | 0.80467 | 0.8177 | 0.83073 | 0.84377 | 0.8568 | 0.86983 | 0.88287 | 0.8959 | 0.90893 | 0.92197 | 0.935 | 0.952 | 0.969 | 0.986 | 1.003 | 1.02 | 1.037 | 1.054 | 1.071 | 1.088 | 1.105 | 1.122 | 1.139 | 1.156 | 1.173 | 1.19 | 1.2473 | 1.3046 | 1.3619 | 1.4193 | 1.4766 | 1.5339 | 1.5912 | 1.6485 | 1.7058 | 1.7632 | 1.8205 | 1.8778 | 1.9351 | 1.9924 | 2.0497 | 2.1071 | 2.1644 | 2.2217 | 2.279 | 2.3363 | 2.3936 | 2.451 | 2.5083 | 2.5656 | 2.6229 | 2.6802 | 2.7375 | 2.7949 | 2.8522 | 2.9095 | 2.9665 | 3.0236 | 3.0806 | 3.1376 | 3.1947 | 3.2517 | 3.3087 | 3.3658 | 3.4228 | 3.4798 | 3.5369 | 3.5939 | 3.6509 | 3.708 | 3.765 | 3.822 | 3.8791 | 3.9361 | 3.9931 | 4.0502 | 4.1072 | 4.1642 | 4.2213 | 4.2783 | 4.3353 | 4.3924 | 4.4494 | 4.5064 | 4.5635 | 4.6205 | 4.6662 | 4.7119 | 4.7576 | 4.8033 | 4.849 | 4.8947 | 4.9404 | 4.9861 | 5.0318 | 5.0775 | 5.1232 | 5.1689 | 5.2146 | 5.2603 | 5.306 | 5.3517 | 5.3974 | 5.4431 | 5.4888 | 5.5345 | 5.5802 | 5.6259 | 5.6716 | 5.7173 | 5.763 | 5.8087 | 5.8544 | 5.9001 | 5.9458 | 5.9915 | 6.0254 | 6.0593 | 6.0931 | 6.127 | 6.1609 | 6.1948 | 6.2287 | 6.2626 | 6.2964 | 6.3303 | 6.3642 | 6.3981 | 6.432 | 6.4659 | 6.4997 | 6.5336 | 6.5675 | 6.6014 | 6.6353 | 6.6692 | 6.703 | 6.7369 | 6.7708 | 6.8047 | 6.8386 | 6.8725 | 6.9063 | 6.9402 | 6.9741 | 7.008
4.15 | 0 | 0.965 | 0.84675 | 0.85 | 0.75925 | 0.9625 | 1.225 | 3.0043 | 4.7657 | 6.1773 | 7.222 | 0 | 0.0965 | 0.193 | 0.2895 | 0.386 | 0.4825 | 0.579 | 0.6755 | 0.772 | 0.8685 | 0.965 | 0.94135 | 0.9177 | 0.89405 | 0.8704 | 0.84675 | 0.8474 | 0.84805 | 0.8487 | 0.84935 | 0.85 | 0.84093 | 0.83185 | 0.82278 | 0.8137 | 0.80463 | 0.79555 | 0.78648 | 0.7774 | 0.76833 | 0.75925 | 0.7728 | 0.78635 | 0.7999 | 0.81345 | 0.827 | 0.84055 | 0.8541 | 0.86765 | 0.8812 | 0.89475 | 0.9083 | 0.92185 | 0.9354 | 0.94895 | 0.9625 | 0.98 | 0.9975 | 1.015 | 1.0325 | 1.05 | 1.0675 | 1.085 | 1.1025 | 1.12 | 1.1375 | 1.155 | 1.1725 | 1.19 | 1.2075 | 1.225 | 1.2843 | 1.3436 | 1.4029 | 1.4622 | 1.5215 | 1.5809 | 1.6402 | 1.6995 | 1.7588 | 1.8181 | 1.8774 | 1.9367 | 1.996 | 2.0553 | 2.1146 | 2.1739 | 2.2332 | 2.2926 | 2.3519 | 2.4112 | 2.4705 | 2.5298 | 2.5891 | 2.6484 | 2.7077 | 2.767 | 2.8263 | 2.8856 | 2.9449 | 3.0043 | 3.063 | 3.1217 | 3.1804 | 3.2391 | 3.2978 | 3.3565 | 3.4153 | 3.474 | 3.5327 | 3.5914 | 3.6501 | 3.7088 | 3.7676 | 3.8263 | 3.885 | 3.9437 | 4.0024 | 4.0611 | 4.1199 | 4.1786 | 4.2373 | 4.296 | 4.3547 | 4.4134 | 4.4722 | 4.5309 | 4.5896 | 4.6483 | 4.707 | 4.7658 | 4.8128 | 4.8599 | 4.9069 | 4.954 | 5.001 | 5.0481 | 5.0951 | 5.1422 | 5.1892 | 5.2363 | 5.2833 | 5.3304 | 5.3774 | 5.4245 | 5.4715 | 5.5186 | 5.5656 | 5.6127 | 5.6597 | 5.7068 | 5.7538 | 5.8009 | 5.8479 | 5.895 | 5.942 | 5.9891 | 6.0361 | 6.0832 | 6.1302 | 6.1773 | 6.2121 | 6.2469 | 6.2817 | 6.3166 | 6.3514 | 6.3862 | 6.421 | 6.4559 | 6.4907 | 6.5255 | 6.5603 | 6.5952 | 6.63 | 6.6648 | 6.6996 | 6.7345 | 6.7693 | 6.8041 | 6.8389 | 6.8738 | 6.9086 | 6.9434 | 6.9782 | 7.0131 | 7.0479 | 7.0827 | 7.1175 | 7.1524 | 7.1872 | 7.222
4.2 | 0 | 0.99 | 0.869 | 0.87 | 0.779 | 0.99 | 1.26 | 3.099 | 4.911 | 6.363 | 7.436 | 0 | 0.099 | 0.198 | 0.297 | 0.396 | 0.495 | 0.594 | 0.693 | 0.792 | 0.891 | 0.99 | 0.9658 | 0.9416 | 0.9174 | 0.8932 | 0.869 | 0.8692 | 0.8694 | 0.8696 | 0.8698 | 0.87 | 0.8609 | 0.8518 | 0.8427 | 0.8336 | 0.8245 | 0.8154 | 0.8063 | 0.7972 | 0.7881 | 0.779 | 0.79307 | 0.80713 | 0.8212 | 0.83527 | 0.84933 | 0.8634 | 0.87747 | 0.89153 | 0.9056 | 0.91967 | 0.93373 | 0.9478 | 0.96187 | 0.97593 | 0.99 | 1.008 | 1.026 | 1.044 | 1.062 | 1.08 | 1.098 | 1.116 | 1.134 | 1.152 | 1.17 | 1.188 | 1.206 | 1.224 | 1.242 | 1.26 | 1.3213 | 1.3826 | 1.4439 | 1.5052 | 1.5665 | 1.6278 | 1.6891 | 1.7504 | 1.8117 | 1.873 | 1.9343 | 1.9956 | 2.0569 | 2.1182 | 2.1795 | 2.2408 | 2.3021 | 2.3634 | 2.4247 | 2.486 | 2.5473 | 2.6086 | 2.6699 | 2.7312 | 2.7925 | 2.8538 | 2.9151 | 2.9764 | 3.0377 | 3.099 | 3.1594 | 3.2198 | 3.2802 | 3.3406 | 3.401 | 3.4614 | 3.5218 | 3.5822 | 3.6426 | 3.703 | 3.7634 | 3.8238 | 3.8842 | 3.9446 | 4.005 | 4.0654 | 4.1258 | 4.1862 | 4.2466 | 4.307 | 4.3674 | 4.4278 | 4.4882 | 4.5486 | 4.609 | 4.6694 | 4.7298 | 4.7902 | 4.8506 | 4.911 | 4.9594 | 5.0078 | 5.0562 | 5.1046 | 5.153 | 5.2014 | 5.2498 | 5.2982 | 5.3466 | 5.395 | 5.4434 | 5.4918 | 5.5402 | 5.5886 | 5.637 | 5.6854 | 5.7338 | 5.7822 | 5.8306 | 5.879 | 5.9274 | 5.9758 | 6.0242 | 6.0726 | 6.121 | 6.1694 | 6.2178 | 6.2662 | 6.3146 | 6.363 | 6.3988 | 6.4345 | 6.4703 | 6.5061 | 6.5418 | 6.5776 | 6.6134 | 6.6491 | 6.6849 | 6.7207 | 6.7564 | 6.7922 | 6.828 | 6.8637 | 6.8995 | 6.9353 | 6.971 | 7.0068 | 7.0426 | 7.0783 | 7.1141 | 7.1499 | 7.1856 | 7.2214 | 7.2572 | 7.2929 | 7.3287 | 7.3645 | 7.4002 | 7.436
4.25 | 0 | 1.015 | 0.89125 | 0.89 | 0.79875 | 1.0175 | 1.295 | 3.1937 | 5.0562 | 6.5488 | 7.65 | 1.1102e-16 | 0.1015 | 0.203 | 0.3045 | 0.406 | 0.5075 | 0.609 | 0.7105 | 0.812 | 0.9135 | 1.015 | 0.99025 | 0.9655 | 0.94075 | 0.916 | 0.89125 | 0.891 | 0.89075 | 0.8905 | 0.89025 | 0.89 | 0.88088 | 0.87175 | 0.86263 | 0.8535 | 0.84437 | 0.83525 | 0.82612 | 0.817 | 0.80787 | 0.79875 | 0.81333 | 0.82792 | 0.8425 | 0.85708 | 0.87167 | 0.88625 | 0.90083 | 0.91542 | 0.93 | 0.94458 | 0.95917 | 0.97375 | 0.98833 | 1.0029 | 1.0175 | 1.036 | 1.0545 | 1.073 | 1.0915 | 1.11 | 1.1285 | 1.147 | 1.1655 | 1.184 | 1.2025 | 1.221 | 1.2395 | 1.258 | 1.2765 | 1.295 | 1.3583 | 1.4216 | 1.4849 | 1.5482 | 1.6115 | 1.6748 | 1.738 | 1.8013 | 1.8646 | 1.9279 | 1.9912 | 2.0545 | 2.1178 | 2.1811 | 2.2444 | 2.3077 | 2.371 | 2.4343 | 2.4975 | 2.5608 | 2.6241 | 2.6874 | 2.7507 | 2.814 | 2.8773 | 2.9406 | 3.0039 | 3.0672 | 3.1305 | 3.1937 | 3.2558 | 3.3179 | 3.38 | 3.4421 | 3.5042 | 3.5663 | 3.6283 | 3.6904 | 3.7525 | 3.8146 | 3.8767 | 3.9387 | 4.0008 | 4.0629 | 4.125 | 4.1871 | 4.2492 | 4.3113 | 4.3733 | 4.4354 | 4.4975 | 4.5596 | 4.6217 | 4.6837 | 4.7458 | 4.8079 | 4.87 | 4.9321 | 4.9942 | 5.0562 | 5.106 | 5.1558 | 5.2055 | 5.2553 | 5.305 | 5.3548 | 5.4045 | 5.4543 | 5.504 | 5.5537 | 5.6035 | 5.6532 | 5.703 | 5.7527 | 5.8025 | 5.8523 | 5.902 | 5.9518 | 6.0015 | 6.0513 | 6.101 | 6.1508 | 6.2005 | 6.2503 | 6.3 | 6.3498 | 6.3995 | 6.4493 | 6.499 | 6.5488 | 6.5855 | 6.6222 | 6.6589 | 6.6956 | 6.7323 | 6.769 | 6.8057 | 6.8424 | 6.8791 | 6.9158 | 6.9525 | 6.9893 | 7.026 | 7.0627 | 7.0994 | 7.1361 | 7.1728 | 7.2095 | 7.2462 | 7.2829 | 7.3196 | 7.3563 | 7.393 | 7.4297 | 7.4665 | 7.5032 | 7.5399 | 7.5766 | 7.6133 | 7.65
4.3 | 0 | 1.04 | 0.9135 | 0.91 | 0.8185 | 1.045 | 1.33 | 3.2885 | 5.2015 | 6.7345 | 7.864 | 0 | 0.104 | 0.208 | 0.312 | 0.416 | 0.52 | 0.624 | 0.728 | 0.832 | 0.936 | 1.04 | 1.0147 | 0.9894 | 0.9641 | 0.9388 | 0.9135 | 0.9128 | 0.9121 | 0.9114 | 0.9107 | 0.91 | 0.90085 | 0.8917 | 0.88255 | 0.8734 | 0.86425 | 0.8551 | 0.84595 | 0.8368 | 0.82765 | 0.8185 | 0.8336 | 0.8487 | 0.8638 | 0.8789 | 0.894 | 0.9091 | 0.9242 | 0.9393 | 0.9544 | 0.9695 | 0.9846 | 0.9997 | 1.0148 | 1.0299 | 1.045 | 1.064 | 1.083 | 1.102 | 1.121 | 1.14 | 1.159 | 1.178 | 1.197 | 1.216 | 1.235 | 1.254 | 1.273 | 1.292 | 1.311 | 1.33 | 1.3953 | 1.4606 | 1.5259 | 1.5911 | 1.6564 | 1.7217 | 1.787 | 1.8523 | 1.9176 | 1.9828 | 2.0481 | 2.1134 | 2.1787 | 2.244 | 2.3092 | 2.3745 | 2.4398 | 2.5051 | 2.5704 | 2.6357 | 2.7009 | 2.7662 | 2.8315 | 2.8968 | 2.9621 | 3.0274 | 3.0926 | 3.1579 | 3.2232 | 3.2885 | 3.3523 | 3.416 | 3.4798 | 3.5436 | 3.6073 | 3.6711 | 3.7349 | 3.7986 | 3.8624 | 3.9262 | 3.9899 | 4.0537 | 4.1175 | 4.1812 | 4.245 | 4.3088 | 4.3725 | 4.4363 | 4.5001 | 4.5638 | 4.6276 | 4.6914 | 4.7551 | 4.8189 | 4.8827 | 4.9464 | 5.0102 | 5.074 | 5.1377 | 5.2015 | 5.2526 | 5.3037 | 5.3548 | 5.4059 | 5.457 | 5.5081 | 5.5592 | 5.6103 | 5.6614 | 5.7125 | 5.7636 | 5.8147 | 5.8658 | 5.9169 | 5.968 | 6.0191 | 6.0702 | 6.1213 | 6.1724 | 6.2235 | 6.2746 | 6.3257 | 6.3768 | 6.4279 | 6.479 | 6.5301 | 6.5812 | 6.6323 | 6.6834 | 6.7345 | 6.7721 | 6.8098 | 6.8474 | 6.8851 | 6.9227 | 6.9604 | 6.998 | 7.0357 | 7.0733 | 7.111 | 7.1486 | 7.1863 | 7.2239 | 7.2616 | 7.2992 | 7.3369 | 7.3745 | 7.4122 | 7.4498 | 7.4875 | 7.5251 | 7.5628 | 7.6004 | 7.6381 | 7.6757 | 7.7134 | 7.751 | 7.7887 | 7.8263 | 7.864
4.35 | 0 | 1.065 | 0.93575 | 0.93 | 0.83825 | 1.0725 | 1.365 | 3.3832 | 5.3467 | 6.9202 | 8.078 | 0 | 0.1065 | 0.213 | 0.3195 | 0.426 | 0.5325 | 0.639 | 0.7455 | 0.852 | 0.9585 | 1.065 | 1.0392 | 1.0133 | 0.98745 | 0.9616 | 0.93575 | 0.9346 | 0.93345 | 0.9323 | 0.93115 | 0.93 | 0.92082 | 0.91165 | 0.90247 | 0.8933 | 0.88412 | 0.87495 | 0.86577 | 0.8566 | 0.84742 | 0.83825 | 0.85387 | 0.86948 | 0.8851 | 0.90072 | 0.91633 | 0.93195 | 0.94757 | 0.96318 | 0.9788 | 0.99442 | 1.01 | 1.0256 | 1.0413 | 1.0569 | 1.0725 | 1.092 | 1.1115 | 1.131 | 1.1505 | 1.17 | 1.1895 | 1.209 | 1.2285 | 1.248 | 1.2675 | 1.287 | 1.3065 | 1.326 | 1.3455 | 1.365 | 1.4323 | 1.4995 | 1.5668 | 1.6341 | 1.7014 | 1.7686 | 1.8359 | 1.9032 | 1.9705 | 2.0377 | 2.105 | 2.1723 | 2.2396 | 2.3068 | 2.3741 | 2.4414 | 2.5087 | 2.5759 | 2.6432 | 2.7105 | 2.7778 | 2.845 | 2.9123 | 2.9796 | 3.0469 | 3.1141 | 3.1814 | 3.2487 | 3.316 | 3.3832 | 3.4487 | 3.5141 | 3.5796 | 3.645 | 3.7105 | 3.7759 | 3.8414 | 3.9068 | 3.9723 | 4.0377 | 4.1032 | 4.1686 | 4.2341 | 4.2995 | 4.365 | 4.4304 | 4.4959 | 4.5613 | 4.6268 | 4.6922 | 4.7577 | 4.8231 | 4.8886 | 4.954 | 5.0195 | 5.0849 | 5.1504 | 5.2158 | 5.2813 | 5.3467 | 5.3992 | 5.4516 | 5.5041 | 5.5565 | 5.609 | 5.6614 | 5.7139 | 5.7663 | 5.8188 | 5.8712 | 5.9237 | 5.9761 | 6.0286 | 6.081 | 6.1335 | 6.1859 | 6.2384 | 6.2908 | 6.3433 | 6.3957 | 6.4482 | 6.5006 | 6.5531 | 6.6055 | 6.658 | 6.7104 | 6.7629 | 6.8153 | 6.8678 | 6.9202 | 6.9588 | 6.9974 | 7.036 | 7.0746 | 7.1132 | 7.1518 | 7.1904 | 7.229 | 7.2676 | 7.3062 | 7.3448 | 7.3833 | 7.4219 | 7.4605 | 7.4991 | 7.5377 | 7.5763 | 7.6149 | 7.6535 | 7.6921 | 7.7307 | 7.7693 | 7.8079 | 7.8464 | 7.885 | 7.9236 | 7.9622 | 8.0008 | 8.0394 | 8.078
4.4 | 0 | 1.09 | 0.958 | 0.95 | 0.858 | 1.1 | 1.4 | 3.478 | 5.492 | 7.106 | 8.292 | 0 | 0.109 | 0.218 | 0.327 | 0.436 | 0.545 | 0.654 | 0.763 | 0.872 | 0.981 | 1.09 | 1.0636 | 1.0372 | 1.0108 | 0.9844 | 0.958 | 0.9564 | 0.9548 | 0.9532 | 0.9516 | 0.95 | 0.9408 | 0.9316 | 0.9224 | 0.9132 | 0.904 | 0.8948 | 0.8856 | 0.8764 | 0.8672 | 0.858 | 0.87413 | 0.89027 | 0.9064 | 0.92253 | 0.93867 | 0.9548 | 0.97093 | 0.98707 | 1.0032 | 1.0193 | 1.0355 | 1.0516 | 1.0677 | 1.0839 | 1.1 | 1.12 | 1.14 | 1.16 | 1.18 | 1.2 | 1.22 | 1.24 | 1.26 | 1.28 | 1.3 | 1.32 | 1.34 | 1.36 | 1.38 | 1.4 | 1.4693 | 1.5385 | 1.6078 | 1.6771 | 1.7463 | 1.8156 | 1.8849 | 1.9541 | 2.0234 | 2.0927 | 2.1619 | 2.2312 | 2.3005 | 2.3697 | 2.439 | 2.5083 | 2.5775 | 2.6468 | 2.7161 | 2.7853 | 2.8546 | 2.9239 | 2.9931 | 3.0624 | 3.1317 | 3.2009 | 3.2702 | 3.3395 | 3.4087 | 3.478 | 3.5451 | 3.6123 | 3.6794 | 3.7465 | 3.8137 | 3.8808 | 3.9479 | 4.0151 | 4.0822 | 4.1493 | 4.2165 | 4.2836 | 4.3507 | 4.4179 | 4.485 | 4.5521 | 4.6193 | 4.6864 | 4.7535 | 4.8207 | 4.8878 | 4.9549 | 5.0221 | 5.0892 | 5.1563 | 5.2235 | 5.2906 | 5.3577 | 5.4249 | 5.492 | 5.5458 | 5.5996 | 5.6534 | 5.7072 | 5.761 | 5.8148 | 5.8686 | 5.9224 | 5.9762 | 6.03 | 6.0838 | 6.1376 | 6.1914 | 6.2452 | 6.299 | 6.3528 | 6.4066 | 6.4604 | 6.5142 | 6.568 | 6.6218 | 6.6756 | 6.7294 | 6.7832 | 6.837 | 6.8908 | 6.9446 | 6.9984 | 7.0522 | 7.106 | 7.1455 | 7.1851 | 7.2246 | 7.2641 | 7.3037 | 7.3432 | 7.3827 | 7.4223 | 7.4618 | 7.5013 | 7.5409 | 7.5804 | 7.6199 | 7.6595 | 7.699 | 7.7385 | 7.7781 | 7.8176 | 7.8571 | 7.8967 | 7.9362 | 7.9757 | 8.0153 | 8.0548 | 8.0943 | 8.1339 | 8.1734 | 8.2129 | 8.2525 | 8.292
4.45 | 0 | 1.115 | 0.98025 | 0.97 | 0.87775 | 1.1275 | 1.435 | 3.5727 | 5.6372 | 7.2918 | 8.506 | 0 | 0.1115 | 0.223 | 0.3345 | 0.446 | 0.5575 | 0.669 | 0.7805 | 0.892 | 1.0035 | 1.115 | 1.088 | 1.0611 | 1.0341 | 1.0072 | 0.98025 | 0.9782 | 0.97615 | 0.9741 | 0.97205 | 0.97 | 0.96078 | 0.95155 | 0.94233 | 0.9331 | 0.92388 | 0.91465 | 0.90543 | 0.8962 | 0.88698 | 0.87775 | 0.8944 | 0.91105 | 0.9277 | 0.94435 | 0.961 | 0.97765 | 0.9943 | 1.011 | 1.0276 | 1.0443 | 1.0609 | 1.0776 | 1.0942 | 1.1109 | 1.1275 | 1.148 | 1.1685 | 1.189 | 1.2095 | 1.23 | 1.2505 | 1.271 | 1.2915 | 1.312 | 1.3325 | 1.353 | 1.3735 | 1.394 | 1.4145 | 1.435 | 1.5063 | 1.5775 | 1.6488 | 1.72 | 1.7913 | 1.8625 | 1.9338 | 2.0051 | 2.0763 | 2.1476 | 2.2188 | 2.2901 | 2.3614 | 2.4326 | 2.5039 | 2.5751 | 2.6464 | 2.7176 | 2.7889 | 2.8602 | 2.9314 | 3.0027 | 3.0739 | 3.1452 | 3.2165 | 3.2877 | 3.359 | 3.4302 | 3.5015 | 3.5727 | 3.6416 | 3.7104 | 3.7792 | 3.848 | 3.9168 | 3.9856 | 4.0545 | 4.1233 | 4.1921 | 4.2609 | 4.3297 | 4.3985 | 4.4674 | 4.5362 | 4.605 | 4.6738 | 4.7426 | 4.8114 | 4.8803 | 4.9491 | 5.0179 | 5.0867 | 5.1555 | 5.2243 | 5.2932 | 5.362 | 5.4308 | 5.4996 | 5.5684 | 5.6372 | 5.6924 | 5.7475 | 5.8027 | 5.8578 | 5.913 | 5.9681 | 6.0233 | 6.0784 | 6.1336 | 6.1887 | 6.2439 | 6.299 | 6.3542 | 6.4093 | 6.4645 | 6.5196 | 6.5748 | 6.63 | 6.6851 | 6.7402 | 6.7954 | 6.8506 | 6.9057 | 6.9608 | 7.016 | 7.0711 | 7.1263 | 7.1814 | 7.2366 | 7.2917 | 7.3322 | 7.3727 | 7.4132 | 7.4536 | 7.4941 | 7.5346 | 7.5751 | 7.6155 | 7.656 | 7.6965 | 7.737 | 7.7774 | 7.8179 | 7.8584 | 7.8989 | 7.9394 | 7.9798 | 8.0203 | 8.0608 | 8.1013 | 8.1417 | 8.1822 | 8.2227 | 8.2631 | 8.3036 | 8.3441 | 8.3846 | 8.425 | 8.4655 | 8.506
4.5 | 0 | 1.14 | 1.0025 | 0.99 | 0.8975 | 1.155 | 1.47 | 3.6675 | 5.7825 | 7.4775 | 8.72 | 0 | 0.114 | 0.228 | 0.342 | 0.456 | 0.57 | 0.684 | 0.798 | 0.912 | 1.026 | 1.14 | 1.1125 | 1.085 | 1.0575 | 1.03 | 1.0025 | 1 | 0.9975 | 0.995 | 0.9925 | 0.99 | 0.98075 | 0.9715 | 0.96225 | 0.953 | 0.94375 | 0.9345 | 0.92525 | 0.916 | 0.90675 | 0.8975 | 0.91467 | 0.93183 | 0.949 | 0.96617 | 0.98333 | 1.0005 | 1.0177 | 1.0348 | 1.052 | 1.0692 | 1.0863 | 1.1035 | 1.1207 | 1.1378 | 1.155 | 1.176 | 1.197 | 1.218 | 1.239 | 1.26 | 1.281 | 1.302 | 1.323 | 1.344 | 1.365 | 1.386 | 1.407 | 1.428 | 1.449 | 1.47 | 1.5433 | 1.6165 | 1.6898 | 1.763 | 1.8363 | 1.9095 | 1.9828 | 2.056 | 2.1293 | 2.2025 | 2.2758 | 2.349 | 2.4223 | 2.4955 | 2.5688 | 2.642 | 2.7153 | 2.7885 | 2.8618 | 2.935 | 3.0083 | 3.0815 | 3.1548 | 3.228 | 3.3013 | 3.3745 | 3.4478 | 3.521 | 3.5943 | 3.6675 | 3.738 | 3.8085 | 3.879 | 3.9495 | 4.02 | 4.0905 | 4.161 | 4.2315 | 4.302 | 4.3725 | 4.443 | 4.5135 | 4.584 | 4.6545 | 4.725 | 4.7955 | 4.866 | 4.9365 | 5.007 | 5.0775 | 5.148 | 5.2185 | 5.289 | 5.3595 | 5.43 | 5.5005 | 5.571 | 5.6415 | 5.712 | 5.7825 | 5.839 | 5.8955 | 5.952 | 6.0085 | 6.065 | 6.1215 | 6.178 | 6.2345 | 6.291 | 6.3475 | 6.404 | 6.4605 | 6.517 | 6.5735 | 6.63 | 6.6865 | 6.743 | 6.7995 | 6.856 | 6.9125 | 6.969 | 7.0255 | 7.082 | 7.1385 | 7.195 | 7.2515 | 7.308 | 7.3645 | 7.421 | 7.4775 | 7.5189 | 7.5603 | 7.6017 | 7.6432 | 7.6846 | 7.726 | 7.7674 | 7.8088 | 7.8502 | 7.8917 | 7.9331 | 7.9745 | 8.0159 | 8.0573 | 8.0987 | 8.1402 | 8.1816 | 8.223 | 8.2644 | 8.3058 | 8.3472 | 8.3887 | 8.4301 | 8.4715 | 8.5129 | 8.5543 | 8.5957 | 8.6372 | 8.6786 | 8.72
4.55 | 0 | 1.165 | 1.0248 | 1.01 | 0.91725 | 1.1825 | 1.505 | 3.7622 | 5.9277 | 7.6632 | 8.934 | -1.1102e-16 | 0.1165 | 0.233 | 0.3495 | 0.466 | 0.5825 | 0.699 | 0.8155 | 0.932 | 1.0485 | 1.165 | 1.137 | 1.1089 | 1.0809 | 1.0528 | 1.0247 | 1.0218 | 1.0188 | 1.0159 | 1.0129 | 1.01 | 1.0007 | 0.99145 | 0.98218 | 0.9729 | 0.96362 | 0.95435 | 0.94507 | 0.9358 | 0.92652 | 0.91725 | 0.93493 | 0.95262 | 0.9703 | 0.98798 | 1.0057 | 1.0233 | 1.041 | 1.0587 | 1.0764 | 1.0941 | 1.1118 | 1.1294 | 1.1471 | 1.1648 | 1.1825 | 1.204 | 1.2255 | 1.247 | 1.2685 | 1.29 | 1.3115 | 1.333 | 1.3545 | 1.376 | 1.3975 | 1.419 | 1.4405 | 1.462 | 1.4835 | 1.505 | 1.5802 | 1.6555 | 1.7307 | 1.806 | 1.8812 | 1.9565 | 2.0317 | 2.1069 | 2.1822 | 2.2574 | 2.3327 | 2.4079 | 2.4831 | 2.5584 | 2.6336 | 2.7089 | 2.7841 | 2.8594 | 2.9346 | 3.0098 | 3.0851 | 3.1603 | 3.2356 | 3.3108 | 3.386 | 3.4613 | 3.5365 | 3.6118 | 3.687 | 3.7622 | 3.8344 | 3.9066 | 3.9788 | 4.051 | 4.1232 | 4.1953 | 4.2675 | 4.3397 | 4.4119 | 4.4841 | 4.5563 | 4.6284 | 4.7006 | 4.7728 | 4.845 | 4.9172 | 4.9894 | 5.0615 | 5.1337 | 5.2059 | 5.2781 | 5.3503 | 5.4225 | 5.4946 | 5.5668 | 5.639 | 5.7112 | 5.7834 | 5.8556 | 5.9277 | 5.9856 | 6.0434 | 6.1013 | 6.1591 | 6.217 | 6.2748 | 6.3327 | 6.3905 | 6.4484 | 6.5062 | 6.5641 | 6.6219 | 6.6798 | 6.7376 | 6.7955 | 6.8533 | 6.9112 | 6.969 | 7.0269 | 7.0847 | 7.1426 | 7.2004 | 7.2583 | 7.3161 | 7.374 | 7.4318 | 7.4897 | 7.5475 | 7.6054 | 7.6632 | 7.7056 | 7.748 | 7.7903 | 7.8327 | 7.875 | 7.9174 | 7.9598 | 8.0021 | 8.0445 | 8.0868 | 8.1292 | 8.1715 | 8.2139 | 8.2563 | 8.2986 | 8.341 | 8.3833 | 8.4257 | 8.4681 | 8.5104 | 8.5528 | 8.5951 | 8.6375 | 8.6798 | 8.7222 | 8.7646 | 8.8069 | 8.8493 | 8.8916 | 8.934
4.6 | 0 | 1.19 | 1.047 | 1.03 | 0.937 | 1.21 | 1.54 | 3.857 | 6.073 | 7.849 | 9.148 | 0 | 0.119 | 0.238 | 0.357 | 0.476 | 0.595 | 0.714 | 0.833 | 0.952 | 1.071 | 1.19 | 1.1614 | 1.1328 | 1.1042 | 1.0756 | 1.047 | 1.0436 | 1.0402 | 1.0368 | 1.0334 | 1.03 | 1.0207 | 1.0114 | 1.0021 | 0.9928 | 0.9835 | 0.9742 | 0.9649 | 0.9556 | 0.9463 | 0.937 | 0.9552 | 0.9734 | 0.9916 | 1.0098 | 1.028 | 1.0462 | 1.0644 | 1.0826 | 1.1008 | 1.119 | 1.1372 | 1.1554 | 1.1736 | 1.1918 | 1.21 | 1.232 | 1.254 | 1.276 | 1.298 | 1.32 | 1.342 | 1.364 | 1.386 | 1.408 | 1.43 | 1.452 | 1.474 | 1.496 | 1.518 | 1.54 | 1.6172 | 1.6945 | 1.7717 | 1.8489 | 1.9262 | 2.0034 | 2.0806 | 2.1579 | 2.2351 | 2.3123 | 2.3896 | 2.4668 | 2.544 | 2.6213 | 2.6985 | 2.7757 | 2.853 | 2.9302 | 3.0074 | 3.0847 | 3.1619 | 3.2391 | 3.3164 | 3.3936 | 3.4708 | 3.5481 | 3.6253 | 3.7025 | 3.7798 | 3.857 | 3.9309 | 4.0047 | 4.0786 | 4.1525 | 4.2263 | 4.3002 | 4.3741 | 4.4479 | 4.5218 | 4.5957 | 4.6695 | 4.7434 | 4.8173 | 4.8911 | 4.965 | 5.0389 | 5.1127 | 5.1866 | 5.2605 | 5.3343 | 5.4082 | 5.4821 | 5.5559 | 5.6298 | 5.7037 | 5.7775 | 5.8514 | 5.9253 | 5.9991 | 6.073 | 6.1322 | 6.1914 | 6.2506 | 6.3098 | 6.369 | 6.4282 | 6.4874 | 6.5466 | 6.6058 | 6.665 | 6.7242 | 6.7834 | 6.8426 | 6.9018 | 6.961 | 7.0202 | 7.0794 | 7.1386 | 7.1978 | 7.257 | 7.3162 | 7.3754 | 7.4346 | 7.4938 | 7.553 | 7.6122 | 7.6714 | 7.7306 | 7.7898 | 7.849 | 7.8923 | 7.9356 | 7.9789 | 8.0222 | 8.0655 | 8.1088 | 8.1521 | 8.1954 | 8.2387 | 8.282 | 8.3253 | 8.3686 | 8.4119 | 8.4552 | 8.4985 | 8.5418 | 8.5851 | 8.6284 | 8.6717 | 8.715 | 8.7583 | 8.8016 | 8.8449 | 8.8882 | 8.9315 | 8.9748 | 9.0181 | 9.0614 | 9.1047 | 9.148
4.65 | 0 | 1.215 | 1.0693 | 1.05 | 0.95675 | 1.2375 | 1.575 | 3.9518 | 6.2183 | 8.0348 | 9.362 | 1.1102e-16 | 0.1215 | 0.243 | 0.3645 | 0.486 | 0.6075 | 0.729 | 0.8505 | 0.972 | 1.0935 | 1.215 | 1.1858 | 1.1567 | 1.1276 | 1.0984 | 1.0693 | 1.0654 | 1.0616 | 1.0577 | 1.0539 | 1.05 | 1.0407 | 1.0314 | 1.022 | 1.0127 | 1.0034 | 0.99405 | 0.98473 | 0.9754 | 0.96608 | 0.95675 | 0.97547 | 0.99418 | 1.0129 | 1.0316 | 1.0503 | 1.0691 | 1.0878 | 1.1065 | 1.1252 | 1.1439 | 1.1626 | 1.1814 | 1.2001 | 1.2188 | 1.2375 | 1.26 | 1.2825 | 1.305 | 1.3275 | 1.35 | 1.3725 | 1.395 | 1.4175 | 1.44 | 1.4625 | 1.485 | 1.5075 | 1.53 | 1.5525 | 1.575 | 1.6542 | 1.7334 | 1.8127 | 1.8919 | 1.9711 | 2.0504 | 2.1296 | 2.2088 | 2.288 | 2.3672 | 2.4465 | 2.5257 | 2.6049 | 2.6842 | 2.7634 | 2.8426 | 2.9218 | 3.001 | 3.0803 | 3.1595 | 3.2387 | 3.318 | 3.3972 | 3.4764 | 3.5556 | 3.6349 | 3.7141 | 3.7933 | 3.8725 | 3.9518 | 4.0273 | 4.1029 | 4.1784 | 4.254 | 4.3295 | 4.4051 | 4.4806 | 4.5562 | 4.6317 | 4.7073 | 4.7828 | 4.8584 | 4.9339 | 5.0095 | 5.085 | 5.1605 | 5.2361 | 5.3117 | 5.3872 | 5.4628 | 5.5383 | 5.6139 | 5.6894 | 5.7649 | 5.8405 | 5.9161 | 5.9916 | 6.0672 | 6.1427 | 6.2183 | 6.2788 | 6.3394 | 6.3999 | 6.4605 | 6.521 | 6.5816 | 6.6421 | 6.7027 | 6.7632 | 6.8238 | 6.8843 | 6.9449 | 7.0054 | 7.066 | 7.1265 | 7.1871 | 7.2476 | 7.3082 | 7.3687 | 7.4293 | 7.4898 | 7.5504 | 7.6109 | 7.6715 | 7.732 | 7.7926 | 7.8531 | 7.9137 | 7.9742 | 8.0348 | 8.079 | 8.1232 | 8.1675 | 8.2117 | 8.256 | 8.3002 | 8.3444 | 8.3887 | 8.4329 | 8.4772 | 8.5214 | 8.5657 | 8.6099 | 8.6541 | 8.6984 | 8.7426 | 8.7869 | 8.8311 | 8.8753 | 8.9196 | 8.9638 | 9.0081 | 9.0523 | 9.0965 | 9.1408 | 9.185 | 9.2293 | 9.2735 | 9.3178 | 9.362
4.7 | 0 | 1.24 | 1.0915 | 1.07 | 0.9765 | 1.265 | 1.61 | 4.0465 | 6.3635 | 8.2205 | 9.576 | 0 | 0.124 | 0.248 | 0.372 | 0.496 | 0.62 | 0.744 | 0.868 | 0.992 | 1.116 | 1.24 | 1.2103 | 1.1806 | 1.1509 | 1.1212 | 1.0915 | 1.0872 | 1.0829 | 1.0786 | 1.0743 | 1.07 | 1.0606 | 1.0513 | 1.0419 | 1.0326 | 1.0232 | 1.0139 | 1.0045 | 0.9952 | 0.98585 | 0.9765 | 0.99573 | 1.015 | 1.0342 | 1.0534 | 1.0727 | 1.0919 | 1.1111 | 1.1304 | 1.1496 | 1.1688 | 1.1881 | 1.2073 | 1.2265 | 1.2458 | 1.265 | 1.288 | 1.311 | 1.334 | 1.357 | 1.38 | 1.403 | 1.426 | 1.449 | 1.472 | 1.495 | 1.518 | 1.541 | 1.564 | 1.587 | 1.61 | 1.6912 | 1.7724 | 1.8537 | 1.9349 | 2.0161 | 2.0973 | 2.1785 | 2.2597 | 2.3409 | 2.4222 | 2.5034 | 2.5846 | 2.6658 | 2.747 | 2.8283 | 2.9095 | 2.9907 | 3.0719 | 3.1531 | 3.2343 | 3.3155 | 3.3968 | 3.478 | 3.5592 | 3.6404 | 3.7216 | 3.8028 | 3.8841 | 3.9653 | 4.0465 | 4.1237 | 4.201 | 4.2782 | 4.3554 | 4.4327 | 4.5099 | 4.5871 | 4.6644 | 4.7416 | 4.8188 | 4.8961 | 4.9733 | 5.0505 | 5.1278 | 5.205 | 5.2822 | 5.3595 | 5.4367 | 5.5139 | 5.5912 | 5.6684 | 5.7456 | 5.8229 | 5.9001 | 5.9773 | 6.0546 | 6.1318 | 6.209 | 6.2863 | 6.3635 | 6.4254 | 6.4873 | 6.5492 | 6.6111 | 6.673 | 6.7349 | 6.7968 | 6.8587 | 6.9206 | 6.9825 | 7.0444 | 7.1063 | 7.1682 | 7.2301 | 7.292 | 7.3539 | 7.4158 | 7.4777 | 7.5396 | 7.6015 | 7.6634 | 7.7253 | 7.7872 | 7.8491 | 7.911 | 7.9729 | 8.0348 | 8.0967 | 8.1586 | 8.2205 | 8.2657 | 8.3109 | 8.356 | 8.4012 | 8.4464 | 8.4916 | 8.5368 | 8.582 | 8.6272 | 8.6723 | 8.7175 | 8.7627 | 8.8079 | 8.8531 | 8.8983 | 8.9434 | 8.9886 | 9.0338 | 9.079 | 9.1242 | 9.1694 | 9.2145 | 9.2597 | 9.3049 | 9.3501 | 9.3953 | 9.4405 | 9.4856 | 9.5308 | 9.576
4.75 | 0 | 1.265 | 1.1138 | 1.09 | 0.99625 | 1.2925 | 1.645 | 4.1412 | 6.5088 | 8.4062 | 9.79 | 1.1102e-16 | 0.1265 | 0.253 | 0.3795 | 0.506 | 0.6325 | 0.759 | 0.8855 | 1.012 | 1.1385 | 1.265 | 1.2348 | 1.2045 | 1.1743 | 1.144 | 1.1138 | 1.109 | 1.1043 | 1.0995 | 1.0948 | 1.09 | 1.0806 | 1.0713 | 1.0619 | 1.0525 | 1.0431 | 1.0338 | 1.0244 | 1.015 | 1.0056 | 0.99625 | 1.016 | 1.0358 | 1.0555 | 1.0753 | 1.095 | 1.1148 | 1.1345 | 1.1543 | 1.174 | 1.1938 | 1.2135 | 1.2333 | 1.253 | 1.2728 | 1.2925 | 1.316 | 1.3395 | 1.363 | 1.3865 | 1.41 | 1.4335 | 1.457 | 1.4805 | 1.504 | 1.5275 | 1.551 | 1.5745 | 1.598 | 1.6215 | 1.645 | 1.7282 | 1.8114 | 1.8946 | 1.9778 | 2.061 | 2.1442 | 2.2275 | 2.3107 | 2.3939 | 2.4771 | 2.5603 | 2.6435 | 2.7267 | 2.8099 | 2.8931 | 2.9763 | 3.0595 | 3.1427 | 3.226 | 3.3092 | 3.3924 | 3.4756 | 3.5588 | 3.642 | 3.7252 | 3.8084 | 3.8916 | 3.9748 | 4.058 | 4.1412 | 4.2202 | 4.2991 | 4.378 | 4.4569 | 4.5358 | 4.6147 | 4.6937 | 4.7726 | 4.8515 | 4.9304 | 5.0093 | 5.0882 | 5.1672 | 5.2461 | 5.325 | 5.4039 | 5.4828 | 5.5617 | 5.6407 | 5.7196 | 5.7985 | 5.8774 | 5.9563 | 6.0352 | 6.1142 | 6.1931 | 6.272 | 6.3509 | 6.4298 | 6.5087 | 6.572 | 6.6352 | 6.6985 | 6.7617 | 6.825 | 6.8882 | 6.9515 | 7.0147 | 7.078 | 7.1412 | 7.2045 | 7.2677 | 7.331 | 7.3942 | 7.4575 | 7.5207 | 7.584 | 7.6472 | 7.7105 | 7.7737 | 7.837 | 7.9002 | 7.9635 | 8.0267 | 8.09 | 8.1532 | 8.2165 | 8.2797 | 8.343 | 8.4062 | 8.4524 | 8.4985 | 8.5446 | 8.5907 | 8.6369 | 8.683 | 8.7291 | 8.7752 | 8.8214 | 8.8675 | 8.9136 | 8.9597 | 9.0059 | 9.052 | 9.0981 | 9.1442 | 9.1904 | 9.2365 | 9.2826 | 9.3287 | 9.3749 | 9.421 | 9.4671 | 9.5132 | 9.5594 | 9.6055 | 9.6516 | 9.6977 | 9.7439 | 9.79
4.8 | 0 | 1.29 | 1.136 | 1.11 | 1.016 | 1.32 | 1.68 | 4.236 | 6.654 | 8.592 | 10.004 | 0 | 0.129 | 0.258 | 0.387 | 0.516 | 0.645 | 0.774 | 0.903 | 1.032 | 1.161 | 1.29 | 1.2592 | 1.2284 | 1.1976 | 1.1668 | 1.136 | 1.1308 | 1.1256 | 1.1204 | 1.1152 | 1.11 | 1.1006 | 1.0912 | 1.0818 | 1.0724 | 1.063 | 1.0536 | 1.0442 | 1.0348 | 1.0254 | 1.016 | 1.0363 | 1.0565 | 1.0768 | 1.0971 | 1.1173 | 1.1376 | 1.1579 | 1.1781 | 1.1984 | 1.2187 | 1.2389 | 1.2592 | 1.2795 | 1.2997 | 1.32 | 1.344 | 1.368 | 1.392 | 1.416 | 1.44 | 1.464 | 1.488 | 1.512 | 1.536 | 1.56 | 1.584 | 1.608 | 1.632 | 1.656 | 1.68 | 1.7652 | 1.8504 | 1.9356 | 2.0208 | 2.106 | 2.1912 | 2.2764 | 2.3616 | 2.4468 | 2.532 | 2.6172 | 2.7024 | 2.7876 | 2.8728 | 2.958 | 3.0432 | 3.1284 | 3.2136 | 3.2988 | 3.384 | 3.4692 | 3.5544 | 3.6396 | 3.7248 | 3.81 | 3.8952 | 3.9804 | 4.0656 | 4.1508 | 4.236 | 4.3166 | 4.3972 | 4.4778 | 4.5584 | 4.639 | 4.7196 | 4.8002 | 4.8808 | 4.9614 | 5.042 | 5.1226 | 5.2032 | 5.2838 | 5.3644 | 5.445 | 5.5256 | 5.6062 | 5.6868 | 5.7674 | 5.848 | 5.9286 | 6.0092 | 6.0898 | 6.1704 | 6.251 | 6.3316 | 6.4122 | 6.4928 | 6.5734 | 6.654 | 6.7186 | 6.7832 | 6.8478 | 6.9124 | 6.977 | 7.0416 | 7.1062 | 7.1708 | 7.2354 | 7.3 | 7.3646 | 7.4292 | 7.4938 | 7.5584 | 7.623 | 7.6876 | 7.7522 | 7.8168 | 7.8814 | 7.946 | 8.0106 | 8.0752 | 8.1398 | 8.2044 | 8.269 | 8.3336 | 8.3982 | 8.4628 | 8.5274 | 8.592 | 8.6391 | 8.6861 | 8.7332 | 8.7803 | 8.8273 | 8.8744 | 8.9215 | 8.9685 | 9.0156 | 9.0627 | 9.1097 | 9.1568 | 9.2039 | 9.2509 | 9.298 | 9.3451 | 9.3921 | 9.4392 | 9.4863 | 9.5333 | 9.5804 | 9.6275 | 9.6745 | 9.7216 | 9.7687 | 9.8157 | 9.8628 | 9.9099 | 9.9569 | 10.004
4.85 | 0 | 1.315 | 1.1583 | 1.13 | 1.0357 | 1.3475 | 1.715 | 4.3307 | 6.7992 | 8.7777 | 10.218 | 0 | 0.1315 | 0.263 | 0.3945 | 0.526 | 0.6575 | 0.789 | 0.9205 | 1.052 | 1.1835 | 1.315 | 1.2837 | 1.2523 | 1.221 | 1.1896 | 1.1583 | 1.1526 | 1.147 | 1.1413 | 1.1357 | 1.13 | 1.1206 | 1.1111 | 1.1017 | 1.0923 | 1.0829 | 1.0734 | 1.064 | 1.0546 | 1.0452 | 1.0357 | 1.0565 | 1.0773 | 1.0981 | 1.1189 | 1.1397 | 1.1604 | 1.1812 | 1.202 | 1.2228 | 1.2436 | 1.2644 | 1.2851 | 1.3059 | 1.3267 | 1.3475 | 1.372 | 1.3965 | 1.421 | 1.4455 | 1.47 | 1.4945 | 1.519 | 1.5435 | 1.568 | 1.5925 | 1.617 | 1.6415 | 1.666 | 1.6905 | 1.715 | 1.8022 | 1.8894 | 1.9766 | 2.0638 | 2.151 | 2.2381 | 2.3253 | 2.4125 | 2.4997 | 2.5869 | 2.6741 | 2.7613 | 2.8485 | 2.9357 | 3.0229 | 3.1101 | 3.1973 | 3.2844 | 3.3716 | 3.4588 | 3.546 | 3.6332 | 3.7204 | 3.8076 | 3.8948 | 3.982 | 4.0692 | 4.1564 | 4.2436 | 4.3307 | 4.413 | 4.4953 | 4.5776 | 4.6599 | 4.7422 | 4.8244 | 4.9067 | 4.989 | 5.0713 | 5.1536 | 5.2359 | 5.3181 | 5.4004 | 5.4827 | 5.565 | 5.6473 | 5.7296 | 5.8118 | 5.8941 | 5.9764 | 6.0587 | 6.141 | 6.2233 | 6.3055 | 6.3878 | 6.4701 | 6.5524 | 6.6347 | 6.717 | 6.7992 | 6.8652 | 6.9311 | 6.9971 | 7.063 | 7.129 | 7.1949 | 7.2609 | 7.3268 | 7.3928 | 7.4587 | 7.5247 | 7.5906 | 7.6566 | 7.7225 | 7.7885 | 7.8544 | 7.9204 | 7.9863 | 8.0523 | 8.1182 | 8.1842 | 8.2501 | 8.3161 | 8.382 | 8.448 | 8.5139 | 8.5799 | 8.6458 | 8.7118 | 8.7777 | 8.8258 | 8.8738 | 8.9218 | 8.9698 | 9.0178 | 9.0658 | 9.1138 | 9.1618 | 9.2098 | 9.2578 | 9.3058 | 9.3538 | 9.4019 | 9.4499 | 9.4979 | 9.5459 | 9.5939 | 9.6419 | 9.6899 | 9.7379 | 9.7859 | 9.8339 | 9.8819 | 9.9299 | 9.978 | 10.026 | 10.074 | 10.122 | 10.17 | 10.218
4.9 | 0 | 1.34 | 1.1805 | 1.15 | 1.0555 | 1.375 | 1.75 | 4.4255 | 6.9445 | 8.9635 | 10.432 | 0 | 0.134 | 0.268 | 0.402 | 0.536 | 0.67 | 0.804 | 0.938 | 1.072 | 1.206 | 1.34 | 1.3081 | 1.2762 | 1.2443 | 1.2124 | 1.1805 | 1.1744 | 1.1683 | 1.1622 | 1.1561 | 1.15 | 1.1406 | 1.1311 | 1.1217 | 1.1122 | 1.1028 | 1.0933 | 1.0838 | 1.0744 | 1.065 | 1.0555 | 1.0768 | 1.0981 | 1.1194 | 1.1407 | 1.162 | 1.1833 | 1.2046 | 1.2259 | 1.2472 | 1.2685 | 1.2898 | 1.3111 | 1.3324 | 1.3537 | 1.375 | 1.4 | 1.425 | 1.45 | 1.475 | 1.5 | 1.525 | 1.55 | 1.575 | 1.6 | 1.625 | 1.65 | 1.675 | 1.7 | 1.725 | 1.75 | 1.8392 | 1.9284 | 2.0175 | 2.1067 | 2.1959 | 2.2851 | 2.3743 | 2.4635 | 2.5526 | 2.6418 | 2.731 | 2.8202 | 2.9094 | 2.9986 | 3.0877 | 3.1769 | 3.2661 | 3.3553 | 3.4445 | 3.5337 | 3.6228 | 3.712 | 3.8012 | 3.8904 | 3.9796 | 4.0688 | 4.1579 | 4.2471 | 4.3363 | 4.4255 | 4.5095 | 4.5934 | 4.6774 | 4.7614 | 4.8453 | 4.9293 | 5.0133 | 5.0972 | 5.1812 | 5.2652 | 5.3491 | 5.4331 | 5.5171 | 5.601 | 5.685 | 5.769 | 5.8529 | 5.9369 | 6.0209 | 6.1048 | 6.1888 | 6.2728 | 6.3567 | 6.4407 | 6.5247 | 6.6086 | 6.6926 | 6.7766 | 6.8605 | 6.9445 | 7.0118 | 7.0791 | 7.1464 | 7.2137 | 7.281 | 7.3483 | 7.4156 | 7.4829 | 7.5502 | 7.6175 | 7.6848 | 7.7521 | 7.8194 | 7.8867 | 7.954 | 8.0213 | 8.0886 | 8.1559 | 8.2232 | 8.2905 | 8.3578 | 8.4251 | 8.4924 | 8.5597 | 8.627 | 8.6943 | 8.7616 | 8.8289 | 8.8962 | 8.9635 | 9.0124 | 9.0614 | 9.1104 | 9.1593 | 9.2082 | 9.2572 | 9.3061 | 9.3551 | 9.404 | 9.453 | 9.5019 | 9.5509 | 9.5998 | 9.6488 | 9.6977 | 9.7467 | 9.7956 | 9.8446 | 9.8935 | 9.9425 | 9.9914 | 10.0404 | 10.0893 | 10.1383 | 10.1872 | 10.2362 | 10.2851 | 10.3341 | 10.383 | 10.432
4.95 | 0 | 1.365 | 1.2028 | 1.17 | 1.0753 | 1.4025 | 1.785 | 4.5203 | 7.0897 | 9.1492 | 10.646 | -1.1102e-16 | 0.1365 | 0.273 | 0.4095 | 0.546 | 0.6825 | 0.819 | 0.9555 | 1.092 | 1.2285 | 1.365 | 1.3325 | 1.3001 | 1.2677 | 1.2352 | 1.2028 | 1.1962 | 1.1897 | 1.1831 | 1.1766 | 1.17 | 1.1605 | 1.1511 | 1.1416 | 1.1321 | 1.1226 | 1.1132 | 1.1037 | 1.0942 | 1.0847 | 1.0753 | 1.0971 | 1.1189 | 1.1407 | 1.1625 | 1.1843 | 1.2062 | 1.228 | 1.2498 | 1.2716 | 1.2934 | 1.3152 | 1.3371 | 1.3589 | 1.3807 | 1.4025 | 1.428 | 1.4535 | 1.479 | 1.5045 | 1.53 | 1.5555 | 1.581 | 1.6065 | 1.632 | 1.6575 | 1.683 | 1.7085 | 1.734 | 1.7595 | 1.785 | 1.8762 | 1.9673 | 2.0585 | 2.1497 | 2.2409 | 2.3321 | 2.4232 | 2.5144 | 2.6056 | 2.6968 | 2.7879 | 2.8791 | 2.9703 | 3.0615 | 3.1526 | 3.2438 | 3.335 | 3.4262 | 3.5173 | 3.6085 | 3.6997 | 3.7909 | 3.882 | 3.9732 | 4.0644 | 4.1556 | 4.2467 | 4.3379 | 4.4291 | 4.5202 | 4.6059 | 4.6916 | 4.7772 | 4.8628 | 4.9485 | 5.0342 | 5.1198 | 5.2054 | 5.2911 | 5.3767 | 5.4624 | 5.548 | 5.6337 | 5.7194 | 5.805 | 5.8906 | 5.9763 | 6.0619 | 6.1476 | 6.2332 | 6.3189 | 6.4045 | 6.4902 | 6.5758 | 6.6615 | 6.7471 | 6.8328 | 6.9184 | 7.0041 | 7.0898 | 7.1584 | 7.2271 | 7.2957 | 7.3643 | 7.433 | 7.5016 | 7.5703 | 7.6389 | 7.7076 | 7.7762 | 7.8449 | 7.9135 | 7.9822 | 8.0508 | 8.1195 | 8.1881 | 8.2568 | 8.3254 | 8.3941 | 8.4627 | 8.5314 | 8.6 | 8.6687 | 8.7373 | 8.806 | 8.8746 | 8.9433 | 9.0119 | 9.0806 | 9.1492 | 9.1991 | 9.249 | 9.2989 | 9.3488 | 9.3987 | 9.4486 | 9.4985 | 9.5484 | 9.5983 | 9.6482 | 9.6981 | 9.7479 | 9.7978 | 9.8477 | 9.8976 | 9.9475 | 9.9974 | 10.0473 | 10.0972 | 10.1471 | 10.197 | 10.2469 | 10.2968 | 10.3467 | 10.3965 | 10.4464 | 10.4963 | 10.5462 | 10.5961 | 10.646
5 | 0 | 1.39 | 1.225 | 1.19 | 1.095 | 1.43 | 1.82 | 4.615 | 7.235 | 9.335 | 10.86 | 0 | 0.139 | 0.278 | 0.417 | 0.556 | 0.695 | 0.834 | 0.973 | 1.112 | 1.251 | 1.39 | 1.357 | 1.324 | 1.291 | 1.258 | 1.225 | 1.218 | 1.211 | 1.204 | 1.197 | 1.19 | 1.1805 | 1.171 | 1.1615 | 1.152 | 1.1425 | 1.133 | 1.1235 | 1.114 | 1.1045 | 1.095 | 1.1173 | 1.1397 | 1.162 | 1.1843 | 1.2067 | 1.229 | 1.2513 | 1.2737 | 1.296 | 1.3183 | 1.3407 | 1.363 | 1.3853 | 1.4077 | 1.43 | 1.456 | 1.482 | 1.508 | 1.534 | 1.56 | 1.586 | 1.612 | 1.638 | 1.664 | 1.69 | 1.716 | 1.742 | 1.768 | 1.794 | 1.82 | 1.9132 | 2.0063 | 2.0995 | 2.1927 | 2.2858 | 2.379 | 2.4722 | 2.5653 | 2.6585 | 2.7517 | 2.8448 | 2.938 | 3.0312 | 3.1243 | 3.2175 | 3.3107 | 3.4038 | 3.497 | 3.5902 | 3.6833 | 3.7765 | 3.8697 | 3.9628 | 4.056 | 4.1492 | 4.2423 | 4.3355 | 4.4287 | 4.5218 | 4.615 | 4.7023 | 4.7897 | 4.877 | 4.9643 | 5.0517 | 5.139 | 5.2263 | 5.3137 | 5.401 | 5.4883 | 5.5757 | 5.663 | 5.7503 | 5.8377 | 5.925 | 6.0123 | 6.0997 | 6.187 | 6.2743 | 6.3617 | 6.449 | 6.5363 | 6.6237 | 6.711 | 6.7983 | 6.8857 | 6.973 | 7.0603 | 7.1477 | 7.235 | 7.305 | 7.375 | 7.445 | 7.515 | 7.585 | 7.655 | 7.725 | 7.795 | 7.865 | 7.935 | 8.005 | 8.075 | 8.145 | 8.215 | 8.285 | 8.355 | 8.425 | 8.495 | 8.565 | 8.635 | 8.705 | 8.775 | 8.845 | 8.915 | 8.985 | 9.055 | 9.125 | 9.195 | 9.265 | 9.335 | 9.3858 | 9.4367 | 9.4875 | 9.5383 | 9.5892 | 9.64 | 9.6908 | 9.7417 | 9.7925 | 9.8433 | 9.8942 | 9.945 | 9.9958 | 10.0467 | 10.0975 | 10.1483 | 10.1992 | 10.25 | 10.3008 | 10.3517 | 10.4025 | 10.4533 | 10.5042 | 10.555 | 10.6058 | 10.6567 | 10.7075 | 10.7583 | 10.8092 | 10.86
5.05 | 0 | 1.415 | 1.2473 | 1.21 | 1.1147 | 1.4575 | 1.855 | 4.7097 | 7.3802 | 9.5207 | 11.074 | 0 | 0.1415 | 0.283 | 0.4245 | 0.566 | 0.7075 | 0.849 | 0.9905 | 1.132 | 1.2735 | 1.415 | 1.3815 | 1.3479 | 1.3144 | 1.2808 | 1.2473 | 1.2398 | 1.2324 | 1.2249 | 1.2174 | 1.21 | 1.2005 | 1.1909 | 1.1814 | 1.1719 | 1.1624 | 1.1528 | 1.1433 | 1.1338 | 1.1243 | 1.1147 | 1.1376 | 1.1604 | 1.1833 | 1.2062 | 1.229 | 1.2519 | 1.2747 | 1.2976 | 1.3204 | 1.3433 | 1.3661 | 1.389 | 1.4118 | 1.4347 | 1.4575 | 1.484 | 1.5105 | 1.537 | 1.5635 | 1.59 | 1.6165 | 1.643 | 1.6695 | 1.696 | 1.7225 | 1.749 | 1.7755 | 1.802 | 1.8285 | 1.855 | 1.9502 | 2.0453 | 2.1405 | 2.2356 | 2.3308 | 2.4259 | 2.5211 | 2.6163 | 2.7114 | 2.8066 | 2.9017 | 2.9969 | 3.0921 | 3.1872 | 3.2824 | 3.3775 | 3.4727 | 3.5678 | 3.663 | 3.7582 | 3.8533 | 3.9485 | 4.0436 | 4.1388 | 4.234 | 4.3291 | 4.4243 | 4.5194 | 4.6146 | 4.7097 | 4.7988 | 4.8878 | 4.9768 | 5.0658 | 5.1548 | 5.2439 | 5.3329 | 5.4219 | 5.5109 | 5.5999 | 5.6889 | 5.7779 | 5.867 | 5.956 | 6.045 | 6.134 | 6.223 | 6.312 | 6.4011 | 6.4901 | 6.5791 | 6.6681 | 6.7571 | 6.8461 | 6.9352 | 7.0242 | 7.1132 | 7.2022 | 7.2912 | 7.3803 | 7.4516 | 7.5229 | 7.5943 | 7.6657 | 7.737 | 7.8084 | 7.8797 | 7.9511 | 8.0224 | 8.0938 | 8.1651 | 8.2364 | 8.3078 | 8.3792 | 8.4505 | 8.5219 | 8.5932 | 8.6646 | 8.7359 | 8.8072 | 8.8786 | 8.95 | 9.0213 | 9.0927 | 9.164 | 9.2354 | 9.3067 | 9.378 | 9.4494 | 9.5207 | 9.5725 | 9.6243 | 9.6761 | 9.7279 | 9.7796 | 9.8314 | 9.8832 | 9.9349 | 9.9867 | 10.0385 | 10.0903 | 10.142 | 10.1938 | 10.2456 | 10.2974 | 10.3491 | 10.4009 | 10.4527 | 10.5045 | 10.5562 | 10.608 | 10.6598 | 10.7116 | 10.7633 | 10.8151 | 10.8669 | 10.9187 | 10.9704 | 11.0222 | 11.074
5.1 | 0 | 1.44 | 1.2695 | 1.23 | 1.1345 | 1.485 | 1.89 | 4.8045 | 7.5255 | 9.7065 | 11.288 | 1.1102e-16 | 0.144 | 0.288 | 0.432 | 0.576 | 0.72 | 0.864 | 1.008 | 1.152 | 1.296 | 1.44 | 1.4059 | 1.3718 | 1.3377 | 1.3036 | 1.2695 | 1.2616 | 1.2537 | 1.2458 | 1.2379 | 1.23 | 1.2204 | 1.2109 | 1.2013 | 1.1918 | 1.1822 | 1.1727 | 1.1631 | 1.1536 | 1.144 | 1.1345 | 1.1579 | 1.1812 | 1.2046 | 1.228 | 1.2513 | 1.2747 | 1.2981 | 1.3214 | 1.3448 | 1.3682 | 1.3915 | 1.4149 | 1.4383 | 1.4616 | 1.485 | 1.512 | 1.539 | 1.566 | 1.593 | 1.62 | 1.647 | 1.674 | 1.701 | 1.728 | 1.755 | 1.782 | 1.809 | 1.836 | 1.863 | 1.89 | 1.9871 | 2.0843 | 2.1814 | 2.2786 | 2.3757 | 2.4729 | 2.57 | 2.6672 | 2.7643 | 2.8615 | 2.9586 | 3.0558 | 3.1529 | 3.2501 | 3.3472 | 3.4444 | 3.5415 | 3.6387 | 3.7358 | 3.833 | 3.9301 | 4.0273 | 4.1244 | 4.2216 | 4.3187 | 4.4159 | 4.513 | 4.6102 | 4.7073 | 4.8045 | 4.8952 | 4.9859 | 5.0766 | 5.1673 | 5.258 | 5.3487 | 5.4394 | 5.5301 | 5.6208 | 5.7115 | 5.8022 | 5.8929 | 5.9836 | 6.0743 | 6.165 | 6.2557 | 6.3464 | 6.4371 | 6.5278 | 6.6185 | 6.7092 | 6.7999 | 6.8906 | 6.9813 | 7.072 | 7.1627 | 7.2534 | 7.3441 | 7.4348 | 7.5255 | 7.5982 | 7.6709 | 7.7436 | 7.8163 | 7.889 | 7.9617 | 8.0344 | 8.1071 | 8.1798 | 8.2525 | 8.3252 | 8.3979 | 8.4706 | 8.5433 | 8.616 | 8.6887 | 8.7614 | 8.8341 | 8.9068 | 8.9795 | 9.0522 | 9.1249 | 9.1976 | 9.2703 | 9.343 | 9.4157 | 9.4884 | 9.5611 | 9.6338 | 9.7065 | 9.7592 | 9.8119 | 9.8646 | 9.9174 | 9.9701 | 10.0228 | 10.0755 | 10.1282 | 10.1809 | 10.2337 | 10.2864 | 10.3391 | 10.3918 | 10.4445 | 10.4972 | 10.55 | 10.6027 | 10.6554 | 10.7081 | 10.7608 | 10.8135 | 10.8663 | 10.919 | 10.9717 | 11.0244 | 11.0771 | 11.1298 | 11.1826 | 11.2353 | 11.288
5.15 | 0 | 1.465 | 1.2918 | 1.25 | 1.1542 | 1.5125 | 1.925 | 4.8993 | 7.6708 | 9.8923 | 11.502 | 1.1102e-16 | 0.1465 | 0.293 | 0.4395 | 0.586 | 0.7325 | 0.879 | 1.0255 | 1.172 | 1.3185 | 1.465 | 1.4303 | 1.3957 | 1.3611 | 1.3264 | 1.2918 | 1.2834 | 1.2751 | 1.2667 | 1.2584 | 1.25 | 1.2404 | 1.2308 | 1.2213 | 1.2117 | 1.2021 | 1.1925 | 1.183 | 1.1734 | 1.1638 | 1.1542 | 1.1781 | 1.202 | 1.2259 | 1.2498 | 1.2737 | 1.2976 | 1.3214 | 1.3453 | 1.3692 | 1.3931 | 1.417 | 1.4409 | 1.4647 | 1.4886 | 1.5125 | 1.54 | 1.5675 | 1.595 | 1.6225 | 1.65 | 1.6775 | 1.705 | 1.7325 | 1.76 | 1.7875 | 1.815 | 1.8425 | 1.87 | 1.8975 | 1.925 | 2.0241 | 2.1233 | 2.2224 | 2.3216 | 2.4207 | 2.5198 | 2.619 | 2.7181 | 2.8173 | 2.9164 | 3.0156 | 3.1147 | 3.2138 | 3.313 | 3.4121 | 3.5113 | 3.6104 | 3.7095 | 3.8087 | 3.9078 | 4.007 | 4.1061 | 4.2053 | 4.3044 | 4.4035 | 4.5027 | 4.6018 | 4.701 | 4.8001 | 4.8993 | 4.9916 | 5.084 | 5.1764 | 5.2688 | 5.3612 | 5.4535 | 5.5459 | 5.6383 | 5.7307 | 5.8231 | 5.9155 | 6.0079 | 6.1002 | 6.1926 | 6.285 | 6.3774 | 6.4698 | 6.5622 | 6.6545 | 6.7469 | 6.8393 | 6.9317 | 7.0241 | 7.1165 | 7.2088 | 7.3012 | 7.3936 | 7.486 | 7.5784 | 7.6708 | 7.7448 | 7.8189 | 7.8929 | 7.967 | 8.041 | 8.1151 | 8.1891 | 8.2632 | 8.3372 | 8.4113 | 8.4853 | 8.5594 | 8.6334 | 8.7075 | 8.7815 | 8.8556 | 8.9296 | 9.0037 | 9.0777 | 9.1518 | 9.2258 | 9.2999 | 9.3739 | 9.448 | 9.522 | 9.5961 | 9.6701 | 9.7442 | 9.8182 | 9.8923 | 9.9459 | 9.9996 | 10.0532 | 10.1069 | 10.1605 | 10.2142 | 10.2679 | 10.3215 | 10.3752 | 10.4288 | 10.4825 | 10.5361 | 10.5898 | 10.6435 | 10.6971 | 10.7508 | 10.8044 | 10.8581 | 10.9118 | 10.9654 | 11.0191 | 11.0727 | 11.1264 | 11.18 | 11.2337 | 11.2874 | 11.341 | 11.3947 | 11.4483 | 11.502
5.2 | 0 | 1.49 | 1.314 | 1.27 | 1.174 | 1.54 | 1.96 | 4.994 | 7.816 | 10.078 | 11.716 | 0 | 0.149 | 0.298 | 0.447 | 0.596 | 0.745 | 0.894 | 1.043 | 1.192 | 1.341 | 1.49 | 1.4548 | 1.4196 | 1.3844 | 1.3492 | 1.314 | 1.3052 | 1.2964 | 1.2876 | 1.2788 | 1.27 | 1.2604 | 1.2508 | 1.2412 | 1.2316 | 1.222 | 1.2124 | 1.2028 | 1.1932 | 1.1836 | 1.174 | 1.1984 | 1.2228 | 1.2472 | 1.2716 | 1.296 | 1.3204 | 1.3448 | 1.3692 | 1.3936 | 1.418 | 1.4424 | 1.4668 | 1.4912 | 1.5156 | 1.54 | 1.568 | 1.596 | 1.624 | 1.652 | 1.68 | 1.708 | 1.736 | 1.764 | 1.792 | 1.82 | 1.848 | 1.876 | 1.904 | 1.932 | 1.96 | 2.0611 | 2.1623 | 2.2634 | 2.3645 | 2.4657 | 2.5668 | 2.6679 | 2.7691 | 2.8702 | 2.9713 | 3.0725 | 3.1736 | 3.2747 | 3.3759 | 3.477 | 3.5781 | 3.6793 | 3.7804 | 3.8815 | 3.9827 | 4.0838 | 4.1849 | 4.2861 | 4.3872 | 4.4883 | 4.5895 | 4.6906 | 4.7917 | 4.8929 | 4.994 | 5.0881 | 5.1821 | 5.2762 | 5.3703 | 5.4643 | 5.5584 | 5.6525 | 5.7465 | 5.8406 | 5.9347 | 6.0287 | 6.1228 | 6.2169 | 6.3109 | 6.405 | 6.4991 | 6.5931 | 6.6872 | 6.7813 | 6.8753 | 6.9694 | 7.0635 | 7.1575 | 7.2516 | 7.3457 | 7.4397 | 7.5338 | 7.6279 | 7.7219 | 7.816 | 7.8914 | 7.9668 | 8.0422 | 8.1176 | 8.193 | 8.2684 | 8.3438 | 8.4192 | 8.4946 | 8.57 | 8.6454 | 8.7208 | 8.7962 | 8.8716 | 8.947 | 9.0224 | 9.0978 | 9.1732 | 9.2486 | 9.324 | 9.3994 | 9.4748 | 9.5502 | 9.6256 | 9.701 | 9.7764 | 9.8518 | 9.9272 | 10.0026 | 10.078 | 10.1326 | 10.1872 | 10.2418 | 10.2964 | 10.351 | 10.4056 | 10.4602 | 10.5148 | 10.5694 | 10.624 | 10.6786 | 10.7332 | 10.7878 | 10.8424 | 10.897 | 10.9516 | 11.0062 | 11.0608 | 11.1154 | 11.17 | 11.2246 | 11.2792 | 11.3338 | 11.3884 | 11.443 | 11.4976 | 11.5522 | 11.6068 | 11.6614 | 11.716
5.25 | 0 | 1.515 | 1.3363 | 1.29 | 1.1937 | 1.5675 | 1.995 | 5.0887 | 7.9612 | 10.2637 | 11.93 | 0 | 0.1515 | 0.303 | 0.4545 | 0.606 | 0.7575 | 0.909 | 1.0605 | 1.212 | 1.3635 | 1.515 | 1.4793 | 1.4435 | 1.4078 | 1.372 | 1.3363 | 1.327 | 1.3178 | 1.3085 | 1.2993 | 1.29 | 1.2804 | 1.2708 | 1.2611 | 1.2515 | 1.2419 | 1.2322 | 1.2226 | 1.213 | 1.2034 | 1.1937 | 1.2187 | 1.2436 | 1.2685 | 1.2934 | 1.3183 | 1.3433 | 1.3682 | 1.3931 | 1.418 | 1.4429 | 1.4678 | 1.4928 | 1.5177 | 1.5426 | 1.5675 | 1.596 | 1.6245 | 1.653 | 1.6815 | 1.71 | 1.7385 | 1.767 | 1.7955 | 1.824 | 1.8525 | 1.881 | 1.9095 | 1.938 | 1.9665 | 1.995 | 2.0981 | 2.2013 | 2.3044 | 2.4075 | 2.5106 | 2.6138 | 2.7169 | 2.82 | 2.9231 | 3.0263 | 3.1294 | 3.2325 | 3.3356 | 3.4388 | 3.5419 | 3.645 | 3.7481 | 3.8513 | 3.9544 | 4.0575 | 4.1606 | 4.2637 | 4.3669 | 4.47 | 4.5731 | 4.6762 | 4.7794 | 4.8825 | 4.9856 | 5.0887 | 5.1845 | 5.2802 | 5.376 | 5.4717 | 5.5675 | 5.6632 | 5.759 | 5.8547 | 5.9505 | 6.0462 | 6.142 | 6.2377 | 6.3335 | 6.4292 | 6.525 | 6.6207 | 6.7165 | 6.8122 | 6.908 | 7.0037 | 7.0995 | 7.1952 | 7.291 | 7.3867 | 7.4825 | 7.5782 | 7.674 | 7.7697 | 7.8655 | 7.9612 | 8.038 | 8.1147 | 8.1915 | 8.2682 | 8.345 | 8.4217 | 8.4985 | 8.5752 | 8.652 | 8.7287 | 8.8055 | 8.8822 | 8.959 | 9.0357 | 9.1125 | 9.1892 | 9.266 | 9.3427 | 9.4195 | 9.4962 | 9.573 | 9.6497 | 9.7265 | 9.8032 | 9.88 | 9.9567 | 10.0335 | 10.1102 | 10.187 | 10.2637 | 10.3193 | 10.3748 | 10.4304 | 10.4859 | 10.5415 | 10.597 | 10.6525 | 10.7081 | 10.7636 | 10.8192 | 10.8747 | 10.9302 | 10.9858 | 11.0413 | 11.0969 | 11.1524 | 11.208 | 11.2635 | 11.319 | 11.3746 | 11.4301 | 11.4857 | 11.5412 | 11.5968 | 11.6523 | 11.7078 | 11.7634 | 11.8189 | 11.8745 | 11.93
5.3 | 0 | 1.54 | 1.3585 | 1.31 | 1.2135 | 1.595 | 2.03 | 5.1835 | 8.1065 | 10.4495 | 12.144 | -1.1102e-16 | 0.154 | 0.308 | 0.462 | 0.616 | 0.77 | 0.924 | 1.078 | 1.232 | 1.386 | 1.54 | 1.5037 | 1.4674 | 1.4311 | 1.3948 | 1.3585 | 1.3488 | 1.3391 | 1.3294 | 1.3197 | 1.31 | 1.3004 | 1.2907 | 1.2811 | 1.2714 | 1.2618 | 1.2521 | 1.2425 | 1.2328 | 1.2231 | 1.2135 | 1.2389 | 1.2644 | 1.2898 | 1.3152 | 1.3407 | 1.3661 | 1.3915 | 1.417 | 1.4424 | 1.4678 | 1.4933 | 1.5187 | 1.5441 | 1.5696 | 1.595 | 1.624 | 1.653 | 1.682 | 1.711 | 1.74 | 1.769 | 1.798 | 1.827 | 1.856 | 1.885 | 1.914 | 1.943 | 1.972 | 2.001 | 2.03 | 2.1351 | 2.2402 | 2.3453 | 2.4505 | 2.5556 | 2.6607 | 2.7658 | 2.8709 | 2.976 | 3.0812 | 3.1863 | 3.2914 | 3.3965 | 3.5016 | 3.6067 | 3.7119 | 3.817 | 3.9221 | 4.0272 | 4.1323 | 4.2374 | 4.3426 | 4.4477 | 4.5528 | 4.6579 | 4.763 | 4.8681 | 4.9733 | 5.0784 | 5.1835 | 5.2809 | 5.3784 | 5.4758 | 5.5732 | 5.6707 | 5.7681 | 5.8655 | 5.963 | 6.0604 | 6.1578 | 6.2553 | 6.3527 | 6.4501 | 6.5476 | 6.645 | 6.7424 | 6.8399 | 6.9373 | 7.0347 | 7.1322 | 7.2296 | 7.327 | 7.4245 | 7.5219 | 7.6193 | 7.7168 | 7.8142 | 7.9116 | 8.0091 | 8.1065 | 8.1846 | 8.2627 | 8.3408 | 8.4189 | 8.497 | 8.5751 | 8.6532 | 8.7313 | 8.8094 | 8.8875 | 8.9656 | 9.0437 | 9.1218 | 9.1999 | 9.278 | 9.3561 | 9.4342 | 9.5123 | 9.5904 | 9.6685 | 9.7466 | 9.8247 | 9.9028 | 9.9809 | 10.059 | 10.1371 | 10.2152 | 10.2933 | 10.3714 | 10.4495 | 10.506 | 10.5625 | 10.6189 | 10.6754 | 10.7319 | 10.7884 | 10.8449 | 10.9014 | 10.9578 | 11.0143 | 11.0708 | 11.1273 | 11.1838 | 11.2403 | 11.2967 | 11.3532 | 11.4097 | 11.4662 | 11.5227 | 11.5792 | 11.6356 | 11.6921 | 11.7486 | 11.8051 | 11.8616 | 11.9181 | 11.9745 | 12.031 | 12.0875 | 12.144
5.35 | 0 | 1.565 | 1.3807 | 1.33 | 1.2332 | 1.6225 | 2.065 | 5.2782 | 8.2517 | 10.6352 | 12.358 | 0 | 0.1565 | 0.313 | 0.4695 | 0.626 | 0.7825 | 0.939 | 1.0955 | 1.252 | 1.4085 | 1.565 | 1.5281 | 1.4913 | 1.4544 | 1.4176 | 1.3807 | 1.3706 | 1.3604 | 1.3503 | 1.3401 | 1.33 | 1.3203 | 1.3107 | 1.301 | 1.2913 | 1.2816 | 1.272 | 1.2623 | 1.2526 | 1.2429 | 1.2332 | 1.2592 | 1.2851 | 1.3111 | 1.337 | 1.363 | 1.3889 | 1.4149 | 1.4408 | 1.4668 | 1.4928 | 1.5187 | 1.5446 | 1.5706 | 1.5965 | 1.6225 | 1.652 | 1.6815 | 1.711 | 1.7405 | 1.77 | 1.7995 | 1.829 | 1.8585 | 1.888 | 1.9175 | 1.947 | 1.9765 | 2.006 | 2.0355 | 2.065 | 2.1721 | 2.2792 | 2.3863 | 2.4934 | 2.6005 | 2.7076 | 2.8148 | 2.9219 | 3.029 | 3.1361 | 3.2432 | 3.3503 | 3.4574 | 3.5645 | 3.6716 | 3.7787 | 3.8858 | 3.9929 | 4.1001 | 4.2072 | 4.3143 | 4.4214 | 4.5285 | 4.6356 | 4.7427 | 4.8498 | 4.9569 | 5.064 | 5.1711 | 5.2782 | 5.3774 | 5.4765 | 5.5756 | 5.6747 | 5.7738 | 5.8729 | 5.9721 | 6.0712 | 6.1703 | 6.2694 | 6.3685 | 6.4676 | 6.5668 | 6.6659 | 6.765 | 6.8641 | 6.9632 | 7.0623 | 7.1615 | 7.2606 | 7.3597 | 7.4588 | 7.5579 | 7.657 | 7.7562 | 7.8553 | 7.9544 | 8.0535 | 8.1526 | 8.2517 | 8.3312 | 8.4106 | 8.4901 | 8.5695 | 8.649 | 8.7284 | 8.8079 | 8.8873 | 8.9668 | 9.0462 | 9.1257 | 9.2051 | 9.2846 | 9.364 | 9.4435 | 9.5229 | 9.6024 | 9.6818 | 9.7613 | 9.8407 | 9.9202 | 9.9996 | 10.0791 | 10.1585 | 10.238 | 10.3174 | 10.3969 | 10.4763 | 10.5558 | 10.6352 | 10.6927 | 10.7501 | 10.8075 | 10.8649 | 10.9224 | 10.9798 | 11.0372 | 11.0946 | 11.1521 | 11.2095 | 11.2669 | 11.3243 | 11.3818 | 11.4392 | 11.4966 | 11.554 | 11.6115 | 11.6689 | 11.7263 | 11.7837 | 11.8412 | 11.8986 | 11.956 | 12.0134 | 12.0709 | 12.1283 | 12.1857 | 12.2431 | 12.3006 | 12.358
5.4 | 0 | 1.59 | 1.403 | 1.35 | 1.253 | 1.65 | 2.1 | 5.373 | 8.397 | 10.821 | 12.572 | 0 | 0.159 | 0.318 | 0.477 | 0.636 | 0.795 | 0.954 | 1.113 | 1.272 | 1.431 | 1.59 | 1.5526 | 1.5152 | 1.4778 | 1.4404 | 1.403 | 1.3924 | 1.3818 | 1.3712 | 1.3606 | 1.35 | 1.3403 | 1.3306 | 1.3209 | 1.3112 | 1.3015 | 1.2918 | 1.2821 | 1.2724 | 1.2627 | 1.253 | 1.2795 | 1.3059 | 1.3324 | 1.3589 | 1.3853 | 1.4118 | 1.4383 | 1.4647 | 1.4912 | 1.5177 | 1.5441 | 1.5706 | 1.5971 | 1.6235 | 1.65 | 1.68 | 1.71 | 1.74 | 1.77 | 1.8 | 1.83 | 1.86 | 1.89 | 1.92 | 1.95 | 1.98 | 2.01 | 2.04 | 2.07 | 2.1 | 2.2091 | 2.3182 | 2.4273 | 2.5364 | 2.6455 | 2.7546 | 2.8637 | 2.9728 | 3.0819 | 3.191 | 3.3001 | 3.4092 | 3.5183 | 3.6274 | 3.7365 | 3.8456 | 3.9547 | 4.0638 | 4.1729 | 4.282 | 4.3911 | 4.5002 | 4.6093 | 4.7184 | 4.8275 | 4.9366 | 5.0457 | 5.1548 | 5.2639 | 5.373 | 5.4738 | 5.5746 | 5.6754 | 5.7762 | 5.877 | 5.9778 | 6.0786 | 6.1794 | 6.2802 | 6.381 | 6.4818 | 6.5826 | 6.6834 | 6.7842 | 6.885 | 6.9858 | 7.0866 | 7.1874 | 7.2882 | 7.389 | 7.4898 | 7.5906 | 7.6914 | 7.7922 | 7.893 | 7.9938 | 8.0946 | 8.1954 | 8.2962 | 8.397 | 8.4778 | 8.5586 | 8.6394 | 8.7202 | 8.801 | 8.8818 | 8.9626 | 9.0434 | 9.1242 | 9.205 | 9.2858 | 9.3666 | 9.4474 | 9.5282 | 9.609 | 9.6898 | 9.7706 | 9.8514 | 9.9322 | 10.013 | 10.0938 | 10.1746 | 10.2554 | 10.3362 | 10.417 | 10.4978 | 10.5786 | 10.6594 | 10.7402 | 10.821 | 10.8794 | 10.9377 | 10.9961 | 11.0545 | 11.1128 | 11.1712 | 11.2296 | 11.2879 | 11.3463 | 11.4047 | 11.463 | 11.5214 | 11.5798 | 11.6381 | 11.6965 | 11.7549 | 11.8132 | 11.8716 | 11.93 | 11.9883 | 12.0467 | 12.1051 | 12.1634 | 12.2218 | 12.2802 | 12.3385 | 12.3969 | 12.4553 | 12.5136 | 12.572
5.45 | 0 | 1.615 | 1.4253 | 1.37 | 1.2728 | 1.6775 | 2.135 | 5.4678 | 8.5422 | 11.0068 | 12.786 | 1.1102e-16 | 0.1615 | 0.323 | 0.4845 | 0.646 | 0.8075 | 0.969 | 1.1305 | 1.292 | 1.4535 | 1.615 | 1.5771 | 1.5391 | 1.5011 | 1.4632 | 1.4253 | 1.4142 | 1.4032 | 1.3921 | 1.3811 | 1.37 | 1.3603 | 1.3506 | 1.3408 | 1.3311 | 1.3214 | 1.3116 | 1.3019 | 1.2922 | 1.2825 | 1.2727 | 1.2997 | 1.3267 | 1.3537 | 1.3807 | 1.4077 | 1.4346 | 1.4616 | 1.4886 | 1.5156 | 1.5426 | 1.5696 | 1.5966 | 1.6235 | 1.6505 | 1.6775 | 1.708 | 1.7385 | 1.769 | 1.7995 | 1.83 | 1.8605 | 1.891 | 1.9215 | 1.952 | 1.9825 | 2.013 | 2.0435 | 2.074 | 2.1045 | 2.135 | 2.2461 | 2.3572 | 2.4683 | 2.5794 | 2.6905 | 2.8015 | 2.9126 | 3.0237 | 3.1348 | 3.2459 | 3.357 | 3.4681 | 3.5792 | 3.6903 | 3.8014 | 3.9125 | 4.0236 | 4.1347 | 4.2457 | 4.3568 | 4.4679 | 4.579 | 4.6901 | 4.8012 | 4.9123 | 5.0234 | 5.1345 | 5.2456 | 5.3567 | 5.4678 | 5.5702 | 5.6727 | 5.7752 | 5.8777 | 5.9802 | 6.0827 | 6.1851 | 6.2876 | 6.3901 | 6.4926 | 6.5951 | 6.6976 | 6.8 | 6.9025 | 7.005 | 7.1075 | 7.21 | 7.3125 | 7.4149 | 7.5174 | 7.6199 | 7.7224 | 7.8249 | 7.9273 | 8.0298 | 8.1323 | 8.2348 | 8.3373 | 8.4398 | 8.5422 | 8.6244 | 8.7065 | 8.7887 | 8.8708 | 8.953 | 9.0351 | 9.1173 | 9.1994 | 9.2816 | 9.3637 | 9.4459 | 9.528 | 9.6102 | 9.6923 | 9.7745 | 9.8566 | 9.9388 | 10.0209 | 10.1031 | 10.1852 | 10.2674 | 10.3495 | 10.4317 | 10.5138 | 10.596 | 10.6781 | 10.7603 | 10.8424 | 10.9246 | 11.0068 | 11.0661 | 11.1254 | 11.1847 | 11.244 | 11.3033 | 11.3626 | 11.4219 | 11.4812 | 11.5405 | 11.5998 | 11.6591 | 11.7184 | 11.7778 | 11.8371 | 11.8964 | 11.9557 | 12.015 | 12.0743 | 12.1336 | 12.1929 | 12.2522 | 12.3115 | 12.3708 | 12.4301 | 12.4895 | 12.5488 | 12.6081 | 12.6674 | 12.7267 | 12.786
5.5 | 0 | 1.64 | 1.4475 | 1.39 | 1.2925 | 1.705 | 2.17 | 5.5625 | 8.6875 | 11.1925 | 13 | 1.1102e-16 | 0.164 | 0.328 | 0.492 | 0.656 | 0.82 | 0.984 | 1.148 | 1.312 | 1.476 | 1.64 | 1.6015 | 1.563 | 1.5245 | 1.486 | 1.4475 | 1.436 | 1.4245 | 1.413 | 1.4015 | 1.39 | 1.3802 | 1.3705 | 1.3607 | 1.351 | 1.3413 | 1.3315 | 1.3217 | 1.312 | 1.3022 | 1.2925 | 1.32 | 1.3475 | 1.375 | 1.4025 | 1.43 | 1.4575 | 1.485 | 1.5125 | 1.54 | 1.5675 | 1.595 | 1.6225 | 1.65 | 1.6775 | 1.705 | 1.736 | 1.767 | 1.798 | 1.829 | 1.86 | 1.891 | 1.922 | 1.953 | 1.984 | 2.015 | 2.046 | 2.077 | 2.108 | 2.139 | 2.17 | 2.2831 | 2.3962 | 2.5092 | 2.6223 | 2.7354 | 2.8485 | 2.9616 | 3.0747 | 3.1877 | 3.3008 | 3.4139 | 3.527 | 3.6401 | 3.7532 | 3.8662 | 3.9793 | 4.0924 | 4.2055 | 4.3186 | 4.4317 | 4.5447 | 4.6578 | 4.7709 | 4.884 | 4.9971 | 5.1102 | 5.2232 | 5.3363 | 5.4494 | 5.5625 | 5.6667 | 5.7708 | 5.875 | 5.9792 | 6.0833 | 6.1875 | 6.2917 | 6.3958 | 6.5 | 6.6042 | 6.7083 | 6.8125 | 6.9167 | 7.0208 | 7.125 | 7.2292 | 7.3333 | 7.4375 | 7.5417 | 7.6458 | 7.75 | 7.8542 | 7.9583 | 8.0625 | 8.1667 | 8.2708 | 8.375 | 8.4792 | 8.5833 | 8.6875 | 8.771 | 8.8545 | 8.938 | 9.0215 | 9.105 | 9.1885 | 9.272 | 9.3555 | 9.439 | 9.5225 | 9.606 | 9.6895 | 9.773 | 9.8565 | 9.94 | 10.0235 | 10.107 | 10.1905 | 10.274 | 10.3575 | 10.441 | 10.5245 | 10.608 | 10.6915 | 10.775 | 10.8585 | 10.942 | 11.0255 | 11.109 | 11.1925 | 11.2527 | 11.313 | 11.3732 | 11.4335 | 11.4937 | 11.554 | 11.6142 | 11.6745 | 11.7348 | 11.795 | 11.8552 | 11.9155 | 11.9757 | 12.036 | 12.0962 | 12.1565 | 12.2167 | 12.277 | 12.3372 | 12.3975 | 12.4577 | 12.518 | 12.5782 | 12.6385 | 12.6988 | 12.759 | 12.8193 | 12.8795 | 12.9398 | 13
5.55 | 0 | 1.665 | 1.4697 | 1.41 | 1.3122 | 1.7325 | 2.205 | 5.6572 | 8.8327 | 11.3782 | 13.214 | 0 | 0.1665 | 0.333 | 0.4995 | 0.666 | 0.8325 | 0.999 | 1.1655 | 1.332 | 1.4985 | 1.665 | 1.6259 | 1.5869 | 1.5478 | 1.5088 | 1.4697 | 1.4578 | 1.4459 | 1.4339 | 1.422 | 1.41 | 1.4002 | 1.3904 | 1.3807 | 1.3709 | 1.3611 | 1.3514 | 1.3416 | 1.3318 | 1.322 | 1.3122 | 1.3403 | 1.3683 | 1.3963 | 1.4243 | 1.4523 | 1.4804 | 1.5084 | 1.5364 | 1.5644 | 1.5924 | 1.6204 | 1.6485 | 1.6765 | 1.7045 | 1.7325 | 1.764 | 1.7955 | 1.827 | 1.8585 | 1.89 | 1.9215 | 1.953 | 1.9845 | 2.016 | 2.0475 | 2.079 | 2.1105 | 2.142 | 2.1735 | 2.205 | 2.3201 | 2.4352 | 2.5502 | 2.6653 | 2.7804 | 2.8955 | 3.0105 | 3.1256 | 3.2407 | 3.3558 | 3.4708 | 3.5859 | 3.701 | 3.8161 | 3.9311 | 4.0462 | 4.1613 | 4.2764 | 4.3914 | 4.5065 | 4.6216 | 4.7366 | 4.8517 | 4.9668 | 5.0819 | 5.1969 | 5.312 | 5.4271 | 5.5422 | 5.6573 | 5.7631 | 5.8689 | 5.9748 | 6.0806 | 6.1865 | 6.2923 | 6.3982 | 6.504 | 6.6099 | 6.7157 | 6.8216 | 6.9274 | 7.0333 | 7.1391 | 7.245 | 7.3508 | 7.4567 | 7.5625 | 7.6684 | 7.7742 | 7.8801 | 7.9859 | 8.0918 | 8.1976 | 8.3035 | 8.4093 | 8.5152 | 8.621 | 8.7269 | 8.8327 | 8.9176 | 9.0024 | 9.0873 | 9.1721 | 9.257 | 9.3418 | 9.4267 | 9.5115 | 9.5964 | 9.6812 | 9.7661 | 9.8509 | 9.9358 | 10.0206 | 10.1055 | 10.1903 | 10.2752 | 10.36 | 10.4449 | 10.5297 | 10.6146 | 10.6994 | 10.7843 | 10.8691 | 10.954 | 11.0388 | 11.1237 | 11.2085 | 11.2934 | 11.3782 | 11.4394 | 11.5006 | 11.5618 | 11.623 | 11.6842 | 11.7454 | 11.8066 | 11.8678 | 11.929 | 11.9902 | 12.0514 | 12.1125 | 12.1737 | 12.2349 | 12.2961 | 12.3573 | 12.4185 | 12.4797 | 12.5409 | 12.6021 | 12.6633 | 12.7245 | 12.7857 | 12.8468 | 12.908 | 12.9692 | 13.0304 | 13.0916 | 13.1528 | 13.214
5.6 | 0 | 1.69 | 1.492 | 1.43 | 1.332 | 1.76 | 2.24 | 5.752 | 8.978 | 11.564 | 13.428 | -1.1102e-16 | 0.169 | 0.338 | 0.507 | 0.676 | 0.845 | 1.014 | 1.183 | 1.352 | 1.521 | 1.69 | 1.6504 | 1.6108 | 1.5712 | 1.5316 | 1.492 | 1.4796 | 1.4672 | 1.4548 | 1.4424 | 1.43 | 1.4202 | 1.4104 | 1.4006 | 1.3908 | 1.381 | 1.3712 | 1.3614 | 1.3516 | 1.3418 | 1.332 | 1.3605 | 1.3891 | 1.4176 | 1.4461 | 1.4747 | 1.5032 | 1.5317 | 1.5603 | 1.5888 | 1.6173 | 1.6459 | 1.6744 | 1.7029 | 1.7315 | 1.76 | 1.792 | 1.824 | 1.856 | 1.888 | 1.92 | 1.952 | 1.984 | 2.016 | 2.048 | 2.08 | 2.112 | 2.144 | 2.176 | 2.208 | 2.24 | 2.3571 | 2.4741 | 2.5912 | 2.7083 | 2.8253 | 2.9424 | 3.0595 | 3.1765 | 3.2936 | 3.4107 | 3.5277 | 3.6448 | 3.7619 | 3.8789 | 3.996 | 4.1131 | 4.2301 | 4.3472 | 4.4643 | 4.5813 | 4.6984 | 4.8155 | 4.9325 | 5.0496 | 5.1667 | 5.2837 | 5.4008 | 5.5179 | 5.6349 | 5.752 | 5.8595 | 5.9671 | 6.0746 | 6.1821 | 6.2897 | 6.3972 | 6.5047 | 6.6123 | 6.7198 | 6.8273 | 6.9349 | 7.0424 | 7.1499 | 7.2575 | 7.365 | 7.4725 | 7.5801 | 7.6876 | 7.7951 | 7.9027 | 8.0102 | 8.1177 | 8.2253 | 8.3328 | 8.4403 | 8.5479 | 8.6554 | 8.7629 | 8.8705 | 8.978 | 9.0642 | 9.1504 | 9.2366 | 9.3228 | 9.409 | 9.4952 | 9.5814 | 9.6676 | 9.7538 | 9.84 | 9.9262 | 10.0124 | 10.0986 | 10.1848 | 10.271 | 10.3572 | 10.4434 | 10.5296 | 10.6158 | 10.702 | 10.7882 | 10.8744 | 10.9606 | 11.0468 | 11.133 | 11.2192 | 11.3054 | 11.3916 | 11.4778 | 11.564 | 11.6261 | 11.6883 | 11.7504 | 11.8125 | 11.8747 | 11.9368 | 11.9989 | 12.0611 | 12.1232 | 12.1853 | 12.2475 | 12.3096 | 12.3717 | 12.4339 | 12.496 | 12.5581 | 12.6203 | 12.6824 | 12.7445 | 12.8067 | 12.8688 | 12.9309 | 12.9931 | 13.0552 | 13.1173 | 13.1795 | 13.2416 | 13.3037 | 13.3659 | 13.428
5.65 | 0 | 1.715 | 1.5143 | 1.45 | 1.3518 | 1.7875 | 2.275 | 5.8468 | 9.1232 | 11.7498 | 13.642 | 0 | 0.1715 | 0.343 | 0.5145 | 0.686 | 0.8575 | 1.029 | 1.2005 | 1.372 | 1.5435 | 1.715 | 1.6748 | 1.6347 | 1.5946 | 1.5544 | 1.5143 | 1.5014 | 1.4886 | 1.4757 | 1.4629 | 1.45 | 1.4402 | 1.4304 | 1.4205 | 1.4107 | 1.4009 | 1.3911 | 1.3812 | 1.3714 | 1.3616 | 1.3518 | 1.3808 | 1.4099 | 1.4389 | 1.468 | 1.497 | 1.5261 | 1.5551 | 1.5842 | 1.6132 | 1.6423 | 1.6713 | 1.7004 | 1.7294 | 1.7585 | 1.7875 | 1.82 | 1.8525 | 1.885 | 1.9175 | 1.95 | 1.9825 | 2.015 | 2.0475 | 2.08 | 2.1125 | 2.145 | 2.1775 | 2.21 | 2.2425 | 2.275 | 2.3941 | 2.5131 | 2.6322 | 2.7512 | 2.8703 | 2.9894 | 3.1084 | 3.2275 | 3.3465 | 3.4656 | 3.5846 | 3.7037 | 3.8228 | 3.9418 | 4.0609 | 4.1799 | 4.299 | 4.4181 | 4.5371 | 4.6562 | 4.7752 | 4.8943 | 5.0133 | 5.1324 | 5.2515 | 5.3705 | 5.4896 | 5.6086 | 5.7277 | 5.8468 | 5.956 | 6.0652 | 6.1744 | 6.2836 | 6.3928 | 6.502 | 6.6113 | 6.7205 | 6.8297 | 6.9389 | 7.0481 | 7.1573 | 7.2666 | 7.3758 | 7.485 | 7.5942 | 7.7034 | 7.8126 | 7.9219 | 8.0311 | 8.1403 | 8.2495 | 8.3587 | 8.4679 | 8.5772 | 8.6864 | 8.7956 | 8.9048 | 9.014 | 9.1232 | 9.2108 | 9.2983 | 9.3859 | 9.4734 | 9.561 | 9.6485 | 9.7361 | 9.8236 | 9.9112 | 9.9987 | 10.0863 | 10.1738 | 10.2614 | 10.349 | 10.4365 | 10.524 | 10.6116 | 10.6991 | 10.7867 | 10.8742 | 10.9618 | 11.0494 | 11.1369 | 11.2245 | 11.312 | 11.3996 | 11.4871 | 11.5747 | 11.6622 | 11.7498 | 11.8128 | 11.8759 | 11.939 | 12.0021 | 12.0651 | 12.1282 | 12.1913 | 12.2544 | 12.3174 | 12.3805 | 12.4436 | 12.5067 | 12.5697 | 12.6328 | 12.6959 | 12.759 | 12.822 | 12.8851 | 12.9482 | 13.0113 | 13.0743 | 13.1374 | 13.2005 | 13.2635 | 13.3266 | 13.3897 | 13.4528 | 13.5158 | 13.5789 | 13.642
5.7 | 0 | 1.74 | 1.5365 | 1.47 | 1.3715 | 1.815 | 2.31 | 5.9415 | 9.2685 | 11.9355 | 13.856 | 1.1102e-16 | 0.174 | 0.348 | 0.522 | 0.696 | 0.87 | 1.044 | 1.218 | 1.392 | 1.566 | 1.74 | 1.6993 | 1.6586 | 1.6179 | 1.5772 | 1.5365 | 1.5232 | 1.5099 | 1.4966 | 1.4833 | 1.47 | 1.4602 | 1.4503 | 1.4405 | 1.4306 | 1.4207 | 1.4109 | 1.4011 | 1.3912 | 1.3813 | 1.3715 | 1.4011 | 1.4306 | 1.4602 | 1.4898 | 1.5193 | 1.5489 | 1.5785 | 1.608 | 1.6376 | 1.6672 | 1.6967 | 1.7263 | 1.7559 | 1.7854 | 1.815 | 1.848 | 1.881 | 1.914 | 1.947 | 1.98 | 2.013 | 2.046 | 2.079 | 2.112 | 2.145 | 2.178 | 2.211 | 2.244 | 2.277 | 2.31 | 2.431 | 2.5521 | 2.6731 | 2.7942 | 2.9153 | 3.0363 | 3.1573 | 3.2784 | 3.3994 | 3.5205 | 3.6416 | 3.7626 | 3.8836 | 4.0047 | 4.1258 | 4.2468 | 4.3679 | 4.4889 | 4.6099 | 4.731 | 4.8521 | 4.9731 | 5.0941 | 5.2152 | 5.3362 | 5.4573 | 5.5784 | 5.6994 | 5.8204 | 5.9415 | 6.0524 | 6.1633 | 6.2742 | 6.3851 | 6.496 | 6.6069 | 6.7178 | 6.8287 | 6.9396 | 7.0505 | 7.1614 | 7.2723 | 7.3832 | 7.4941 | 7.605 | 7.7159 | 7.8268 | 7.9377 | 8.0486 | 8.1595 | 8.2704 | 8.3813 | 8.4922 | 8.6031 | 8.714 | 8.8249 | 8.9358 | 9.0467 | 9.1576 | 9.2685 | 9.3574 | 9.4463 | 9.5352 | 9.6241 | 9.713 | 9.8019 | 9.8908 | 9.9797 | 10.0686 | 10.1575 | 10.2464 | 10.3353 | 10.4242 | 10.5131 | 10.602 | 10.6909 | 10.7798 | 10.8687 | 10.9576 | 11.0465 | 11.1354 | 11.2243 | 11.3132 | 11.4021 | 11.491 | 11.5799 | 11.6688 | 11.7577 | 11.8466 | 11.9355 | 11.9995 | 12.0635 | 12.1276 | 12.1916 | 12.2556 | 12.3196 | 12.3836 | 12.4476 | 12.5117 | 12.5757 | 12.6397 | 12.7037 | 12.7677 | 12.8317 | 12.8957 | 12.9598 | 13.0238 | 13.0878 | 13.1518 | 13.2158 | 13.2798 | 13.3439 | 13.4079 | 13.4719 | 13.5359 | 13.5999 | 13.6639 | 13.728 | 13.792 | 13.856
5.75 | 0 | 1.765 | 1.5588 | 1.49 | 1.3913 | 1.8425 | 2.345 | 6.0362 | 9.4138 | 12.1212 | 14.07 | 0 | 0.1765 | 0.353 | 0.5295 | 0.706 | 0.8825 | 1.059 | 1.2355 | 1.412 | 1.5885 | 1.765 | 1.7238 | 1.6825 | 1.6413 | 1.6 | 1.5588 | 1.545 | 1.5313 | 1.5175 | 1.5038 | 1.49 | 1.4801 | 1.4703 | 1.4604 | 1.4505 | 1.4406 | 1.4308 | 1.4209 | 1.411 | 1.4011 | 1.3913 | 1.4213 | 1.4514 | 1.4815 | 1.5116 | 1.5417 | 1.5718 | 1.6018 | 1.6319 | 1.662 | 1.6921 | 1.7222 | 1.7523 | 1.7823 | 1.8124 | 1.8425 | 1.876 | 1.9095 | 1.943 | 1.9765 | 2.01 | 2.0435 | 2.077 | 2.1105 | 2.144 | 2.1775 | 2.211 | 2.2445 | 2.278 | 2.3115 | 2.345 | 2.468 | 2.5911 | 2.7141 | 2.8372 | 2.9602 | 3.0832 | 3.2063 | 3.3293 | 3.4524 | 3.5754 | 3.6985 | 3.8215 | 3.9445 | 4.0676 | 4.1906 | 4.3137 | 4.4367 | 4.5597 | 4.6828 | 4.8058 | 4.9289 | 5.0519 | 5.175 | 5.298 | 5.421 | 5.5441 | 5.6671 | 5.7902 | 5.9132 | 6.0362 | 6.1488 | 6.2614 | 6.374 | 6.4866 | 6.5992 | 6.7118 | 6.8243 | 6.9369 | 7.0495 | 7.1621 | 7.2747 | 7.3872 | 7.4998 | 7.6124 | 7.725 | 7.8376 | 7.9502 | 8.0628 | 8.1753 | 8.2879 | 8.4005 | 8.5131 | 8.6257 | 8.7383 | 8.8508 | 8.9634 | 9.076 | 9.1886 | 9.3012 | 9.4138 | 9.504 | 9.5943 | 9.6845 | 9.7747 | 9.865 | 9.9552 | 10.0455 | 10.1357 | 10.226 | 10.3163 | 10.4065 | 10.4968 | 10.587 | 10.6772 | 10.7675 | 10.8577 | 10.948 | 11.0382 | 11.1285 | 11.2188 | 11.309 | 11.3993 | 11.4895 | 11.5797 | 11.67 | 11.7602 | 11.8505 | 11.9407 | 12.031 | 12.1212 | 12.1862 | 12.2512 | 12.3161 | 12.3811 | 12.446 | 12.511 | 12.576 | 12.6409 | 12.7059 | 12.7708 | 12.8358 | 12.9007 | 12.9657 | 13.0307 | 13.0956 | 13.1606 | 13.2255 | 13.2905 | 13.3555 | 13.4204 | 13.4854 | 13.5503 | 13.6153 | 13.6802 | 13.7452 | 13.8102 | 13.8751 | 13.9401 | 14.005 | 14.07
5.8 | 0 | 1.79 | 1.581 | 1.51 | 1.411 | 1.87 | 2.38 | 6.131 | 9.559 | 12.307 | 14.284 | -1.1102e-16 | 0.179 | 0.358 | 0.537 | 0.716 | 0.895 | 1.074 | 1.253 | 1.432 | 1.611 | 1.79 | 1.7482 | 1.7064 | 1.6646 | 1.6228 | 1.581 | 1.5668 | 1.5526 | 1.5384 | 1.5242 | 1.51 | 1.5001 | 1.4902 | 1.4803 | 1.4704 | 1.4605 | 1.4506 | 1.4407 | 1.4308 | 1.4209 | 1.411 | 1.4416 | 1.4722 | 1.5028 | 1.5334 | 1.564 | 1.5946 | 1.6252 | 1.6558 | 1.6864 | 1.717 | 1.7476 | 1.7782 | 1.8088 | 1.8394 | 1.87 | 1.904 | 1.938 | 1.972 | 2.006 | 2.04 | 2.074 | 2.108 | 2.142 | 2.176 | 2.21 | 2.244 | 2.278 | 2.312 | 2.346 | 2.38 | 2.505 | 2.6301 | 2.7551 | 2.8801 | 3.0052 | 3.1302 | 3.2552 | 3.3803 | 3.5053 | 3.6303 | 3.7554 | 3.8804 | 4.0054 | 4.1305 | 4.2555 | 4.3805 | 4.5056 | 4.6306 | 4.7556 | 4.8807 | 5.0057 | 5.1307 | 5.2558 | 5.3808 | 5.5058 | 5.6309 | 5.7559 | 5.8809 | 6.006 | 6.131 | 6.2453 | 6.3595 | 6.4738 | 6.5881 | 6.7023 | 6.8166 | 6.9309 | 7.0451 | 7.1594 | 7.2737 | 7.3879 | 7.5022 | 7.6165 | 7.7307 | 7.845 | 7.9593 | 8.0735 | 8.1878 | 8.3021 | 8.4163 | 8.5306 | 8.6449 | 8.7591 | 8.8734 | 8.9877 | 9.1019 | 9.2162 | 9.3305 | 9.4447 | 9.559 | 9.6506 | 9.7422 | 9.8338 | 9.9254 | 10.017 | 10.1086 | 10.2002 | 10.2918 | 10.3834 | 10.475 | 10.5666 | 10.6582 | 10.7498 | 10.8414 | 10.933 | 11.0246 | 11.1162 | 11.2078 | 11.2994 | 11.391 | 11.4826 | 11.5742 | 11.6658 | 11.7574 | 11.849 | 11.9406 | 12.0322 | 12.1238 | 12.2154 | 12.307 | 12.3729 | 12.4388 | 12.5047 | 12.5706 | 12.6365 | 12.7024 | 12.7683 | 12.8342 | 12.9001 | 12.966 | 13.0319 | 13.0978 | 13.1637 | 13.2296 | 13.2955 | 13.3614 | 13.4273 | 13.4932 | 13.5591 | 13.625 | 13.6909 | 13.7568 | 13.8227 | 13.8886 | 13.9545 | 14.0204 | 14.0863 | 14.1522 | 14.2181 | 14.284
5.85 | 0 | 1.815 | 1.6033 | 1.53 | 1.4307 | 1.8975 | 2.415 | 6.2257 | 9.7042 | 12.4927 | 14.498 | -1.1102e-16 | 0.1815 | 0.363 | 0.5445 | 0.726 | 0.9075 | 1.089 | 1.2705 | 1.452 | 1.6335 | 1.815 | 1.7726 | 1.7303 | 1.6879 | 1.6456 | 1.6033 | 1.5886 | 1.5739 | 1.5593 | 1.5446 | 1.53 | 1.5201 | 1.5101 | 1.5002 | 1.4903 | 1.4804 | 1.4704 | 1.4605 | 1.4506 | 1.4407 | 1.4307 | 1.4619 | 1.493 | 1.5241 | 1.5552 | 1.5863 | 1.6175 | 1.6486 | 1.6797 | 1.7108 | 1.7419 | 1.773 | 1.8042 | 1.8353 | 1.8664 | 1.8975 | 1.932 | 1.9665 | 2.001 | 2.0355 | 2.07 | 2.1045 | 2.139 | 2.1735 | 2.208 | 2.2425 | 2.277 | 2.3115 | 2.346 | 2.3805 | 2.415 | 2.542 | 2.6691 | 2.7961 | 2.9231 | 3.0501 | 3.1771 | 3.3042 | 3.4312 | 3.5582 | 3.6852 | 3.8123 | 3.9393 | 4.0663 | 4.1933 | 4.3204 | 4.4474 | 4.5744 | 4.7014 | 4.8285 | 4.9555 | 5.0825 | 5.2095 | 5.3366 | 5.4636 | 5.5906 | 5.7176 | 5.8447 | 5.9717 | 6.0987 | 6.2257 | 6.3417 | 6.4576 | 6.5736 | 6.6895 | 6.8055 | 6.9214 | 7.0374 | 7.1533 | 7.2693 | 7.3852 | 7.5012 | 7.6171 | 7.7331 | 7.849 | 7.965 | 8.0809 | 8.1969 | 8.3128 | 8.4288 | 8.5447 | 8.6607 | 8.7766 | 8.8926 | 9.0085 | 9.1245 | 9.2404 | 9.3564 | 9.4723 | 9.5883 | 9.7042 | 9.7972 | 9.8901 | 9.9831 | 10.076 | 10.169 | 10.2619 | 10.3549 | 10.4478 | 10.5408 | 10.6337 | 10.7267 | 10.8196 | 10.9126 | 11.0055 | 11.0985 | 11.1914 | 11.2844 | 11.3773 | 11.4703 | 11.5632 | 11.6562 | 11.7491 | 11.8421 | 11.935 | 12.028 | 12.1209 | 12.2139 | 12.3068 | 12.3998 | 12.4927 | 12.5596 | 12.6264 | 12.6933 | 12.7601 | 12.827 | 12.8938 | 12.9606 | 13.0275 | 13.0943 | 13.1612 | 13.228 | 13.2948 | 13.3617 | 13.4285 | 13.4954 | 13.5622 | 13.6291 | 13.6959 | 13.7627 | 13.8296 | 13.8964 | 13.9633 | 14.0301 | 14.0969 | 14.1638 | 14.2306 | 14.2975 | 14.3643 | 14.4312 | 14.498
5.9 | 0 | 1.84 | 1.6255 | 1.55 | 1.4505 | 1.925 | 2.45 | 6.3205 | 9.8495 | 12.6785 | 14.712 | -1.1102e-16 | 0.184 | 0.368 | 0.552 | 0.736 | 0.92 | 1.104 | 1.288 | 1.472 | 1.656 | 1.84 | 1.7971 | 1.7542 | 1.7113 | 1.6684 | 1.6255 | 1.6104 | 1.5953 | 1.5802 | 1.5651 | 1.55 | 1.5401 | 1.5301 | 1.5202 | 1.5102 | 1.5003 | 1.4903 | 1.4804 | 1.4704 | 1.4605 | 1.4505 | 1.4821 | 1.5138 | 1.5454 | 1.577 | 1.6087 | 1.6403 | 1.6719 | 1.7036 | 1.7352 | 1.7668 | 1.7985 | 1.8301 | 1.8617 | 1.8934 | 1.925 | 1.96 | 1.995 | 2.03 | 2.065 | 2.1 | 2.135 | 2.17 | 2.205 | 2.24 | 2.275 | 2.31 | 2.345 | 2.38 | 2.415 | 2.45 | 2.579 | 2.708 | 2.8371 | 2.9661 | 3.0951 | 3.2241 | 3.3531 | 3.4821 | 3.6112 | 3.7402 | 3.8692 | 3.9982 | 4.1272 | 4.2562 | 4.3853 | 4.5143 | 4.6433 | 4.7723 | 4.9013 | 5.0303 | 5.1594 | 5.2884 | 5.4174 | 5.5464 | 5.6754 | 5.8044 | 5.9335 | 6.0625 | 6.1915 | 6.3205 | 6.4381 | 6.5558 | 6.6734 | 6.791 | 6.9087 | 7.0263 | 7.1439 | 7.2616 | 7.3792 | 7.4968 | 7.6145 | 7.7321 | 7.8497 | 7.9674 | 8.085 | 8.2026 | 8.3203 | 8.4379 | 8.5555 | 8.6732 | 8.7908 | 8.9084 | 9.0261 | 9.1437 | 9.2613 | 9.379 | 9.4966 | 9.6142 | 9.7319 | 9.8495 | 9.9438 | 10.0381 | 10.1324 | 10.2267 | 10.321 | 10.4153 | 10.5096 | 10.6039 | 10.6982 | 10.7925 | 10.8868 | 10.9811 | 11.0754 | 11.1697 | 11.264 | 11.3583 | 11.4526 | 11.5469 | 11.6412 | 11.7355 | 11.8298 | 11.9241 | 12.0184 | 12.1127 | 12.207 | 12.3013 | 12.3956 | 12.4899 | 12.5842 | 12.6785 | 12.7463 | 12.8141 | 12.8819 | 12.9496 | 13.0174 | 13.0852 | 13.153 | 13.2208 | 13.2885 | 13.3563 | 13.4241 | 13.4919 | 13.5597 | 13.6275 | 13.6952 | 13.763 | 13.8308 | 13.8986 | 13.9664 | 14.0342 | 14.1019 | 14.1697 | 14.2375 | 14.3053 | 14.3731 | 14.4409 | 14.5086 | 14.5764 | 14.6442 | 14.712
5.95 | 0 | 1.865 | 1.6478 | 1.57 | 1.4703 | 1.9525 | 2.485 | 6.4153 | 9.9947 | 12.8643 | 14.926 | 0 | 0.1865 | 0.373 | 0.5595 | 0.746 | 0.9325 | 1.119 | 1.3055 | 1.492 | 1.6785 | 1.865 | 1.8216 | 1.7781 | 1.7347 | 1.6912 | 1.6478 | 1.6322 | 1.6167 | 1.6011 | 1.5856 | 1.57 | 1.56 | 1.5501 | 1.5401 | 1.5301 | 1.5201 | 1.5102 | 1.5002 | 1.4902 | 1.4802 | 1.4703 | 1.5024 | 1.5346 | 1.5667 | 1.5989 | 1.631 | 1.6632 | 1.6953 | 1.7275 | 1.7596 | 1.7918 | 1.8239 | 1.8561 | 1.8882 | 1.9204 | 1.9525 | 1.988 | 2.0235 | 2.059 | 2.0945 | 2.13 | 2.1655 | 2.201 | 2.2365 | 2.272 | 2.3075 | 2.343 | 2.3785 | 2.414 | 2.4495 | 2.485 | 2.616 | 2.747 | 2.878 | 3.009 | 3.14 | 3.271 | 3.4021 | 3.5331 | 3.6641 | 3.7951 | 3.9261 | 4.0571 | 4.1881 | 4.3191 | 4.4501 | 4.5811 | 4.7121 | 4.8431 | 4.9742 | 5.1052 | 5.2362 | 5.3672 | 5.4982 | 5.6292 | 5.7602 | 5.8912 | 6.0222 | 6.1532 | 6.2842 | 6.4153 | 6.5346 | 6.6539 | 6.7732 | 6.8925 | 7.0118 | 7.1312 | 7.2505 | 7.3698 | 7.4891 | 7.6084 | 7.7277 | 7.8471 | 7.9664 | 8.0857 | 8.205 | 8.3243 | 8.4436 | 8.563 | 8.6823 | 8.8016 | 8.9209 | 9.0402 | 9.1595 | 9.2789 | 9.3982 | 9.5175 | 9.6368 | 9.7561 | 9.8754 | 9.9947 | 10.0904 | 10.186 | 10.2817 | 10.3773 | 10.473 | 10.5686 | 10.6643 | 10.7599 | 10.8556 | 10.9512 | 11.0469 | 11.1425 | 11.2382 | 11.3338 | 11.4295 | 11.5252 | 11.6208 | 11.7165 | 11.8121 | 11.9078 | 12.0034 | 12.0991 | 12.1947 | 12.2904 | 12.386 | 12.4817 | 12.5773 | 12.673 | 12.7686 | 12.8643 | 12.933 | 13.0017 | 13.0704 | 13.1392 | 13.2079 | 13.2766 | 13.3453 | 13.4141 | 13.4828 | 13.5515 | 13.6202 | 13.689 | 13.7577 | 13.8264 | 13.8951 | 13.9639 | 14.0326 | 14.1013 | 14.17 | 14.2387 | 14.3075 | 14.3762 | 14.4449 | 14.5137 | 14.5824 | 14.6511 | 14.7198 | 14.7885 | 14.8573 | 14.926
6 | 0 | 1.89 | 1.67 | 1.59 | 1.49 | 1.98 | 2.52 | 6.51 | 10.14 | 13.05 | 15.14 | -1.1102e-16 | 0.189 | 0.378 | 0.567 | 0.756 | 0.945 | 1.134 | 1.323 | 1.512 | 1.701 | 1.89 | 1.846 | 1.802 | 1.758 | 1.714 | 1.67 | 1.654 | 1.638 | 1.622 | 1.606 | 1.59 | 1.58 | 1.57 | 1.56 | 1.55 | 1.54 | 1.53 | 1.52 | 1.51 | 1.5 | 1.49 | 1.5227 | 1.5553 | 1.588 | 1.6207 | 1.6533 | 1.686 | 1.7187 | 1.7513 | 1.784 | 1.8167 | 1.8493 | 1.882 | 1.9147 | 1.9473 | 1.98 | 2.016 | 2.052 | 2.088 | 2.124 | 2.16 | 2.196 | 2.232 | 2.268 | 2.304 | 2.34 | 2.376 | 2.412 | 2.448 | 2.484 | 2.52 | 2.653 | 2.786 | 2.919 | 3.052 | 3.185 | 3.318 | 3.451 | 3.584 | 3.717 | 3.85 | 3.983 | 4.116 | 4.249 | 4.382 | 4.515 | 4.648 | 4.781 | 4.914 | 5.047 | 5.18 | 5.313 | 5.446 | 5.579 | 5.712 | 5.845 | 5.978 | 6.111 | 6.244 | 6.377 | 6.51 | 6.631 | 6.752 | 6.873 | 6.994 | 7.115 | 7.236 | 7.357 | 7.478 | 7.599 | 7.72 | 7.841 | 7.962 | 8.083 | 8.204 | 8.325 | 8.446 | 8.567 | 8.688 | 8.809 | 8.93 | 9.051 | 9.172 | 9.293 | 9.414 | 9.535 | 9.656 | 9.777 | 9.898 | 10.019 | 10.14 | 10.237 | 10.334 | 10.431 | 10.528 | 10.625 | 10.722 | 10.819 | 10.916 | 11.013 | 11.11 | 11.207 | 11.304 | 11.401 | 11.498 | 11.595 | 11.692 | 11.789 | 11.886 | 11.983 | 12.08 | 12.177 | 12.274 | 12.371 | 12.468 | 12.565 | 12.662 | 12.759 | 12.856 | 12.953 | 13.05 | 13.1197 | 13.1893 | 13.259 | 13.3287 | 13.3983 | 13.468 | 13.5377 | 13.6073 | 13.677 | 13.7467 | 13.8163 | 13.886 | 13.9557 | 14.0253 | 14.095 | 14.1647 | 14.2343 | 14.304 | 14.3737 | 14.4433 | 14.513 | 14.5827 | 14.6523 | 14.722 | 14.7917 | 14.8613 | 14.931 | 15.0007 | 15.0703 | 15.14
6.05 | 0 | 1.93 | 1.7156 | 1.6345 | 1.5345 | 2.0365 | 2.5891 | 6.6669 | 10.3766 | 13.3504 | 15.4889 | -1.1102e-16 | 0.193 | 0.386 | 0.579 | 0.772 | 0.965 | 1.158 | 1.351 | 1.544 | 1.737 | 1.93 | 1.8871 | 1.8442 | 1.8014 | 1.7585 | 1.7156 | 1.6994 | 1.6832 | 1.667 | 1.6507 | 1.6345 | 1.6245 | 1.6145 | 1.6045 | 1.5945 | 1.5845 | 1.5745 | 1.5645 | 1.5545 | 1.5445 | 1.5345 | 1.568 | 1.6014 | 1.6349 | 1.6684 | 1.7018 | 1.7353 | 1.7688 | 1.8022 | 1.8357 | 1.8692 | 1.9026 | 1.9361 | 1.9696 | 2.003 | 2.0365 | 2.0733 | 2.1102 | 2.147 | 2.1839 | 2.2207 | 2.2576 | 2.2944 | 2.3312 | 2.3681 | 2.4049 | 2.4418 | 2.4786 | 2.5154 | 2.5523 | 2.5891 | 2.725 | 2.861 | 2.9969 | 3.1328 | 3.2688 | 3.4047 | 3.5406 | 3.6765 | 3.8125 | 3.9484 | 4.0843 | 4.2202 | 4.3562 | 4.4921 | 4.628 | 4.7639 | 4.8999 | 5.0358 | 5.1717 | 5.3076 | 5.4436 | 5.5795 | 5.7154 | 5.8513 | 5.9873 | 6.1232 | 6.2591 | 6.395 | 6.531 | 6.6669 | 6.7905 | 6.9142 | 7.0379 | 7.1615 | 7.2852 | 7.4088 | 7.5325 | 7.6561 | 7.7798 | 7.9035 | 8.0271 | 8.1508 | 8.2744 | 8.3981 | 8.5218 | 8.6454 | 8.7691 | 8.8927 | 9.0164 | 9.14 | 9.2637 | 9.3874 | 9.511 | 9.6347 | 9.7583 | 9.882 | 10.0057 | 10.1293 | 10.253 | 10.3766 | 10.4757 | 10.5749 | 10.674 | 10.7731 | 10.8722 | 10.9714 | 11.0705 | 11.1696 | 11.2688 | 11.3679 | 11.467 | 11.5661 | 11.6653 | 11.7644 | 11.8635 | 11.9626 | 12.0617 | 12.1609 | 12.26 | 12.3591 | 12.4582 | 12.5574 | 12.6565 | 12.7556 | 12.8547 | 12.9539 | 13.053 | 13.1521 | 13.2512 | 13.3504 | 13.4217 | 13.4929 | 13.5642 | 13.6355 | 13.7068 | 13.7781 | 13.8494 | 13.9206 | 13.9919 | 14.0632 | 14.1345 | 14.2058 | 14.2771 | 14.3483 | 14.4196 | 14.4909 | 14.5622 | 14.6335 | 14.7048 | 14.776 | 14.8473 | 14.9186 | 14.9899 | 15.0612 | 15.1325 | 15.2037 | 15.275 | 15.3463 | 15.4176 | 15.4889
6.1 | 0 | 1.97 | 1.7612 | 1.679 | 1.579 | 2.093 | 2.6582 | 6.8238 | 10.6132 | 13.6507 | 15.8377 | 0 | 0.197 | 0.394 | 0.591 | 0.788 | 0.985 | 1.182 | 1.379 | 1.576 | 1.773 | 1.97 | 1.9282 | 1.8865 | 1.8447 | 1.803 | 1.7612 | 1.7448 | 1.7283 | 1.7119 | 1.6954 | 1.679 | 1.669 | 1.659 | 1.649 | 1.639 | 1.629 | 1.619 | 1.609 | 1.599 | 1.589 | 1.579 | 1.6133 | 1.6475 | 1.6818 | 1.7161 | 1.7503 | 1.7846 | 1.8189 | 1.8531 | 1.8874 | 1.9217 | 1.9559 | 1.9902 | 2.0245 | 2.0587 | 2.093 | 2.1307 | 2.1684 | 2.206 | 2.2437 | 2.2814 | 2.3191 | 2.3568 | 2.3945 | 2.4321 | 2.4698 | 2.5075 | 2.5452 | 2.5829 | 2.6206 | 2.6582 | 2.7971 | 2.936 | 3.0748 | 3.2136 | 3.3525 | 3.4913 | 3.6302 | 3.7691 | 3.9079 | 4.0467 | 4.1856 | 4.3245 | 4.4633 | 4.6021 | 4.741 | 4.8798 | 5.0187 | 5.1576 | 5.2964 | 5.4352 | 5.5741 | 5.713 | 5.8518 | 5.9907 | 6.1295 | 6.2683 | 6.4072 | 6.5461 | 6.6849 | 6.8238 | 6.9501 | 7.0764 | 7.2027 | 7.329 | 7.4553 | 7.5817 | 7.708 | 7.8343 | 7.9606 | 8.0869 | 8.2132 | 8.3395 | 8.4659 | 8.5922 | 8.7185 | 8.8448 | 8.9711 | 9.0974 | 9.2238 | 9.3501 | 9.4764 | 9.6027 | 9.729 | 9.8553 | 9.9817 | 10.108 | 10.2343 | 10.3606 | 10.4869 | 10.6132 | 10.7145 | 10.8157 | 10.917 | 11.0182 | 11.1195 | 11.2207 | 11.322 | 11.4232 | 11.5245 | 11.6257 | 11.727 | 11.8282 | 11.9295 | 12.0307 | 12.132 | 12.2332 | 12.3345 | 12.4357 | 12.537 | 12.6382 | 12.7395 | 12.8407 | 12.942 | 13.0432 | 13.1445 | 13.2457 | 13.347 | 13.4482 | 13.5495 | 13.6507 | 13.7236 | 13.7965 | 13.8694 | 13.9423 | 14.0152 | 14.0881 | 14.161 | 14.2339 | 14.3068 | 14.3797 | 14.4526 | 14.5255 | 14.5984 | 14.6713 | 14.7442 | 14.8171 | 14.89 | 14.9629 | 15.0358 | 15.1087 | 15.1816 | 15.2545 | 15.3274 | 15.4003 | 15.4733 | 15.5461 | 15.619 | 15.692 | 15.7648 | 15.8377
6.15 | 0 | 2.01 | 1.8069 | 1.7235 | 1.6235 | 2.1495 | 2.7274 | 6.9806 | 10.8499 | 13.9511 | 16.1866 | 0 | 0.201 | 0.402 | 0.603 | 0.804 | 1.005 | 1.206 | 1.407 | 1.608 | 1.809 | 2.01 | 1.9694 | 1.9288 | 1.8881 | 1.8475 | 1.8069 | 1.7902 | 1.7735 | 1.7569 | 1.7402 | 1.7235 | 1.7135 | 1.7035 | 1.6935 | 1.6835 | 1.6735 | 1.6635 | 1.6535 | 1.6435 | 1.6335 | 1.6235 | 1.6586 | 1.6936 | 1.7287 | 1.7638 | 1.7988 | 1.8339 | 1.869 | 1.904 | 1.9391 | 1.9742 | 2.0092 | 2.0443 | 2.0794 | 2.1144 | 2.1495 | 2.188 | 2.2266 | 2.2651 | 2.3036 | 2.3421 | 2.3807 | 2.4192 | 2.4577 | 2.4962 | 2.5348 | 2.5733 | 2.6118 | 2.6503 | 2.6889 | 2.7274 | 2.8692 | 3.0109 | 3.1527 | 3.2945 | 3.4363 | 3.578 | 3.7198 | 3.8616 | 4.0034 | 4.1451 | 4.2869 | 4.4287 | 4.5705 | 4.7122 | 4.854 | 4.9958 | 5.1376 | 5.2793 | 5.4211 | 5.5629 | 5.7047 | 5.8464 | 5.9882 | 6.13 | 6.2718 | 6.4135 | 6.5553 | 6.6971 | 6.8389 | 6.9806 | 7.1096 | 7.2386 | 7.3676 | 7.4965 | 7.6255 | 7.7545 | 7.8835 | 8.0124 | 8.1414 | 8.2704 | 8.3994 | 8.5283 | 8.6573 | 8.7863 | 8.9153 | 9.0442 | 9.1732 | 9.3022 | 9.4312 | 9.5601 | 9.6891 | 9.8181 | 9.9471 | 10.076 | 10.205 | 10.334 | 10.463 | 10.5919 | 10.7209 | 10.8499 | 10.9533 | 11.0566 | 11.16 | 11.2634 | 11.3668 | 11.4701 | 11.5735 | 11.6769 | 11.7803 | 11.8836 | 11.987 | 12.0904 | 12.1937 | 12.2971 | 12.4005 | 12.5039 | 12.6073 | 12.7106 | 12.814 | 12.9174 | 13.0207 | 13.1241 | 13.2275 | 13.3309 | 13.4342 | 13.5376 | 13.641 | 13.7444 | 13.8477 | 13.9511 | 14.0256 | 14.1002 | 14.1747 | 14.2492 | 14.3237 | 14.3982 | 14.4727 | 14.5473 | 14.6218 | 14.6963 | 14.7708 | 14.8453 | 14.9198 | 14.9944 | 15.0689 | 15.1434 | 15.2179 | 15.2924 | 15.3669 | 15.4415 | 15.516 | 15.5905 | 15.665 | 15.7395 | 15.814 | 15.8886 | 15.9631 | 16.0376 | 16.1121 | 16.1866
6.2 | 0 | 2.05 | 1.8525 | 1.768 | 1.668 | 2.206 | 2.7965 | 7.1375 | 11.0865 | 14.2515 | 16.5355 | 0 | 0.205 | 0.41 | 0.615 | 0.82 | 1.025 | 1.23 | 1.435 | 1.64 | 1.845 | 2.05 | 2.0105 | 1.971 | 1.9315 | 1.892 | 1.8525 | 1.8356 | 1.8187 | 1.8018 | 1.7849 | 1.768 | 1.758 | 1.748 | 1.738 | 1.728 | 1.718 | 1.708 | 1.698 | 1.688 | 1.678 | 1.668 | 1.7039 | 1.7397 | 1.7756 | 1.8115 | 1.8473 | 1.8832 | 1.9191 | 1.9549 | 1.9908 | 2.0267 | 2.0625 | 2.0984 | 2.1343 | 2.1701 | 2.206 | 2.2454 | 2.2847 | 2.3241 | 2.3635 | 2.4028 | 2.4422 | 2.4816 | 2.5209 | 2.5603 | 2.5997 | 2.639 | 2.6784 | 2.7178 | 2.7571 | 2.7965 | 2.9412 | 3.0859 | 3.2306 | 3.3753 | 3.52 | 3.6647 | 3.8094 | 3.9541 | 4.0988 | 4.2435 | 4.3882 | 4.5329 | 4.6776 | 4.8223 | 4.967 | 5.1117 | 5.2564 | 5.4011 | 5.5458 | 5.6905 | 5.8352 | 5.9799 | 6.1246 | 6.2693 | 6.414 | 6.5587 | 6.7034 | 6.8481 | 6.9928 | 7.1375 | 7.2691 | 7.4008 | 7.5324 | 7.664 | 7.7957 | 7.9273 | 8.0589 | 8.1906 | 8.3222 | 8.4538 | 8.5855 | 8.7171 | 8.8487 | 8.9804 | 9.112 | 9.2436 | 9.3753 | 9.5069 | 9.6385 | 9.7702 | 9.9018 | 10.0334 | 10.1651 | 10.2967 | 10.4283 | 10.56 | 10.6916 | 10.8232 | 10.9549 | 11.0865 | 11.192 | 11.2975 | 11.403 | 11.5085 | 11.614 | 11.7195 | 11.825 | 11.9305 | 12.036 | 12.1415 | 12.247 | 12.3525 | 12.458 | 12.5635 | 12.669 | 12.7745 | 12.88 | 12.9855 | 13.091 | 13.1965 | 13.302 | 13.4075 | 13.513 | 13.6185 | 13.724 | 13.8295 | 13.935 | 14.0405 | 14.146 | 14.2515 | 14.3276 | 14.4038 | 14.4799 | 14.556 | 14.6322 | 14.7083 | 14.7844 | 14.8606 | 14.9367 | 15.0128 | 15.089 | 15.1651 | 15.2412 | 15.3174 | 15.3935 | 15.4696 | 15.5458 | 15.6219 | 15.698 | 15.7742 | 15.8503 | 15.9264 | 16.0026 | 16.0787 | 16.1548 | 16.231 | 16.3071 | 16.3832 | 16.4594 | 16.5355
6.25 | 0 | 2.09 | 1.8981 | 1.8125 | 1.7125 | 2.2625 | 2.8656 | 7.2944 | 11.3231 | 14.5519 | 16.8844 | -2.2204e-16 | 0.209 | 0.418 | 0.627 | 0.836 | 1.045 | 1.254 | 1.463 | 1.672 | 1.881 | 2.09 | 2.0516 | 2.0132 | 1.9749 | 1.9365 | 1.8981 | 1.881 | 1.8639 | 1.8468 | 1.8296 | 1.8125 | 1.8025 | 1.7925 | 1.7825 | 1.7725 | 1.7625 | 1.7525 | 1.7425 | 1.7325 | 1.7225 | 1.7125 | 1.7492 | 1.7858 | 1.8225 | 1.8592 | 1.8958 | 1.9325 | 1.9692 | 2.0058 | 2.0425 | 2.0792 | 2.1158 | 2.1525 | 2.1892 | 2.2258 | 2.2625 | 2.3027 | 2.3429 | 2.3831 | 2.4233 | 2.4635 | 2.5037 | 2.544 | 2.5842 | 2.6244 | 2.6646 | 2.7048 | 2.745 | 2.7852 | 2.8254 | 2.8656 | 3.0132 | 3.1609 | 3.3085 | 3.4561 | 3.6037 | 3.7514 | 3.899 | 4.0466 | 4.1942 | 4.3419 | 4.4895 | 4.6371 | 4.7847 | 4.9324 | 5.08 | 5.2276 | 5.3753 | 5.5229 | 5.6705 | 5.8181 | 5.9658 | 6.1134 | 6.261 | 6.4086 | 6.5563 | 6.7039 | 6.8515 | 6.9991 | 7.1468 | 7.2944 | 7.4287 | 7.563 | 7.6973 | 7.8315 | 7.9658 | 8.1001 | 8.2344 | 8.3687 | 8.503 | 8.6373 | 8.7716 | 8.9059 | 9.0402 | 9.1745 | 9.3088 | 9.443 | 9.5773 | 9.7116 | 9.8459 | 9.9802 | 10.1145 | 10.2488 | 10.3831 | 10.5174 | 10.6517 | 10.786 | 10.9203 | 11.0545 | 11.1888 | 11.3231 | 11.4308 | 11.5384 | 11.646 | 11.7536 | 11.8613 | 11.9689 | 12.0765 | 12.1841 | 12.2918 | 12.3994 | 12.507 | 12.6146 | 12.7222 | 12.8299 | 12.9375 | 13.0451 | 13.1527 | 13.2604 | 13.368 | 13.4756 | 13.5832 | 13.6909 | 13.7985 | 13.9061 | 14.0137 | 14.1214 | 14.229 | 14.3366 | 14.4442 | 14.5519 | 14.6296 | 14.7074 | 14.7851 | 14.8629 | 14.9406 | 15.0184 | 15.0961 | 15.1739 | 15.2516 | 15.3294 | 15.4071 | 15.4849 | 15.5626 | 15.6404 | 15.7181 | 15.7959 | 15.8736 | 15.9514 | 16.0291 | 16.1069 | 16.1846 | 16.2624 | 16.3401 | 16.4179 | 16.4956 | 16.5734 | 16.6511 | 16.7289 | 16.8066 | 16.8844
6.3 | 0 | 2.13 | 1.9437 | 1.857 | 1.757 | 2.319 | 2.9347 | 7.4513 | 11.5598 | 14.8522 | 17.2332 | 0 | 0.213 | 0.426 | 0.639 | 0.852 | 1.065 | 1.278 | 1.491 | 1.704 | 1.917 | 2.13 | 2.0927 | 2.0555 | 2.0182 | 1.981 | 1.9437 | 1.9264 | 1.909 | 1.8917 | 1.8743 | 1.857 | 1.847 | 1.837 | 1.827 | 1.817 | 1.807 | 1.797 | 1.787 | 1.777 | 1.767 | 1.757 | 1.7945 | 1.8319 | 1.8694 | 1.9069 | 1.9443 | 1.9818 | 2.0193 | 2.0567 | 2.0942 | 2.1317 | 2.1691 | 2.2066 | 2.2441 | 2.2815 | 2.319 | 2.36 | 2.4011 | 2.4421 | 2.4832 | 2.5242 | 2.5653 | 2.6063 | 2.6474 | 2.6884 | 2.7295 | 2.7705 | 2.8116 | 2.8526 | 2.8937 | 2.9348 | 3.0853 | 3.2359 | 3.3864 | 3.537 | 3.6875 | 3.838 | 3.9886 | 4.1391 | 4.2897 | 4.4402 | 4.5908 | 4.7413 | 4.8919 | 5.0425 | 5.193 | 5.3436 | 5.4941 | 5.6447 | 5.7952 | 5.9458 | 6.0963 | 6.2469 | 6.3974 | 6.548 | 6.6985 | 6.8491 | 6.9996 | 7.1502 | 7.3007 | 7.4512 | 7.5882 | 7.7252 | 7.8621 | 7.9991 | 8.136 | 8.2729 | 8.4099 | 8.5469 | 8.6838 | 8.8208 | 8.9577 | 9.0947 | 9.2316 | 9.3686 | 9.5055 | 9.6425 | 9.7794 | 9.9164 | 10.0533 | 10.1903 | 10.3272 | 10.4642 | 10.6011 | 10.7381 | 10.875 | 11.012 | 11.1489 | 11.2859 | 11.4228 | 11.5598 | 11.6695 | 11.7792 | 11.889 | 11.9987 | 12.1085 | 12.2182 | 12.328 | 12.4377 | 12.5475 | 12.6572 | 12.767 | 12.8767 | 12.9865 | 13.0962 | 13.206 | 13.3157 | 13.4255 | 13.5352 | 13.645 | 13.7547 | 13.8645 | 13.9742 | 14.084 | 14.1937 | 14.3035 | 14.4132 | 14.523 | 14.6327 | 14.7425 | 14.8522 | 14.9316 | 15.011 | 15.0903 | 15.1697 | 15.2491 | 15.3284 | 15.4078 | 15.4872 | 15.5665 | 15.6459 | 15.7253 | 15.8046 | 15.884 | 15.9634 | 16.0427 | 16.1221 | 16.2015 | 16.2809 | 16.3602 | 16.4396 | 16.5189 | 16.5983 | 16.6777 | 16.757 | 16.8364 | 16.9158 | 16.9951 | 17.0745 | 17.1539 | 17.2332
6.35 | 0 | 2.17 | 1.9894 | 1.9015 | 1.8015 | 2.3755 | 3.0039 | 7.6081 | 11.7964 | 15.1526 | 17.5821 | -2.2204e-16 | 0.217 | 0.434 | 0.651 | 0.868 | 1.085 | 1.302 | 1.519 | 1.736 | 1.953 | 2.17 | 2.1339 | 2.0977 | 2.0616 | 2.0255 | 1.9894 | 1.9718 | 1.9542 | 1.9366 | 1.9191 | 1.9015 | 1.8915 | 1.8815 | 1.8715 | 1.8615 | 1.8515 | 1.8415 | 1.8315 | 1.8215 | 1.8115 | 1.8015 | 1.8398 | 1.878 | 1.9163 | 1.9546 | 1.9928 | 2.0311 | 2.0694 | 2.1076 | 2.1459 | 2.1842 | 2.2224 | 2.2607 | 2.299 | 2.3372 | 2.3755 | 2.4174 | 2.4593 | 2.5012 | 2.5431 | 2.585 | 2.6268 | 2.6687 | 2.7106 | 2.7525 | 2.7944 | 2.8363 | 2.8782 | 2.9201 | 2.962 | 3.0039 | 3.1573 | 3.3108 | 3.4643 | 3.6178 | 3.7712 | 3.9247 | 4.0782 | 4.2317 | 4.3851 | 4.5386 | 4.6921 | 4.8456 | 4.999 | 5.1525 | 5.306 | 5.4595 | 5.613 | 5.7664 | 5.9199 | 6.0734 | 6.2268 | 6.3803 | 6.5338 | 6.6873 | 6.8408 | 6.9942 | 7.1477 | 7.3012 | 7.4546 | 7.6081 | 7.7477 | 7.8873 | 8.027 | 8.1666 | 8.3062 | 8.4458 | 8.5854 | 8.725 | 8.8646 | 9.0042 | 9.1438 | 9.2834 | 9.423 | 9.5626 | 9.7022 | 9.8419 | 9.9815 | 10.1211 | 10.2607 | 10.4003 | 10.5399 | 10.6795 | 10.8191 | 10.9587 | 11.0983 | 11.2379 | 11.3775 | 11.5172 | 11.6568 | 11.7964 | 11.9082 | 12.0201 | 12.132 | 12.2439 | 12.3557 | 12.4676 | 12.5795 | 12.6914 | 12.8032 | 12.9151 | 13.027 | 13.1389 | 13.2507 | 13.3626 | 13.4745 | 13.5864 | 13.6982 | 13.8101 | 13.922 | 14.0339 | 14.1457 | 14.2576 | 14.3695 | 14.4814 | 14.5932 | 14.7051 | 14.817 | 14.9289 | 15.0407 | 15.1526 | 15.2336 | 15.3146 | 15.3956 | 15.4766 | 15.5575 | 15.6385 | 15.7195 | 15.8005 | 15.8815 | 15.9625 | 16.0434 | 16.1244 | 16.2054 | 16.2864 | 16.3674 | 16.4484 | 16.5293 | 16.6103 | 16.6913 | 16.7723 | 16.8533 | 16.9343 | 17.0152 | 17.0962 | 17.1772 | 17.2582 | 17.3392 | 17.4202 | 17.5011 | 17.5821
6.4 | 0 | 2.21 | 2.035 | 1.946 | 1.846 | 2.432 | 3.073 | 7.765 | 12.033 | 15.453 | 17.931 | 0 | 0.221 | 0.442 | 0.663 | 0.884 | 1.105 | 1.326 | 1.547 | 1.768 | 1.989 | 2.21 | 2.175 | 2.14 | 2.105 | 2.07 | 2.035 | 2.0172 | 1.9994 | 1.9816 | 1.9638 | 1.946 | 1.936 | 1.926 | 1.916 | 1.906 | 1.896 | 1.886 | 1.876 | 1.866 | 1.856 | 1.846 | 1.8851 | 1.9241 | 1.9632 | 2.0023 | 2.0413 | 2.0804 | 2.1195 | 2.1585 | 2.1976 | 2.2367 | 2.2757 | 2.3148 | 2.3539 | 2.3929 | 2.432 | 2.4747 | 2.5175 | 2.5602 | 2.6029 | 2.6457 | 2.6884 | 2.7311 | 2.7739 | 2.8166 | 2.8593 | 2.9021 | 2.9448 | 2.9875 | 3.0303 | 3.073 | 3.2294 | 3.3858 | 3.5422 | 3.6986 | 3.855 | 4.0114 | 4.1678 | 4.3242 | 4.4806 | 4.637 | 4.7934 | 4.9498 | 5.1062 | 5.2626 | 5.419 | 5.5754 | 5.7318 | 5.8882 | 6.0446 | 6.201 | 6.3574 | 6.5138 | 6.6702 | 6.8266 | 6.983 | 7.1394 | 7.2958 | 7.4522 | 7.6086 | 7.765 | 7.9073 | 8.0495 | 8.1918 | 8.3341 | 8.4763 | 8.6186 | 8.7609 | 8.9031 | 9.0454 | 9.1877 | 9.3299 | 9.4722 | 9.6145 | 9.7567 | 9.899 | 10.0413 | 10.1835 | 10.3258 | 10.4681 | 10.6103 | 10.7526 | 10.8949 | 11.0371 | 11.1794 | 11.3217 | 11.4639 | 11.6062 | 11.7485 | 11.8907 | 12.033 | 12.147 | 12.261 | 12.375 | 12.489 | 12.603 | 12.717 | 12.831 | 12.945 | 13.059 | 13.173 | 13.287 | 13.401 | 13.515 | 13.629 | 13.743 | 13.857 | 13.971 | 14.085 | 14.199 | 14.313 | 14.427 | 14.541 | 14.655 | 14.769 | 14.883 | 14.997 | 15.111 | 15.225 | 15.339 | 15.453 | 15.5356 | 15.6182 | 15.7008 | 15.7834 | 15.866 | 15.9486 | 16.0312 | 16.1138 | 16.1964 | 16.279 | 16.3616 | 16.4442 | 16.5268 | 16.6094 | 16.692 | 16.7746 | 16.8572 | 16.9398 | 17.0224 | 17.105 | 17.1876 | 17.2702 | 17.3528 | 17.4354 | 17.518 | 17.6006 | 17.6832 | 17.7658 | 17.8484 | 17.931
6.45 | 0 | 2.25 | 2.0806 | 1.9905 | 1.8905 | 2.4885 | 3.1421 | 7.9219 | 12.2696 | 15.7534 | 18.2799 | -2.2204e-16 | 0.225 | 0.45 | 0.675 | 0.9 | 1.125 | 1.35 | 1.575 | 1.8 | 2.025 | 2.25 | 2.2161 | 2.1822 | 2.1484 | 2.1145 | 2.0806 | 2.0626 | 2.0446 | 2.0266 | 2.0085 | 1.9905 | 1.9805 | 1.9705 | 1.9605 | 1.9505 | 1.9405 | 1.9305 | 1.9205 | 1.9105 | 1.9005 | 1.8905 | 1.9304 | 1.9702 | 2.0101 | 2.05 | 2.0898 | 2.1297 | 2.1696 | 2.2094 | 2.2493 | 2.2892 | 2.329 | 2.3689 | 2.4088 | 2.4486 | 2.4885 | 2.5321 | 2.5757 | 2.6192 | 2.6628 | 2.7064 | 2.75 | 2.7935 | 2.8371 | 2.8807 | 2.9243 | 2.9678 | 3.0114 | 3.055 | 3.0986 | 3.1421 | 3.3014 | 3.4608 | 3.6201 | 3.7794 | 3.9388 | 4.0981 | 4.2574 | 4.4167 | 4.5761 | 4.7354 | 4.8947 | 5.054 | 5.2134 | 5.3727 | 5.532 | 5.6913 | 5.8506 | 6.01 | 6.1693 | 6.3286 | 6.4879 | 6.6473 | 6.8066 | 6.9659 | 7.1252 | 7.2846 | 7.4439 | 7.6032 | 7.7625 | 7.9219 | 8.0668 | 8.2117 | 8.3567 | 8.5016 | 8.6465 | 8.7914 | 8.9364 | 9.0813 | 9.2262 | 9.3711 | 9.516 | 9.661 | 9.8059 | 9.9508 | 10.0958 | 10.2407 | 10.3856 | 10.5305 | 10.6755 | 10.8204 | 10.9653 | 11.1102 | 11.2552 | 11.4001 | 11.545 | 11.6899 | 11.8349 | 11.9798 | 12.1247 | 12.2696 | 12.3857 | 12.5019 | 12.618 | 12.7341 | 12.8503 | 12.9664 | 13.0825 | 13.1986 | 13.3148 | 13.4309 | 13.547 | 13.6631 | 13.7792 | 13.8954 | 14.0115 | 14.1276 | 14.2437 | 14.3599 | 14.476 | 14.5921 | 14.7082 | 14.8244 | 14.9405 | 15.0566 | 15.1727 | 15.2889 | 15.405 | 15.5211 | 15.6372 | 15.7534 | 15.8376 | 15.9218 | 16.006 | 16.0902 | 16.1745 | 16.2587 | 16.3429 | 16.4271 | 16.5113 | 16.5955 | 16.6798 | 16.764 | 16.8482 | 16.9324 | 17.0166 | 17.1008 | 17.1851 | 17.2693 | 17.3535 | 17.4377 | 17.5219 | 17.6061 | 17.6904 | 17.7746 | 17.8588 | 17.943 | 18.0272 | 18.1114 | 18.1957 | 18.2799
6.5 | 0 | 2.29 | 2.1262 | 2.035 | 1.935 | 2.545 | 3.2112 | 8.0787 | 12.5063 | 16.0538 | 18.6287 | 0 | 0.229 | 0.458 | 0.687 | 0.916 | 1.145 | 1.374 | 1.603 | 1.832 | 2.061 | 2.29 | 2.2572 | 2.2245 | 2.1918 | 2.159 | 2.1262 | 2.108 | 2.0897 | 2.0715 | 2.0533 | 2.035 | 2.025 | 2.015 | 2.005 | 1.995 | 1.985 | 1.975 | 1.965 | 1.955 | 1.945 | 1.935 | 1.9757 | 2.0163 | 2.057 | 2.0977 | 2.1383 | 2.179 | 2.2197 | 2.2603 | 2.301 | 2.3417 | 2.3823 | 2.423 | 2.4637 | 2.5043 | 2.545 | 2.5894 | 2.6338 | 2.6782 | 2.7227 | 2.7671 | 2.8115 | 2.8559 | 2.9003 | 2.9447 | 2.9892 | 3.0336 | 3.078 | 3.1224 | 3.1668 | 3.2113 | 3.3735 | 3.5358 | 3.698 | 3.8603 | 4.0225 | 4.1848 | 4.347 | 4.5092 | 4.6715 | 4.8338 | 4.996 | 5.1583 | 5.3205 | 5.4828 | 5.645 | 5.8072 | 5.9695 | 6.1318 | 6.294 | 6.4563 | 6.6185 | 6.7807 | 6.943 | 7.1052 | 7.2675 | 7.4298 | 7.592 | 7.7543 | 7.9165 | 8.0788 | 8.2263 | 8.3739 | 8.5215 | 8.6691 | 8.8167 | 8.9642 | 9.1118 | 9.2594 | 9.407 | 9.5546 | 9.7022 | 9.8498 | 9.9973 | 10.1449 | 10.2925 | 10.4401 | 10.5877 | 10.7353 | 10.8828 | 11.0304 | 11.178 | 11.3256 | 11.4732 | 11.6208 | 11.7683 | 11.9159 | 12.0635 | 12.2111 | 12.3587 | 12.5063 | 12.6245 | 12.7428 | 12.861 | 12.9793 | 13.0975 | 13.2158 | 13.334 | 13.4523 | 13.5705 | 13.6888 | 13.807 | 13.9253 | 14.0435 | 14.1618 | 14.28 | 14.3983 | 14.5165 | 14.6348 | 14.753 | 14.8712 | 14.9895 | 15.1077 | 15.226 | 15.3443 | 15.4625 | 15.5808 | 15.699 | 15.8173 | 15.9355 | 16.0538 | 16.1396 | 16.2254 | 16.3113 | 16.3971 | 16.4829 | 16.5688 | 16.6546 | 16.7404 | 16.8263 | 16.9121 | 16.9979 | 17.0837 | 17.1696 | 17.2554 | 17.3412 | 17.4271 | 17.5129 | 17.5987 | 17.6846 | 17.7704 | 17.8562 | 17.9421 | 18.0279 | 18.1137 | 18.1996 | 18.2854 | 18.3712 | 18.4571 | 18.5429 | 18.6287
6.55 | 0 | 2.33 | 2.1719 | 2.0795 | 1.9795 | 2.6015 | 3.2804 | 8.2356 | 12.7429 | 16.3541 | 18.9776 | -2.2204e-16 | 0.233 | 0.466 | 0.699 | 0.932 | 1.165 | 1.398 | 1.631 | 1.864 | 2.097 | 2.33 | 2.2984 | 2.2668 | 2.2351 | 2.2035 | 2.1719 | 2.1534 | 2.1349 | 2.1164 | 2.098 | 2.0795 | 2.0695 | 2.0595 | 2.0495 | 2.0395 | 2.0295 | 2.0195 | 2.0095 | 1.9995 | 1.9895 | 1.9795 | 2.021 | 2.0624 | 2.1039 | 2.1454 | 2.1868 | 2.2283 | 2.2698 | 2.3112 | 2.3527 | 2.3942 | 2.4356 | 2.4771 | 2.5186 | 2.56 | 2.6015 | 2.6468 | 2.692 | 2.7373 | 2.7825 | 2.8278 | 2.8731 | 2.9183 | 2.9636 | 3.0088 | 3.0541 | 3.0993 | 3.1446 | 3.1899 | 3.2351 | 3.2804 | 3.4455 | 3.6107 | 3.7759 | 3.9411 | 4.1062 | 4.2714 | 4.4366 | 4.6018 | 4.7669 | 4.9321 | 5.0973 | 5.2625 | 5.4276 | 5.5928 | 5.758 | 5.9232 | 6.0883 | 6.2535 | 6.4187 | 6.5839 | 6.749 | 6.9142 | 7.0794 | 7.2446 | 7.4097 | 7.5749 | 7.7401 | 7.9053 | 8.0704 | 8.2356 | 8.3859 | 8.5361 | 8.6863 | 8.8366 | 8.9868 | 9.1371 | 9.2873 | 9.4376 | 9.5878 | 9.738 | 9.8883 | 10.0385 | 10.1888 | 10.339 | 10.4892 | 10.6395 | 10.7897 | 10.94 | 11.0902 | 11.2405 | 11.3907 | 11.5409 | 11.6912 | 11.8414 | 11.9917 | 12.1419 | 12.2921 | 12.4424 | 12.5926 | 12.7429 | 12.8632 | 12.9836 | 13.104 | 13.2244 | 13.3447 | 13.4651 | 13.5855 | 13.7059 | 13.8262 | 13.9466 | 14.067 | 14.1874 | 14.3077 | 14.4281 | 14.5485 | 14.6689 | 14.7892 | 14.9096 | 15.03 | 15.1504 | 15.2707 | 15.3911 | 15.5115 | 15.6319 | 15.7522 | 15.8726 | 15.993 | 16.1134 | 16.2337 | 16.3541 | 16.4416 | 16.529 | 16.6165 | 16.7039 | 16.7914 | 16.8788 | 16.9663 | 17.0537 | 17.1412 | 17.2286 | 17.3161 | 17.4035 | 17.491 | 17.5784 | 17.6659 | 17.7533 | 17.8408 | 17.9282 | 18.0157 | 18.1031 | 18.1906 | 18.278 | 18.3655 | 18.4529 | 18.5404 | 18.6278 | 18.7153 | 18.8027 | 18.8902 | 18.9776
6.6 | 0 | 2.37 | 2.2175 | 2.124 | 2.024 | 2.658 | 3.3495 | 8.3925 | 12.9795 | 16.6545 | 19.3265 | 0 | 0.237 | 0.474 | 0.711 | 0.948 | 1.185 | 1.422 | 1.659 | 1.896 | 2.133 | 2.37 | 2.3395 | 2.309 | 2.2785 | 2.248 | 2.2175 | 2.1988 | 2.1801 | 2.1614 | 2.1427 | 2.124 | 2.114 | 2.104 | 2.094 | 2.084 | 2.074 | 2.064 | 2.054 | 2.044 | 2.034 | 2.024 | 2.0663 | 2.1085 | 2.1508 | 2.1931 | 2.2353 | 2.2776 | 2.3199 | 2.3621 | 2.4044 | 2.4467 | 2.4889 | 2.5312 | 2.5735 | 2.6157 | 2.658 | 2.7041 | 2.7502 | 2.7963 | 2.8424 | 2.8885 | 2.9346 | 2.9807 | 3.0268 | 3.0729 | 3.119 | 3.1651 | 3.2112 | 3.2573 | 3.3034 | 3.3495 | 3.5176 | 3.6857 | 3.8538 | 4.0219 | 4.19 | 4.3581 | 4.5262 | 4.6943 | 4.8624 | 5.0305 | 5.1986 | 5.3667 | 5.5348 | 5.7029 | 5.871 | 6.0391 | 6.2072 | 6.3753 | 6.5434 | 6.7115 | 6.8796 | 7.0477 | 7.2158 | 7.3839 | 7.552 | 7.7201 | 7.8882 | 8.0563 | 8.2244 | 8.3925 | 8.5454 | 8.6983 | 8.8512 | 9.0041 | 9.157 | 9.3099 | 9.4628 | 9.6157 | 9.7686 | 9.9215 | 10.0744 | 10.2273 | 10.3802 | 10.5331 | 10.686 | 10.8389 | 10.9918 | 11.1447 | 11.2976 | 11.4505 | 11.6034 | 11.7563 | 11.9092 | 12.0621 | 12.215 | 12.3679 | 12.5208 | 12.6737 | 12.8266 | 12.9795 | 13.102 | 13.2245 | 13.347 | 13.4695 | 13.592 | 13.7145 | 13.837 | 13.9595 | 14.082 | 14.2045 | 14.327 | 14.4495 | 14.572 | 14.6945 | 14.817 | 14.9395 | 15.062 | 15.1845 | 15.307 | 15.4295 | 15.552 | 15.6745 | 15.797 | 15.9195 | 16.042 | 16.1645 | 16.287 | 16.4095 | 16.532 | 16.6545 | 16.7436 | 16.8326 | 16.9217 | 17.0108 | 17.0998 | 17.1889 | 17.278 | 17.367 | 17.4561 | 17.5452 | 17.6342 | 17.7233 | 17.8124 | 17.9014 | 17.9905 | 18.0796 | 18.1686 | 18.2577 | 18.3468 | 18.4358 | 18.5249 | 18.614 | 18.703 | 18.7921 | 18.8812 | 18.9702 | 19.0593 | 19.1484 | 19.2374 | 19.3265
6.65 | 0 | 2.41 | 2.2631 | 2.1685 | 2.0685 | 2.7145 | 3.4186 | 8.5494 | 13.2161 | 16.9549 | 19.6754 | -2.2204e-16 | 0.241 | 0.482 | 0.723 | 0.964 | 1.205 | 1.446 | 1.687 | 1.928 | 2.169 | 2.41 | 2.3806 | 2.3513 | 2.3219 | 2.2925 | 2.2631 | 2.2442 | 2.2253 | 2.2064 | 2.1874 | 2.1685 | 2.1585 | 2.1485 | 2.1385 | 2.1285 | 2.1185 | 2.1085 | 2.0985 | 2.0885 | 2.0785 | 2.0685 | 2.1116 | 2.1546 | 2.1977 | 2.2408 | 2.2838 | 2.3269 | 2.37 | 2.413 | 2.4561 | 2.4992 | 2.5422 | 2.5853 | 2.6284 | 2.6714 | 2.7145 | 2.7614 | 2.8084 | 2.8553 | 2.9023 | 2.9492 | 2.9962 | 3.0431 | 3.09 | 3.137 | 3.1839 | 3.2309 | 3.2778 | 3.3247 | 3.3717 | 3.4186 | 3.5896 | 3.7607 | 3.9317 | 4.1027 | 4.2738 | 4.4448 | 4.6158 | 4.7868 | 4.9578 | 5.1289 | 5.2999 | 5.4709 | 5.642 | 5.813 | 5.984 | 6.155 | 6.3261 | 6.4971 | 6.6681 | 6.8391 | 7.0102 | 7.1812 | 7.3522 | 7.5232 | 7.6943 | 7.8653 | 8.0363 | 8.2073 | 8.3784 | 8.5494 | 8.7049 | 8.8605 | 9.0161 | 9.1716 | 9.3272 | 9.4827 | 9.6383 | 9.7938 | 9.9494 | 10.105 | 10.2605 | 10.4161 | 10.5716 | 10.7272 | 10.8828 | 11.0383 | 11.1939 | 11.3494 | 11.505 | 11.6605 | 11.8161 | 11.9717 | 12.1272 | 12.2828 | 12.4383 | 12.5939 | 12.7495 | 12.905 | 13.0606 | 13.2161 | 13.3408 | 13.4654 | 13.59 | 13.7146 | 13.8393 | 13.9639 | 14.0885 | 14.2131 | 14.3378 | 14.4624 | 14.587 | 14.7116 | 14.8363 | 14.9609 | 15.0855 | 15.2101 | 15.3348 | 15.4594 | 15.584 | 15.7086 | 15.8333 | 15.9579 | 16.0825 | 16.2071 | 16.3317 | 16.4564 | 16.581 | 16.7056 | 16.8302 | 16.9549 | 17.0456 | 17.1362 | 17.2269 | 17.3176 | 17.4083 | 17.499 | 17.5897 | 17.6803 | 17.771 | 17.8617 | 17.9524 | 18.0431 | 18.1338 | 18.2244 | 18.3151 | 18.4058 | 18.4965 | 18.5872 | 18.6779 | 18.7685 | 18.8592 | 18.9499 | 19.0406 | 19.1313 | 19.222 | 19.3126 | 19.4033 | 19.494 | 19.5847 | 19.6754
6.7 | 0 | 2.45 | 2.3087 | 2.213 | 2.113 | 2.771 | 3.4878 | 8.7063 | 13.4528 | 17.2552 | 20.0243 | 0 | 0.245 | 0.49 | 0.735 | 0.98 | 1.225 | 1.47 | 1.715 | 1.96 | 2.205 | 2.45 | 2.4217 | 2.3935 | 2.3652 | 2.337 | 2.3087 | 2.2896 | 2.2704 | 2.2513 | 2.2321 | 2.213 | 2.203 | 2.193 | 2.183 | 2.173 | 2.163 | 2.153 | 2.143 | 2.133 | 2.123 | 2.113 | 2.1569 | 2.2007 | 2.2446 | 2.2885 | 2.3323 | 2.3762 | 2.4201 | 2.4639 | 2.5078 | 2.5517 | 2.5955 | 2.6394 | 2.6833 | 2.7271 | 2.771 | 2.8188 | 2.8666 | 2.9144 | 2.9621 | 3.0099 | 3.0577 | 3.1055 | 3.1533 | 3.2011 | 3.2488 | 3.2966 | 3.3444 | 3.3922 | 3.44 | 3.4877 | 3.6617 | 3.8357 | 4.0096 | 4.1835 | 4.3575 | 4.5314 | 4.7054 | 4.8793 | 5.0533 | 5.2272 | 5.4012 | 5.5751 | 5.7491 | 5.923 | 6.097 | 6.271 | 6.4449 | 6.6188 | 6.7928 | 6.9668 | 7.1407 | 7.3146 | 7.4886 | 7.6626 | 7.8365 | 8.0104 | 8.1844 | 8.3584 | 8.5323 | 8.7063 | 8.8645 | 9.0227 | 9.1809 | 9.3391 | 9.4973 | 9.6556 | 9.8138 | 9.972 | 10.1302 | 10.2884 | 10.4466 | 10.6049 | 10.7631 | 10.9213 | 11.0795 | 11.2377 | 11.3959 | 11.5542 | 11.7124 | 11.8706 | 12.0288 | 12.187 | 12.3452 | 12.5035 | 12.6617 | 12.8199 | 12.9781 | 13.1363 | 13.2945 | 13.4528 | 13.5795 | 13.7063 | 13.833 | 13.9598 | 14.0865 | 14.2133 | 14.34 | 14.4668 | 14.5935 | 14.7203 | 14.847 | 14.9737 | 15.1005 | 15.2273 | 15.354 | 15.4808 | 15.6075 | 15.7342 | 15.861 | 15.9877 | 16.1145 | 16.2412 | 16.368 | 16.4947 | 16.6215 | 16.7482 | 16.875 | 17.0017 | 17.1285 | 17.2552 | 17.3475 | 17.4398 | 17.5321 | 17.6244 | 17.7167 | 17.809 | 17.9013 | 17.9936 | 18.0859 | 18.1782 | 18.2706 | 18.3628 | 18.4551 | 18.5474 | 18.6397 | 18.7321 | 18.8243 | 18.9166 | 19.0089 | 19.1013 | 19.1936 | 19.2858 | 19.3781 | 19.4704 | 19.5628 | 19.6551 | 19.7473 | 19.8396 | 19.932 | 20.0242
6.75 | 0 | 2.49 | 2.3544 | 2.2575 | 2.1575 | 2.8275 | 3.5569 | 8.8631 | 13.6894 | 17.5556 | 20.3731 | -2.2204e-16 | 0.249 | 0.498 | 0.747 | 0.996 | 1.245 | 1.494 | 1.743 | 1.992 | 2.241 | 2.49 | 2.4629 | 2.4357 | 2.4086 | 2.3815 | 2.3544 | 2.335 | 2.3156 | 2.2963 | 2.2769 | 2.2575 | 2.2475 | 2.2375 | 2.2275 | 2.2175 | 2.2075 | 2.1975 | 2.1875 | 2.1775 | 2.1675 | 2.1575 | 2.2022 | 2.2468 | 2.2915 | 2.3362 | 2.3808 | 2.4255 | 2.4702 | 2.5148 | 2.5595 | 2.6042 | 2.6488 | 2.6935 | 2.7382 | 2.7828 | 2.8275 | 2.8761 | 2.9248 | 2.9734 | 3.022 | 3.0706 | 3.1193 | 3.1679 | 3.2165 | 3.2651 | 3.3137 | 3.3624 | 3.411 | 3.4596 | 3.5082 | 3.5569 | 3.7337 | 3.9106 | 4.0875 | 4.2644 | 4.4413 | 4.6181 | 4.795 | 4.9719 | 5.1488 | 5.3256 | 5.5025 | 5.6794 | 5.8563 | 6.0331 | 6.21 | 6.3869 | 6.5637 | 6.7406 | 6.9175 | 7.0944 | 7.2713 | 7.4481 | 7.625 | 7.8019 | 7.9788 | 8.1556 | 8.3325 | 8.5094 | 8.6863 | 8.8631 | 9.024 | 9.1849 | 9.3457 | 9.5066 | 9.6675 | 9.8284 | 9.9893 | 10.1501 | 10.311 | 10.4719 | 10.6327 | 10.7936 | 10.9545 | 11.1154 | 11.2763 | 11.4371 | 11.598 | 11.7589 | 11.9198 | 12.0806 | 12.2415 | 12.4024 | 12.5633 | 12.7241 | 12.885 | 13.0459 | 13.2067 | 13.3676 | 13.5285 | 13.6894 | 13.8183 | 13.9471 | 14.076 | 14.2049 | 14.3338 | 14.4626 | 14.5915 | 14.7204 | 14.8493 | 14.9781 | 15.107 | 15.2359 | 15.3648 | 15.4936 | 15.6225 | 15.7514 | 15.8803 | 16.0091 | 16.138 | 16.2669 | 16.3957 | 16.5246 | 16.6535 | 16.7824 | 16.9113 | 17.0401 | 17.169 | 17.2979 | 17.4267 | 17.5556 | 17.6495 | 17.7435 | 17.8374 | 17.9313 | 18.0252 | 18.1191 | 18.213 | 18.307 | 18.4009 | 18.4948 | 18.5887 | 18.6826 | 18.7765 | 18.8705 | 18.9644 | 19.0583 | 19.1522 | 19.2461 | 19.34 | 19.434 | 19.5279 | 19.6218 | 19.7157 | 19.8096 | 19.9035 | 19.9975 | 20.0914 | 20.1853 | 20.2792 | 20.3731
6.8 | 0 | 2.53 | 2.4 | 2.302 | 2.202 | 2.884 | 3.626 | 9.02 | 13.926 | 17.856 | 20.722 | 2.2204e-16 | 0.253 | 0.506 | 0.759 | 1.012 | 1.265 | 1.518 | 1.771 | 2.024 | 2.277 | 2.53 | 2.504 | 2.478 | 2.452 | 2.426 | 2.4 | 2.3804 | 2.3608 | 2.3412 | 2.3216 | 2.302 | 2.292 | 2.282 | 2.272 | 2.262 | 2.252 | 2.242 | 2.232 | 2.222 | 2.212 | 2.202 | 2.2475 | 2.2929 | 2.3384 | 2.3839 | 2.4293 | 2.4748 | 2.5203 | 2.5657 | 2.6112 | 2.6567 | 2.7021 | 2.7476 | 2.7931 | 2.8385 | 2.884 | 2.9335 | 2.9829 | 3.0324 | 3.0819 | 3.1313 | 3.1808 | 3.2303 | 3.2797 | 3.3292 | 3.3787 | 3.4281 | 3.4776 | 3.5271 | 3.5765 | 3.626 | 3.8058 | 3.9856 | 4.1654 | 4.3452 | 4.525 | 4.7048 | 4.8846 | 5.0644 | 5.2442 | 5.424 | 5.6038 | 5.7836 | 5.9634 | 6.1432 | 6.323 | 6.5028 | 6.6826 | 6.8624 | 7.0422 | 7.222 | 7.4018 | 7.5816 | 7.7614 | 7.9412 | 8.121 | 8.3008 | 8.4806 | 8.6604 | 8.8402 | 9.02 | 9.1835 | 9.3471 | 9.5106 | 9.6741 | 9.8377 | 10.0012 | 10.1647 | 10.3283 | 10.4918 | 10.6553 | 10.8189 | 10.9824 | 11.1459 | 11.3095 | 11.473 | 11.6365 | 11.8001 | 11.9636 | 12.1271 | 12.2907 | 12.4542 | 12.6177 | 12.7813 | 12.9448 | 13.1083 | 13.2719 | 13.4354 | 13.5989 | 13.7625 | 13.926 | 14.057 | 14.188 | 14.319 | 14.45 | 14.581 | 14.712 | 14.843 | 14.974 | 15.105 | 15.236 | 15.367 | 15.498 | 15.629 | 15.76 | 15.891 | 16.022 | 16.153 | 16.284 | 16.415 | 16.546 | 16.677 | 16.808 | 16.939 | 17.07 | 17.201 | 17.332 | 17.463 | 17.594 | 17.725 | 17.856 | 17.9515 | 18.0471 | 18.1426 | 18.2381 | 18.3337 | 18.4292 | 18.5247 | 18.6203 | 18.7158 | 18.8113 | 18.9069 | 19.0024 | 19.0979 | 19.1935 | 19.289 | 19.3845 | 19.4801 | 19.5756 | 19.6711 | 19.7667 | 19.8622 | 19.9577 | 20.0533 | 20.1488 | 20.2443 | 20.3399 | 20.4354 | 20.5309 | 20.6265 | 20.722
6.85 | 0 | 2.57 | 2.4456 | 2.3465 | 2.2465 | 2.9405 | 3.6951 | 9.1769 | 14.1626 | 18.1564 | 21.0709 | -2.2204e-16 | 0.257 | 0.514 | 0.771 | 1.028 | 1.285 | 1.542 | 1.799 | 2.056 | 2.313 | 2.57 | 2.5451 | 2.5203 | 2.4954 | 2.4705 | 2.4456 | 2.4258 | 2.406 | 2.3861 | 2.3663 | 2.3465 | 2.3365 | 2.3265 | 2.3165 | 2.3065 | 2.2965 | 2.2865 | 2.2765 | 2.2665 | 2.2565 | 2.2465 | 2.2928 | 2.339 | 2.3853 | 2.4316 | 2.4778 | 2.5241 | 2.5704 | 2.6166 | 2.6629 | 2.7092 | 2.7554 | 2.8017 | 2.848 | 2.8942 | 2.9405 | 2.9908 | 3.0411 | 3.0914 | 3.1417 | 3.192 | 3.2423 | 3.2927 | 3.343 | 3.3933 | 3.4436 | 3.4939 | 3.5442 | 3.5945 | 3.6448 | 3.6951 | 3.8778 | 4.0606 | 4.2433 | 4.426 | 4.6087 | 4.7915 | 4.9742 | 5.1569 | 5.3396 | 5.5224 | 5.7051 | 5.8878 | 6.0705 | 6.2533 | 6.436 | 6.6187 | 6.8014 | 6.9842 | 7.1669 | 7.3496 | 7.5323 | 7.7151 | 7.8978 | 8.0805 | 8.2632 | 8.446 | 8.6287 | 8.8114 | 8.9941 | 9.1769 | 9.3431 | 9.5093 | 9.6754 | 9.8416 | 10.0078 | 10.174 | 10.3402 | 10.5064 | 10.6726 | 10.8388 | 11.005 | 11.1712 | 11.3374 | 11.5036 | 11.6698 | 11.8359 | 12.0021 | 12.1683 | 12.3345 | 12.5007 | 12.6669 | 12.8331 | 12.9993 | 13.1655 | 13.3317 | 13.4979 | 13.664 | 13.8302 | 13.9964 | 14.1626 | 14.2958 | 14.4289 | 14.562 | 14.6951 | 14.8283 | 14.9614 | 15.0945 | 15.2276 | 15.3608 | 15.4939 | 15.627 | 15.7601 | 15.8933 | 16.0264 | 16.1595 | 16.2926 | 16.4258 | 16.5589 | 16.692 | 16.8251 | 16.9583 | 17.0914 | 17.2245 | 17.3576 | 17.4908 | 17.6239 | 17.757 | 17.8901 | 18.0233 | 18.1564 | 18.2535 | 18.3507 | 18.4478 | 18.545 | 18.6421 | 18.7393 | 18.8364 | 18.9336 | 19.0307 | 19.1279 | 19.225 | 19.3222 | 19.4193 | 19.5165 | 19.6136 | 19.7108 | 19.8079 | 19.9051 | 20.0022 | 20.0994 | 20.1965 | 20.2937 | 20.3908 | 20.488 | 20.5851 | 20.6823 | 20.7794 | 20.8766 | 20.9737 | 21.0709
6.9 | 0 | 2.61 | 2.4912 | 2.391 | 2.291 | 2.997 | 3.7643 | 9.3338 | 14.3993 | 18.4567 | 21.4198 | 2.2204e-16 | 0.261 | 0.522 | 0.783 | 1.044 | 1.305 | 1.566 | 1.827 | 2.088 | 2.349 | 2.61 | 2.5863 | 2.5625 | 2.5388 | 2.515 | 2.4912 | 2.4712 | 2.4512 | 2.4311 | 2.411 | 2.391 | 2.381 | 2.371 | 2.361 | 2.351 | 2.341 | 2.331 | 2.321 | 2.311 | 2.301 | 2.291 | 2.3381 | 2.3851 | 2.4322 | 2.4793 | 2.5263 | 2.5734 | 2.6205 | 2.6675 | 2.7146 | 2.7617 | 2.8087 | 2.8558 | 2.9029 | 2.9499 | 2.997 | 3.0482 | 3.0993 | 3.1505 | 3.2016 | 3.2528 | 3.3039 | 3.3551 | 3.4062 | 3.4574 | 3.5085 | 3.5597 | 3.6108 | 3.662 | 3.7131 | 3.7643 | 3.9499 | 4.1356 | 4.3212 | 4.5069 | 4.6925 | 4.8781 | 5.0638 | 5.2494 | 5.4351 | 5.6208 | 5.8064 | 5.9921 | 6.1777 | 6.3634 | 6.549 | 6.7347 | 6.9203 | 7.1059 | 7.2916 | 7.4773 | 7.6629 | 7.8486 | 8.0342 | 8.2199 | 8.4055 | 8.5912 | 8.7768 | 8.9625 | 9.1481 | 9.3338 | 9.5026 | 9.6715 | 9.8403 | 10.0092 | 10.178 | 10.3469 | 10.5157 | 10.6846 | 10.8534 | 11.0223 | 11.1911 | 11.36 | 11.5288 | 11.6977 | 11.8665 | 12.0354 | 12.2042 | 12.3731 | 12.5419 | 12.7108 | 12.8796 | 13.0485 | 13.2173 | 13.3862 | 13.555 | 13.7239 | 13.8927 | 14.0616 | 14.2304 | 14.3993 | 14.5345 | 14.6698 | 14.805 | 14.9403 | 15.0755 | 15.2108 | 15.346 | 15.4813 | 15.6165 | 15.7518 | 15.887 | 16.0223 | 16.1575 | 16.2928 | 16.428 | 16.5633 | 16.6985 | 16.8338 | 16.969 | 17.1043 | 17.2395 | 17.3748 | 17.51 | 17.6453 | 17.7805 | 17.9158 | 18.051 | 18.1863 | 18.3215 | 18.4567 | 18.5555 | 18.6543 | 18.7531 | 18.8518 | 18.9506 | 19.0493 | 19.1481 | 19.2469 | 19.3456 | 19.4444 | 19.5432 | 19.642 | 19.7407 | 19.8395 | 19.9383 | 20.037 | 20.1358 | 20.2345 | 20.3333 | 20.4321 | 20.5309 | 20.6296 | 20.7284 | 20.8271 | 20.9259 | 21.0247 | 21.1235 | 21.2222 | 21.321 | 21.4197
6.95 | 0 | 2.65 | 2.5369 | 2.4355 | 2.3355 | 3.0535 | 3.8334 | 9.4906 | 14.6359 | 18.7571 | 21.7686 | -2.2204e-16 | 0.265 | 0.53 | 0.795 | 1.06 | 1.325 | 1.59 | 1.855 | 2.12 | 2.385 | 2.65 | 2.6274 | 2.6048 | 2.5821 | 2.5595 | 2.5369 | 2.5166 | 2.4963 | 2.4761 | 2.4558 | 2.4355 | 2.4255 | 2.4155 | 2.4055 | 2.3955 | 2.3855 | 2.3755 | 2.3655 | 2.3555 | 2.3455 | 2.3355 | 2.3834 | 2.4312 | 2.4791 | 2.527 | 2.5748 | 2.6227 | 2.6706 | 2.7184 | 2.7663 | 2.8142 | 2.862 | 2.9099 | 2.9578 | 3.0056 | 3.0535 | 3.1055 | 3.1575 | 3.2095 | 3.2615 | 3.3135 | 3.3655 | 3.4174 | 3.4694 | 3.5214 | 3.5734 | 3.6254 | 3.6774 | 3.7294 | 3.7814 | 3.8334 | 4.022 | 4.2105 | 4.3991 | 4.5877 | 4.7763 | 4.9648 | 5.1534 | 5.342 | 5.5306 | 5.7191 | 5.9077 | 6.0963 | 6.2849 | 6.4734 | 6.662 | 6.8506 | 7.0392 | 7.2277 | 7.4163 | 7.6049 | 7.7935 | 7.982 | 8.1706 | 8.3592 | 8.5478 | 8.7363 | 8.9249 | 9.1135 | 9.3021 | 9.4906 | 9.6621 | 9.8336 | 10.0052 | 10.1767 | 10.3482 | 10.5197 | 10.6912 | 10.8627 | 11.0342 | 11.2057 | 11.3772 | 11.5487 | 11.7202 | 11.8917 | 12.0633 | 12.2348 | 12.4063 | 12.5778 | 12.7493 | 12.9208 | 13.0923 | 13.2638 | 13.4353 | 13.6068 | 13.7783 | 13.9498 | 14.1214 | 14.2929 | 14.4644 | 14.6359 | 14.7732 | 14.9106 | 15.048 | 15.1854 | 15.3227 | 15.4601 | 15.5975 | 15.7349 | 15.8722 | 16.0096 | 16.147 | 16.2844 | 16.4217 | 16.5591 | 16.6965 | 16.8339 | 16.9712 | 17.1086 | 17.246 | 17.3834 | 17.5207 | 17.6581 | 17.7955 | 17.9329 | 18.0702 | 18.2076 | 18.345 | 18.4824 | 18.6197 | 18.7571 | 18.8575 | 18.9579 | 19.0583 | 19.1587 | 19.259 | 19.3594 | 19.4598 | 19.5602 | 19.6606 | 19.761 | 19.8613 | 19.9617 | 20.0621 | 20.1625 | 20.2629 | 20.3633 | 20.4636 | 20.564 | 20.6644 | 20.7648 | 20.8652 | 20.9656 | 21.0659 | 21.1663 | 21.2667 | 21.3671 | 21.4675 | 21.5679 | 21.6682 | 21.7686
7 | 0 | 2.69 | 2.5825 | 2.48 | 2.38 | 3.11 | 3.9025 | 9.6475 | 14.8725 | 19.0575 | 22.1175 | 2.2204e-16 | 0.269 | 0.538 | 0.807 | 1.076 | 1.345 | 1.614 | 1.883 | 2.152 | 2.421 | 2.69 | 2.6685 | 2.647 | 2.6255 | 2.604 | 2.5825 | 2.562 | 2.5415 | 2.521 | 2.5005 | 2.48 | 2.47 | 2.46 | 2.45 | 2.44 | 2.43 | 2.42 | 2.41 | 2.4 | 2.39 | 2.38 | 2.4287 | 2.4773 | 2.526 | 2.5747 | 2.6233 | 2.672 | 2.7207 | 2.7693 | 2.818 | 2.8667 | 2.9153 | 2.964 | 3.0127 | 3.0613 | 3.11 | 3.1628 | 3.2157 | 3.2685 | 3.3213 | 3.3742 | 3.427 | 3.4798 | 3.5327 | 3.5855 | 3.6383 | 3.6912 | 3.744 | 3.7968 | 3.8497 | 3.9025 | 4.094 | 4.2855 | 4.477 | 4.6685 | 4.86 | 5.0515 | 5.243 | 5.4345 | 5.626 | 5.8175 | 6.009 | 6.2005 | 6.392 | 6.5835 | 6.775 | 6.9665 | 7.158 | 7.3495 | 7.541 | 7.7325 | 7.924 | 8.1155 | 8.307 | 8.4985 | 8.69 | 8.8815 | 9.073 | 9.2645 | 9.456 | 9.6475 | 9.8217 | 9.9958 | 10.17 | 10.3442 | 10.5183 | 10.6925 | 10.8667 | 11.0408 | 11.215 | 11.3892 | 11.5633 | 11.7375 | 11.9117 | 12.0858 | 12.26 | 12.4342 | 12.6083 | 12.7825 | 12.9567 | 13.1308 | 13.305 | 13.4792 | 13.6533 | 13.8275 | 14.0017 | 14.1758 | 14.35 | 14.5242 | 14.6983 | 14.8725 | 15.012 | 15.1515 | 15.291 | 15.4305 | 15.57 | 15.7095 | 15.849 | 15.9885 | 16.128 | 16.2675 | 16.407 | 16.5465 | 16.686 | 16.8255 | 16.965 | 17.1045 | 17.244 | 17.3835 | 17.523 | 17.6625 | 17.802 | 17.9415 | 18.081 | 18.2205 | 18.36 | 18.4995 | 18.639 | 18.7785 | 18.918 | 19.0575 | 19.1595 | 19.2615 | 19.3635 | 19.4655 | 19.5675 | 19.6695 | 19.7715 | 19.8735 | 19.9755 | 20.0775 | 20.1795 | 20.2815 | 20.3835 | 20.4855 | 20.5875 | 20.6895 | 20.7915 | 20.8935 | 20.9955 | 21.0975 | 21.1995 | 21.3015 | 21.4035 | 21.5055 | 21.6075 | 21.7095 | 21.8115 | 21.9135 | 22.0155 | 22.1175
7.05 | 0 | 2.73 | 2.6281 | 2.5245 | 2.4245 | 3.1665 | 3.9716 | 9.8044 | 15.1091 | 19.3579 | 22.4664 | -2.2204e-16 | 0.273 | 0.546 | 0.819 | 1.092 | 1.365 | 1.638 | 1.911 | 2.184 | 2.457 | 2.73 | 2.7096 | 2.6892 | 2.6689 | 2.6485 | 2.6281 | 2.6074 | 2.5867 | 2.5659 | 2.5452 | 2.5245 | 2.5145 | 2.5045 | 2.4945 | 2.4845 | 2.4745 | 2.4645 | 2.4545 | 2.4445 | 2.4345 | 2.4245 | 2.474 | 2.5234 | 2.5729 | 2.6224 | 2.6718 | 2.7213 | 2.7708 | 2.8202 | 2.8697 | 2.9192 | 2.9686 | 3.0181 | 3.0676 | 3.117 | 3.1665 | 3.2202 | 3.2738 | 3.3275 | 3.3812 | 3.4349 | 3.4885 | 3.5422 | 3.5959 | 3.6496 | 3.7032 | 3.7569 | 3.8106 | 3.8643 | 3.9179 | 3.9716 | 4.166 | 4.3605 | 4.5549 | 4.7493 | 4.9437 | 5.1382 | 5.3326 | 5.527 | 5.7214 | 5.9159 | 6.1103 | 6.3047 | 6.4991 | 6.6936 | 6.888 | 7.0824 | 7.2768 | 7.4713 | 7.6657 | 7.8601 | 8.0545 | 8.249 | 8.4434 | 8.6378 | 8.8322 | 9.0267 | 9.2211 | 9.4155 | 9.6099 | 9.8044 | 9.9812 | 10.158 | 10.3349 | 10.5117 | 10.6885 | 10.8653 | 11.0422 | 11.219 | 11.3958 | 11.5726 | 11.7495 | 11.9263 | 12.1031 | 12.2799 | 12.4568 | 12.6336 | 12.8104 | 12.9872 | 13.1641 | 13.3409 | 13.5177 | 13.6945 | 13.8714 | 14.0482 | 14.225 | 14.4018 | 14.5787 | 14.7555 | 14.9323 | 15.1091 | 15.2508 | 15.3924 | 15.534 | 15.6756 | 15.8173 | 15.9589 | 16.1005 | 16.2421 | 16.3838 | 16.5254 | 16.667 | 16.8086 | 16.9503 | 17.0919 | 17.2335 | 17.3751 | 17.5168 | 17.6584 | 17.8 | 17.9416 | 18.0832 | 18.2249 | 18.3665 | 18.5081 | 18.6498 | 18.7914 | 18.933 | 19.0746 | 19.2162 | 19.3579 | 19.4615 | 19.5651 | 19.6687 | 19.7723 | 19.876 | 19.9796 | 20.0832 | 20.1868 | 20.2904 | 20.394 | 20.4977 | 20.6013 | 20.7049 | 20.8085 | 20.9121 | 21.0157 | 21.1194 | 21.223 | 21.3266 | 21.4302 | 21.5338 | 21.6374 | 21.7411 | 21.8447 | 21.9483 | 22.0519 | 22.1555 | 22.2591 | 22.3628 | 22.4664
7.1 | 0 | 2.77 | 2.6738 | 2.569 | 2.469 | 3.223 | 4.0407 | 9.9612 | 15.3457 | 19.6582 | 22.8152 | 0 | 0.277 | 0.554 | 0.831 | 1.108 | 1.385 | 1.662 | 1.939 | 2.216 | 2.493 | 2.77 | 2.7507 | 2.7315 | 2.7123 | 2.693 | 2.6738 | 2.6528 | 2.6319 | 2.6109 | 2.5899 | 2.569 | 2.559 | 2.549 | 2.539 | 2.529 | 2.519 | 2.509 | 2.499 | 2.489 | 2.479 | 2.469 | 2.5193 | 2.5695 | 2.6198 | 2.6701 | 2.7203 | 2.7706 | 2.8209 | 2.8711 | 2.9214 | 2.9717 | 3.0219 | 3.0722 | 3.1225 | 3.1727 | 3.223 | 3.2775 | 3.332 | 3.3866 | 3.4411 | 3.4956 | 3.5501 | 3.6046 | 3.6591 | 3.7136 | 3.7682 | 3.8227 | 3.8772 | 3.9317 | 3.9862 | 4.0407 | 4.2381 | 4.4354 | 4.6328 | 4.8301 | 5.0275 | 5.2248 | 5.4222 | 5.6196 | 5.8169 | 6.0143 | 6.2116 | 6.4089 | 6.6063 | 6.8036 | 7.001 | 7.1983 | 7.3957 | 7.593 | 7.7904 | 7.9878 | 8.1851 | 8.3825 | 8.5798 | 8.7772 | 8.9745 | 9.1719 | 9.3692 | 9.5666 | 9.7639 | 9.9613 | 10.1407 | 10.3202 | 10.4997 | 10.6792 | 10.8587 | 11.0381 | 11.2176 | 11.3971 | 11.5766 | 11.7561 | 11.9356 | 12.1151 | 12.2945 | 12.474 | 12.6535 | 12.833 | 13.0125 | 13.192 | 13.3714 | 13.5509 | 13.7304 | 13.9099 | 14.0894 | 14.2688 | 14.4483 | 14.6278 | 14.8073 | 14.9868 | 15.1663 | 15.3457 | 15.4895 | 15.6332 | 15.777 | 15.9207 | 16.0645 | 16.2082 | 16.352 | 16.4957 | 16.6395 | 16.7832 | 16.927 | 17.0707 | 17.2145 | 17.3582 | 17.502 | 17.6457 | 17.7895 | 17.9332 | 18.077 | 18.2207 | 18.3645 | 18.5082 | 18.652 | 18.7957 | 18.9395 | 19.0832 | 19.227 | 19.3707 | 19.5145 | 19.6582 | 19.7635 | 19.8687 | 19.9739 | 20.0792 | 20.1844 | 20.2896 | 20.3949 | 20.5001 | 20.6053 | 20.7106 | 20.8158 | 20.921 | 21.0263 | 21.1315 | 21.2367 | 21.342 | 21.4472 | 21.5524 | 21.6577 | 21.7629 | 21.8681 | 21.9734 | 22.0786 | 22.1838 | 22.2891 | 22.3943 | 22.4995 | 22.6048 | 22.71 | 22.8152
7.15 | 0 | 2.81 | 2.7194 | 2.6135 | 2.5135 | 3.2795 | 4.1099 | 10.1181 | 15.5824 | 19.9586 | 23.1641 | -2.2204e-16 | 0.281 | 0.562 | 0.843 | 1.124 | 1.405 | 1.686 | 1.967 | 2.248 | 2.529 | 2.81 | 2.7919 | 2.7737 | 2.7556 | 2.7375 | 2.7194 | 2.6982 | 2.677 | 2.6559 | 2.6347 | 2.6135 | 2.6035 | 2.5935 | 2.5835 | 2.5735 | 2.5635 | 2.5535 | 2.5435 | 2.5335 | 2.5235 | 2.5135 | 2.5646 | 2.6156 | 2.6667 | 2.7178 | 2.7688 | 2.8199 | 2.871 | 2.922 | 2.9731 | 3.0242 | 3.0752 | 3.1263 | 3.1774 | 3.2284 | 3.2795 | 3.3349 | 3.3902 | 3.4456 | 3.5009 | 3.5563 | 3.6117 | 3.667 | 3.7224 | 3.7777 | 3.8331 | 3.8884 | 3.9438 | 3.9992 | 4.0545 | 4.1099 | 4.3102 | 4.5104 | 4.7107 | 4.911 | 5.1113 | 5.3115 | 5.5118 | 5.7121 | 5.9124 | 6.1126 | 6.3129 | 6.5132 | 6.7135 | 6.9137 | 7.114 | 7.3143 | 7.5146 | 7.7148 | 7.9151 | 8.1154 | 8.3157 | 8.5159 | 8.7162 | 8.9165 | 9.1168 | 9.317 | 9.5173 | 9.7176 | 9.9179 | 10.1181 | 10.3003 | 10.4824 | 10.6646 | 10.8467 | 11.0288 | 11.211 | 11.3931 | 11.5753 | 11.7574 | 11.9395 | 12.1217 | 12.3038 | 12.486 | 12.6681 | 12.8503 | 13.0324 | 13.2145 | 13.3967 | 13.5788 | 13.761 | 13.9431 | 14.1252 | 14.3074 | 14.4895 | 14.6717 | 14.8538 | 15.036 | 15.2181 | 15.4002 | 15.5824 | 15.7283 | 15.8741 | 16.02 | 16.1659 | 16.3117 | 16.4576 | 16.6035 | 16.7494 | 16.8953 | 17.0411 | 17.187 | 17.3329 | 17.4787 | 17.6246 | 17.7705 | 17.9164 | 18.0622 | 18.2081 | 18.354 | 18.4999 | 18.6457 | 18.7916 | 18.9375 | 19.0834 | 19.2292 | 19.3751 | 19.521 | 19.6669 | 19.8127 | 19.9586 | 20.0655 | 20.1723 | 20.2792 | 20.386 | 20.4929 | 20.5997 | 20.7066 | 20.8134 | 20.9203 | 21.0271 | 21.134 | 21.2408 | 21.3477 | 21.4545 | 21.5614 | 21.6682 | 21.7751 | 21.8819 | 21.9888 | 22.0956 | 22.2025 | 22.3093 | 22.4162 | 22.523 | 22.6299 | 22.7367 | 22.8436 | 22.9504 | 23.0573 | 23.1641
7.2 | 0 | 2.85 | 2.765 | 2.658 | 2.558 | 3.336 | 4.179 | 10.275 | 15.819 | 20.259 | 23.513 | 2.2204e-16 | 0.285 | 0.57 | 0.855 | 1.14 | 1.425 | 1.71 | 1.995 | 2.28 | 2.565 | 2.85 | 2.833 | 2.816 | 2.799 | 2.782 | 2.765 | 2.7436 | 2.7222 | 2.7008 | 2.6794 | 2.658 | 2.648 | 2.638 | 2.628 | 2.618 | 2.608 | 2.598 | 2.588 | 2.578 | 2.568 | 2.558 | 2.6099 | 2.6617 | 2.7136 | 2.7655 | 2.8173 | 2.8692 | 2.9211 | 2.9729 | 3.0248 | 3.0767 | 3.1285 | 3.1804 | 3.2323 | 3.2841 | 3.336 | 3.3922 | 3.4484 | 3.5046 | 3.5608 | 3.617 | 3.6732 | 3.7294 | 3.7856 | 3.8418 | 3.898 | 3.9542 | 4.0104 | 4.0666 | 4.1228 | 4.179 | 4.3822 | 4.5854 | 4.7886 | 4.9918 | 5.195 | 5.3982 | 5.6014 | 5.8046 | 6.0078 | 6.211 | 6.4142 | 6.6174 | 6.8206 | 7.0238 | 7.227 | 7.4302 | 7.6334 | 7.8366 | 8.0398 | 8.243 | 8.4462 | 8.6494 | 8.8526 | 9.0558 | 9.259 | 9.4622 | 9.6654 | 9.8686 | 10.0718 | 10.275 | 10.4598 | 10.6446 | 10.8294 | 11.0142 | 11.199 | 11.3838 | 11.5686 | 11.7534 | 11.9382 | 12.123 | 12.3078 | 12.4926 | 12.6774 | 12.8622 | 13.047 | 13.2318 | 13.4166 | 13.6014 | 13.7862 | 13.971 | 14.1558 | 14.3406 | 14.5254 | 14.7102 | 14.895 | 15.0798 | 15.2646 | 15.4494 | 15.6342 | 15.819 | 15.967 | 16.115 | 16.263 | 16.411 | 16.559 | 16.707 | 16.855 | 17.003 | 17.151 | 17.299 | 17.447 | 17.595 | 17.743 | 17.891 | 18.039 | 18.187 | 18.335 | 18.483 | 18.631 | 18.779 | 18.927 | 19.075 | 19.223 | 19.371 | 19.519 | 19.667 | 19.815 | 19.963 | 20.111 | 20.259 | 20.3675 | 20.4759 | 20.5844 | 20.6929 | 20.8013 | 20.9098 | 21.0183 | 21.1267 | 21.2352 | 21.3437 | 21.4521 | 21.5606 | 21.6691 | 21.7775 | 21.886 | 21.9945 | 22.1029 | 22.2114 | 22.3199 | 22.4283 | 22.5368 | 22.6453 | 22.7537 | 22.8622 | 22.9707 | 23.0791 | 23.1876 | 23.2961 | 23.4045 | 23.513
7.25 | 0 | 2.89 | 2.8106 | 2.7025 | 2.6025 | 3.3925 | 4.2481 | 10.4319 | 16.0556 | 20.5594 | 23.8619 | -2.2204e-16 | 0.289 | 0.578 | 0.867 | 1.156 | 1.445 | 1.734 | 2.023 | 2.312 | 2.601 | 2.89 | 2.8741 | 2.8583 | 2.8424 | 2.8265 | 2.8106 | 2.789 | 2.7674 | 2.7457 | 2.7241 | 2.7025 | 2.6925 | 2.6825 | 2.6725 | 2.6625 | 2.6525 | 2.6425 | 2.6325 | 2.6225 | 2.6125 | 2.6025 | 2.6552 | 2.7078 | 2.7605 | 2.8132 | 2.8658 | 2.9185 | 2.9712 | 3.0238 | 3.0765 | 3.1292 | 3.1818 | 3.2345 | 3.2872 | 3.3398 | 3.3925 | 3.4495 | 3.5066 | 3.5636 | 3.6207 | 3.6777 | 3.7348 | 3.7918 | 3.8488 | 3.9059 | 3.9629 | 4.02 | 4.077 | 4.134 | 4.1911 | 4.2481 | 4.4542 | 4.6604 | 4.8665 | 5.0726 | 5.2787 | 5.4849 | 5.691 | 5.8971 | 6.1032 | 6.3094 | 6.5155 | 6.7216 | 6.9277 | 7.1339 | 7.34 | 7.5461 | 7.7523 | 7.9584 | 8.1645 | 8.3706 | 8.5768 | 8.7829 | 8.989 | 9.1951 | 9.4013 | 9.6074 | 9.8135 | 10.0196 | 10.2258 | 10.4319 | 10.6193 | 10.8068 | 10.9943 | 11.1817 | 11.3692 | 11.5566 | 11.7441 | 11.9315 | 12.119 | 12.3065 | 12.4939 | 12.6814 | 12.8688 | 13.0563 | 13.2438 | 13.4312 | 13.6187 | 13.8061 | 13.9936 | 14.181 | 14.3685 | 14.556 | 14.7434 | 14.9309 | 15.1183 | 15.3058 | 15.4933 | 15.6807 | 15.8682 | 16.0556 | 16.2058 | 16.3559 | 16.506 | 16.6561 | 16.8063 | 16.9564 | 17.1065 | 17.2566 | 17.4067 | 17.5569 | 17.707 | 17.8571 | 18.0072 | 18.1574 | 18.3075 | 18.4576 | 18.6077 | 18.7579 | 18.908 | 19.0581 | 19.2082 | 19.3584 | 19.5085 | 19.6586 | 19.8087 | 19.9589 | 20.109 | 20.2591 | 20.4092 | 20.5594 | 20.6695 | 20.7795 | 20.8896 | 20.9997 | 21.1098 | 21.2199 | 21.33 | 21.44 | 21.5501 | 21.6602 | 21.7703 | 21.8804 | 21.9905 | 22.1005 | 22.2106 | 22.3207 | 22.4308 | 22.5409 | 22.651 | 22.761 | 22.8711 | 22.9812 | 23.0913 | 23.2014 | 23.3115 | 23.4215 | 23.5316 | 23.6417 | 23.7518 | 23.8619
7.3 | 0 | 2.93 | 2.8563 | 2.747 | 2.647 | 3.449 | 4.3172 | 10.5888 | 16.2922 | 20.8597 | 24.2107 | 0 | 0.293 | 0.586 | 0.879 | 1.172 | 1.465 | 1.758 | 2.051 | 2.344 | 2.637 | 2.93 | 2.9152 | 2.9005 | 2.8857 | 2.871 | 2.8563 | 2.8344 | 2.8125 | 2.7907 | 2.7689 | 2.747 | 2.737 | 2.727 | 2.717 | 2.707 | 2.697 | 2.687 | 2.677 | 2.667 | 2.657 | 2.647 | 2.7005 | 2.7539 | 2.8074 | 2.8609 | 2.9143 | 2.9678 | 3.0213 | 3.0747 | 3.1282 | 3.1817 | 3.2351 | 3.2886 | 3.3421 | 3.3955 | 3.449 | 3.5069 | 3.5648 | 3.6226 | 3.6805 | 3.7384 | 3.7963 | 3.8542 | 3.9121 | 3.9699 | 4.0278 | 4.0857 | 4.1436 | 4.2015 | 4.2594 | 4.3173 | 4.5263 | 4.7354 | 4.9444 | 5.1535 | 5.3625 | 5.5716 | 5.7806 | 5.9897 | 6.1987 | 6.4078 | 6.6168 | 6.8259 | 7.0349 | 7.244 | 7.453 | 7.6621 | 7.8711 | 8.0802 | 8.2892 | 8.4983 | 8.7073 | 8.9164 | 9.1254 | 9.3345 | 9.5435 | 9.7526 | 9.9616 | 10.1707 | 10.3797 | 10.5888 | 10.7789 | 10.969 | 11.1591 | 11.3492 | 11.5393 | 11.7294 | 11.9196 | 12.1097 | 12.2998 | 12.4899 | 12.68 | 12.8701 | 13.0603 | 13.2504 | 13.4405 | 13.6306 | 13.8207 | 14.0108 | 14.201 | 14.3911 | 14.5812 | 14.7713 | 14.9614 | 15.1515 | 15.3417 | 15.5318 | 15.7219 | 15.912 | 16.1021 | 16.2922 | 16.4445 | 16.5968 | 16.749 | 16.9013 | 17.0535 | 17.2057 | 17.358 | 17.5102 | 17.6625 | 17.8148 | 17.967 | 18.1192 | 18.2715 | 18.4237 | 18.576 | 18.7282 | 18.8805 | 19.0328 | 19.185 | 19.3372 | 19.4895 | 19.6417 | 19.794 | 19.9462 | 20.0985 | 20.2508 | 20.403 | 20.5552 | 20.7075 | 20.8597 | 20.9714 | 21.0831 | 21.1948 | 21.3065 | 21.4182 | 21.5299 | 21.6416 | 21.7533 | 21.865 | 21.9767 | 22.0884 | 22.2001 | 22.3118 | 22.4235 | 22.5352 | 22.6469 | 22.7586 | 22.8703 | 22.982 | 23.0937 | 23.2054 | 23.3171 | 23.4288 | 23.5405 | 23.6522 | 23.7639 | 23.8756 | 23.9873 | 24.099 | 24.2107
7.35 | 0 | 2.97 | 2.9019 | 2.7915 | 2.6915 | 3.5055 | 4.3864 | 10.7456 | 16.5289 | 21.1601 | 24.5596 | 0 | 0.297 | 0.594 | 0.891 | 1.188 | 1.485 | 1.782 | 2.079 | 2.376 | 2.673 | 2.97 | 2.9564 | 2.9427 | 2.9291 | 2.9155 | 2.9019 | 2.8798 | 2.8577 | 2.8356 | 2.8136 | 2.7915 | 2.7815 | 2.7715 | 2.7615 | 2.7515 | 2.7415 | 2.7315 | 2.7215 | 2.7115 | 2.7015 | 2.6915 | 2.7458 | 2.8 | 2.8543 | 2.9086 | 2.9628 | 3.0171 | 3.0714 | 3.1256 | 3.1799 | 3.2342 | 3.2884 | 3.3427 | 3.397 | 3.4512 | 3.5055 | 3.5642 | 3.6229 | 3.6817 | 3.7404 | 3.7991 | 3.8578 | 3.9166 | 3.9753 | 4.034 | 4.0927 | 4.1515 | 4.2102 | 4.2689 | 4.3276 | 4.3864 | 4.5983 | 4.8103 | 5.0223 | 5.2343 | 5.4463 | 5.6582 | 5.8702 | 6.0822 | 6.2942 | 6.5061 | 6.7181 | 6.9301 | 7.1421 | 7.354 | 7.566 | 7.778 | 7.99 | 8.2019 | 8.4139 | 8.6259 | 8.8378 | 9.0498 | 9.2618 | 9.4738 | 9.6858 | 9.8977 | 10.1097 | 10.3217 | 10.5337 | 10.7456 | 10.9384 | 11.1312 | 11.3239 | 11.5167 | 11.7095 | 11.9023 | 12.095 | 12.2878 | 12.4806 | 12.6734 | 12.8661 | 13.0589 | 13.2517 | 13.4445 | 13.6372 | 13.83 | 14.0228 | 14.2156 | 14.4083 | 14.6011 | 14.7939 | 14.9867 | 15.1794 | 15.3722 | 15.565 | 15.7578 | 15.9505 | 16.1433 | 16.3361 | 16.5289 | 16.6833 | 16.8376 | 16.992 | 17.1464 | 17.3008 | 17.4551 | 17.6095 | 17.7639 | 17.9183 | 18.0726 | 18.227 | 18.3814 | 18.5358 | 18.6901 | 18.8445 | 18.9989 | 19.1532 | 19.3076 | 19.462 | 19.6164 | 19.7707 | 19.9251 | 20.0795 | 20.2339 | 20.3882 | 20.5426 | 20.697 | 20.8514 | 21.0057 | 21.1601 | 21.2734 | 21.3868 | 21.5001 | 21.6134 | 21.7267 | 21.84 | 21.9533 | 22.0667 | 22.18 | 22.2933 | 22.4066 | 22.5199 | 22.6332 | 22.7466 | 22.8599 | 22.9732 | 23.0865 | 23.1998 | 23.3131 | 23.4265 | 23.5398 | 23.6531 | 23.7664 | 23.8797 | 23.993 | 24.1064 | 24.2197 | 24.333 | 24.4463 | 24.5596
7.4 | 0 | 3.01 | 2.9475 | 2.836 | 2.736 | 3.562 | 4.4555 | 10.9025 | 16.7655 | 21.4605 | 24.9085 | 2.2204e-16 | 0.301 | 0.602 | 0.903 | 1.204 | 1.505 | 1.806 | 2.107 | 2.408 | 2.709 | 3.01 | 2.9975 | 2.985 | 2.9725 | 2.96 | 2.9475 | 2.9252 | 2.9029 | 2.8806 | 2.8583 | 2.836 | 2.826 | 2.816 | 2.806 | 2.796 | 2.786 | 2.776 | 2.766 | 2.756 | 2.746 | 2.736 | 2.7911 | 2.8461 | 2.9012 | 2.9563 | 3.0113 | 3.0664 | 3.1215 | 3.1765 | 3.2316 | 3.2867 | 3.3417 | 3.3968 | 3.4519 | 3.5069 | 3.562 | 3.6216 | 3.6811 | 3.7407 | 3.8003 | 3.8598 | 3.9194 | 3.979 | 4.0385 | 4.0981 | 4.1577 | 4.2172 | 4.2768 | 4.3364 | 4.3959 | 4.4555 | 4.6704 | 4.8853 | 5.1002 | 5.3151 | 5.53 | 5.7449 | 5.9598 | 6.1747 | 6.3896 | 6.6045 | 6.8194 | 7.0343 | 7.2492 | 7.4641 | 7.679 | 7.8939 | 8.1088 | 8.3237 | 8.5386 | 8.7535 | 8.9684 | 9.1833 | 9.3982 | 9.6131 | 9.828 | 10.0429 | 10.2578 | 10.4727 | 10.6876 | 10.9025 | 11.0979 | 11.2934 | 11.4888 | 11.6842 | 11.8797 | 12.0751 | 12.2705 | 12.466 | 12.6614 | 12.8568 | 13.0523 | 13.2477 | 13.4431 | 13.6386 | 13.834 | 14.0294 | 14.2249 | 14.4203 | 14.6157 | 14.8112 | 15.0066 | 15.202 | 15.3975 | 15.5929 | 15.7883 | 15.9838 | 16.1792 | 16.3746 | 16.5701 | 16.7655 | 16.922 | 17.0785 | 17.235 | 17.3915 | 17.548 | 17.7045 | 17.861 | 18.0175 | 18.174 | 18.3305 | 18.487 | 18.6435 | 18.8 | 18.9565 | 19.113 | 19.2695 | 19.426 | 19.5825 | 19.739 | 19.8955 | 20.052 | 20.2085 | 20.365 | 20.5215 | 20.678 | 20.8345 | 20.991 | 21.1475 | 21.304 | 21.4605 | 21.5754 | 21.6904 | 21.8053 | 21.9202 | 22.0352 | 22.1501 | 22.265 | 22.38 | 22.4949 | 22.6098 | 22.7248 | 22.8397 | 22.9546 | 23.0696 | 23.1845 | 23.2994 | 23.4144 | 23.5293 | 23.6442 | 23.7592 | 23.8741 | 23.989 | 24.104 | 24.2189 | 24.3338 | 24.4488 | 24.5637 | 24.6786 | 24.7936 | 24.9085
7.45 | 0 | 3.05 | 2.9931 | 2.8805 | 2.7805 | 3.6185 | 4.5246 | 11.0594 | 17.0021 | 21.7609 | 25.2574 | -2.2204e-16 | 0.305 | 0.61 | 0.915 | 1.22 | 1.525 | 1.83 | 2.135 | 2.44 | 2.745 | 3.05 | 3.0386 | 3.0272 | 3.0159 | 3.0045 | 2.9931 | 2.9706 | 2.9481 | 2.9256 | 2.903 | 2.8805 | 2.8705 | 2.8605 | 2.8505 | 2.8405 | 2.8305 | 2.8205 | 2.8105 | 2.8005 | 2.7905 | 2.7805 | 2.8364 | 2.8922 | 2.9481 | 3.004 | 3.0598 | 3.1157 | 3.1716 | 3.2274 | 3.2833 | 3.3392 | 3.395 | 3.4509 | 3.5068 | 3.5626 | 3.6185 | 3.6789 | 3.7393 | 3.7997 | 3.8601 | 3.9205 | 3.981 | 4.0414 | 4.1018 | 4.1622 | 4.2226 | 4.283 | 4.3434 | 4.4038 | 4.4642 | 4.5246 | 4.7425 | 4.9603 | 5.1781 | 5.3959 | 5.6138 | 5.8316 | 6.0494 | 6.2672 | 6.4851 | 6.7029 | 6.9207 | 7.1385 | 7.3564 | 7.5742 | 7.792 | 8.0098 | 8.2277 | 8.4455 | 8.6633 | 8.8811 | 9.099 | 9.3168 | 9.5346 | 9.7524 | 9.9703 | 10.1881 | 10.4059 | 10.6237 | 10.8415 | 11.0594 | 11.2575 | 11.4556 | 11.6537 | 11.8517 | 12.0498 | 12.2479 | 12.446 | 12.6441 | 12.8422 | 13.0403 | 13.2384 | 13.4365 | 13.6346 | 13.8327 | 14.0308 | 14.2288 | 14.4269 | 14.625 | 14.8231 | 15.0212 | 15.2193 | 15.4174 | 15.6155 | 15.8136 | 16.0117 | 16.2098 | 16.4079 | 16.6059 | 16.804 | 17.0021 | 17.1608 | 17.3194 | 17.478 | 17.6366 | 17.7953 | 17.9539 | 18.1125 | 18.2711 | 18.4298 | 18.5884 | 18.747 | 18.9056 | 19.0643 | 19.2229 | 19.3815 | 19.5401 | 19.6988 | 19.8574 | 20.016 | 20.1746 | 20.3333 | 20.4919 | 20.6505 | 20.8091 | 20.9678 | 21.1264 | 21.285 | 21.4436 | 21.6023 | 21.7609 | 21.8774 | 21.994 | 22.1105 | 22.2271 | 22.3436 | 22.4602 | 22.5767 | 22.6933 | 22.8098 | 22.9264 | 23.0429 | 23.1595 | 23.276 | 23.3926 | 23.5091 | 23.6257 | 23.7422 | 23.8588 | 23.9753 | 24.0919 | 24.2084 | 24.325 | 24.4415 | 24.5581 | 24.6746 | 24.7912 | 24.9077 | 25.0243 | 25.1408 | 25.2574
7.5 | 0 | 3.09 | 3.0388 | 2.925 | 2.825 | 3.675 | 4.5938 | 11.2162 | 17.2387 | 22.0613 | 25.6063 | 0 | 0.309 | 0.618 | 0.927 | 1.236 | 1.545 | 1.854 | 2.163 | 2.472 | 2.781 | 3.09 | 3.0798 | 3.0695 | 3.0593 | 3.049 | 3.0388 | 3.016 | 2.9933 | 2.9705 | 2.9478 | 2.925 | 2.915 | 2.905 | 2.895 | 2.885 | 2.875 | 2.865 | 2.855 | 2.845 | 2.835 | 2.825 | 2.8817 | 2.9383 | 2.995 | 3.0517 | 3.1083 | 3.165 | 3.2217 | 3.2783 | 3.335 | 3.3917 | 3.4483 | 3.505 | 3.5617 | 3.6183 | 3.675 | 3.7363 | 3.7975 | 3.8588 | 3.92 | 3.9813 | 4.0425 | 4.1037 | 4.165 | 4.2263 | 4.2875 | 4.3487 | 4.41 | 4.4712 | 4.5325 | 4.5938 | 4.8145 | 5.0353 | 5.256 | 5.4768 | 5.6975 | 5.9183 | 6.139 | 6.3598 | 6.5805 | 6.8013 | 7.022 | 7.2428 | 7.4635 | 7.6843 | 7.905 | 8.1258 | 8.3465 | 8.5672 | 8.788 | 9.0088 | 9.2295 | 9.4502 | 9.671 | 9.8918 | 10.1125 | 10.3333 | 10.554 | 10.7747 | 10.9955 | 11.2162 | 11.417 | 11.6177 | 11.8185 | 12.0192 | 12.22 | 12.4207 | 12.6215 | 12.8222 | 13.023 | 13.2237 | 13.4245 | 13.6252 | 13.826 | 14.0267 | 14.2275 | 14.4282 | 14.629 | 14.8297 | 15.0305 | 15.2312 | 15.432 | 15.6327 | 15.8335 | 16.0342 | 16.235 | 16.4357 | 16.6365 | 16.8372 | 17.038 | 17.2387 | 17.3995 | 17.5602 | 17.721 | 17.8817 | 18.0425 | 18.2032 | 18.364 | 18.5247 | 18.6855 | 18.8462 | 19.007 | 19.1677 | 19.3285 | 19.4892 | 19.65 | 19.8107 | 19.9715 | 20.1322 | 20.293 | 20.4537 | 20.6145 | 20.7752 | 20.936 | 21.0968 | 21.2575 | 21.4183 | 21.579 | 21.7398 | 21.9005 | 22.0613 | 22.1794 | 22.2976 | 22.4158 | 22.5339 | 22.6521 | 22.7703 | 22.8884 | 23.0066 | 23.1248 | 23.2429 | 23.3611 | 23.4793 | 23.5974 | 23.7156 | 23.8338 | 23.9519 | 24.0701 | 24.1883 | 24.3064 | 24.4246 | 24.5428 | 24.6609 | 24.7791 | 24.8973 | 25.0154 | 25.1336 | 25.2518 | 25.3699 | 25.4881 | 25.6062
7.55 | 0 | 3.13 | 3.0844 | 2.9695 | 2.8695 | 3.7315 | 4.6629 | 11.3731 | 17.4754 | 22.3616 | 25.9551 | 0 | 0.313 | 0.626 | 0.939 | 1.252 | 1.565 | 1.878 | 2.191 | 2.504 | 2.817 | 3.13 | 3.1209 | 3.1117 | 3.1026 | 3.0935 | 3.0844 | 3.0614 | 3.0384 | 3.0154 | 2.9925 | 2.9695 | 2.9595 | 2.9495 | 2.9395 | 2.9295 | 2.9195 | 2.9095 | 2.8995 | 2.8895 | 2.8795 | 2.8695 | 2.927 | 2.9844 | 3.0419 | 3.0994 | 3.1568 | 3.2143 | 3.2718 | 3.3292 | 3.3867 | 3.4442 | 3.5016 | 3.5591 | 3.6166 | 3.674 | 3.7315 | 3.7936 | 3.8557 | 3.9178 | 3.9799 | 4.042 | 4.1041 | 4.1661 | 4.2282 | 4.2903 | 4.3524 | 4.4145 | 4.4766 | 4.5387 | 4.6008 | 4.6629 | 4.8865 | 5.1102 | 5.3339 | 5.5576 | 5.7812 | 6.0049 | 6.2286 | 6.4523 | 6.676 | 6.8996 | 7.1233 | 7.347 | 7.5706 | 7.7943 | 8.018 | 8.2417 | 8.4653 | 8.689 | 8.9127 | 9.1364 | 9.36 | 9.5837 | 9.8074 | 10.0311 | 10.2547 | 10.4784 | 10.7021 | 10.9258 | 11.1494 | 11.3731 | 11.5765 | 11.7799 | 11.9833 | 12.1868 | 12.3902 | 12.5936 | 12.797 | 13.0004 | 13.2038 | 13.4072 | 13.6106 | 13.814 | 14.0174 | 14.2208 | 14.4242 | 14.6277 | 14.8311 | 15.0345 | 15.2379 | 15.4413 | 15.6447 | 15.8481 | 16.0515 | 16.2549 | 16.4583 | 16.6617 | 16.8651 | 17.0686 | 17.272 | 17.4754 | 17.6382 | 17.8011 | 17.964 | 18.1269 | 18.2897 | 18.4526 | 18.6155 | 18.7784 | 18.9412 | 19.1041 | 19.267 | 19.4299 | 19.5927 | 19.7556 | 19.9185 | 20.0814 | 20.2442 | 20.4071 | 20.57 | 20.7329 | 20.8957 | 21.0586 | 21.2215 | 21.3844 | 21.5472 | 21.7101 | 21.873 | 22.0359 | 22.1987 | 22.3616 | 22.4814 | 22.6012 | 22.721 | 22.8408 | 22.9605 | 23.0803 | 23.2001 | 23.3199 | 23.4397 | 23.5595 | 23.6792 | 23.799 | 23.9188 | 24.0386 | 24.1584 | 24.2782 | 24.3979 | 24.5177 | 24.6375 | 24.7573 | 24.8771 | 24.9969 | 25.1166 | 25.2364 | 25.3562 | 25.476 | 25.5958 | 25.7156 | 25.8353 | 25.9551
7.6 | 0 | 3.17 | 3.13 | 3.014 | 2.914 | 3.788 | 4.732 | 11.53 | 17.712 | 22.662 | 26.304 | 0 | 0.317 | 0.634 | 0.951 | 1.268 | 1.585 | 1.902 | 2.219 | 2.536 | 2.853 | 3.17 | 3.162 | 3.154 | 3.146 | 3.138 | 3.13 | 3.1068 | 3.0836 | 3.0604 | 3.0372 | 3.014 | 3.004 | 2.994 | 2.984 | 2.974 | 2.964 | 2.954 | 2.944 | 2.934 | 2.924 | 2.914 | 2.9723 | 3.0305 | 3.0888 | 3.1471 | 3.2053 | 3.2636 | 3.3219 | 3.3801 | 3.4384 | 3.4967 | 3.5549 | 3.6132 | 3.6715 | 3.7297 | 3.788 | 3.8509 | 3.9139 | 3.9768 | 4.0397 | 4.1027 | 4.1656 | 4.2285 | 4.2915 | 4.3544 | 4.4173 | 4.4803 | 4.5432 | 4.6061 | 4.6691 | 4.732 | 4.9586 | 5.1852 | 5.4118 | 5.6384 | 5.865 | 6.0916 | 6.3182 | 6.5448 | 6.7714 | 6.998 | 7.2246 | 7.4512 | 7.6778 | 7.9044 | 8.131 | 8.3576 | 8.5842 | 8.8108 | 9.0374 | 9.264 | 9.4906 | 9.7172 | 9.9438 | 10.1704 | 10.397 | 10.6236 | 10.8502 | 11.0768 | 11.3034 | 11.53 | 11.7361 | 11.9421 | 12.1482 | 12.3543 | 12.5603 | 12.7664 | 12.9725 | 13.1785 | 13.3846 | 13.5907 | 13.7967 | 14.0028 | 14.2089 | 14.4149 | 14.621 | 14.8271 | 15.0331 | 15.2392 | 15.4453 | 15.6513 | 15.8574 | 16.0635 | 16.2695 | 16.4756 | 16.6817 | 16.8877 | 17.0938 | 17.2999 | 17.5059 | 17.712 | 17.877 | 18.042 | 18.207 | 18.372 | 18.537 | 18.702 | 18.867 | 19.032 | 19.197 | 19.362 | 19.527 | 19.692 | 19.857 | 20.022 | 20.187 | 20.352 | 20.517 | 20.682 | 20.847 | 21.012 | 21.177 | 21.342 | 21.507 | 21.672 | 21.837 | 22.002 | 22.167 | 22.332 | 22.497 | 22.662 | 22.7834 | 22.9048 | 23.0262 | 23.1476 | 23.269 | 23.3904 | 23.5118 | 23.6332 | 23.7546 | 23.876 | 23.9974 | 24.1188 | 24.2402 | 24.3616 | 24.483 | 24.6044 | 24.7258 | 24.8472 | 24.9686 | 25.09 | 25.2114 | 25.3328 | 25.4542 | 25.5756 | 25.697 | 25.8184 | 25.9398 | 26.0612 | 26.1826 | 26.304
7.65 | 0 | 3.21 | 3.1756 | 3.0585 | 2.9585 | 3.8445 | 4.8011 | 11.6869 | 17.9486 | 22.9624 | 26.6529 | 2.2204e-16 | 0.321 | 0.642 | 0.963 | 1.284 | 1.605 | 1.926 | 2.247 | 2.568 | 2.889 | 3.21 | 3.2031 | 3.1963 | 3.1894 | 3.1825 | 3.1756 | 3.1522 | 3.1288 | 3.1054 | 3.0819 | 3.0585 | 3.0485 | 3.0385 | 3.0285 | 3.0185 | 3.0085 | 2.9985 | 2.9885 | 2.9785 | 2.9685 | 2.9585 | 3.0176 | 3.0766 | 3.1357 | 3.1948 | 3.2538 | 3.3129 | 3.372 | 3.431 | 3.4901 | 3.5492 | 3.6082 | 3.6673 | 3.7264 | 3.7854 | 3.8445 | 3.9083 | 3.972 | 4.0358 | 4.0996 | 4.1634 | 4.2271 | 4.2909 | 4.3547 | 4.4185 | 4.4823 | 4.546 | 4.6098 | 4.6736 | 4.7374 | 4.8011 | 5.0307 | 5.2602 | 5.4897 | 5.7192 | 5.9488 | 6.1783 | 6.4078 | 6.6373 | 6.8669 | 7.0964 | 7.3259 | 7.5554 | 7.785 | 8.0145 | 8.244 | 8.4735 | 8.7031 | 8.9326 | 9.1621 | 9.3916 | 9.6212 | 9.8507 | 10.0802 | 10.3097 | 10.5393 | 10.7688 | 10.9983 | 11.2278 | 11.4574 | 11.6869 | 11.8956 | 12.1043 | 12.3131 | 12.5218 | 12.7305 | 12.9392 | 13.1479 | 13.3567 | 13.5654 | 13.7741 | 13.9829 | 14.1916 | 14.4003 | 14.609 | 14.8178 | 15.0265 | 15.2352 | 15.4439 | 15.6527 | 15.8614 | 16.0701 | 16.2788 | 16.4876 | 16.6963 | 16.905 | 17.1137 | 17.3225 | 17.5312 | 17.7399 | 17.9486 | 18.1157 | 18.2829 | 18.45 | 18.6171 | 18.7843 | 18.9514 | 19.1185 | 19.2856 | 19.4527 | 19.6199 | 19.787 | 19.9541 | 20.1212 | 20.2884 | 20.4555 | 20.6226 | 20.7897 | 20.9569 | 21.124 | 21.2911 | 21.4582 | 21.6254 | 21.7925 | 21.9596 | 22.1267 | 22.2939 | 22.461 | 22.6281 | 22.7952 | 22.9624 | 23.0854 | 23.2084 | 23.3314 | 23.4544 | 23.5775 | 23.7005 | 23.8235 | 23.9465 | 24.0695 | 24.1925 | 24.3156 | 24.4386 | 24.5616 | 24.6846 | 24.8076 | 24.9306 | 25.0537 | 25.1767 | 25.2997 | 25.4227 | 25.5457 | 25.6687 | 25.7918 | 25.9148 | 26.0378 | 26.1608 | 26.2838 | 26.4068 | 26.5299 | 26.6529
7.7 | 0 | 3.25 | 3.2213 | 3.103 | 3.003 | 3.901 | 4.8703 | 11.8438 | 18.1852 | 23.2627 | 27.0018 | 0 | 0.325 | 0.65 | 0.975 | 1.3 | 1.625 | 1.95 | 2.275 | 2.6 | 2.925 | 3.25 | 3.2442 | 3.2385 | 3.2327 | 3.227 | 3.2213 | 3.1976 | 3.174 | 3.1503 | 3.1267 | 3.103 | 3.093 | 3.083 | 3.073 | 3.063 | 3.053 | 3.043 | 3.033 | 3.023 | 3.013 | 3.003 | 3.0629 | 3.1227 | 3.1826 | 3.2425 | 3.3023 | 3.3622 | 3.4221 | 3.4819 | 3.5418 | 3.6017 | 3.6615 | 3.7214 | 3.7813 | 3.8411 | 3.901 | 3.9656 | 4.0302 | 4.0949 | 4.1595 | 4.2241 | 4.2887 | 4.3533 | 4.4179 | 4.4825 | 4.5472 | 4.6118 | 4.6764 | 4.741 | 4.8056 | 4.8702 | 5.1027 | 5.3351 | 5.5676 | 5.8 | 6.0325 | 6.2649 | 6.4974 | 6.7298 | 6.9623 | 7.1947 | 7.4272 | 7.6596 | 7.8921 | 8.1245 | 8.357 | 8.5894 | 8.8219 | 9.0543 | 9.2868 | 9.5192 | 9.7517 | 9.9841 | 10.2166 | 10.449 | 10.6815 | 10.9139 | 11.1464 | 11.3788 | 11.6113 | 11.8437 | 12.0551 | 12.2665 | 12.4779 | 12.6893 | 12.9007 | 13.112 | 13.3234 | 13.5348 | 13.7462 | 13.9576 | 14.169 | 14.3803 | 14.5917 | 14.8031 | 15.0145 | 15.2259 | 15.4373 | 15.6486 | 15.86 | 16.0714 | 16.2828 | 16.4942 | 16.7056 | 16.9169 | 17.1283 | 17.3397 | 17.5511 | 17.7625 | 17.9739 | 18.1852 | 18.3545 | 18.5237 | 18.693 | 18.8622 | 19.0315 | 19.2007 | 19.37 | 19.5392 | 19.7085 | 19.8777 | 20.047 | 20.2162 | 20.3855 | 20.5547 | 20.724 | 20.8932 | 21.0625 | 21.2317 | 21.401 | 21.5702 | 21.7395 | 21.9087 | 22.078 | 22.2472 | 22.4165 | 22.5857 | 22.755 | 22.9242 | 23.0935 | 23.2627 | 23.3874 | 23.512 | 23.6366 | 23.7613 | 23.8859 | 24.0105 | 24.1352 | 24.2598 | 24.3844 | 24.5091 | 24.6337 | 24.7583 | 24.883 | 25.0076 | 25.1322 | 25.2569 | 25.3815 | 25.5061 | 25.6308 | 25.7554 | 25.88 | 26.0047 | 26.1293 | 26.2539 | 26.3786 | 26.5032 | 26.6278 | 26.7525 | 26.8771 | 27.0017
7.75 | 0 | 3.29 | 3.2669 | 3.1475 | 3.0475 | 3.9575 | 4.9394 | 12.0006 | 18.4219 | 23.5631 | 27.3506 | 0 | 0.329 | 0.658 | 0.987 | 1.316 | 1.645 | 1.974 | 2.303 | 2.632 | 2.961 | 3.29 | 3.2854 | 3.2807 | 3.2761 | 3.2715 | 3.2669 | 3.243 | 3.2191 | 3.1952 | 3.1714 | 3.1475 | 3.1375 | 3.1275 | 3.1175 | 3.1075 | 3.0975 | 3.0875 | 3.0775 | 3.0675 | 3.0575 | 3.0475 | 3.1082 | 3.1688 | 3.2295 | 3.2902 | 3.3508 | 3.4115 | 3.4722 | 3.5328 | 3.5935 | 3.6542 | 3.7148 | 3.7755 | 3.8362 | 3.8968 | 3.9575 | 4.023 | 4.0884 | 4.1539 | 4.2193 | 4.2848 | 4.3502 | 4.4157 | 4.4812 | 4.5466 | 4.6121 | 4.6775 | 4.743 | 4.8085 | 4.8739 | 4.9394 | 5.1747 | 5.4101 | 5.6455 | 5.8809 | 6.1162 | 6.3516 | 6.587 | 6.8224 | 7.0577 | 7.2931 | 7.5285 | 7.7639 | 7.9992 | 8.2346 | 8.47 | 8.7054 | 8.9407 | 9.1761 | 9.4115 | 9.6469 | 9.8822 | 10.1176 | 10.353 | 10.5884 | 10.8237 | 11.0591 | 11.2945 | 11.5299 | 11.7652 | 12.0006 | 12.2147 | 12.4287 | 12.6428 | 12.8568 | 13.0708 | 13.2849 | 13.4989 | 13.713 | 13.927 | 14.141 | 14.3551 | 14.5691 | 14.7832 | 14.9972 | 15.2113 | 15.4253 | 15.6393 | 15.8534 | 16.0674 | 16.2815 | 16.4955 | 16.7095 | 16.9236 | 17.1376 | 17.3517 | 17.5657 | 17.7798 | 17.9938 | 18.2078 | 18.4219 | 18.5933 | 18.7646 | 18.936 | 19.1074 | 19.2788 | 19.4501 | 19.6215 | 19.7929 | 19.9643 | 20.1356 | 20.307 | 20.4784 | 20.6498 | 20.8211 | 20.9925 | 21.1639 | 21.3353 | 21.5066 | 21.678 | 21.8494 | 22.0207 | 22.1921 | 22.3635 | 22.5349 | 22.7063 | 22.8776 | 23.049 | 23.2204 | 23.3917 | 23.5631 | 23.6894 | 23.8156 | 23.9419 | 24.0681 | 24.1944 | 24.3206 | 24.4469 | 24.5731 | 24.6994 | 24.8256 | 24.9519 | 25.0781 | 25.2044 | 25.3306 | 25.4569 | 25.5831 | 25.7094 | 25.8356 | 25.9619 | 26.0881 | 26.2144 | 26.3406 | 26.4669 | 26.5931 | 26.7194 | 26.8456 | 26.9719 | 27.0981 | 27.2244 | 27.3506
7.8 | 0 | 3.33 | 3.3125 | 3.192 | 3.092 | 4.014 | 5.0085 | 12.1575 | 18.6585 | 23.8635 | 27.6995 | 0 | 0.333 | 0.666 | 0.999 | 1.332 | 1.665 | 1.998 | 2.331 | 2.664 | 2.997 | 3.33 | 3.3265 | 3.323 | 3.3195 | 3.316 | 3.3125 | 3.2884 | 3.2643 | 3.2402 | 3.2161 | 3.192 | 3.182 | 3.172 | 3.162 | 3.152 | 3.142 | 3.132 | 3.122 | 3.112 | 3.102 | 3.092 | 3.1535 | 3.2149 | 3.2764 | 3.3379 | 3.3993 | 3.4608 | 3.5223 | 3.5837 | 3.6452 | 3.7067 | 3.7681 | 3.8296 | 3.8911 | 3.9525 | 4.014 | 4.0803 | 4.1466 | 4.2129 | 4.2792 | 4.3455 | 4.4118 | 4.4781 | 4.5444 | 4.6107 | 4.677 | 4.7433 | 4.8096 | 4.8759 | 4.9422 | 5.0085 | 5.2468 | 5.4851 | 5.7234 | 5.9617 | 6.2 | 6.4383 | 6.6766 | 6.9149 | 7.1532 | 7.3915 | 7.6298 | 7.8681 | 8.1064 | 8.3447 | 8.583 | 8.8213 | 9.0596 | 9.2979 | 9.5362 | 9.7745 | 10.0128 | 10.2511 | 10.4894 | 10.7277 | 10.966 | 11.2043 | 11.4426 | 11.6809 | 11.9192 | 12.1575 | 12.3742 | 12.5909 | 12.8076 | 13.0243 | 13.241 | 13.4577 | 13.6744 | 13.8911 | 14.1078 | 14.3245 | 14.5412 | 14.7579 | 14.9746 | 15.1913 | 15.408 | 15.6247 | 15.8414 | 16.0581 | 16.2748 | 16.4915 | 16.7082 | 16.9249 | 17.1416 | 17.3583 | 17.575 | 17.7917 | 18.0084 | 18.2251 | 18.4418 | 18.6585 | 18.832 | 19.0055 | 19.179 | 19.3525 | 19.526 | 19.6995 | 19.873 | 20.0465 | 20.22 | 20.3935 | 20.567 | 20.7405 | 20.914 | 21.0875 | 21.261 | 21.4345 | 21.608 | 21.7815 | 21.955 | 22.1285 | 22.302 | 22.4755 | 22.649 | 22.8225 | 22.996 | 23.1695 | 23.343 | 23.5165 | 23.69 | 23.8635 | 23.9914 | 24.1192 | 24.2471 | 24.375 | 24.5028 | 24.6307 | 24.7586 | 24.8864 | 25.0143 | 25.1422 | 25.27 | 25.3979 | 25.5258 | 25.6536 | 25.7815 | 25.9094 | 26.0372 | 26.1651 | 26.293 | 26.4208 | 26.5487 | 26.6766 | 26.8044 | 26.9323 | 27.0602 | 27.188 | 27.3159 | 27.4438 | 27.5716 | 27.6995
7.85 | 0 | 3.37 | 3.3581 | 3.2365 | 3.1365 | 4.0705 | 5.0776 | 12.3144 | 18.8951 | 24.1639 | 28.0484 | 0 | 0.337 | 0.674 | 1.011 | 1.348 | 1.685 | 2.022 | 2.359 | 2.696 | 3.033 | 3.37 | 3.3676 | 3.3652 | 3.3629 | 3.3605 | 3.3581 | 3.3338 | 3.3095 | 3.2851 | 3.2608 | 3.2365 | 3.2265 | 3.2165 | 3.2065 | 3.1965 | 3.1865 | 3.1765 | 3.1665 | 3.1565 | 3.1465 | 3.1365 | 3.1988 | 3.261 | 3.3233 | 3.3856 | 3.4478 | 3.5101 | 3.5724 | 3.6346 | 3.6969 | 3.7592 | 3.8214 | 3.8837 | 3.946 | 4.0082 | 4.0705 | 4.1376 | 4.2048 | 4.2719 | 4.3391 | 4.4062 | 4.4733 | 4.5405 | 4.6076 | 4.6748 | 4.7419 | 4.8091 | 4.8762 | 4.9433 | 5.0105 | 5.0776 | 5.3188 | 5.5601 | 5.8013 | 6.0425 | 6.2837 | 6.525 | 6.7662 | 7.0074 | 7.2486 | 7.4899 | 7.7311 | 7.9723 | 8.2135 | 8.4548 | 8.696 | 8.9372 | 9.1784 | 9.4197 | 9.6609 | 9.9021 | 10.1433 | 10.3846 | 10.6258 | 10.867 | 11.1082 | 11.3495 | 11.5907 | 11.8319 | 12.0731 | 12.3144 | 12.5337 | 12.7531 | 12.9724 | 13.1918 | 13.4112 | 13.6305 | 13.8499 | 14.0692 | 14.2886 | 14.508 | 14.7273 | 14.9467 | 15.166 | 15.3854 | 15.6047 | 15.8241 | 16.0435 | 16.2628 | 16.4822 | 16.7015 | 16.9209 | 17.1403 | 17.3596 | 17.579 | 17.7983 | 18.0177 | 18.237 | 18.4564 | 18.6758 | 18.8951 | 19.0707 | 19.2464 | 19.422 | 19.5976 | 19.7732 | 19.9489 | 20.1245 | 20.3001 | 20.4757 | 20.6514 | 20.827 | 21.0026 | 21.1782 | 21.3539 | 21.5295 | 21.7051 | 21.8807 | 22.0564 | 22.232 | 22.4076 | 22.5832 | 22.7589 | 22.9345 | 23.1101 | 23.2857 | 23.4614 | 23.637 | 23.8126 | 23.9882 | 24.1639 | 24.2934 | 24.4228 | 24.5523 | 24.6818 | 24.8113 | 24.9408 | 25.0703 | 25.1997 | 25.3292 | 25.4587 | 25.5882 | 25.7177 | 25.8472 | 25.9766 | 26.1061 | 26.2356 | 26.3651 | 26.4946 | 26.6241 | 26.7535 | 26.883 | 27.0125 | 27.142 | 27.2715 | 27.401 | 27.5304 | 27.6599 | 27.7894 | 27.9189 | 28.0484
7.9 | 0 | 3.41 | 3.4038 | 3.281 | 3.181 | 4.127 | 5.1468 | 12.4713 | 19.1318 | 24.4643 | 28.3973 | -2.2204e-16 | 0.341 | 0.682 | 1.023 | 1.364 | 1.705 | 2.046 | 2.387 | 2.728 | 3.069 | 3.41 | 3.4088 | 3.4075 | 3.4063 | 3.405 | 3.4038 | 3.3792 | 3.3547 | 3.3301 | 3.3056 | 3.281 | 3.271 | 3.261 | 3.251 | 3.241 | 3.231 | 3.221 | 3.211 | 3.201 | 3.191 | 3.181 | 3.2441 | 3.3071 | 3.3702 | 3.4333 | 3.4963 | 3.5594 | 3.6225 | 3.6855 | 3.7486 | 3.8117 | 3.8747 | 3.9378 | 4.0009 | 4.0639 | 4.127 | 4.195 | 4.263 | 4.331 | 4.3989 | 4.4669 | 4.5349 | 4.6029 | 4.6709 | 4.7389 | 4.8068 | 4.8748 | 4.9428 | 5.0108 | 5.0788 | 5.1468 | 5.3909 | 5.6351 | 5.8792 | 6.1234 | 6.3675 | 6.6117 | 6.8558 | 7.1 | 7.3441 | 7.5883 | 7.8324 | 8.0766 | 8.3207 | 8.5649 | 8.809 | 9.0532 | 9.2973 | 9.5415 | 9.7856 | 10.0298 | 10.2739 | 10.5181 | 10.7622 | 11.0064 | 11.2505 | 11.4947 | 11.7388 | 11.983 | 12.2271 | 12.4713 | 12.6933 | 12.9153 | 13.1373 | 13.3593 | 13.5813 | 13.8034 | 14.0254 | 14.2474 | 14.4694 | 14.6914 | 14.9134 | 15.1355 | 15.3575 | 15.5795 | 15.8015 | 16.0235 | 16.2455 | 16.4676 | 16.6896 | 16.9116 | 17.1336 | 17.3556 | 17.5776 | 17.7997 | 18.0217 | 18.2437 | 18.4657 | 18.6877 | 18.9097 | 19.1318 | 19.3095 | 19.4873 | 19.665 | 19.8428 | 20.0205 | 20.1983 | 20.376 | 20.5538 | 20.7315 | 20.9093 | 21.087 | 21.2648 | 21.4425 | 21.6203 | 21.798 | 21.9758 | 22.1535 | 22.3313 | 22.509 | 22.6868 | 22.8645 | 23.0423 | 23.22 | 23.3978 | 23.5755 | 23.7533 | 23.931 | 24.1088 | 24.2865 | 24.4643 | 24.5954 | 24.7265 | 24.8576 | 24.9887 | 25.1198 | 25.2509 | 25.382 | 25.5131 | 25.6442 | 25.7753 | 25.9064 | 26.0375 | 26.1686 | 26.2997 | 26.4308 | 26.5619 | 26.693 | 26.8241 | 26.9552 | 27.0863 | 27.2174 | 27.3485 | 27.4796 | 27.6107 | 27.7418 | 27.8729 | 28.004 | 28.1351 | 28.2662 | 28.3972
7.95 | 0 | 3.45 | 3.4494 | 3.3255 | 3.2255 | 4.1835 | 5.2159 | 12.6281 | 19.3684 | 24.7646 | 28.7461 | -2.2204e-16 | 0.345 | 0.69 | 1.035 | 1.38 | 1.725 | 2.07 | 2.415 | 2.76 | 3.105 | 3.45 | 3.4499 | 3.4498 | 3.4496 | 3.4495 | 3.4494 | 3.4246 | 3.3998 | 3.3751 | 3.3503 | 3.3255 | 3.3155 | 3.3055 | 3.2955 | 3.2855 | 3.2755 | 3.2655 | 3.2555 | 3.2455 | 3.2355 | 3.2255 | 3.2894 | 3.3532 | 3.4171 | 3.481 | 3.5448 | 3.6087 | 3.6726 | 3.7364 | 3.8003 | 3.8642 | 3.928 | 3.9919 | 4.0558 | 4.1196 | 4.1835 | 4.2523 | 4.3212 | 4.39 | 4.4588 | 4.5276 | 4.5965 | 4.6653 | 4.7341 | 4.8029 | 4.8718 | 4.9406 | 5.0094 | 5.0782 | 5.1471 | 5.2159 | 5.463 | 5.71 | 5.9571 | 6.2042 | 6.4513 | 6.6983 | 6.9454 | 7.1925 | 7.4396 | 7.6866 | 7.9337 | 8.1808 | 8.4279 | 8.6749 | 8.922 | 9.1691 | 9.4162 | 9.6632 | 9.9103 | 10.1574 | 10.4045 | 10.6515 | 10.8986 | 11.1457 | 11.3928 | 11.6398 | 11.8869 | 12.134 | 12.3811 | 12.6281 | 12.8528 | 13.0775 | 13.3022 | 13.5268 | 13.7515 | 13.9762 | 14.2009 | 14.4255 | 14.6502 | 14.8749 | 15.0996 | 15.3242 | 15.5489 | 15.7736 | 15.9983 | 16.2229 | 16.4476 | 16.6723 | 16.897 | 17.1216 | 17.3463 | 17.571 | 17.7957 | 18.0203 | 18.245 | 18.4697 | 18.6944 | 18.919 | 19.1437 | 19.3684 | 19.5483 | 19.7281 | 19.908 | 20.0879 | 20.2678 | 20.4476 | 20.6275 | 20.8074 | 20.9873 | 21.1671 | 21.347 | 21.5269 | 21.7068 | 21.8866 | 22.0665 | 22.2464 | 22.4263 | 22.6061 | 22.786 | 22.9659 | 23.1458 | 23.3256 | 23.5055 | 23.6854 | 23.8653 | 24.0451 | 24.225 | 24.4049 | 24.5848 | 24.7646 | 24.8973 | 25.0301 | 25.1628 | 25.2955 | 25.4282 | 25.5609 | 25.6936 | 25.8264 | 25.9591 | 26.0918 | 26.2245 | 26.3572 | 26.4899 | 26.6227 | 26.7554 | 26.8881 | 27.0208 | 27.1535 | 27.2862 | 27.419 | 27.5517 | 27.6844 | 27.8171 | 27.9498 | 28.0825 | 28.2153 | 28.348 | 28.4807 | 28.6134 | 28.7461
8 | 0 | 3.49 | 3.495 | 3.37 | 3.27 | 4.24 | 5.285 | 12.785 | 19.605 | 25.065 | 29.095 | 0 | 0.349 | 0.698 | 1.047 | 1.396 | 1.745 | 2.094 | 2.443 | 2.792 | 3.141 | 3.49 | 3.491 | 3.492 | 3.493 | 3.494 | 3.495 | 3.47 | 3.445 | 3.42 | 3.395 | 3.37 | 3.36 | 3.35 | 3.34 | 3.33 | 3.32 | 3.31 | 3.3 | 3.29 | 3.28 | 3.27 | 3.3347 | 3.3993 | 3.464 | 3.5287 | 3.5933 | 3.658 | 3.7227 | 3.7873 | 3.852 | 3.9167 | 3.9813 | 4.046 | 4.1107 | 4.1753 | 4.24 | 4.3097 | 4.3793 | 4.449 | 4.5187 | 4.5883 | 4.658 | 4.7277 | 4.7973 | 4.867 | 4.9367 | 5.0063 | 5.076 | 5.1457 | 5.2153 | 5.285 | 5.535 | 5.785 | 6.035 | 6.285 | 6.535 | 6.785 | 7.035 | 7.285 | 7.535 | 7.785 | 8.035 | 8.285 | 8.535 | 8.785 | 9.035 | 9.285 | 9.535 | 9.785 | 10.035 | 10.285 | 10.535 | 10.785 | 11.035 | 11.285 | 11.535 | 11.785 | 12.035 | 12.285 | 12.535 | 12.785 | 13.0123 | 13.2397 | 13.467 | 13.6943 | 13.9217 | 14.149 | 14.3763 | 14.6037 | 14.831 | 15.0583 | 15.2857 | 15.513 | 15.7403 | 15.9677 | 16.195 | 16.4223 | 16.6497 | 16.877 | 17.1043 | 17.3317 | 17.559 | 17.7863 | 18.0137 | 18.241 | 18.4683 | 18.6957 | 18.923 | 19.1503 | 19.3777 | 19.605 | 19.787 | 19.969 | 20.151 | 20.333 | 20.515 | 20.697 | 20.879 | 21.061 | 21.243 | 21.425 | 21.607 | 21.789 | 21.971 | 22.153 | 22.335 | 22.517 | 22.699 | 22.881 | 23.063 | 23.245 | 23.427 | 23.609 | 23.791 | 23.973 | 24.155 | 24.337 | 24.519 | 24.701 | 24.883 | 25.065 | 25.1993 | 25.3337 | 25.468 | 25.6023 | 25.7367 | 25.871 | 26.0053 | 26.1397 | 26.274 | 26.4083 | 26.5427 | 26.677 | 26.8113 | 26.9457 | 27.08 | 27.2143 | 27.3487 | 27.483 | 27.6173 | 27.7517 | 27.886 | 28.0203 | 28.1547 | 28.289 | 28.4233 | 28.5577 | 28.692 | 28.8263 | 28.9607 | 29.095
8.05 | 0 | 3.53 | 3.5406 | 3.4145 | 3.3145 | 4.2965 | 5.3541 | 12.9419 | 19.8416 | 25.3654 | 29.4439 | 2.2204e-16 | 0.353 | 0.706 | 1.059 | 1.412 | 1.765 | 2.118 | 2.471 | 2.824 | 3.177 | 3.53 | 3.5321 | 3.5343 | 3.5364 | 3.5385 | 3.5406 | 3.5154 | 3.4902 | 3.465 | 3.4397 | 3.4145 | 3.4045 | 3.3945 | 3.3845 | 3.3745 | 3.3645 | 3.3545 | 3.3445 | 3.3345 | 3.3245 | 3.3145 | 3.38 | 3.4454 | 3.5109 | 3.5764 | 3.6418 | 3.7073 | 3.7728 | 3.8382 | 3.9037 | 3.9692 | 4.0346 | 4.1001 | 4.1656 | 4.231 | 4.2965 | 4.367 | 4.4375 | 4.508 | 4.5785 | 4.649 | 4.7196 | 4.7901 | 4.8606 | 4.9311 | 5.0016 | 5.0721 | 5.1426 | 5.2131 | 5.2836 | 5.3541 | 5.6071 | 5.86 | 6.1129 | 6.3658 | 6.6188 | 6.8717 | 7.1246 | 7.3775 | 7.6305 | 7.8834 | 8.1363 | 8.3892 | 8.6422 | 8.8951 | 9.148 | 9.4009 | 9.6539 | 9.9068 | 10.1597 | 10.4126 | 10.6656 | 10.9185 | 11.1714 | 11.4243 | 11.6773 | 11.9302 | 12.1831 | 12.436 | 12.689 | 12.9419 | 13.1719 | 13.4019 | 13.6319 | 13.8618 | 14.0918 | 14.3218 | 14.5518 | 14.7818 | 15.0118 | 15.2418 | 15.4718 | 15.7018 | 15.9318 | 16.1618 | 16.3918 | 16.6217 | 16.8517 | 17.0817 | 17.3117 | 17.5417 | 17.7717 | 18.0017 | 18.2317 | 18.4617 | 18.6917 | 18.9217 | 19.1517 | 19.3816 | 19.6116 | 19.8416 | 20.0258 | 20.2099 | 20.394 | 20.5781 | 20.7623 | 20.9464 | 21.1305 | 21.3146 | 21.4988 | 21.6829 | 21.867 | 22.0511 | 22.2353 | 22.4194 | 22.6035 | 22.7876 | 22.9718 | 23.1559 | 23.34 | 23.5241 | 23.7083 | 23.8924 | 24.0765 | 24.2606 | 24.4448 | 24.6289 | 24.813 | 24.9971 | 25.1813 | 25.3654 | 25.5013 | 25.6373 | 25.7732 | 25.9092 | 26.0451 | 26.1811 | 26.317 | 26.453 | 26.5889 | 26.7249 | 26.8608 | 26.9968 | 27.1327 | 27.2687 | 27.4046 | 27.5406 | 27.6765 | 27.8125 | 27.9484 | 28.0844 | 28.2203 | 28.3563 | 28.4922 | 28.6282 | 28.7641 | 28.9001 | 29.036 | 29.172 | 29.3079 | 29.4439
8.1 | 0 | 3.57 | 3.5863 | 3.459 | 3.359 | 4.353 | 5.4233 | 13.0988 | 20.0783 | 25.6658 | 29.7928 | -2.2204e-16 | 0.357 | 0.714 | 1.071 | 1.428 | 1.785 | 2.142 | 2.499 | 2.856 | 3.213 | 3.57 | 3.5733 | 3.5765 | 3.5798 | 3.583 | 3.5863 | 3.5608 | 3.5354 | 3.5099 | 3.4845 | 3.459 | 3.449 | 3.439 | 3.429 | 3.419 | 3.409 | 3.399 | 3.389 | 3.379 | 3.369 | 3.359 | 3.4253 | 3.4915 | 3.5578 | 3.6241 | 3.6903 | 3.7566 | 3.8229 | 3.8891 | 3.9554 | 4.0217 | 4.0879 | 4.1542 | 4.2205 | 4.2867 | 4.353 | 4.4244 | 4.4957 | 4.5671 | 4.6384 | 4.7098 | 4.7811 | 4.8525 | 4.9238 | 4.9952 | 5.0665 | 5.1379 | 5.2092 | 5.2806 | 5.3519 | 5.4233 | 5.6791 | 5.935 | 6.1908 | 6.4467 | 6.7025 | 6.9584 | 7.2142 | 7.4701 | 7.7259 | 7.9818 | 8.2376 | 8.4935 | 8.7493 | 9.0052 | 9.261 | 9.5169 | 9.7727 | 10.0286 | 10.2844 | 10.5403 | 10.7961 | 11.052 | 11.3078 | 11.5637 | 11.8195 | 12.0754 | 12.3312 | 12.5871 | 12.8429 | 13.0988 | 13.3314 | 13.5641 | 13.7967 | 14.0294 | 14.262 | 14.4947 | 14.7273 | 14.96 | 15.1926 | 15.4253 | 15.6579 | 15.8906 | 16.1232 | 16.3559 | 16.5885 | 16.8212 | 17.0538 | 17.2865 | 17.5191 | 17.7518 | 17.9844 | 18.2171 | 18.4497 | 18.6824 | 18.915 | 19.1477 | 19.3803 | 19.613 | 19.8456 | 20.0783 | 20.2645 | 20.4508 | 20.637 | 20.8233 | 21.0095 | 21.1958 | 21.382 | 21.5683 | 21.7545 | 21.9408 | 22.127 | 22.3133 | 22.4995 | 22.6858 | 22.872 | 23.0583 | 23.2445 | 23.4308 | 23.617 | 23.8033 | 23.9895 | 24.1758 | 24.362 | 24.5483 | 24.7345 | 24.9208 | 25.107 | 25.2933 | 25.4795 | 25.6658 | 25.8033 | 25.9409 | 26.0785 | 26.216 | 26.3536 | 26.4912 | 26.6287 | 26.7663 | 26.9039 | 27.0414 | 27.179 | 27.3166 | 27.4541 | 27.5917 | 27.7293 | 27.8668 | 28.0044 | 28.142 | 28.2795 | 28.4171 | 28.5547 | 28.6922 | 28.8298 | 28.9674 | 29.1049 | 29.2425 | 29.3801 | 29.5176 | 29.6552 | 29.7927
8.15 | 0 | 3.61 | 3.6319 | 3.5035 | 3.4035 | 4.4095 | 5.4924 | 13.2556 | 20.3149 | 25.9661 | 30.1416 | 0 | 0.361 | 0.722 | 1.083 | 1.444 | 1.805 | 2.166 | 2.527 | 2.888 | 3.249 | 3.61 | 3.6144 | 3.6188 | 3.6231 | 3.6275 | 3.6319 | 3.6062 | 3.5805 | 3.5549 | 3.5292 | 3.5035 | 3.4935 | 3.4835 | 3.4735 | 3.4635 | 3.4535 | 3.4435 | 3.4335 | 3.4235 | 3.4135 | 3.4035 | 3.4706 | 3.5376 | 3.6047 | 3.6718 | 3.7388 | 3.8059 | 3.873 | 3.94 | 4.0071 | 4.0742 | 4.1412 | 4.2083 | 4.2754 | 4.3424 | 4.4095 | 4.4817 | 4.5539 | 4.6261 | 4.6983 | 4.7705 | 4.8427 | 4.9148 | 4.987 | 5.0592 | 5.1314 | 5.2036 | 5.2758 | 5.348 | 5.4202 | 5.4924 | 5.7512 | 6.0099 | 6.2687 | 6.5275 | 6.7863 | 7.045 | 7.3038 | 7.5626 | 7.8214 | 8.0801 | 8.3389 | 8.5977 | 8.8565 | 9.1152 | 9.374 | 9.6328 | 9.8916 | 10.1503 | 10.4091 | 10.6679 | 10.9267 | 11.1854 | 11.4442 | 11.703 | 11.9618 | 12.2205 | 12.4793 | 12.7381 | 12.9969 | 13.2556 | 13.4909 | 13.7262 | 13.9616 | 14.1969 | 14.4322 | 14.6675 | 14.9028 | 15.1381 | 15.3734 | 15.6087 | 15.844 | 16.0793 | 16.3146 | 16.5499 | 16.7853 | 17.0206 | 17.2559 | 17.4912 | 17.7265 | 17.9618 | 18.1971 | 18.4324 | 18.6677 | 18.903 | 19.1383 | 19.3736 | 19.609 | 19.8443 | 20.0796 | 20.3149 | 20.5033 | 20.6916 | 20.88 | 21.0684 | 21.2568 | 21.4451 | 21.6335 | 21.8219 | 22.0103 | 22.1986 | 22.387 | 22.5754 | 22.7638 | 22.9521 | 23.1405 | 23.3289 | 23.5173 | 23.7056 | 23.894 | 24.0824 | 24.2708 | 24.4591 | 24.6475 | 24.8359 | 25.0243 | 25.2126 | 25.401 | 25.5894 | 25.7778 | 25.9661 | 26.1053 | 26.2445 | 26.3837 | 26.5229 | 26.662 | 26.8012 | 26.9404 | 27.0796 | 27.2188 | 27.358 | 27.4971 | 27.6363 | 27.7755 | 27.9147 | 28.0539 | 28.1931 | 28.3322 | 28.4714 | 28.6106 | 28.7498 | 28.889 | 29.0282 | 29.1673 | 29.3065 | 29.4457 | 29.5849 | 29.7241 | 29.8633 | 30.0024 | 30.1416
8.2 | 0 | 3.65 | 3.6775 | 3.548 | 3.448 | 4.466 | 5.5615 | 13.4125 | 20.5515 | 26.2665 | 30.4905 | 2.2204e-16 | 0.365 | 0.73 | 1.095 | 1.46 | 1.825 | 2.19 | 2.555 | 2.92 | 3.285 | 3.65 | 3.6555 | 3.661 | 3.6665 | 3.672 | 3.6775 | 3.6516 | 3.6257 | 3.5998 | 3.5739 | 3.548 | 3.538 | 3.528 | 3.518 | 3.508 | 3.498 | 3.488 | 3.478 | 3.468 | 3.458 | 3.448 | 3.5159 | 3.5837 | 3.6516 | 3.7195 | 3.7873 | 3.8552 | 3.9231 | 3.9909 | 4.0588 | 4.1267 | 4.1945 | 4.2624 | 4.3303 | 4.3981 | 4.466 | 4.539 | 4.6121 | 4.6851 | 4.7581 | 4.8312 | 4.9042 | 4.9772 | 5.0503 | 5.1233 | 5.1963 | 5.2694 | 5.3424 | 5.4154 | 5.4885 | 5.5615 | 5.8232 | 6.0849 | 6.3466 | 6.6083 | 6.87 | 7.1317 | 7.3934 | 7.6551 | 7.9168 | 8.1785 | 8.4402 | 8.7019 | 8.9636 | 9.2253 | 9.487 | 9.7487 | 10.0104 | 10.2721 | 10.5338 | 10.7955 | 11.0572 | 11.3189 | 11.5806 | 11.8423 | 12.104 | 12.3657 | 12.6274 | 12.8891 | 13.1508 | 13.4125 | 13.6505 | 13.8884 | 14.1264 | 14.3644 | 14.6023 | 14.8403 | 15.0783 | 15.3162 | 15.5542 | 15.7922 | 16.0301 | 16.2681 | 16.5061 | 16.744 | 16.982 | 17.22 | 17.4579 | 17.6959 | 17.9339 | 18.1718 | 18.4098 | 18.6478 | 18.8857 | 19.1237 | 19.3617 | 19.5996 | 19.8376 | 20.0756 | 20.3135 | 20.5515 | 20.742 | 20.9325 | 21.123 | 21.3135 | 21.504 | 21.6945 | 21.885 | 22.0755 | 22.266 | 22.4565 | 22.647 | 22.8375 | 23.028 | 23.2185 | 23.409 | 23.5995 | 23.79 | 23.9805 | 24.171 | 24.3615 | 24.552 | 24.7425 | 24.933 | 25.1235 | 25.314 | 25.5045 | 25.695 | 25.8855 | 26.076 | 26.2665 | 26.4073 | 26.5481 | 26.6889 | 26.8297 | 26.9705 | 27.1113 | 27.2521 | 27.3929 | 27.5337 | 27.6745 | 27.8153 | 27.9561 | 28.0969 | 28.2377 | 28.3785 | 28.5193 | 28.6601 | 28.8009 | 28.9417 | 29.0825 | 29.2233 | 29.3641 | 29.5049 | 29.6457 | 29.7865 | 29.9273 | 30.0681 | 30.2089 | 30.3497 | 30.4905
8.25 | 0 | 3.69 | 3.7231 | 3.5925 | 3.4925 | 4.5225 | 5.6306 | 13.5694 | 20.7881 | 26.5669 | 30.8394 | 2.2204e-16 | 0.369 | 0.738 | 1.107 | 1.476 | 1.845 | 2.214 | 2.583 | 2.952 | 3.321 | 3.69 | 3.6966 | 3.7033 | 3.7099 | 3.7165 | 3.7231 | 3.697 | 3.6709 | 3.6448 | 3.6186 | 3.5925 | 3.5825 | 3.5725 | 3.5625 | 3.5525 | 3.5425 | 3.5325 | 3.5225 | 3.5125 | 3.5025 | 3.4925 | 3.5612 | 3.6298 | 3.6985 | 3.7672 | 3.8358 | 3.9045 | 3.9732 | 4.0418 | 4.1105 | 4.1792 | 4.2478 | 4.3165 | 4.3852 | 4.4538 | 4.5225 | 4.5964 | 4.6703 | 4.7441 | 4.818 | 4.8919 | 4.9658 | 5.0396 | 5.1135 | 5.1874 | 5.2613 | 5.3351 | 5.409 | 5.4829 | 5.5568 | 5.6306 | 5.8953 | 6.1599 | 6.4245 | 6.6891 | 6.9538 | 7.2184 | 7.483 | 7.7476 | 8.0123 | 8.2769 | 8.5415 | 8.8061 | 9.0708 | 9.3354 | 9.6 | 9.8646 | 10.1293 | 10.3939 | 10.6585 | 10.9231 | 11.1878 | 11.4524 | 11.717 | 11.9816 | 12.2463 | 12.5109 | 12.7755 | 13.0401 | 13.3048 | 13.5694 | 13.81 | 14.0506 | 14.2913 | 14.5319 | 14.7725 | 15.0131 | 15.2538 | 15.4944 | 15.735 | 15.9756 | 16.2163 | 16.4569 | 16.6975 | 16.9381 | 17.1788 | 17.4194 | 17.66 | 17.9006 | 18.1413 | 18.3819 | 18.6225 | 18.8631 | 19.1038 | 19.3444 | 19.585 | 19.8256 | 20.0663 | 20.3069 | 20.5475 | 20.7881 | 20.9808 | 21.1734 | 21.366 | 21.5586 | 21.7513 | 21.9439 | 22.1365 | 22.3291 | 22.5218 | 22.7144 | 22.907 | 23.0996 | 23.2923 | 23.4849 | 23.6775 | 23.8701 | 24.0628 | 24.2554 | 24.448 | 24.6406 | 24.8333 | 25.0259 | 25.2185 | 25.4111 | 25.6038 | 25.7964 | 25.989 | 26.1816 | 26.3743 | 26.5669 | 26.7093 | 26.8517 | 26.9941 | 27.1365 | 27.279 | 27.4214 | 27.5638 | 27.7062 | 27.8486 | 27.991 | 28.1335 | 28.2759 | 28.4183 | 28.5607 | 28.7031 | 28.8455 | 28.988 | 29.1304 | 29.2728 | 29.4152 | 29.5576 | 29.7 | 29.8425 | 29.9849 | 30.1273 | 30.2697 | 30.4121 | 30.5545 | 30.697 | 30.8394
8.3 | 0 | 3.73 | 3.7688 | 3.637 | 3.537 | 4.579 | 5.6998 | 13.7263 | 21.0248 | 26.8673 | 31.1883 | 2.2204e-16 | 0.373 | 0.746 | 1.119 | 1.492 | 1.865 | 2.238 | 2.611 | 2.984 | 3.357 | 3.73 | 3.7378 | 3.7455 | 3.7533 | 3.761 | 3.7688 | 3.7424 | 3.7161 | 3.6897 | 3.6634 | 3.637 | 3.627 | 3.617 | 3.607 | 3.597 | 3.587 | 3.577 | 3.567 | 3.557 | 3.547 | 3.537 | 3.6065 | 3.6759 | 3.7454 | 3.8149 | 3.8843 | 3.9538 | 4.0233 | 4.0927 | 4.1622 | 4.2317 | 4.3011 | 4.3706 | 4.4401 | 4.5095 | 4.579 | 4.6537 | 4.7284 | 4.8032 | 4.8779 | 4.9526 | 5.0273 | 5.102 | 5.1767 | 5.2515 | 5.3262 | 5.4009 | 5.4756 | 5.5503 | 5.625 | 5.6998 | 5.9673 | 6.2349 | 6.5024 | 6.77 | 7.0375 | 7.3051 | 7.5726 | 7.8402 | 8.1077 | 8.3753 | 8.6428 | 8.9104 | 9.1779 | 9.4455 | 9.713 | 9.9806 | 10.2481 | 10.5157 | 10.7832 | 11.0508 | 11.3183 | 11.5859 | 11.8534 | 12.121 | 12.3885 | 12.6561 | 12.9236 | 13.1912 | 13.4587 | 13.7263 | 13.9695 | 14.2128 | 14.4561 | 14.6994 | 14.9427 | 15.186 | 15.4292 | 15.6725 | 15.9158 | 16.1591 | 16.4024 | 16.6457 | 16.8889 | 17.1322 | 17.3755 | 17.6188 | 17.8621 | 18.1054 | 18.3486 | 18.5919 | 18.8352 | 19.0785 | 19.3218 | 19.5651 | 19.8083 | 20.0516 | 20.2949 | 20.5382 | 20.7815 | 21.0248 | 21.2195 | 21.4143 | 21.609 | 21.8038 | 21.9985 | 22.1933 | 22.388 | 22.5828 | 22.7775 | 22.9723 | 23.167 | 23.3618 | 23.5565 | 23.7513 | 23.946 | 24.1408 | 24.3355 | 24.5303 | 24.725 | 24.9198 | 25.1145 | 25.3093 | 25.504 | 25.6988 | 25.8935 | 26.0883 | 26.283 | 26.4778 | 26.6725 | 26.8673 | 27.0113 | 27.1553 | 27.2994 | 27.4434 | 27.5874 | 27.7315 | 27.8755 | 28.0195 | 28.1636 | 28.3076 | 28.4516 | 28.5957 | 28.7397 | 28.8837 | 29.0278 | 29.1718 | 29.3158 | 29.4599 | 29.6039 | 29.7479 | 29.892 | 30.036 | 30.18 | 30.3241 | 30.4681 | 30.6121 | 30.7562 | 30.9002 | 31.0442 | 31.1882
8.35 | 0 | 3.77 | 3.8144 | 3.6815 | 3.5815 | 4.6355 | 5.7689 | 13.8831 | 21.2614 | 27.1676 | 31.5371 | -2.2204e-16 | 0.377 | 0.754 | 1.131 | 1.508 | 1.885 | 2.262 | 2.639 | 3.016 | 3.393 | 3.77 | 3.7789 | 3.7878 | 3.7966 | 3.8055 | 3.8144 | 3.7878 | 3.7612 | 3.7347 | 3.7081 | 3.6815 | 3.6715 | 3.6615 | 3.6515 | 3.6415 | 3.6315 | 3.6215 | 3.6115 | 3.6015 | 3.5915 | 3.5815 | 3.6518 | 3.722 | 3.7923 | 3.8626 | 3.9328 | 4.0031 | 4.0734 | 4.1436 | 4.2139 | 4.2842 | 4.3544 | 4.4247 | 4.495 | 4.5652 | 4.6355 | 4.7111 | 4.7866 | 4.8622 | 4.9377 | 5.0133 | 5.0889 | 5.1644 | 5.24 | 5.3155 | 5.3911 | 5.4666 | 5.5422 | 5.6178 | 5.6933 | 5.7689 | 6.0394 | 6.3098 | 6.5803 | 6.8508 | 7.1213 | 7.3917 | 7.6622 | 7.9327 | 8.2032 | 8.4736 | 8.7441 | 9.0146 | 9.2851 | 9.5555 | 9.826 | 10.0965 | 10.367 | 10.6374 | 10.9079 | 11.1784 | 11.4489 | 11.7193 | 11.9898 | 12.2603 | 12.5308 | 12.8012 | 13.0717 | 13.3422 | 13.6127 | 13.8831 | 14.1291 | 14.375 | 14.621 | 14.8669 | 15.1128 | 15.3588 | 15.6047 | 15.8507 | 16.0966 | 16.3425 | 16.5885 | 16.8344 | 17.0804 | 17.3263 | 17.5723 | 17.8182 | 18.0641 | 18.3101 | 18.556 | 18.802 | 19.0479 | 19.2938 | 19.5398 | 19.7857 | 20.0317 | 20.2776 | 20.5236 | 20.7695 | 21.0154 | 21.2614 | 21.4583 | 21.6551 | 21.852 | 22.0489 | 22.2458 | 22.4426 | 22.6395 | 22.8364 | 23.0333 | 23.2301 | 23.427 | 23.6239 | 23.8208 | 24.0176 | 24.2145 | 24.4114 | 24.6083 | 24.8051 | 25.002 | 25.1989 | 25.3958 | 25.5926 | 25.7895 | 25.9864 | 26.1833 | 26.3801 | 26.577 | 26.7739 | 26.9708 | 27.1676 | 27.3133 | 27.4589 | 27.6046 | 27.7502 | 27.8959 | 28.0415 | 28.1872 | 28.3328 | 28.4785 | 28.6241 | 28.7698 | 28.9154 | 29.0611 | 29.2067 | 29.3524 | 29.498 | 29.6437 | 29.7893 | 29.935 | 30.0806 | 30.2263 | 30.3719 | 30.5176 | 30.6632 | 30.8089 | 30.9545 | 31.1002 | 31.2458 | 31.3915 | 31.5371
8.4 | 0 | 3.81 | 3.86 | 3.726 | 3.626 | 4.692 | 5.838 | 14.04 | 21.498 | 27.468 | 31.886 | 0 | 0.381 | 0.762 | 1.143 | 1.524 | 1.905 | 2.286 | 2.667 | 3.048 | 3.429 | 3.81 | 3.82 | 3.83 | 3.84 | 3.85 | 3.86 | 3.8332 | 3.8064 | 3.7796 | 3.7528 | 3.726 | 3.716 | 3.706 | 3.696 | 3.686 | 3.676 | 3.666 | 3.656 | 3.646 | 3.636 | 3.626 | 3.6971 | 3.7681 | 3.8392 | 3.9103 | 3.9813 | 4.0524 | 4.1235 | 4.1945 | 4.2656 | 4.3367 | 4.4077 | 4.4788 | 4.5499 | 4.6209 | 4.692 | 4.7684 | 4.8448 | 4.9212 | 4.9976 | 5.074 | 5.1504 | 5.2268 | 5.3032 | 5.3796 | 5.456 | 5.5324 | 5.6088 | 5.6852 | 5.7616 | 5.838 | 6.1114 | 6.3848 | 6.6582 | 6.9316 | 7.205 | 7.4784 | 7.7518 | 8.0252 | 8.2986 | 8.572 | 8.8454 | 9.1188 | 9.3922 | 9.6656 | 9.939 | 10.2124 | 10.4858 | 10.7592 | 11.0326 | 11.306 | 11.5794 | 11.8528 | 12.1262 | 12.3996 | 12.673 | 12.9464 | 13.2198 | 13.4932 | 13.7666 | 14.04 | 14.2886 | 14.5372 | 14.7858 | 15.0344 | 15.283 | 15.5316 | 15.7802 | 16.0288 | 16.2774 | 16.526 | 16.7746 | 17.0232 | 17.2718 | 17.5204 | 17.769 | 18.0176 | 18.2662 | 18.5148 | 18.7634 | 19.012 | 19.2606 | 19.5092 | 19.7578 | 20.0064 | 20.255 | 20.5036 | 20.7522 | 21.0008 | 21.2494 | 21.498 | 21.697 | 21.896 | 22.095 | 22.294 | 22.493 | 22.692 | 22.891 | 23.09 | 23.289 | 23.488 | 23.687 | 23.886 | 24.085 | 24.284 | 24.483 | 24.682 | 24.881 | 25.08 | 25.279 | 25.478 | 25.677 | 25.876 | 26.075 | 26.274 | 26.473 | 26.672 | 26.871 | 27.07 | 27.269 | 27.468 | 27.6153 | 27.7625 | 27.9098 | 28.0571 | 28.2043 | 28.3516 | 28.4989 | 28.6461 | 28.7934 | 28.9407 | 29.0879 | 29.2352 | 29.3825 | 29.5297 | 29.677 | 29.8243 | 29.9715 | 30.1188 | 30.2661 | 30.4133 | 30.5606 | 30.7079 | 30.8551 | 31.0024 | 31.1497 | 31.2969 | 31.4442 | 31.5915 | 31.7387 | 31.886
8.45 | 0 | 3.85 | 3.9056 | 3.7705 | 3.6705 | 4.7485 | 5.9071 | 14.1969 | 21.7346 | 27.7684 | 32.2349 | 2.2204e-16 | 0.385 | 0.77 | 1.155 | 1.54 | 1.925 | 2.31 | 2.695 | 3.08 | 3.465 | 3.85 | 3.8611 | 3.8723 | 3.8834 | 3.8945 | 3.9056 | 3.8786 | 3.8516 | 3.8246 | 3.7975 | 3.7705 | 3.7605 | 3.7505 | 3.7405 | 3.7305 | 3.7205 | 3.7105 | 3.7005 | 3.6905 | 3.6805 | 3.6705 | 3.7424 | 3.8142 | 3.8861 | 3.958 | 4.0298 | 4.1017 | 4.1736 | 4.2454 | 4.3173 | 4.3892 | 4.461 | 4.5329 | 4.6048 | 4.6766 | 4.7485 | 4.8257 | 4.903 | 4.9802 | 5.0575 | 5.1347 | 5.212 | 5.2892 | 5.3664 | 5.4437 | 5.5209 | 5.5982 | 5.6754 | 5.7526 | 5.8299 | 5.9071 | 6.1835 | 6.4598 | 6.7361 | 7.0124 | 7.2888 | 7.5651 | 7.8414 | 8.1177 | 8.3941 | 8.6704 | 8.9467 | 9.223 | 9.4994 | 9.7757 | 10.052 | 10.3283 | 10.6047 | 10.881 | 11.1573 | 11.4336 | 11.71 | 11.9863 | 12.2626 | 12.5389 | 12.8153 | 13.0916 | 13.3679 | 13.6442 | 13.9206 | 14.1969 | 14.4481 | 14.6994 | 14.9507 | 15.2019 | 15.4532 | 15.7044 | 15.9557 | 16.2069 | 16.4582 | 16.7095 | 16.9607 | 17.212 | 17.4632 | 17.7145 | 17.9658 | 18.217 | 18.4683 | 18.7195 | 18.9708 | 19.222 | 19.4733 | 19.7246 | 19.9758 | 20.2271 | 20.4783 | 20.7296 | 20.9809 | 21.2321 | 21.4834 | 21.7346 | 21.9358 | 22.1369 | 22.338 | 22.5391 | 22.7403 | 22.9414 | 23.1425 | 23.3436 | 23.5448 | 23.7459 | 23.947 | 24.1481 | 24.3493 | 24.5504 | 24.7515 | 24.9526 | 25.1538 | 25.3549 | 25.556 | 25.7571 | 25.9583 | 26.1594 | 26.3605 | 26.5616 | 26.7628 | 26.9639 | 27.165 | 27.3661 | 27.5673 | 27.7684 | 27.9173 | 28.0661 | 28.215 | 28.3639 | 28.5128 | 28.6617 | 28.8106 | 28.9594 | 29.1083 | 29.2572 | 29.4061 | 29.555 | 29.7039 | 29.8527 | 30.0016 | 30.1505 | 30.2994 | 30.4483 | 30.5972 | 30.746 | 30.8949 | 31.0438 | 31.1927 | 31.3416 | 31.4905 | 31.6393 | 31.7882 | 31.9371 | 32.086 | 32.2349
8.5 | 0 | 3.89 | 3.9513 | 3.815 | 3.715 | 4.805 | 5.9763 | 14.3538 | 21.9713 | 28.0688 | 32.5838 | -2.2204e-16 | 0.389 | 0.778 | 1.167 | 1.556 | 1.945 | 2.334 | 2.723 | 3.112 | 3.501 | 3.89 | 3.9023 | 3.9145 | 3.9268 | 3.939 | 3.9513 | 3.924 | 3.8968 | 3.8695 | 3.8423 | 3.815 | 3.805 | 3.795 | 3.785 | 3.775 | 3.765 | 3.755 | 3.745 | 3.735 | 3.725 | 3.715 | 3.7877 | 3.8603 | 3.933 | 4.0057 | 4.0783 | 4.151 | 4.2237 | 4.2963 | 4.369 | 4.4417 | 4.5143 | 4.587 | 4.6597 | 4.7323 | 4.805 | 4.8831 | 4.9612 | 5.0393 | 5.1173 | 5.1954 | 5.2735 | 5.3516 | 5.4297 | 5.5078 | 5.5858 | 5.6639 | 5.742 | 5.8201 | 5.8982 | 5.9763 | 6.2555 | 6.5348 | 6.814 | 7.0933 | 7.3725 | 7.6518 | 7.931 | 8.2103 | 8.4895 | 8.7688 | 9.048 | 9.3273 | 9.6065 | 9.8858 | 10.165 | 10.4443 | 10.7235 | 11.0028 | 11.282 | 11.5613 | 11.8405 | 12.1198 | 12.399 | 12.6783 | 12.9575 | 13.2368 | 13.516 | 13.7953 | 14.0745 | 14.3538 | 14.6077 | 14.8616 | 15.1155 | 15.3694 | 15.6233 | 15.8773 | 16.1312 | 16.3851 | 16.639 | 16.8929 | 17.1468 | 17.4008 | 17.6547 | 17.9086 | 18.1625 | 18.4164 | 18.6703 | 18.9243 | 19.1782 | 19.4321 | 19.686 | 19.9399 | 20.1938 | 20.4478 | 20.7017 | 20.9556 | 21.2095 | 21.4634 | 21.7173 | 21.9713 | 22.1745 | 22.3778 | 22.581 | 22.7843 | 22.9875 | 23.1908 | 23.394 | 23.5973 | 23.8005 | 24.0038 | 24.207 | 24.4103 | 24.6135 | 24.8168 | 25.02 | 25.2233 | 25.4265 | 25.6298 | 25.833 | 26.0363 | 26.2395 | 26.4428 | 26.646 | 26.8493 | 27.0525 | 27.2558 | 27.459 | 27.6623 | 27.8655 | 28.0688 | 28.2193 | 28.3698 | 28.5203 | 28.6708 | 28.8213 | 28.9718 | 29.1223 | 29.2728 | 29.4233 | 29.5738 | 29.7243 | 29.8748 | 30.0253 | 30.1758 | 30.3263 | 30.4768 | 30.6273 | 30.7778 | 30.9283 | 31.0788 | 31.2293 | 31.3798 | 31.5303 | 31.6808 | 31.8313 | 31.9818 | 32.1323 | 32.2828 | 32.4333 | 32.5837
8.55 | 0 | 3.93 | 3.9969 | 3.8595 | 3.7595 | 4.8615 | 6.0454 | 14.5106 | 22.2079 | 28.3691 | 32.9326 | 0 | 0.393 | 0.786 | 1.179 | 1.572 | 1.965 | 2.358 | 2.751 | 3.144 | 3.537 | 3.93 | 3.9434 | 3.9568 | 3.9701 | 3.9835 | 3.9969 | 3.9694 | 3.9419 | 3.9145 | 3.887 | 3.8595 | 3.8495 | 3.8395 | 3.8295 | 3.8195 | 3.8095 | 3.7995 | 3.7895 | 3.7795 | 3.7695 | 3.7595 | 3.833 | 3.9064 | 3.9799 | 4.0534 | 4.1268 | 4.2003 | 4.2738 | 4.3472 | 4.4207 | 4.4942 | 4.5676 | 4.6411 | 4.7146 | 4.788 | 4.8615 | 4.9404 | 5.0194 | 5.0983 | 5.1772 | 5.2561 | 5.3351 | 5.414 | 5.4929 | 5.5718 | 5.6508 | 5.7297 | 5.8086 | 5.8875 | 5.9665 | 6.0454 | 6.3276 | 6.6097 | 6.8919 | 7.1741 | 7.4563 | 7.7384 | 8.0206 | 8.3028 | 8.585 | 8.8671 | 9.1493 | 9.4315 | 9.7137 | 9.9958 | 10.278 | 10.5602 | 10.8424 | 11.1245 | 11.4067 | 11.6889 | 11.9711 | 12.2532 | 12.5354 | 12.8176 | 13.0998 | 13.3819 | 13.6641 | 13.9463 | 14.2285 | 14.5106 | 14.7672 | 15.0238 | 15.2804 | 15.5369 | 15.7935 | 16.0501 | 16.3067 | 16.5632 | 16.8198 | 17.0764 | 17.333 | 17.5895 | 17.8461 | 18.1027 | 18.3593 | 18.6158 | 18.8724 | 19.129 | 19.3856 | 19.6421 | 19.8987 | 20.1553 | 20.4119 | 20.6684 | 20.925 | 21.1816 | 21.4382 | 21.6947 | 21.9513 | 22.2079 | 22.4133 | 22.6186 | 22.824 | 23.0294 | 23.2348 | 23.4401 | 23.6455 | 23.8509 | 24.0563 | 24.2616 | 24.467 | 24.6724 | 24.8778 | 25.0831 | 25.2885 | 25.4939 | 25.6993 | 25.9046 | 26.11 | 26.3154 | 26.5208 | 26.7261 | 26.9315 | 27.1369 | 27.3423 | 27.5476 | 27.753 | 27.9584 | 28.1638 | 28.3691 | 28.5212 | 28.6734 | 28.8255 | 28.9776 | 29.1297 | 29.2818 | 29.4339 | 29.5861 | 29.7382 | 29.8903 | 30.0424 | 30.1945 | 30.3466 | 30.4988 | 30.6509 | 30.803 | 30.9551 | 31.1072 | 31.2593 | 31.4115 | 31.5636 | 31.7157 | 31.8678 | 32.0199 | 32.172 | 32.3242 | 32.4763 | 32.6284 | 32.7805 | 32.9326
8.6 | 0 | 3.97 | 4.0425 | 3.904 | 3.804 | 4.918 | 6.1145 | 14.6675 | 22.4445 | 28.6695 | 33.2815 | 2.2204e-16 | 0.397 | 0.794 | 1.191 | 1.588 | 1.985 | 2.382 | 2.779 | 3.176 | 3.573 | 3.97 | 3.9845 | 3.999 | 4.0135 | 4.028 | 4.0425 | 4.0148 | 3.9871 | 3.9594 | 3.9317 | 3.904 | 3.894 | 3.884 | 3.874 | 3.864 | 3.854 | 3.844 | 3.834 | 3.824 | 3.814 | 3.804 | 3.8783 | 3.9525 | 4.0268 | 4.1011 | 4.1753 | 4.2496 | 4.3239 | 4.3981 | 4.4724 | 4.5467 | 4.6209 | 4.6952 | 4.7695 | 4.8437 | 4.918 | 4.9978 | 5.0775 | 5.1573 | 5.2371 | 5.3168 | 5.3966 | 5.4764 | 5.5561 | 5.6359 | 5.7157 | 5.7954 | 5.8752 | 5.955 | 6.0347 | 6.1145 | 6.3996 | 6.6847 | 6.9698 | 7.2549 | 7.54 | 7.8251 | 8.1102 | 8.3953 | 8.6804 | 8.9655 | 9.2506 | 9.5357 | 9.8208 | 10.1059 | 10.391 | 10.6761 | 10.9612 | 11.2463 | 11.5314 | 11.8165 | 12.1016 | 12.3867 | 12.6718 | 12.9569 | 13.242 | 13.5271 | 13.8122 | 14.0973 | 14.3824 | 14.6675 | 14.9267 | 15.186 | 15.4452 | 15.7044 | 15.9637 | 16.2229 | 16.4821 | 16.7414 | 17.0006 | 17.2598 | 17.5191 | 17.7783 | 18.0375 | 18.2968 | 18.556 | 18.8152 | 19.0745 | 19.3337 | 19.5929 | 19.8522 | 20.1114 | 20.3706 | 20.6299 | 20.8891 | 21.1483 | 21.4076 | 21.6668 | 21.926 | 22.1853 | 22.4445 | 22.652 | 22.8595 | 23.067 | 23.2745 | 23.482 | 23.6895 | 23.897 | 24.1045 | 24.312 | 24.5195 | 24.727 | 24.9345 | 25.142 | 25.3495 | 25.557 | 25.7645 | 25.972 | 26.1795 | 26.387 | 26.5945 | 26.802 | 27.0095 | 27.217 | 27.4245 | 27.632 | 27.8395 | 28.047 | 28.2545 | 28.462 | 28.6695 | 28.8232 | 28.977 | 29.1307 | 29.2844 | 29.4382 | 29.5919 | 29.7456 | 29.8994 | 30.0531 | 30.2068 | 30.3606 | 30.5143 | 30.668 | 30.8218 | 30.9755 | 31.1292 | 31.283 | 31.4367 | 31.5904 | 31.7442 | 31.8979 | 32.0516 | 32.2054 | 32.3591 | 32.5128 | 32.6666 | 32.8203 | 32.974 | 33.1278 | 33.2815
8.65 | 0 | 4.01 | 4.0881 | 3.9485 | 3.8485 | 4.9745 | 6.1836 | 14.8244 | 22.6811 | 28.9699 | 33.6304 | 4.4409e-16 | 0.401 | 0.802 | 1.203 | 1.604 | 2.005 | 2.406 | 2.807 | 3.208 | 3.609 | 4.01 | 4.0256 | 4.0413 | 4.0569 | 4.0725 | 4.0881 | 4.0602 | 4.0323 | 4.0044 | 3.9764 | 3.9485 | 3.9385 | 3.9285 | 3.9185 | 3.9085 | 3.8985 | 3.8885 | 3.8785 | 3.8685 | 3.8585 | 3.8485 | 3.9236 | 3.9986 | 4.0737 | 4.1488 | 4.2238 | 4.2989 | 4.374 | 4.449 | 4.5241 | 4.5992 | 4.6742 | 4.7493 | 4.8244 | 4.8994 | 4.9745 | 5.0551 | 5.1357 | 5.2163 | 5.2969 | 5.3775 | 5.4582 | 5.5388 | 5.6194 | 5.7 | 5.7806 | 5.8612 | 5.9418 | 6.0224 | 6.103 | 6.1836 | 6.4717 | 6.7597 | 7.0477 | 7.3357 | 7.6238 | 7.9118 | 8.1998 | 8.4878 | 8.7759 | 9.0639 | 9.3519 | 9.6399 | 9.928 | 10.216 | 10.504 | 10.792 | 11.0801 | 11.3681 | 11.6561 | 11.9441 | 12.2322 | 12.5202 | 12.8082 | 13.0962 | 13.3843 | 13.6723 | 13.9603 | 14.2483 | 14.5364 | 14.8244 | 15.0863 | 15.3482 | 15.6101 | 15.8719 | 16.1338 | 16.3957 | 16.6576 | 16.9195 | 17.1814 | 17.4433 | 17.7052 | 17.9671 | 18.229 | 18.4909 | 18.7528 | 19.0146 | 19.2765 | 19.5384 | 19.8003 | 20.0622 | 20.3241 | 20.586 | 20.8479 | 21.1098 | 21.3717 | 21.6336 | 21.8955 | 22.1573 | 22.4192 | 22.6811 | 22.8908 | 23.1004 | 23.31 | 23.5196 | 23.7293 | 23.9389 | 24.1485 | 24.3581 | 24.5678 | 24.7774 | 24.987 | 25.1966 | 25.4063 | 25.6159 | 25.8255 | 26.0351 | 26.2448 | 26.4544 | 26.664 | 26.8736 | 27.0833 | 27.2929 | 27.5025 | 27.7121 | 27.9218 | 28.1314 | 28.341 | 28.5506 | 28.7603 | 28.9699 | 29.1252 | 29.2806 | 29.4359 | 29.5913 | 29.7466 | 29.902 | 30.0573 | 30.2127 | 30.368 | 30.5234 | 30.6787 | 30.8341 | 30.9894 | 31.1448 | 31.3001 | 31.4555 | 31.6108 | 31.7662 | 31.9215 | 32.0769 | 32.2322 | 32.3876 | 32.5429 | 32.6983 | 32.8536 | 33.009 | 33.1643 | 33.3197 | 33.475 | 33.6304
8.7 | 0 | 4.05 | 4.1338 | 3.993 | 3.893 | 5.031 | 6.2528 | 14.9813 | 22.9178 | 29.2703 | 33.9793 | 0 | 0.405 | 0.81 | 1.215 | 1.62 | 2.025 | 2.43 | 2.835 | 3.24 | 3.645 | 4.05 | 4.0668 | 4.0835 | 4.1003 | 4.117 | 4.1338 | 4.1056 | 4.0775 | 4.0493 | 4.0212 | 3.993 | 3.983 | 3.973 | 3.963 | 3.953 | 3.943 | 3.933 | 3.923 | 3.913 | 3.903 | 3.893 | 3.9689 | 4.0447 | 4.1206 | 4.1965 | 4.2723 | 4.3482 | 4.4241 | 4.4999 | 4.5758 | 4.6517 | 4.7275 | 4.8034 | 4.8793 | 4.9551 | 5.031 | 5.1125 | 5.1939 | 5.2754 | 5.3568 | 5.4383 | 5.5197 | 5.6012 | 5.6826 | 5.7641 | 5.8455 | 5.927 | 6.0084 | 6.0899 | 6.1713 | 6.2528 | 6.5437 | 6.8347 | 7.1256 | 7.4166 | 7.7075 | 7.9985 | 8.2894 | 8.5804 | 8.8713 | 9.1623 | 9.4532 | 9.7442 | 10.0351 | 10.3261 | 10.617 | 10.908 | 11.1989 | 11.4899 | 11.7808 | 12.0718 | 12.3627 | 12.6537 | 12.9446 | 13.2356 | 13.5265 | 13.8175 | 14.1084 | 14.3994 | 14.6903 | 14.9813 | 15.2458 | 15.5104 | 15.7749 | 16.0395 | 16.304 | 16.5686 | 16.8331 | 17.0977 | 17.3622 | 17.6268 | 17.8913 | 18.1559 | 18.4204 | 18.685 | 18.9495 | 19.2141 | 19.4786 | 19.7432 | 20.0077 | 20.2723 | 20.5368 | 20.8014 | 21.0659 | 21.3305 | 21.595 | 21.8596 | 22.1241 | 22.3887 | 22.6532 | 22.9178 | 23.1295 | 23.3413 | 23.553 | 23.7648 | 23.9765 | 24.1883 | 24.4 | 24.6118 | 24.8235 | 25.0353 | 25.247 | 25.4588 | 25.6705 | 25.8823 | 26.094 | 26.3058 | 26.5175 | 26.7293 | 26.941 | 27.1528 | 27.3645 | 27.5763 | 27.788 | 27.9998 | 28.2115 | 28.4233 | 28.635 | 28.8468 | 29.0585 | 29.2703 | 29.4272 | 29.5842 | 29.7412 | 29.8981 | 30.0551 | 30.2121 | 30.369 | 30.526 | 30.683 | 30.8399 | 30.9969 | 31.1539 | 31.3108 | 31.4678 | 31.6248 | 31.7817 | 31.9387 | 32.0957 | 32.2526 | 32.4096 | 32.5666 | 32.7235 | 32.8805 | 33.0375 | 33.1944 | 33.3514 | 33.5084 | 33.6653 | 33.8223 | 33.9792
8.75 | 0 | 4.09 | 4.1794 | 4.0375 | 3.9375 | 5.0875 | 6.3219 | 15.1381 | 23.1544 | 29.5706 | 34.3281 | 0 | 0.409 | 0.818 | 1.227 | 1.636 | 2.045 | 2.454 | 2.863 | 3.272 | 3.681 | 4.09 | 4.1079 | 4.1258 | 4.1436 | 4.1615 | 4.1794 | 4.151 | 4.1226 | 4.0943 | 4.0659 | 4.0375 | 4.0275 | 4.0175 | 4.0075 | 3.9975 | 3.9875 | 3.9775 | 3.9675 | 3.9575 | 3.9475 | 3.9375 | 4.0142 | 4.0908 | 4.1675 | 4.2442 | 4.3208 | 4.3975 | 4.4742 | 4.5508 | 4.6275 | 4.7042 | 4.7808 | 4.8575 | 4.9342 | 5.0108 | 5.0875 | 5.1698 | 5.2521 | 5.3344 | 5.4167 | 5.499 | 5.5813 | 5.6635 | 5.7458 | 5.8281 | 5.9104 | 5.9927 | 6.075 | 6.1573 | 6.2396 | 6.3219 | 6.6158 | 6.9096 | 7.2035 | 7.4974 | 7.7913 | 8.0851 | 8.379 | 8.6729 | 8.9668 | 9.2606 | 9.5545 | 9.8484 | 10.1423 | 10.4361 | 10.73 | 11.0239 | 11.3178 | 11.6116 | 11.9055 | 12.1994 | 12.4933 | 12.7871 | 13.081 | 13.3749 | 13.6688 | 13.9626 | 14.2565 | 14.5504 | 14.8443 | 15.1381 | 15.4053 | 15.6725 | 15.9398 | 16.207 | 16.4742 | 16.7414 | 17.0086 | 17.2758 | 17.543 | 17.8102 | 18.0774 | 18.3446 | 18.6118 | 18.879 | 19.1463 | 19.4135 | 19.6807 | 19.9479 | 20.2151 | 20.4823 | 20.7495 | 21.0167 | 21.2839 | 21.5511 | 21.8183 | 22.0855 | 22.3528 | 22.62 | 22.8872 | 23.1544 | 23.3683 | 23.5821 | 23.796 | 24.0099 | 24.2238 | 24.4376 | 24.6515 | 24.8654 | 25.0793 | 25.2931 | 25.507 | 25.7209 | 25.9348 | 26.1486 | 26.3625 | 26.5764 | 26.7903 | 27.0041 | 27.218 | 27.4319 | 27.6458 | 27.8596 | 28.0735 | 28.2874 | 28.5013 | 28.7151 | 28.929 | 29.1429 | 29.3568 | 29.5706 | 29.7292 | 29.8878 | 30.0464 | 30.205 | 30.3635 | 30.5221 | 30.6807 | 30.8393 | 30.9979 | 31.1565 | 31.315 | 31.4736 | 31.6322 | 31.7908 | 31.9494 | 32.108 | 32.2665 | 32.4251 | 32.5837 | 32.7423 | 32.9009 | 33.0595 | 33.218 | 33.3766 | 33.5352 | 33.6938 | 33.8524 | 34.011 | 34.1695 | 34.3281
8.8 | 0 | 4.13 | 4.225 | 4.082 | 3.982 | 5.144 | 6.391 | 15.295 | 23.391 | 29.871 | 34.677 | 0 | 0.413 | 0.826 | 1.239 | 1.652 | 2.065 | 2.478 | 2.891 | 3.304 | 3.717 | 4.13 | 4.149 | 4.168 | 4.187 | 4.206 | 4.225 | 4.1964 | 4.1678 | 4.1392 | 4.1106 | 4.082 | 4.072 | 4.062 | 4.052 | 4.042 | 4.032 | 4.022 | 4.012 | 4.002 | 3.992 | 3.982 | 4.0595 | 4.1369 | 4.2144 | 4.2919 | 4.3693 | 4.4468 | 4.5243 | 4.6017 | 4.6792 | 4.7567 | 4.8341 | 4.9116 | 4.9891 | 5.0665 | 5.144 | 5.2271 | 5.3103 | 5.3934 | 5.4765 | 5.5597 | 5.6428 | 5.7259 | 5.8091 | 5.8922 | 5.9753 | 6.0585 | 6.1416 | 6.2247 | 6.3079 | 6.391 | 6.6878 | 6.9846 | 7.2814 | 7.5782 | 7.875 | 8.1718 | 8.4686 | 8.7654 | 9.0622 | 9.359 | 9.6558 | 9.9526 | 10.2494 | 10.5462 | 10.843 | 11.1398 | 11.4366 | 11.7334 | 12.0302 | 12.327 | 12.6238 | 12.9206 | 13.2174 | 13.5142 | 13.811 | 14.1078 | 14.4046 | 14.7014 | 14.9982 | 15.295 | 15.5649 | 15.8347 | 16.1046 | 16.3745 | 16.6443 | 16.9142 | 17.1841 | 17.4539 | 17.7238 | 17.9937 | 18.2635 | 18.5334 | 18.8033 | 19.0731 | 19.343 | 19.6129 | 19.8827 | 20.1526 | 20.4225 | 20.6923 | 20.9622 | 21.2321 | 21.5019 | 21.7718 | 22.0417 | 22.3115 | 22.5814 | 22.8513 | 23.1211 | 23.391 | 23.607 | 23.823 | 24.039 | 24.255 | 24.471 | 24.687 | 24.903 | 25.119 | 25.335 | 25.551 | 25.767 | 25.983 | 26.199 | 26.415 | 26.631 | 26.847 | 27.063 | 27.279 | 27.495 | 27.711 | 27.927 | 28.143 | 28.359 | 28.575 | 28.791 | 29.007 | 29.223 | 29.439 | 29.655 | 29.871 | 30.0312 | 30.1914 | 30.3516 | 30.5118 | 30.672 | 30.8322 | 30.9924 | 31.1526 | 31.3128 | 31.473 | 31.6332 | 31.7934 | 31.9536 | 32.1138 | 32.274 | 32.4342 | 32.5944 | 32.7546 | 32.9148 | 33.075 | 33.2352 | 33.3954 | 33.5556 | 33.7158 | 33.876 | 34.0362 | 34.1964 | 34.3566 | 34.5168 | 34.677
8.85 | 0 | 4.17 | 4.2706 | 4.1265 | 4.0265 | 5.2005 | 6.4601 | 15.4519 | 23.6276 | 30.1714 | 35.0259 | 0 | 0.417 | 0.834 | 1.251 | 1.668 | 2.085 | 2.502 | 2.919 | 3.336 | 3.753 | 4.17 | 4.1901 | 4.2103 | 4.2304 | 4.2505 | 4.2706 | 4.2418 | 4.213 | 4.1842 | 4.1553 | 4.1265 | 4.1165 | 4.1065 | 4.0965 | 4.0865 | 4.0765 | 4.0665 | 4.0565 | 4.0465 | 4.0365 | 4.0265 | 4.1048 | 4.183 | 4.2613 | 4.3396 | 4.4178 | 4.4961 | 4.5744 | 4.6526 | 4.7309 | 4.8092 | 4.8874 | 4.9657 | 5.044 | 5.1222 | 5.2005 | 5.2845 | 5.3685 | 5.4524 | 5.5364 | 5.6204 | 5.7044 | 5.7883 | 5.8723 | 5.9563 | 6.0403 | 6.1242 | 6.2082 | 6.2922 | 6.3762 | 6.4601 | 6.7599 | 7.0596 | 7.3593 | 7.659 | 7.9588 | 8.2585 | 8.5582 | 8.8579 | 9.1577 | 9.4574 | 9.7571 | 10.0568 | 10.3566 | 10.6563 | 10.956 | 11.2557 | 11.5555 | 11.8552 | 12.1549 | 12.4546 | 12.7544 | 13.0541 | 13.3538 | 13.6535 | 13.9533 | 14.253 | 14.5527 | 14.8524 | 15.1522 | 15.4519 | 15.7244 | 15.9969 | 16.2695 | 16.542 | 16.8145 | 17.087 | 17.3596 | 17.6321 | 17.9046 | 18.1771 | 18.4497 | 18.7222 | 18.9947 | 19.2672 | 19.5398 | 19.8123 | 20.0848 | 20.3573 | 20.6299 | 20.9024 | 21.1749 | 21.4474 | 21.72 | 21.9925 | 22.265 | 22.5375 | 22.8101 | 23.0826 | 23.3551 | 23.6276 | 23.8458 | 24.0639 | 24.282 | 24.5001 | 24.7183 | 24.9364 | 25.1545 | 25.3726 | 25.5908 | 25.8089 | 26.027 | 26.2451 | 26.4633 | 26.6814 | 26.8995 | 27.1176 | 27.3358 | 27.5539 | 27.772 | 27.9901 | 28.2083 | 28.4264 | 28.6445 | 28.8626 | 29.0808 | 29.2989 | 29.517 | 29.7351 | 29.9533 | 30.1714 | 30.3332 | 30.495 | 30.6568 | 30.8186 | 30.9805 | 31.1423 | 31.3041 | 31.4659 | 31.6277 | 31.7895 | 31.9514 | 32.1132 | 32.275 | 32.4368 | 32.5986 | 32.7604 | 32.9223 | 33.0841 | 33.2459 | 33.4077 | 33.5695 | 33.7313 | 33.8932 | 34.055 | 34.2168 | 34.3786 | 34.5404 | 34.7022 | 34.8641 | 35.0259
8.9 | 0 | 4.21 | 4.3163 | 4.171 | 4.071 | 5.257 | 6.5293 | 15.6088 | 23.8643 | 30.4718 | 35.3748 | 0 | 0.421 | 0.842 | 1.263 | 1.684 | 2.105 | 2.526 | 2.947 | 3.368 | 3.789 | 4.21 | 4.2313 | 4.2525 | 4.2738 | 4.295 | 4.3163 | 4.2872 | 4.2582 | 4.2291 | 4.2001 | 4.171 | 4.161 | 4.151 | 4.141 | 4.131 | 4.121 | 4.111 | 4.101 | 4.091 | 4.081 | 4.071 | 4.1501 | 4.2291 | 4.3082 | 4.3873 | 4.4663 | 4.5454 | 4.6245 | 4.7035 | 4.7826 | 4.8617 | 4.9407 | 5.0198 | 5.0989 | 5.1779 | 5.257 | 5.3418 | 5.4266 | 5.5115 | 5.5963 | 5.6811 | 5.7659 | 5.8507 | 5.9355 | 6.0204 | 6.1052 | 6.19 | 6.2748 | 6.3596 | 6.4444 | 6.5293 | 6.8319 | 7.1346 | 7.4372 | 7.7399 | 8.0425 | 8.3452 | 8.6478 | 8.9505 | 9.2531 | 9.5558 | 9.8584 | 10.1611 | 10.4637 | 10.7664 | 11.069 | 11.3717 | 11.6743 | 11.977 | 12.2796 | 12.5823 | 12.8849 | 13.1876 | 13.4902 | 13.7929 | 14.0955 | 14.3982 | 14.7008 | 15.0035 | 15.3061 | 15.6088 | 15.8839 | 16.1591 | 16.4343 | 16.7095 | 16.9847 | 17.2599 | 17.535 | 17.8102 | 18.0854 | 18.3606 | 18.6358 | 18.911 | 19.1861 | 19.4613 | 19.7365 | 20.0117 | 20.2869 | 20.5621 | 20.8372 | 21.1124 | 21.3876 | 21.6628 | 21.938 | 22.2132 | 22.4883 | 22.7635 | 23.0387 | 23.3139 | 23.5891 | 23.8643 | 24.0845 | 24.3048 | 24.525 | 24.7453 | 24.9655 | 25.1858 | 25.406 | 25.6263 | 25.8465 | 26.0668 | 26.287 | 26.5073 | 26.7275 | 26.9478 | 27.168 | 27.3883 | 27.6085 | 27.8288 | 28.049 | 28.2693 | 28.4895 | 28.7098 | 28.93 | 29.1503 | 29.3705 | 29.5908 | 29.811 | 30.0313 | 30.2515 | 30.4718 | 30.6352 | 30.7986 | 30.9621 | 31.1255 | 31.2889 | 31.4524 | 31.6158 | 31.7792 | 31.9427 | 32.1061 | 32.2695 | 32.433 | 32.5964 | 32.7598 | 32.9233 | 33.0867 | 33.2501 | 33.4136 | 33.577 | 33.7404 | 33.9039 | 34.0673 | 34.2307 | 34.3942 | 34.5576 | 34.721 | 34.8845 | 35.0479 | 35.2113 | 35.3747
8.95 | 0 | 4.25 | 4.3619 | 4.2155 | 4.1155 | 5.3135 | 6.5984 | 15.7656 | 24.1009 | 30.7721 | 35.7236 | 0 | 0.425 | 0.85 | 1.275 | 1.7 | 2.125 | 2.55 | 2.975 | 3.4 | 3.825 | 4.25 | 4.2724 | 4.2948 | 4.3171 | 4.3395 | 4.3619 | 4.3326 | 4.3033 | 4.2741 | 4.2448 | 4.2155 | 4.2055 | 4.1955 | 4.1855 | 4.1755 | 4.1655 | 4.1555 | 4.1455 | 4.1355 | 4.1255 | 4.1155 | 4.1954 | 4.2752 | 4.3551 | 4.435 | 4.5148 | 4.5947 | 4.6746 | 4.7544 | 4.8343 | 4.9142 | 4.994 | 5.0739 | 5.1538 | 5.2336 | 5.3135 | 5.3992 | 5.4848 | 5.5705 | 5.6561 | 5.7418 | 5.8275 | 5.9131 | 5.9988 | 6.0844 | 6.1701 | 6.2557 | 6.3414 | 6.4271 | 6.5127 | 6.5984 | 6.904 | 7.2095 | 7.5151 | 7.8207 | 8.1263 | 8.4318 | 8.7374 | 9.043 | 9.3486 | 9.6541 | 9.9597 | 10.2653 | 10.5709 | 10.8764 | 11.182 | 11.4876 | 11.7932 | 12.0987 | 12.4043 | 12.7099 | 13.0155 | 13.321 | 13.6266 | 13.9322 | 14.2378 | 14.5433 | 14.8489 | 15.1545 | 15.4601 | 15.7656 | 16.0435 | 16.3213 | 16.5992 | 16.877 | 17.1548 | 17.4327 | 17.7105 | 17.9884 | 18.2662 | 18.544 | 18.8219 | 19.0997 | 19.3776 | 19.6554 | 19.9333 | 20.2111 | 20.4889 | 20.7668 | 21.0446 | 21.3225 | 21.6003 | 21.8781 | 22.156 | 22.4338 | 22.7117 | 22.9895 | 23.2674 | 23.5452 | 23.823 | 24.1009 | 24.3233 | 24.5456 | 24.768 | 24.9904 | 25.2128 | 25.4351 | 25.6575 | 25.8799 | 26.1023 | 26.3246 | 26.547 | 26.7694 | 26.9918 | 27.2141 | 27.4365 | 27.6589 | 27.8813 | 28.1036 | 28.326 | 28.5484 | 28.7708 | 28.9931 | 29.2155 | 29.4379 | 29.6603 | 29.8826 | 30.105 | 30.3274 | 30.5498 | 30.7721 | 30.9372 | 31.1022 | 31.2673 | 31.4323 | 31.5974 | 31.7624 | 31.9275 | 32.0925 | 32.2576 | 32.4226 | 32.5877 | 32.7527 | 32.9178 | 33.0828 | 33.2479 | 33.4129 | 33.578 | 33.743 | 33.9081 | 34.0731 | 34.2382 | 34.4032 | 34.5683 | 34.7333 | 34.8984 | 35.0634 | 35.2285 | 35.3935 | 35.5586 | 35.7236
9 | 0 | 4.29 | 4.4075 | 4.26 | 4.16 | 5.37 | 6.6675 | 15.9225 | 24.3375 | 31.0725 | 36.0725 | 0 | 0.429 | 0.858 | 1.287 | 1.716 | 2.145 | 2.574 | 3.003 | 3.432 | 3.861 | 4.29 | 4.3135 | 4.337 | 4.3605 | 4.384 | 4.4075 | 4.378 | 4.3485 | 4.319 | 4.2895 | 4.26 | 4.25 | 4.24 | 4.23 | 4.22 | 4.21 | 4.2 | 4.19 | 4.18 | 4.17 | 4.16 | 4.2407 | 4.3213 | 4.402 | 4.4827 | 4.5633 | 4.644 | 4.7247 | 4.8053 | 4.886 | 4.9667 | 5.0473 | 5.128 | 5.2087 | 5.2893 | 5.37 | 5.4565 | 5.543 | 5.6295 | 5.716 | 5.8025 | 5.889 | 5.9755 | 6.062 | 6.1485 | 6.235 | 6.3215 | 6.408 | 6.4945 | 6.581 | 6.6675 | 6.976 | 7.2845 | 7.593 | 7.9015 | 8.21 | 8.5185 | 8.827 | 9.1355 | 9.444 | 9.7525 | 10.061 | 10.3695 | 10.678 | 10.9865 | 11.295 | 11.6035 | 11.912 | 12.2205 | 12.529 | 12.8375 | 13.146 | 13.4545 | 13.763 | 14.0715 | 14.38 | 14.6885 | 14.997 | 15.3055 | 15.614 | 15.9225 | 16.203 | 16.4835 | 16.764 | 17.0445 | 17.325 | 17.6055 | 17.886 | 18.1665 | 18.447 | 18.7275 | 19.008 | 19.2885 | 19.569 | 19.8495 | 20.13 | 20.4105 | 20.691 | 20.9715 | 21.252 | 21.5325 | 21.813 | 22.0935 | 22.374 | 22.6545 | 22.935 | 23.2155 | 23.496 | 23.7765 | 24.057 | 24.3375 | 24.562 | 24.7865 | 25.011 | 25.2355 | 25.46 | 25.6845 | 25.909 | 26.1335 | 26.358 | 26.5825 | 26.807 | 27.0315 | 27.256 | 27.4805 | 27.705 | 27.9295 | 28.154 | 28.3785 | 28.603 | 28.8275 | 29.052 | 29.2765 | 29.501 | 29.7255 | 29.95 | 30.1745 | 30.399 | 30.6235 | 30.848 | 31.0725 | 31.2392 | 31.4058 | 31.5725 | 31.7392 | 31.9058 | 32.0725 | 32.2392 | 32.4058 | 32.5725 | 32.7392 | 32.9058 | 33.0725 | 33.2392 | 33.4058 | 33.5725 | 33.7392 | 33.9058 | 34.0725 | 34.2392 | 34.4058 | 34.5725 | 34.7392 | 34.9058 | 35.0725 | 35.2392 | 35.4058 | 35.5725 | 35.7392 | 35.9058 | 36.0725
9.05 | 0 | 4.33 | 4.4531 | 4.3045 | 4.2045 | 5.4265 | 6.7366 | 16.0794 | 24.5741 | 31.3729 | 36.4214 | 4.4409e-16 | 0.433 | 0.866 | 1.299 | 1.732 | 2.165 | 2.598 | 3.031 | 3.464 | 3.897 | 4.33 | 4.3546 | 4.3793 | 4.4039 | 4.4285 | 4.4531 | 4.4234 | 4.3937 | 4.364 | 4.3342 | 4.3045 | 4.2945 | 4.2845 | 4.2745 | 4.2645 | 4.2545 | 4.2445 | 4.2345 | 4.2245 | 4.2145 | 4.2045 | 4.286 | 4.3674 | 4.4489 | 4.5304 | 4.6118 | 4.6933 | 4.7748 | 4.8562 | 4.9377 | 5.0192 | 5.1006 | 5.1821 | 5.2636 | 5.345 | 5.4265 | 5.5138 | 5.6012 | 5.6885 | 5.7759 | 5.8632 | 5.9506 | 6.0379 | 6.1252 | 6.2126 | 6.2999 | 6.3873 | 6.4746 | 6.5619 | 6.6493 | 6.7366 | 7.0481 | 7.3595 | 7.6709 | 7.9823 | 8.2938 | 8.6052 | 8.9166 | 9.228 | 9.5395 | 9.8509 | 10.1623 | 10.4737 | 10.7852 | 11.0966 | 11.408 | 11.7194 | 12.0309 | 12.3423 | 12.6537 | 12.9651 | 13.2766 | 13.588 | 13.8994 | 14.2108 | 14.5223 | 14.8337 | 15.1451 | 15.4565 | 15.768 | 16.0794 | 16.3625 | 16.6457 | 16.9289 | 17.212 | 17.4952 | 17.7783 | 18.0615 | 18.3446 | 18.6278 | 18.911 | 19.1941 | 19.4773 | 19.7604 | 20.0436 | 20.3268 | 20.6099 | 20.8931 | 21.1762 | 21.4594 | 21.7425 | 22.0257 | 22.3089 | 22.592 | 22.8752 | 23.1583 | 23.4415 | 23.7247 | 24.0078 | 24.291 | 24.5741 | 24.8008 | 25.0274 | 25.254 | 25.4806 | 25.7073 | 25.9339 | 26.1605 | 26.3871 | 26.6138 | 26.8404 | 27.067 | 27.2936 | 27.5203 | 27.7469 | 27.9735 | 28.2001 | 28.4268 | 28.6534 | 28.88 | 29.1066 | 29.3333 | 29.5599 | 29.7865 | 30.0131 | 30.2398 | 30.4664 | 30.693 | 30.9196 | 31.1463 | 31.3729 | 31.5412 | 31.7094 | 31.8777 | 32.046 | 32.2143 | 32.3826 | 32.5509 | 32.7191 | 32.8874 | 33.0557 | 33.224 | 33.3923 | 33.5606 | 33.7288 | 33.8971 | 34.0654 | 34.2337 | 34.402 | 34.5703 | 34.7385 | 34.9068 | 35.0751 | 35.2434 | 35.4117 | 35.58 | 35.7482 | 35.9165 | 36.0848 | 36.2531 | 36.4214
9.1 | 0 | 4.37 | 4.4988 | 4.349 | 4.249 | 5.483 | 6.8058 | 16.2363 | 24.8108 | 31.6733 | 36.7703 | 0 | 0.437 | 0.874 | 1.311 | 1.748 | 2.185 | 2.622 | 3.059 | 3.496 | 3.933 | 4.37 | 4.3958 | 4.4215 | 4.4473 | 4.473 | 4.4988 | 4.4688 | 4.4389 | 4.4089 | 4.379 | 4.349 | 4.339 | 4.329 | 4.319 | 4.309 | 4.299 | 4.289 | 4.279 | 4.269 | 4.259 | 4.249 | 4.3313 | 4.4135 | 4.4958 | 4.5781 | 4.6603 | 4.7426 | 4.8249 | 4.9071 | 4.9894 | 5.0717 | 5.1539 | 5.2362 | 5.3185 | 5.4007 | 5.483 | 5.5712 | 5.6594 | 5.7476 | 5.8357 | 5.9239 | 6.0121 | 6.1003 | 6.1885 | 6.2767 | 6.3648 | 6.453 | 6.5412 | 6.6294 | 6.7176 | 6.8058 | 7.1201 | 7.4345 | 7.7488 | 8.0632 | 8.3775 | 8.6919 | 9.0062 | 9.3206 | 9.6349 | 9.9493 | 10.2636 | 10.578 | 10.8923 | 11.2067 | 11.521 | 11.8354 | 12.1497 | 12.4641 | 12.7784 | 13.0928 | 13.4071 | 13.7215 | 14.0358 | 14.3502 | 14.6645 | 14.9789 | 15.2932 | 15.6076 | 15.9219 | 16.2363 | 16.5221 | 16.8079 | 17.0937 | 17.3795 | 17.6653 | 17.9512 | 18.237 | 18.5228 | 18.8086 | 19.0944 | 19.3802 | 19.6661 | 19.9519 | 20.2377 | 20.5235 | 20.8093 | 21.0951 | 21.381 | 21.6668 | 21.9526 | 22.2384 | 22.5242 | 22.81 | 23.0959 | 23.3817 | 23.6675 | 23.9533 | 24.2391 | 24.5249 | 24.8108 | 25.0395 | 25.2683 | 25.497 | 25.7258 | 25.9545 | 26.1833 | 26.412 | 26.6408 | 26.8695 | 27.0983 | 27.327 | 27.5558 | 27.7845 | 28.0133 | 28.242 | 28.4708 | 28.6995 | 28.9283 | 29.157 | 29.3858 | 29.6145 | 29.8433 | 30.072 | 30.3008 | 30.5295 | 30.7583 | 30.987 | 31.2158 | 31.4445 | 31.6733 | 31.8432 | 32.0131 | 32.183 | 32.3529 | 32.5228 | 32.6927 | 32.8626 | 33.0325 | 33.2024 | 33.3723 | 33.5422 | 33.7121 | 33.882 | 34.0519 | 34.2218 | 34.3917 | 34.5616 | 34.7315 | 34.9014 | 35.0713 | 35.2412 | 35.4111 | 35.581 | 35.7509 | 35.9208 | 36.0907 | 36.2606 | 36.4305 | 36.6004 | 36.7702
9.15 | 0 | 4.41 | 4.5444 | 4.3935 | 4.2935 | 5.5395 | 6.8749 | 16.3931 | 25.0474 | 31.9736 | 37.1191 | 0 | 0.441 | 0.882 | 1.323 | 1.764 | 2.205 | 2.646 | 3.087 | 3.528 | 3.969 | 4.41 | 4.4369 | 4.4638 | 4.4906 | 4.5175 | 4.5444 | 4.5142 | 4.484 | 4.4539 | 4.4237 | 4.3935 | 4.3835 | 4.3735 | 4.3635 | 4.3535 | 4.3435 | 4.3335 | 4.3235 | 4.3135 | 4.3035 | 4.2935 | 4.3766 | 4.4596 | 4.5427 | 4.6258 | 4.7088 | 4.7919 | 4.875 | 4.958 | 5.0411 | 5.1242 | 5.2072 | 5.2903 | 5.3734 | 5.4564 | 5.5395 | 5.6285 | 5.7176 | 5.8066 | 5.8956 | 5.9846 | 6.0737 | 6.1627 | 6.2517 | 6.3407 | 6.4298 | 6.5188 | 6.6078 | 6.6968 | 6.7859 | 6.8749 | 7.1922 | 7.5094 | 7.8267 | 8.144 | 8.4613 | 8.7785 | 9.0958 | 9.4131 | 9.7304 | 10.0476 | 10.3649 | 10.6822 | 10.9995 | 11.3167 | 11.634 | 11.9513 | 12.2686 | 12.5858 | 12.9031 | 13.2204 | 13.5377 | 13.8549 | 14.1722 | 14.4895 | 14.8068 | 15.124 | 15.4413 | 15.7586 | 16.0759 | 16.3931 | 16.6816 | 16.9701 | 17.2586 | 17.547 | 17.8355 | 18.124 | 18.4125 | 18.7009 | 18.9894 | 19.2779 | 19.5664 | 19.8548 | 20.1433 | 20.4318 | 20.7203 | 21.0087 | 21.2972 | 21.5857 | 21.8742 | 22.1626 | 22.4511 | 22.7396 | 23.0281 | 23.3165 | 23.605 | 23.8935 | 24.182 | 24.4704 | 24.7589 | 25.0474 | 25.2783 | 25.5091 | 25.74 | 25.9709 | 26.2018 | 26.4326 | 26.6635 | 26.8944 | 27.1253 | 27.3561 | 27.587 | 27.8179 | 28.0488 | 28.2796 | 28.5105 | 28.7414 | 28.9723 | 29.2031 | 29.434 | 29.6649 | 29.8958 | 30.1266 | 30.3575 | 30.5884 | 30.8193 | 31.0501 | 31.281 | 31.5119 | 31.7428 | 31.9736 | 32.1451 | 32.3167 | 32.4882 | 32.6597 | 32.8312 | 33.0027 | 33.1742 | 33.3458 | 33.5173 | 33.6888 | 33.8603 | 34.0318 | 34.2033 | 34.3749 | 34.5464 | 34.7179 | 34.8894 | 35.0609 | 35.2324 | 35.404 | 35.5755 | 35.747 | 35.9185 | 36.09 | 36.2615 | 36.4331 | 36.6046 | 36.7761 | 36.9476 | 37.1191
9.2 | 0 | 4.45 | 4.59 | 4.438 | 4.338 | 5.596 | 6.944 | 16.55 | 25.284 | 32.274 | 37.468 | 0 | 0.445 | 0.89 | 1.335 | 1.78 | 2.225 | 2.67 | 3.115 | 3.56 | 4.005 | 4.45 | 4.478 | 4.506 | 4.534 | 4.562 | 4.59 | 4.5596 | 4.5292 | 4.4988 | 4.4684 | 4.438 | 4.428 | 4.418 | 4.408 | 4.398 | 4.388 | 4.378 | 4.368 | 4.358 | 4.348 | 4.338 | 4.4219 | 4.5057 | 4.5896 | 4.6735 | 4.7573 | 4.8412 | 4.9251 | 5.0089 | 5.0928 | 5.1767 | 5.2605 | 5.3444 | 5.4283 | 5.5121 | 5.596 | 5.6859 | 5.7757 | 5.8656 | 5.9555 | 6.0453 | 6.1352 | 6.2251 | 6.3149 | 6.4048 | 6.4947 | 6.5845 | 6.6744 | 6.7643 | 6.8541 | 6.944 | 7.2642 | 7.5844 | 7.9046 | 8.2248 | 8.545 | 8.8652 | 9.1854 | 9.5056 | 9.8258 | 10.146 | 10.4662 | 10.7864 | 11.1066 | 11.4268 | 11.747 | 12.0672 | 12.3874 | 12.7076 | 13.0278 | 13.348 | 13.6682 | 13.9884 | 14.3086 | 14.6288 | 14.949 | 15.2692 | 15.5894 | 15.9096 | 16.2298 | 16.55 | 16.8411 | 17.1323 | 17.4234 | 17.7145 | 18.0057 | 18.2968 | 18.5879 | 18.8791 | 19.1702 | 19.4613 | 19.7525 | 20.0436 | 20.3347 | 20.6259 | 20.917 | 21.2081 | 21.4993 | 21.7904 | 22.0815 | 22.3727 | 22.6638 | 22.9549 | 23.2461 | 23.5372 | 23.8283 | 24.1195 | 24.4106 | 24.7017 | 24.9929 | 25.284 | 25.517 | 25.75 | 25.983 | 26.216 | 26.449 | 26.682 | 26.915 | 27.148 | 27.381 | 27.614 | 27.847 | 28.08 | 28.313 | 28.546 | 28.779 | 29.012 | 29.245 | 29.478 | 29.711 | 29.944 | 30.177 | 30.41 | 30.643 | 30.876 | 31.109 | 31.342 | 31.575 | 31.808 | 32.041 | 32.274 | 32.4471 | 32.6203 | 32.7934 | 32.9665 | 33.1397 | 33.3128 | 33.4859 | 33.6591 | 33.8322 | 34.0053 | 34.1785 | 34.3516 | 34.5247 | 34.6979 | 34.871 | 35.0441 | 35.2173 | 35.3904 | 35.5635 | 35.7367 | 35.9098 | 36.0829 | 36.2561 | 36.4292 | 36.6023 | 36.7755 | 36.9486 | 37.1217 | 37.2949 | 37.468
9.25 | 0 | 4.49 | 4.6356 | 4.4825 | 4.3825 | 5.6525 | 7.0131 | 16.7069 | 25.5206 | 32.5744 | 37.8169 | 0 | 0.449 | 0.898 | 1.347 | 1.796 | 2.245 | 2.694 | 3.143 | 3.592 | 4.041 | 4.49 | 4.5191 | 4.5483 | 4.5774 | 4.6065 | 4.6356 | 4.605 | 4.5744 | 4.5438 | 4.5131 | 4.4825 | 4.4725 | 4.4625 | 4.4525 | 4.4425 | 4.4325 | 4.4225 | 4.4125 | 4.4025 | 4.3925 | 4.3825 | 4.4672 | 4.5518 | 4.6365 | 4.7212 | 4.8058 | 4.8905 | 4.9752 | 5.0598 | 5.1445 | 5.2292 | 5.3138 | 5.3985 | 5.4832 | 5.5678 | 5.6525 | 5.7432 | 5.8339 | 5.9246 | 6.0153 | 6.106 | 6.1968 | 6.2875 | 6.3782 | 6.4689 | 6.5596 | 6.6503 | 6.741 | 6.8317 | 6.9224 | 7.0131 | 7.3363 | 7.6594 | 7.9825 | 8.3056 | 8.6288 | 8.9519 | 9.275 | 9.5981 | 9.9213 | 10.2444 | 10.5675 | 10.8906 | 11.2138 | 11.5369 | 11.86 | 12.1831 | 12.5063 | 12.8294 | 13.1525 | 13.4756 | 13.7988 | 14.1219 | 14.445 | 14.7681 | 15.0913 | 15.4144 | 15.7375 | 16.0606 | 16.3838 | 16.7069 | 17.0007 | 17.2945 | 17.5883 | 17.882 | 18.1758 | 18.4696 | 18.7634 | 19.0572 | 19.351 | 19.6448 | 19.9386 | 20.2324 | 20.5262 | 20.82 | 21.1138 | 21.4075 | 21.7013 | 21.9951 | 22.2889 | 22.5827 | 22.8765 | 23.1703 | 23.4641 | 23.7579 | 24.0517 | 24.3455 | 24.6393 | 24.933 | 25.2268 | 25.5206 | 25.7558 | 25.9909 | 26.226 | 26.4611 | 26.6963 | 26.9314 | 27.1665 | 27.4016 | 27.6368 | 27.8719 | 28.107 | 28.3421 | 28.5773 | 28.8124 | 29.0475 | 29.2826 | 29.5178 | 29.7529 | 29.988 | 30.2231 | 30.4583 | 30.6934 | 30.9285 | 31.1636 | 31.3988 | 31.6339 | 31.869 | 32.1041 | 32.3393 | 32.5744 | 32.7491 | 32.9239 | 33.0986 | 33.2734 | 33.4481 | 33.6229 | 33.7976 | 33.9724 | 34.1471 | 34.3219 | 34.4966 | 34.6714 | 34.8461 | 35.0209 | 35.1956 | 35.3704 | 35.5451 | 35.7199 | 35.8946 | 36.0694 | 36.2441 | 36.4189 | 36.5936 | 36.7684 | 36.9431 | 37.1179 | 37.2926 | 37.4674 | 37.6421 | 37.8169
9.3 | 0 | 4.53 | 4.6813 | 4.527 | 4.427 | 5.709 | 7.0823 | 16.8638 | 25.7573 | 32.8748 | 38.1658 | 0 | 0.453 | 0.906 | 1.359 | 1.812 | 2.265 | 2.718 | 3.171 | 3.624 | 4.077 | 4.53 | 4.5603 | 4.5905 | 4.6208 | 4.651 | 4.6813 | 4.6504 | 4.6196 | 4.5887 | 4.5579 | 4.527 | 4.517 | 4.507 | 4.497 | 4.487 | 4.477 | 4.467 | 4.457 | 4.447 | 4.437 | 4.427 | 4.5125 | 4.5979 | 4.6834 | 4.7689 | 4.8543 | 4.9398 | 5.0253 | 5.1107 | 5.1962 | 5.2817 | 5.3671 | 5.4526 | 5.5381 | 5.6235 | 5.709 | 5.8006 | 5.8921 | 5.9837 | 6.0752 | 6.1668 | 6.2583 | 6.3499 | 6.4414 | 6.533 | 6.6245 | 6.7161 | 6.8076 | 6.8992 | 6.9907 | 7.0823 | 7.4083 | 7.7344 | 8.0604 | 8.3865 | 8.7125 | 9.0386 | 9.3646 | 9.6907 | 10.0167 | 10.3428 | 10.6688 | 10.9949 | 11.3209 | 11.647 | 11.973 | 12.2991 | 12.6251 | 12.9512 | 13.2772 | 13.6033 | 13.9293 | 14.2554 | 14.5814 | 14.9075 | 15.2335 | 15.5596 | 15.8856 | 16.2117 | 16.5377 | 16.8638 | 17.1602 | 17.4567 | 17.7531 | 18.0496 | 18.346 | 18.6425 | 18.9389 | 19.2354 | 19.5318 | 19.8283 | 20.1247 | 20.4212 | 20.7176 | 21.0141 | 21.3105 | 21.607 | 21.9034 | 22.1999 | 22.4963 | 22.7928 | 23.0892 | 23.3857 | 23.6821 | 23.9786 | 24.275 | 24.5715 | 24.8679 | 25.1644 | 25.4608 | 25.7573 | 25.9945 | 26.2318 | 26.469 | 26.7063 | 26.9435 | 27.1808 | 27.418 | 27.6553 | 27.8925 | 28.1298 | 28.367 | 28.6043 | 28.8415 | 29.0788 | 29.316 | 29.5533 | 29.7905 | 30.0278 | 30.265 | 30.5023 | 30.7395 | 30.9768 | 31.214 | 31.4513 | 31.6885 | 31.9258 | 32.163 | 32.4003 | 32.6375 | 32.8748 | 33.0511 | 33.2275 | 33.4039 | 33.5802 | 33.7566 | 33.933 | 34.1093 | 34.2857 | 34.4621 | 34.6384 | 34.8148 | 34.9912 | 35.1675 | 35.3439 | 35.5203 | 35.6966 | 35.873 | 36.0494 | 36.2257 | 36.4021 | 36.5785 | 36.7548 | 36.9312 | 37.1076 | 37.2839 | 37.4603 | 37.6367 | 37.813 | 37.9894 | 38.1657
9.35 | 0 | 4.57 | 4.7269 | 4.5715 | 4.4715 | 5.7655 | 7.1514 | 17.0206 | 25.9939 | 33.1751 | 38.5146 | 0 | 0.457 | 0.914 | 1.371 | 1.828 | 2.285 | 2.742 | 3.199 | 3.656 | 4.113 | 4.57 | 4.6014 | 4.6328 | 4.6641 | 4.6955 | 4.7269 | 4.6958 | 4.6647 | 4.6337 | 4.6026 | 4.5715 | 4.5615 | 4.5515 | 4.5415 | 4.5315 | 4.5215 | 4.5115 | 4.5015 | 4.4915 | 4.4815 | 4.4715 | 4.5578 | 4.644 | 4.7303 | 4.8166 | 4.9028 | 4.9891 | 5.0754 | 5.1616 | 5.2479 | 5.3342 | 5.4204 | 5.5067 | 5.593 | 5.6792 | 5.7655 | 5.8579 | 5.9503 | 6.0427 | 6.1351 | 6.2275 | 6.3199 | 6.4122 | 6.5046 | 6.597 | 6.6894 | 6.7818 | 6.8742 | 6.9666 | 7.059 | 7.1514 | 7.4804 | 7.8093 | 8.1383 | 8.4673 | 8.7963 | 9.1252 | 9.4542 | 9.7832 | 10.1122 | 10.4411 | 10.7701 | 11.0991 | 11.4281 | 11.757 | 12.086 | 12.415 | 12.744 | 13.0729 | 13.4019 | 13.7309 | 14.0599 | 14.3888 | 14.7178 | 15.0468 | 15.3758 | 15.7047 | 16.0337 | 16.3627 | 16.6917 | 17.0206 | 17.3197 | 17.6188 | 17.918 | 18.2171 | 18.5162 | 18.8153 | 19.1144 | 19.4135 | 19.7126 | 20.0117 | 20.3108 | 20.6099 | 20.909 | 21.2081 | 21.5073 | 21.8064 | 22.1055 | 22.4046 | 22.7037 | 23.0028 | 23.3019 | 23.601 | 23.9001 | 24.1992 | 24.4983 | 24.7974 | 25.0966 | 25.3957 | 25.6948 | 25.9939 | 26.2333 | 26.4726 | 26.712 | 26.9514 | 27.1908 | 27.4301 | 27.6695 | 27.9089 | 28.1483 | 28.3876 | 28.627 | 28.8664 | 29.1058 | 29.3451 | 29.5845 | 29.8239 | 30.0633 | 30.3026 | 30.542 | 30.7814 | 31.0208 | 31.2601 | 31.4995 | 31.7389 | 31.9783 | 32.2176 | 32.457 | 32.6964 | 32.9358 | 33.1751 | 33.3531 | 33.5311 | 33.7091 | 33.8871 | 34.065 | 34.243 | 34.421 | 34.599 | 34.777 | 34.955 | 35.1329 | 35.3109 | 35.4889 | 35.6669 | 35.8449 | 36.0229 | 36.2008 | 36.3788 | 36.5568 | 36.7348 | 36.9128 | 37.0908 | 37.2687 | 37.4467 | 37.6247 | 37.8027 | 37.9807 | 38.1587 | 38.3366 | 38.5146
9.4 | 0 | 4.61 | 4.7725 | 4.616 | 4.516 | 5.822 | 7.2205 | 17.1775 | 26.2305 | 33.4755 | 38.8635 | 0 | 0.461 | 0.922 | 1.383 | 1.844 | 2.305 | 2.766 | 3.227 | 3.688 | 4.149 | 4.61 | 4.6425 | 4.675 | 4.7075 | 4.74 | 4.7725 | 4.7412 | 4.7099 | 4.6786 | 4.6473 | 4.616 | 4.606 | 4.596 | 4.586 | 4.576 | 4.566 | 4.556 | 4.546 | 4.536 | 4.526 | 4.516 | 4.6031 | 4.6901 | 4.7772 | 4.8643 | 4.9513 | 5.0384 | 5.1255 | 5.2125 | 5.2996 | 5.3867 | 5.4737 | 5.5608 | 5.6479 | 5.7349 | 5.822 | 5.9152 | 6.0085 | 6.1017 | 6.1949 | 6.2882 | 6.3814 | 6.4746 | 6.5679 | 6.6611 | 6.7543 | 6.8476 | 6.9408 | 7.034 | 7.1273 | 7.2205 | 7.5524 | 7.8843 | 8.2162 | 8.5481 | 8.88 | 9.2119 | 9.5438 | 9.8757 | 10.2076 | 10.5395 | 10.8714 | 11.2033 | 11.5352 | 11.8671 | 12.199 | 12.5309 | 12.8628 | 13.1947 | 13.5266 | 13.8585 | 14.1904 | 14.5223 | 14.8542 | 15.1861 | 15.518 | 15.8499 | 16.1818 | 16.5137 | 16.8456 | 17.1775 | 17.4793 | 17.781 | 18.0828 | 18.3846 | 18.6863 | 18.9881 | 19.2899 | 19.5916 | 19.8934 | 20.1952 | 20.4969 | 20.7987 | 21.1005 | 21.4022 | 21.704 | 22.0058 | 22.3075 | 22.6093 | 22.9111 | 23.2128 | 23.5146 | 23.8164 | 24.1181 | 24.4199 | 24.7217 | 25.0234 | 25.3252 | 25.627 | 25.9287 | 26.2305 | 26.472 | 26.7135 | 26.955 | 27.1965 | 27.438 | 27.6795 | 27.921 | 28.1625 | 28.404 | 28.6455 | 28.887 | 29.1285 | 29.37 | 29.6115 | 29.853 | 30.0945 | 30.336 | 30.5775 | 30.819 | 31.0605 | 31.302 | 31.5435 | 31.785 | 32.0265 | 32.268 | 32.5095 | 32.751 | 32.9925 | 33.234 | 33.4755 | 33.6551 | 33.8347 | 34.0143 | 34.1939 | 34.3735 | 34.5531 | 34.7327 | 34.9123 | 35.0919 | 35.2715 | 35.4511 | 35.6307 | 35.8103 | 35.9899 | 36.1695 | 36.3491 | 36.5287 | 36.7083 | 36.8879 | 37.0675 | 37.2471 | 37.4267 | 37.6063 | 37.7859 | 37.9655 | 38.1451 | 38.3247 | 38.5043 | 38.6839 | 38.8635
9.45 | 0 | 4.65 | 4.8181 | 4.6605 | 4.5605 | 5.8785 | 7.2896 | 17.3344 | 26.4671 | 33.7759 | 39.2124 | 4.4409e-16 | 0.465 | 0.93 | 1.395 | 1.86 | 2.325 | 2.79 | 3.255 | 3.72 | 4.185 | 4.65 | 4.6836 | 4.7173 | 4.7509 | 4.7845 | 4.8181 | 4.7866 | 4.7551 | 4.7236 | 4.692 | 4.6605 | 4.6505 | 4.6405 | 4.6305 | 4.6205 | 4.6105 | 4.6005 | 4.5905 | 4.5805 | 4.5705 | 4.5605 | 4.6484 | 4.7362 | 4.8241 | 4.912 | 4.9998 | 5.0877 | 5.1756 | 5.2634 | 5.3513 | 5.4392 | 5.527 | 5.6149 | 5.7028 | 5.7906 | 5.8785 | 5.9726 | 6.0667 | 6.1607 | 6.2548 | 6.3489 | 6.443 | 6.537 | 6.6311 | 6.7252 | 6.8193 | 6.9133 | 7.0074 | 7.1015 | 7.1956 | 7.2896 | 7.6245 | 7.9593 | 8.2941 | 8.6289 | 8.9638 | 9.2986 | 9.6334 | 9.9682 | 10.3031 | 10.6379 | 10.9727 | 11.3075 | 11.6424 | 11.9772 | 12.312 | 12.6468 | 12.9817 | 13.3165 | 13.6513 | 13.9861 | 14.321 | 14.6558 | 14.9906 | 15.3254 | 15.6603 | 15.9951 | 16.3299 | 16.6647 | 16.9996 | 17.3344 | 17.6388 | 17.9432 | 18.2477 | 18.5521 | 18.8565 | 19.1609 | 19.4654 | 19.7698 | 20.0742 | 20.3786 | 20.6831 | 20.9875 | 21.2919 | 21.5963 | 21.9008 | 22.2052 | 22.5096 | 22.814 | 23.1185 | 23.4229 | 23.7273 | 24.0317 | 24.3362 | 24.6406 | 24.945 | 25.2494 | 25.5539 | 25.8583 | 26.1627 | 26.4671 | 26.7108 | 26.9544 | 27.198 | 27.4416 | 27.6853 | 27.9289 | 28.1725 | 28.4161 | 28.6598 | 28.9034 | 29.147 | 29.3906 | 29.6343 | 29.8779 | 30.1215 | 30.3651 | 30.6088 | 30.8524 | 31.096 | 31.3396 | 31.5833 | 31.8269 | 32.0705 | 32.3141 | 32.5578 | 32.8014 | 33.045 | 33.2886 | 33.5323 | 33.7759 | 33.9571 | 34.1383 | 34.3195 | 34.5007 | 34.682 | 34.8632 | 35.0444 | 35.2256 | 35.4068 | 35.588 | 35.7693 | 35.9505 | 36.1317 | 36.3129 | 36.4941 | 36.6753 | 36.8566 | 37.0378 | 37.219 | 37.4002 | 37.5814 | 37.7626 | 37.9439 | 38.1251 | 38.3063 | 38.4875 | 38.6687 | 38.8499 | 39.0312 | 39.2124
9.5 | 0 | 4.69 | 4.8638 | 4.705 | 4.605 | 5.935 | 7.3588 | 17.4913 | 26.7038 | 34.0763 | 39.5613 | 0 | 0.469 | 0.938 | 1.407 | 1.876 | 2.345 | 2.814 | 3.283 | 3.752 | 4.221 | 4.69 | 4.7248 | 4.7595 | 4.7943 | 4.829 | 4.8638 | 4.832 | 4.8003 | 4.7685 | 4.7368 | 4.705 | 4.695 | 4.685 | 4.675 | 4.665 | 4.655 | 4.645 | 4.635 | 4.625 | 4.615 | 4.605 | 4.6937 | 4.7823 | 4.871 | 4.9597 | 5.0483 | 5.137 | 5.2257 | 5.3143 | 5.403 | 5.4917 | 5.5803 | 5.669 | 5.7577 | 5.8463 | 5.935 | 6.0299 | 6.1248 | 6.2198 | 6.3147 | 6.4096 | 6.5045 | 6.5994 | 6.6943 | 6.7893 | 6.8842 | 6.9791 | 7.074 | 7.1689 | 7.2638 | 7.3588 | 7.6965 | 8.0343 | 8.372 | 8.7098 | 9.0475 | 9.3853 | 9.723 | 10.0608 | 10.3985 | 10.7363 | 11.074 | 11.4118 | 11.7495 | 12.0873 | 12.425 | 12.7628 | 13.1005 | 13.4383 | 13.776 | 14.1138 | 14.4515 | 14.7893 | 15.127 | 15.4648 | 15.8025 | 16.1403 | 16.478 | 16.8158 | 17.1535 | 17.4913 | 17.7983 | 18.1054 | 18.4125 | 18.7196 | 19.0267 | 19.3338 | 19.6408 | 19.9479 | 20.255 | 20.5621 | 20.8692 | 21.1763 | 21.4833 | 21.7904 | 22.0975 | 22.4046 | 22.7117 | 23.0188 | 23.3258 | 23.6329 | 23.94 | 24.2471 | 24.5542 | 24.8613 | 25.1683 | 25.4754 | 25.7825 | 26.0896 | 26.3967 | 26.7038 | 26.9495 | 27.1953 | 27.441 | 27.6868 | 27.9325 | 28.1783 | 28.424 | 28.6698 | 28.9155 | 29.1613 | 29.407 | 29.6528 | 29.8985 | 30.1443 | 30.39 | 30.6358 | 30.8815 | 31.1273 | 31.373 | 31.6188 | 31.8645 | 32.1103 | 32.356 | 32.6018 | 32.8475 | 33.0933 | 33.339 | 33.5848 | 33.8305 | 34.0763 | 34.2591 | 34.4419 | 34.6248 | 34.8076 | 34.9904 | 35.1733 | 35.3561 | 35.5389 | 35.7218 | 35.9046 | 36.0874 | 36.2703 | 36.4531 | 36.6359 | 36.8188 | 37.0016 | 37.1844 | 37.3673 | 37.5501 | 37.7329 | 37.9158 | 38.0986 | 38.2814 | 38.4643 | 38.6471 | 38.8299 | 39.0128 | 39.1956 | 39.3784 | 39.5612
9.55 | 0 | 4.73 | 4.9094 | 4.7495 | 4.6495 | 5.9915 | 7.4279 | 17.6481 | 26.9404 | 34.3766 | 39.9101 | 0 | 0.473 | 0.946 | 1.419 | 1.892 | 2.365 | 2.838 | 3.311 | 3.784 | 4.257 | 4.73 | 4.7659 | 4.8018 | 4.8376 | 4.8735 | 4.9094 | 4.8774 | 4.8454 | 4.8135 | 4.7815 | 4.7495 | 4.7395 | 4.7295 | 4.7195 | 4.7095 | 4.6995 | 4.6895 | 4.6795 | 4.6695 | 4.6595 | 4.6495 | 4.739 | 4.8284 | 4.9179 | 5.0074 | 5.0968 | 5.1863 | 5.2758 | 5.3652 | 5.4547 | 5.5442 | 5.6336 | 5.7231 | 5.8126 | 5.902 | 5.9915 | 6.0873 | 6.183 | 6.2788 | 6.3745 | 6.4703 | 6.5661 | 6.6618 | 6.7576 | 6.8533 | 6.9491 | 7.0448 | 7.1406 | 7.2364 | 7.3321 | 7.4279 | 7.7686 | 8.1092 | 8.4499 | 8.7906 | 9.1313 | 9.4719 | 9.8126 | 10.1533 | 10.494 | 10.8346 | 11.1753 | 11.516 | 11.8567 | 12.1973 | 12.538 | 12.8787 | 13.2194 | 13.56 | 13.9007 | 14.2414 | 14.5821 | 14.9227 | 15.2634 | 15.6041 | 15.9448 | 16.2854 | 16.6261 | 16.9668 | 17.3075 | 17.6481 | 17.9579 | 18.2676 | 18.5774 | 18.8871 | 19.1968 | 19.5066 | 19.8163 | 20.1261 | 20.4358 | 20.7455 | 21.0553 | 21.365 | 21.6748 | 21.9845 | 22.2943 | 22.604 | 22.9137 | 23.2235 | 23.5332 | 23.843 | 24.1527 | 24.4624 | 24.7722 | 25.0819 | 25.3917 | 25.7014 | 26.0112 | 26.3209 | 26.6306 | 26.9404 | 27.1883 | 27.4361 | 27.684 | 27.9319 | 28.1798 | 28.4276 | 28.6755 | 28.9234 | 29.1713 | 29.4191 | 29.667 | 29.9149 | 30.1628 | 30.4106 | 30.6585 | 30.9064 | 31.1543 | 31.4021 | 31.65 | 31.8979 | 32.1458 | 32.3936 | 32.6415 | 32.8894 | 33.1373 | 33.3851 | 33.633 | 33.8809 | 34.1288 | 34.3766 | 34.5611 | 34.7455 | 34.93 | 35.1144 | 35.2989 | 35.4833 | 35.6678 | 35.8522 | 36.0367 | 36.2211 | 36.4056 | 36.59 | 36.7745 | 36.9589 | 37.1434 | 37.3278 | 37.5123 | 37.6967 | 37.8812 | 38.0656 | 38.2501 | 38.4345 | 38.619 | 38.8034 | 38.9879 | 39.1723 | 39.3568 | 39.5412 | 39.7257 | 39.9101
9.6 | 0 | 4.77 | 4.955 | 4.794 | 4.694 | 6.048 | 7.497 | 17.805 | 27.177 | 34.677 | 40.259 | 0 | 0.477 | 0.954 | 1.431 | 1.908 | 2.385 | 2.862 | 3.339 | 3.816 | 4.293 | 4.77 | 4.807 | 4.844 | 4.881 | 4.918 | 4.955 | 4.9228 | 4.8906 | 4.8584 | 4.8262 | 4.794 | 4.784 | 4.774 | 4.764 | 4.754 | 4.744 | 4.734 | 4.724 | 4.714 | 4.704 | 4.694 | 4.7843 | 4.8745 | 4.9648 | 5.0551 | 5.1453 | 5.2356 | 5.3259 | 5.4161 | 5.5064 | 5.5967 | 5.6869 | 5.7772 | 5.8675 | 5.9577 | 6.048 | 6.1446 | 6.2412 | 6.3378 | 6.4344 | 6.531 | 6.6276 | 6.7242 | 6.8208 | 6.9174 | 7.014 | 7.1106 | 7.2072 | 7.3038 | 7.4004 | 7.497 | 7.8406 | 8.1842 | 8.5278 | 8.8714 | 9.215 | 9.5586 | 9.9022 | 10.2458 | 10.5894 | 10.933 | 11.2766 | 11.6202 | 11.9638 | 12.3074 | 12.651 | 12.9946 | 13.3382 | 13.6818 | 14.0254 | 14.369 | 14.7126 | 15.0562 | 15.3998 | 15.7434 | 16.087 | 16.4306 | 16.7742 | 17.1178 | 17.4614 | 17.805 | 18.1174 | 18.4298 | 18.7422 | 19.0546 | 19.367 | 19.6794 | 19.9918 | 20.3042 | 20.6166 | 20.929 | 21.2414 | 21.5538 | 21.8662 | 22.1786 | 22.491 | 22.8034 | 23.1158 | 23.4282 | 23.7406 | 24.053 | 24.3654 | 24.6778 | 24.9902 | 25.3026 | 25.615 | 25.9274 | 26.2398 | 26.5522 | 26.8646 | 27.177 | 27.427 | 27.677 | 27.927 | 28.177 | 28.427 | 28.677 | 28.927 | 29.177 | 29.427 | 29.677 | 29.927 | 30.177 | 30.427 | 30.677 | 30.927 | 31.177 | 31.427 | 31.677 | 31.927 | 32.177 | 32.427 | 32.677 | 32.927 | 33.177 | 33.427 | 33.677 | 33.927 | 34.177 | 34.427 | 34.677 | 34.8631 | 35.0491 | 35.2352 | 35.4213 | 35.6073 | 35.7934 | 35.9795 | 36.1655 | 36.3516 | 36.5377 | 36.7237 | 36.9098 | 37.0959 | 37.2819 | 37.468 | 37.6541 | 37.8401 | 38.0262 | 38.2123 | 38.3983 | 38.5844 | 38.7705 | 38.9565 | 39.1426 | 39.3287 | 39.5147 | 39.7008 | 39.8869 | 40.0729 | 40.259
9.65 | 0 | 4.81 | 5.0006 | 4.8385 | 4.7385 | 6.1045 | 7.5661 | 17.9619 | 27.4136 | 34.9774 | 40.6079 | -4.4409e-16 | 0.481 | 0.962 | 1.443 | 1.924 | 2.405 | 2.886 | 3.367 | 3.848 | 4.329 | 4.81 | 4.8481 | 4.8863 | 4.9244 | 4.9625 | 5.0006 | 4.9682 | 4.9358 | 4.9034 | 4.8709 | 4.8385 | 4.8285 | 4.8185 | 4.8085 | 4.7985 | 4.7885 | 4.7785 | 4.7685 | 4.7585 | 4.7485 | 4.7385 | 4.8296 | 4.9206 | 5.0117 | 5.1028 | 5.1938 | 5.2849 | 5.376 | 5.467 | 5.5581 | 5.6492 | 5.7402 | 5.8313 | 5.9224 | 6.0134 | 6.1045 | 6.2019 | 6.2994 | 6.3968 | 6.4943 | 6.5917 | 6.6892 | 6.7866 | 6.884 | 6.9815 | 7.0789 | 7.1764 | 7.2738 | 7.3712 | 7.4687 | 7.5661 | 7.9127 | 8.2592 | 8.6057 | 8.9522 | 9.2988 | 9.6453 | 9.9918 | 10.3383 | 10.6849 | 11.0314 | 11.3779 | 11.7244 | 12.071 | 12.4175 | 12.764 | 13.1105 | 13.4571 | 13.8036 | 14.1501 | 14.4966 | 14.8432 | 15.1897 | 15.5362 | 15.8827 | 16.2293 | 16.5758 | 16.9223 | 17.2688 | 17.6154 | 17.9619 | 18.2769 | 18.592 | 18.9071 | 19.2221 | 19.5372 | 19.8522 | 20.1673 | 20.4823 | 20.7974 | 21.1125 | 21.4275 | 21.7426 | 22.0576 | 22.3727 | 22.6878 | 23.0028 | 23.3179 | 23.6329 | 23.948 | 24.263 | 24.5781 | 24.8932 | 25.2082 | 25.5233 | 25.8383 | 26.1534 | 26.4685 | 26.7835 | 27.0986 | 27.4136 | 27.6658 | 27.9179 | 28.17 | 28.4221 | 28.6743 | 28.9264 | 29.1785 | 29.4306 | 29.6828 | 29.9349 | 30.187 | 30.4391 | 30.6913 | 30.9434 | 31.1955 | 31.4476 | 31.6998 | 31.9519 | 32.204 | 32.4561 | 32.7083 | 32.9604 | 33.2125 | 33.4646 | 33.7168 | 33.9689 | 34.221 | 34.4731 | 34.7253 | 34.9774 | 35.1651 | 35.3527 | 35.5404 | 35.7281 | 35.9158 | 36.1035 | 36.2912 | 36.4788 | 36.6665 | 36.8542 | 37.0419 | 37.2296 | 37.4173 | 37.6049 | 37.7926 | 37.9803 | 38.168 | 38.3557 | 38.5434 | 38.731 | 38.9187 | 39.1064 | 39.2941 | 39.4818 | 39.6695 | 39.8571 | 40.0448 | 40.2325 | 40.4202 | 40.6079
9.7 | 0 | 4.85 | 5.0463 | 4.883 | 4.783 | 6.161 | 7.6353 | 18.1188 | 27.6503 | 35.2778 | 40.9568 | 0 | 0.485 | 0.97 | 1.455 | 1.94 | 2.425 | 2.91 | 3.395 | 3.88 | 4.365 | 4.85 | 4.8893 | 4.9285 | 4.9678 | 5.007 | 5.0463 | 5.0136 | 4.981 | 4.9483 | 4.9157 | 4.883 | 4.873 | 4.863 | 4.853 | 4.843 | 4.833 | 4.823 | 4.813 | 4.803 | 4.793 | 4.783 | 4.8749 | 4.9667 | 5.0586 | 5.1505 | 5.2423 | 5.3342 | 5.4261 | 5.5179 | 5.6098 | 5.7017 | 5.7935 | 5.8854 | 5.9773 | 6.0691 | 6.161 | 6.2593 | 6.3576 | 6.4559 | 6.5541 | 6.6524 | 6.7507 | 6.849 | 6.9473 | 7.0456 | 7.1438 | 7.2421 | 7.3404 | 7.4387 | 7.537 | 7.6353 | 7.9847 | 8.3342 | 8.6836 | 9.0331 | 9.3825 | 9.732 | 10.0814 | 10.4309 | 10.7803 | 11.1298 | 11.4792 | 11.8287 | 12.1781 | 12.5276 | 12.877 | 13.2265 | 13.5759 | 13.9254 | 14.2748 | 14.6243 | 14.9737 | 15.3232 | 15.6726 | 16.0221 | 16.3715 | 16.721 | 17.0704 | 17.4199 | 17.7693 | 18.1188 | 18.4365 | 18.7542 | 19.0719 | 19.3896 | 19.7073 | 20.0251 | 20.3428 | 20.6605 | 20.9782 | 21.2959 | 21.6136 | 21.9314 | 22.2491 | 22.5668 | 22.8845 | 23.2022 | 23.5199 | 23.8377 | 24.1554 | 24.4731 | 24.7908 | 25.1085 | 25.4262 | 25.744 | 26.0617 | 26.3794 | 26.6971 | 27.0148 | 27.3325 | 27.6503 | 27.9045 | 28.1588 | 28.413 | 28.6673 | 28.9215 | 29.1758 | 29.43 | 29.6843 | 29.9385 | 30.1928 | 30.447 | 30.7013 | 30.9555 | 31.2098 | 31.464 | 31.7183 | 31.9725 | 32.2268 | 32.481 | 32.7353 | 32.9895 | 33.2438 | 33.498 | 33.7523 | 34.0065 | 34.2608 | 34.515 | 34.7693 | 35.0235 | 35.2778 | 35.4671 | 35.6564 | 35.8457 | 36.035 | 36.2243 | 36.4136 | 36.6029 | 36.7922 | 36.9815 | 37.1708 | 37.3601 | 37.5494 | 37.7387 | 37.928 | 38.1173 | 38.3066 | 38.4959 | 38.6852 | 38.8745 | 39.0638 | 39.2531 | 39.4424 | 39.6317 | 39.821 | 40.0103 | 40.1996 | 40.3889 | 40.5782 | 40.7675 | 40.9567
9.75 | 0 | 4.89 | 5.0919 | 4.9275 | 4.8275 | 6.2175 | 7.7044 | 18.2756 | 27.8869 | 35.5781 | 41.3056 | 0 | 0.489 | 0.978 | 1.467 | 1.956 | 2.445 | 2.934 | 3.423 | 3.912 | 4.401 | 4.89 | 4.9304 | 4.9708 | 5.0111 | 5.0515 | 5.0919 | 5.059 | 5.0261 | 4.9933 | 4.9604 | 4.9275 | 4.9175 | 4.9075 | 4.8975 | 4.8875 | 4.8775 | 4.8675 | 4.8575 | 4.8475 | 4.8375 | 4.8275 | 4.9202 | 5.0128 | 5.1055 | 5.1982 | 5.2908 | 5.3835 | 5.4762 | 5.5688 | 5.6615 | 5.7542 | 5.8468 | 5.9395 | 6.0322 | 6.1248 | 6.2175 | 6.3166 | 6.4158 | 6.5149 | 6.614 | 6.7131 | 6.8123 | 6.9114 | 7.0105 | 7.1096 | 7.2088 | 7.3079 | 7.407 | 7.5061 | 7.6053 | 7.7044 | 8.0568 | 8.4091 | 8.7615 | 9.1139 | 9.4663 | 9.8186 | 10.171 | 10.5234 | 10.8758 | 11.2281 | 11.5805 | 11.9329 | 12.2853 | 12.6376 | 12.99 | 13.3424 | 13.6948 | 14.0471 | 14.3995 | 14.7519 | 15.1043 | 15.4566 | 15.809 | 16.1614 | 16.5138 | 16.8661 | 17.2185 | 17.5709 | 17.9233 | 18.2756 | 18.596 | 18.9164 | 19.2368 | 19.5571 | 19.8775 | 20.1979 | 20.5183 | 20.8386 | 21.159 | 21.4794 | 21.7998 | 22.1201 | 22.4405 | 22.7609 | 23.0813 | 23.4016 | 23.722 | 24.0424 | 24.3628 | 24.6831 | 25.0035 | 25.3239 | 25.6443 | 25.9646 | 26.285 | 26.6054 | 26.9258 | 27.2461 | 27.5665 | 27.8869 | 28.1433 | 28.3996 | 28.656 | 28.9124 | 29.1688 | 29.4251 | 29.6815 | 29.9379 | 30.1943 | 30.4506 | 30.707 | 30.9634 | 31.2198 | 31.4761 | 31.7325 | 31.9889 | 32.2453 | 32.5016 | 32.758 | 33.0144 | 33.2708 | 33.5271 | 33.7835 | 34.0399 | 34.2963 | 34.5526 | 34.809 | 35.0654 | 35.3218 | 35.5781 | 35.769 | 35.96 | 36.1509 | 36.3418 | 36.5327 | 36.7236 | 36.9145 | 37.1055 | 37.2964 | 37.4873 | 37.6782 | 37.8691 | 38.06 | 38.251 | 38.4419 | 38.6328 | 38.8237 | 39.0146 | 39.2055 | 39.3965 | 39.5874 | 39.7783 | 39.9692 | 40.1601 | 40.351 | 40.542 | 40.7329 | 40.9238 | 41.1147 | 41.3056
9.8 | 0 | 4.93 | 5.1375 | 4.972 | 4.872 | 6.274 | 7.7735 | 18.4325 | 28.1235 | 35.8785 | 41.6545 | 0 | 0.493 | 0.986 | 1.479 | 1.972 | 2.465 | 2.958 | 3.451 | 3.944 | 4.437 | 4.93 | 4.9715 | 5.013 | 5.0545 | 5.096 | 5.1375 | 5.1044 | 5.0713 | 5.0382 | 5.0051 | 4.972 | 4.962 | 4.952 | 4.942 | 4.932 | 4.922 | 4.912 | 4.902 | 4.892 | 4.882 | 4.872 | 4.9655 | 5.0589 | 5.1524 | 5.2459 | 5.3393 | 5.4328 | 5.5263 | 5.6197 | 5.7132 | 5.8067 | 5.9001 | 5.9936 | 6.0871 | 6.1805 | 6.274 | 6.374 | 6.4739 | 6.5739 | 6.6739 | 6.7738 | 6.8738 | 6.9738 | 7.0737 | 7.1737 | 7.2737 | 7.3736 | 7.4736 | 7.5736 | 7.6735 | 7.7735 | 8.1288 | 8.4841 | 8.8394 | 9.1947 | 9.55 | 9.9053 | 10.2606 | 10.6159 | 10.9712 | 11.3265 | 11.6818 | 12.0371 | 12.3924 | 12.7477 | 13.103 | 13.4583 | 13.8136 | 14.1689 | 14.5242 | 14.8795 | 15.2348 | 15.5901 | 15.9454 | 16.3007 | 16.656 | 17.0113 | 17.3666 | 17.7219 | 18.0772 | 18.4325 | 18.7555 | 19.0786 | 19.4016 | 19.7246 | 20.0477 | 20.3707 | 20.6937 | 21.0168 | 21.3398 | 21.6628 | 21.9859 | 22.3089 | 22.6319 | 22.955 | 23.278 | 23.601 | 23.9241 | 24.2471 | 24.5701 | 24.8932 | 25.2162 | 25.5392 | 25.8623 | 26.1853 | 26.5083 | 26.8314 | 27.1544 | 27.4774 | 27.8005 | 28.1235 | 28.382 | 28.6405 | 28.899 | 29.1575 | 29.416 | 29.6745 | 29.933 | 30.1915 | 30.45 | 30.7085 | 30.967 | 31.2255 | 31.484 | 31.7425 | 32.001 | 32.2595 | 32.518 | 32.7765 | 33.035 | 33.2935 | 33.552 | 33.8105 | 34.069 | 34.3275 | 34.586 | 34.8445 | 35.103 | 35.3615 | 35.62 | 35.8785 | 36.071 | 36.2636 | 36.4561 | 36.6486 | 36.8412 | 37.0337 | 37.2262 | 37.4188 | 37.6113 | 37.8038 | 37.9964 | 38.1889 | 38.3814 | 38.574 | 38.7665 | 38.959 | 39.1516 | 39.3441 | 39.5366 | 39.7292 | 39.9217 | 40.1142 | 40.3068 | 40.4993 | 40.6918 | 40.8844 | 41.0769 | 41.2694 | 41.462 | 41.6545
9.85 | 0 | 4.97 | 5.1831 | 5.0165 | 4.9165 | 6.3305 | 7.8426 | 18.5894 | 28.3601 | 36.1789 | 42.0034 | 0 | 0.497 | 0.994 | 1.491 | 1.988 | 2.485 | 2.982 | 3.479 | 3.976 | 4.473 | 4.97 | 5.0126 | 5.0553 | 5.0979 | 5.1405 | 5.1831 | 5.1498 | 5.1165 | 5.0832 | 5.0498 | 5.0165 | 5.0065 | 4.9965 | 4.9865 | 4.9765 | 4.9665 | 4.9565 | 4.9465 | 4.9365 | 4.9265 | 4.9165 | 5.0108 | 5.105 | 5.1993 | 5.2936 | 5.3878 | 5.4821 | 5.5764 | 5.6706 | 5.7649 | 5.8592 | 5.9534 | 6.0477 | 6.142 | 6.2362 | 6.3305 | 6.4313 | 6.5321 | 6.6329 | 6.7337 | 6.8345 | 6.9354 | 7.0362 | 7.137 | 7.2378 | 7.3386 | 7.4394 | 7.5402 | 7.641 | 7.7418 | 7.8426 | 8.2009 | 8.5591 | 8.9173 | 9.2755 | 9.6338 | 9.992 | 10.3502 | 10.7084 | 11.0667 | 11.4249 | 11.7831 | 12.1413 | 12.4996 | 12.8578 | 13.216 | 13.5742 | 13.9325 | 14.2907 | 14.6489 | 15.0071 | 15.3654 | 15.7236 | 16.0818 | 16.44 | 16.7983 | 17.1565 | 17.5147 | 17.8729 | 18.2312 | 18.5894 | 18.9151 | 19.2408 | 19.5665 | 19.8921 | 20.2178 | 20.5435 | 20.8692 | 21.1949 | 21.5206 | 21.8463 | 22.172 | 22.4977 | 22.8234 | 23.1491 | 23.4748 | 23.8004 | 24.1261 | 24.4518 | 24.7775 | 25.1032 | 25.4289 | 25.7546 | 26.0803 | 26.406 | 26.7317 | 27.0574 | 27.3831 | 27.7087 | 28.0344 | 28.3601 | 28.6208 | 28.8814 | 29.142 | 29.4026 | 29.6633 | 29.9239 | 30.1845 | 30.4451 | 30.7058 | 30.9664 | 31.227 | 31.4876 | 31.7483 | 32.0089 | 32.2695 | 32.5301 | 32.7908 | 33.0514 | 33.312 | 33.5726 | 33.8333 | 34.0939 | 34.3545 | 34.6151 | 34.8758 | 35.1364 | 35.397 | 35.6576 | 35.9183 | 36.1789 | 36.373 | 36.5672 | 36.7613 | 36.9555 | 37.1496 | 37.3438 | 37.5379 | 37.7321 | 37.9262 | 38.1204 | 38.3145 | 38.5087 | 38.7028 | 38.897 | 39.0911 | 39.2853 | 39.4794 | 39.6736 | 39.8677 | 40.0619 | 40.256 | 40.4502 | 40.6443 | 40.8385 | 41.0326 | 41.2268 | 41.4209 | 41.6151 | 41.8092 | 42.0034
9.9 | 0 | 5.01 | 5.2288 | 5.061 | 4.961 | 6.387 | 7.9118 | 18.7463 | 28.5968 | 36.4793 | 42.3523 | 0 | 0.501 | 1.002 | 1.503 | 2.004 | 2.505 | 3.006 | 3.507 | 4.008 | 4.509 | 5.01 | 5.0538 | 5.0975 | 5.1413 | 5.185 | 5.2288 | 5.1952 | 5.1617 | 5.1281 | 5.0946 | 5.061 | 5.051 | 5.041 | 5.031 | 5.021 | 5.011 | 5.001 | 4.991 | 4.981 | 4.971 | 4.961 | 5.0561 | 5.1511 | 5.2462 | 5.3413 | 5.4363 | 5.5314 | 5.6265 | 5.7215 | 5.8166 | 5.9117 | 6.0067 | 6.1018 | 6.1969 | 6.2919 | 6.387 | 6.4887 | 6.5903 | 6.692 | 6.7936 | 6.8953 | 6.9969 | 7.0986 | 7.2002 | 7.3019 | 7.4035 | 7.5052 | 7.6068 | 7.7085 | 7.8101 | 7.9118 | 8.2729 | 8.6341 | 8.9952 | 9.3564 | 9.7175 | 10.0787 | 10.4398 | 10.801 | 11.1621 | 11.5233 | 11.8844 | 12.2456 | 12.6067 | 12.9679 | 13.329 | 13.6902 | 14.0513 | 14.4125 | 14.7736 | 15.1348 | 15.4959 | 15.8571 | 16.2182 | 16.5794 | 16.9405 | 17.3017 | 17.6628 | 18.024 | 18.3851 | 18.7463 | 19.0746 | 19.403 | 19.7313 | 20.0597 | 20.388 | 20.7164 | 21.0447 | 21.3731 | 21.7014 | 22.0298 | 22.3581 | 22.6865 | 23.0148 | 23.3432 | 23.6715 | 23.9999 | 24.3282 | 24.6566 | 24.9849 | 25.3133 | 25.6416 | 25.97 | 26.2983 | 26.6267 | 26.955 | 27.2834 | 27.6117 | 27.9401 | 28.2684 | 28.5968 | 28.8595 | 29.1223 | 29.385 | 29.6478 | 29.9105 | 30.1733 | 30.436 | 30.6988 | 30.9615 | 31.2243 | 31.487 | 31.7498 | 32.0125 | 32.2753 | 32.538 | 32.8008 | 33.0635 | 33.3263 | 33.589 | 33.8518 | 34.1145 | 34.3773 | 34.64 | 34.9028 | 35.1655 | 35.4283 | 35.691 | 35.9538 | 36.2165 | 36.4793 | 36.675 | 36.8708 | 37.0666 | 37.2623 | 37.4581 | 37.6539 | 37.8496 | 38.0454 | 38.2412 | 38.4369 | 38.6327 | 38.8285 | 39.0242 | 39.22 | 39.4158 | 39.6115 | 39.8073 | 40.0031 | 40.1988 | 40.3946 | 40.5904 | 40.7861 | 40.9819 | 41.1777 | 41.3734 | 41.5692 | 41.765 | 41.9607 | 42.1565 | 42.3522
9.95 | 0 | 5.05 | 5.2744 | 5.1055 | 5.0055 | 6.4435 | 7.9809 | 18.9031 | 28.8334 | 36.7796 | 42.7011 | 0 | 0.505 | 1.01 | 1.515 | 2.02 | 2.525 | 3.03 | 3.535 | 4.04 | 4.545 | 5.05 | 5.0949 | 5.1398 | 5.1846 | 5.2295 | 5.2744 | 5.2406 | 5.2068 | 5.1731 | 5.1393 | 5.1055 | 5.0955 | 5.0855 | 5.0755 | 5.0655 | 5.0555 | 5.0455 | 5.0355 | 5.0255 | 5.0155 | 5.0055 | 5.1014 | 5.1972 | 5.2931 | 5.389 | 5.4848 | 5.5807 | 5.6766 | 5.7724 | 5.8683 | 5.9642 | 6.06 | 6.1559 | 6.2518 | 6.3476 | 6.4435 | 6.546 | 6.6485 | 6.751 | 6.8535 | 6.956 | 7.0585 | 7.1609 | 7.2634 | 7.3659 | 7.4684 | 7.5709 | 7.6734 | 7.7759 | 7.8784 | 7.9809 | 8.345 | 8.709 | 9.0731 | 9.4372 | 9.8013 | 10.1653 | 10.5294 | 10.8935 | 11.2576 | 11.6216 | 11.9857 | 12.3498 | 12.7139 | 13.0779 | 13.442 | 13.8061 | 14.1702 | 14.5342 | 14.8983 | 15.2624 | 15.6265 | 15.9905 | 16.3546 | 16.7187 | 17.0828 | 17.4468 | 17.8109 | 18.175 | 18.5391 | 18.9031 | 19.2341 | 19.5651 | 19.8962 | 20.2272 | 20.5582 | 20.8892 | 21.2202 | 21.5512 | 21.8822 | 22.2132 | 22.5442 | 22.8752 | 23.2062 | 23.5372 | 23.8683 | 24.1993 | 24.5303 | 24.8613 | 25.1923 | 25.5233 | 25.8543 | 26.1853 | 26.5163 | 26.8473 | 27.1783 | 27.5093 | 27.8404 | 28.1714 | 28.5024 | 28.8334 | 29.0983 | 29.3631 | 29.628 | 29.8929 | 30.1578 | 30.4226 | 30.6875 | 30.9524 | 31.2173 | 31.4821 | 31.747 | 32.0119 | 32.2768 | 32.5416 | 32.8065 | 33.0714 | 33.3363 | 33.6011 | 33.866 | 34.1309 | 34.3958 | 34.6606 | 34.9255 | 35.1904 | 35.4553 | 35.7201 | 35.985 | 36.2499 | 36.5148 | 36.7796 | 36.977 | 37.1744 | 37.3718 | 37.5692 | 37.7665 | 37.9639 | 38.1613 | 38.3587 | 38.5561 | 38.7535 | 38.9508 | 39.1482 | 39.3456 | 39.543 | 39.7404 | 39.9378 | 40.1351 | 40.3325 | 40.5299 | 40.7273 | 40.9247 | 41.1221 | 41.3194 | 41.5168 | 41.7142 | 41.9116 | 42.109 | 42.3064 | 42.5037 | 42.7011
10 | 0 | 5.09 | 5.32 | 5.15 | 5.05 | 6.5 | 8.05 | 19.06 | 29.07 | 37.08 | 43.05 | 0 | 0.509 | 1.018 | 1.527 | 2.036 | 2.545 | 3.054 | 3.563 | 4.072 | 4.581 | 5.09 | 5.136 | 5.182 | 5.228 | 5.274 | 5.32 | 5.286 | 5.252 | 5.218 | 5.184 | 5.15 | 5.14 | 5.13 | 5.12 | 5.11 | 5.1 | 5.09 | 5.08 | 5.07 | 5.06 | 5.05 | 5.1467 | 5.2433 | 5.34 | 5.4367 | 5.5333 | 5.63 | 5.7267 | 5.8233 | 5.92 | 6.0167 | 6.1133 | 6.21 | 6.3067 | 6.4033 | 6.5 | 6.6033 | 6.7067 | 6.81 | 6.9133 | 7.0167 | 7.12 | 7.2233 | 7.3267 | 7.43 | 7.5333 | 7.6367 | 7.74 | 7.8433 | 7.9467 | 8.05 | 8.417 | 8.784 | 9.151 | 9.518 | 9.885 | 10.252 | 10.619 | 10.986 | 11.353 | 11.72 | 12.087 | 12.454 | 12.821 | 13.188 | 13.555 | 13.922 | 14.289 | 14.656 | 15.023 | 15.39 | 15.757 | 16.124 | 16.491 | 16.858 | 17.225 | 17.592 | 17.959 | 18.326 | 18.693 | 19.06 | 19.3937 | 19.7273 | 20.061 | 20.3947 | 20.7283 | 21.062 | 21.3957 | 21.7293 | 22.063 | 22.3967 | 22.7303 | 23.064 | 23.3977 | 23.7313 | 24.065 | 24.3987 | 24.7323 | 25.066 | 25.3997 | 25.7333 | 26.067 | 26.4007 | 26.7343 | 27.068 | 27.4017 | 27.7353 | 28.069 | 28.4027 | 28.7363 | 29.07 | 29.337 | 29.604 | 29.871 | 30.138 | 30.405 | 30.672 | 30.939 | 31.206 | 31.473 | 31.74 | 32.007 | 32.274 | 32.541 | 32.808 | 33.075 | 33.342 | 33.609 | 33.876 | 34.143 | 34.41 | 34.677 | 34.944 | 35.211 | 35.478 | 35.745 | 36.012 | 36.279 | 36.546 | 36.813 | 37.08 | 37.279 | 37.478 | 37.677 | 37.876 | 38.075 | 38.274 | 38.473 | 38.672 | 38.871 | 39.07 | 39.269 | 39.468 | 39.667 | 39.866 | 40.065 | 40.264 | 40.463 | 40.662 | 40.861 | 41.06 | 41.259 | 41.458 | 41.657 | 41.856 | 42.055 | 42.254 | 42.453 | 42.652 | 42.851 | 43.05

## Sheet2
ER4-2 Transition, Pyramidal, Exhaust Air Systems
Transition Length, L | 230 | mm
Incoming (Pre-Transition) | (A0)
Duct Width, W (mm) | 300 | mm
Duct Height, H (mm) | 300 | mm
Air Flow, Q (CFM) | 600 | CFM
Air Velocity, VC (FPM) | 619.5787 | FPM
Velocity Pressure, VP ("w.g.) | 0.023932 | "w.g.
Outgoing (Post-Transition) | (A1)
Duct Width, W (mm) | 200 | mm
Duct Height, H (mm) | 200 | mm
Air Flow, Q (CFM) | 600 | CFM
Air Velocity, VC (FPM) | 1394.052 | FPM
Velocity Pressure, VP ("w.g.) | 0.12116 | "w.g.
θ1 (Side) | 24.5264 | °
θ2 (Top) | 24.5264 | °
θ (Max) | 25 | °
A0 /A1 | 2.25
C | 0.29437
Frictional Pressure Loss, ΔP | 0.0070451 | "w.g.
| 1.7613 | Pa
Ashrae ER4-2
A0 /A1 |  | θ
| 0 | 10 | 15 | 20 | 30 | 45 | 60 | 90 | 120 | 150 | 180
0.06 | 0 | 0.3 | 0.54 | 0.53 | 0.65 | 0.77 | 0.88 | 0.95 | 0.98 | 0.98 | 0.93
0.1 | 0 | 0.3 | 0.5 | 0.53 | 0.64 | 0.75 | 0.84 | 0.89 | 0.91 | 0.91 | 0.88
0.25 | 0 | 0.25 | 0.36 | 0.45 | 0.52 | 0.58 | 0.62 | 0.64 | 0.64 | 0.64 | 0.64
0.5 | 0 | 0.15 | 0.21 | 0.25 | 0.3 | 0.33 | 0.33 | 0.33 | 0.32 | 0.31 | 0.3
1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 0 | 0.24 | 0.28 | 0.26 | 0.2 | 0.22 | 0.24 | 0.49 | 0.73 | 0.97 | 1.04
4 | 0 | 0.89 | 0.78 | 0.79 | 0.7 | 0.88 | 1.12 | 2.72 | 4.33 | 5.62 | 6.58
6 | 0 | 1.89 | 1.67 | 1.59 | 1.49 | 1.98 | 2.52 | 6.51 | 10.14 | 13.05 | 15.14
10 | 0 | 5.09 | 5.32 | 5.15 | 5.05 | 6.5 | 8.05 | 19.06 | 29.07 | 37.08 | 43.05
A0 /A1 θ | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 41 | 42 | 43 | 44 | 45 | 46 | 47 | 48 | 49 | 50 | 51 | 52 | 53 | 54 | 55 | 56 | 57 | 58 | 59 | 60 | 61 | 62 | 63 | 64 | 65 | 66 | 67 | 68 | 69 | 70 | 71 | 72 | 73 | 74 | 75 | 76 | 77 | 78 | 79 | 80 | 81 | 82 | 83 | 84 | 85 | 86 | 87 | 88 | 89 | 90 | 91 | 92 | 93 | 94 | 95 | 96 | 97 | 98 | 99 | 100 | 101 | 102 | 103 | 104 | 105 | 106 | 107 | 108 | 109 | 110 | 111 | 112 | 113 | 114 | 115 | 116 | 117 | 118 | 119 | 120 | 121 | 122 | 123 | 124 | 125 | 126 | 127 | 128 | 129 | 130 | 131 | 132 | 133 | 134 | 135 | 136 | 137 | 138 | 139 | 140 | 141 | 142 | 143 | 144 | 145 | 146 | 147 | 148 | 149 | 150 | 151 | 152 | 153 | 154 | 155 | 156 | 157 | 158 | 159 | 160 | 161 | 162 | 163 | 164 | 165 | 166 | 167 | 168 | 169 | 170 | 171 | 172 | 173 | 174 | 175 | 176 | 177 | 178 | 179 | 180
0.06 | 0 | 0.03 | 0.06 | 0.09 | 0.12 | 0.15 | 0.18 | 0.21 | 0.24 | 0.27 | 0.3 | 0.348 | 0.396 | 0.444 | 0.492 | 0.54 | 0.538 | 0.536 | 0.534 | 0.532 | 0.53 | 0.542 | 0.554 | 0.566 | 0.578 | 0.59 | 0.602 | 0.614 | 0.626 | 0.638 | 0.65 | 0.658 | 0.666 | 0.674 | 0.682 | 0.69 | 0.698 | 0.706 | 0.714 | 0.722 | 0.73 | 0.738 | 0.746 | 0.754 | 0.762 | 0.77 | 0.77733 | 0.78467 | 0.792 | 0.79933 | 0.80667 | 0.814 | 0.82133 | 0.82867 | 0.836 | 0.84333 | 0.85067 | 0.858 | 0.86533 | 0.87267 | 0.88 | 0.88233 | 0.88467 | 0.887 | 0.88933 | 0.89167 | 0.894 | 0.89633 | 0.89867 | 0.901 | 0.90333 | 0.90567 | 0.908 | 0.91033 | 0.91267 | 0.915 | 0.91733 | 0.91967 | 0.922 | 0.92433 | 0.92667 | 0.929 | 0.93133 | 0.93367 | 0.936 | 0.93833 | 0.94067 | 0.943 | 0.94533 | 0.94767 | 0.95 | 0.951 | 0.952 | 0.953 | 0.954 | 0.955 | 0.956 | 0.957 | 0.958 | 0.959 | 0.96 | 0.961 | 0.962 | 0.963 | 0.964 | 0.965 | 0.966 | 0.967 | 0.968 | 0.969 | 0.97 | 0.971 | 0.972 | 0.973 | 0.974 | 0.975 | 0.976 | 0.977 | 0.978 | 0.979 | 0.98 | 0.98 | 0.98 | 0.98 | 0.98 | 0.98 | 0.98 | 0.98 | 0.98 | 0.98 | 0.98 | 0.98 | 0.98 | 0.98 | 0.98 | 0.98 | 0.98 | 0.98 | 0.98 | 0.98 | 0.98 | 0.98 | 0.98 | 0.98 | 0.98 | 0.98 | 0.98 | 0.98 | 0.98 | 0.98 | 0.98 | 0.97833 | 0.97667 | 0.975 | 0.97333 | 0.97167 | 0.97 | 0.96833 | 0.96667 | 0.965 | 0.96333 | 0.96167 | 0.96 | 0.95833 | 0.95667 | 0.955 | 0.95333 | 0.95167 | 0.95 | 0.94833 | 0.94667 | 0.945 | 0.94333 | 0.94167 | 0.94 | 0.93833 | 0.93667 | 0.935 | 0.93333 | 0.93167 | 0.93
0.1 | 0 | 0.03 | 0.06 | 0.09 | 0.12 | 0.15 | 0.18 | 0.21 | 0.24 | 0.27 | 0.3 | 0.34 | 0.38 | 0.42 | 0.46 | 0.5 | 0.506 | 0.512 | 0.518 | 0.524 | 0.53 | 0.541 | 0.552 | 0.563 | 0.574 | 0.585 | 0.596 | 0.607 | 0.618 | 0.629 | 0.64 | 0.64733 | 0.65467 | 0.662 | 0.66933 | 0.67667 | 0.684 | 0.69133 | 0.69867 | 0.706 | 0.71333 | 0.72067 | 0.728 | 0.73533 | 0.74267 | 0.75 | 0.756 | 0.762 | 0.768 | 0.774 | 0.78 | 0.786 | 0.792 | 0.798 | 0.804 | 0.81 | 0.816 | 0.822 | 0.828 | 0.834 | 0.84 | 0.84167 | 0.84333 | 0.845 | 0.84667 | 0.84833 | 0.85 | 0.85167 | 0.85333 | 0.855 | 0.85667 | 0.85833 | 0.86 | 0.86167 | 0.86333 | 0.865 | 0.86667 | 0.86833 | 0.87 | 0.87167 | 0.87333 | 0.875 | 0.87667 | 0.87833 | 0.88 | 0.88167 | 0.88333 | 0.885 | 0.88667 | 0.88833 | 0.89 | 0.89067 | 0.89133 | 0.892 | 0.89267 | 0.89333 | 0.894 | 0.89467 | 0.89533 | 0.896 | 0.89667 | 0.89733 | 0.898 | 0.89867 | 0.89933 | 0.9 | 0.90067 | 0.90133 | 0.902 | 0.90267 | 0.90333 | 0.904 | 0.90467 | 0.90533 | 0.906 | 0.90667 | 0.90733 | 0.908 | 0.90867 | 0.90933 | 0.91 | 0.91 | 0.91 | 0.91 | 0.91 | 0.91 | 0.91 | 0.91 | 0.91 | 0.91 | 0.91 | 0.91 | 0.91 | 0.91 | 0.91 | 0.91 | 0.91 | 0.91 | 0.91 | 0.91 | 0.91 | 0.91 | 0.91 | 0.91 | 0.91 | 0.91 | 0.91 | 0.91 | 0.91 | 0.91 | 0.91 | 0.909 | 0.908 | 0.907 | 0.906 | 0.905 | 0.904 | 0.903 | 0.902 | 0.901 | 0.9 | 0.899 | 0.898 | 0.897 | 0.896 | 0.895 | 0.894 | 0.893 | 0.892 | 0.891 | 0.89 | 0.889 | 0.888 | 0.887 | 0.886 | 0.885 | 0.884 | 0.883 | 0.882 | 0.881 | 0.88
0.15 | 0 | 0.028333 | 0.056667 | 0.085 | 0.11333 | 0.14167 | 0.17 | 0.19833 | 0.22667 | 0.255 | 0.28333 | 0.31733 | 0.35133 | 0.38533 | 0.41933 | 0.45333 | 0.46333 | 0.47333 | 0.48333 | 0.49333 | 0.50333 | 0.513 | 0.52267 | 0.53233 | 0.542 | 0.55167 | 0.56133 | 0.571 | 0.58067 | 0.59033 | 0.6 | 0.60622 | 0.61244 | 0.61867 | 0.62489 | 0.63111 | 0.63733 | 0.64356 | 0.64978 | 0.656 | 0.66222 | 0.66844 | 0.67467 | 0.68089 | 0.68711 | 0.69333 | 0.69822 | 0.70311 | 0.708 | 0.71289 | 0.71778 | 0.72267 | 0.72756 | 0.73244 | 0.73733 | 0.74222 | 0.74711 | 0.752 | 0.75689 | 0.76178 | 0.76667 | 0.768 | 0.76933 | 0.77067 | 0.772 | 0.77333 | 0.77467 | 0.776 | 0.77733 | 0.77867 | 0.78 | 0.78133 | 0.78267 | 0.784 | 0.78533 | 0.78667 | 0.788 | 0.78933 | 0.79067 | 0.792 | 0.79333 | 0.79467 | 0.796 | 0.79733 | 0.79867 | 0.8 | 0.80133 | 0.80267 | 0.804 | 0.80533 | 0.80667 | 0.80711 | 0.80756 | 0.808 | 0.80844 | 0.80889 | 0.80933 | 0.80978 | 0.81022 | 0.81067 | 0.81111 | 0.81156 | 0.812 | 0.81244 | 0.81289 | 0.81333 | 0.81378 | 0.81422 | 0.81467 | 0.81511 | 0.81556 | 0.816 | 0.81644 | 0.81689 | 0.81733 | 0.81778 | 0.81822 | 0.81867 | 0.81911 | 0.81956 | 0.82 | 0.82 | 0.82 | 0.82 | 0.82 | 0.82 | 0.82 | 0.82 | 0.82 | 0.82 | 0.82 | 0.82 | 0.82 | 0.82 | 0.82 | 0.82 | 0.82 | 0.82 | 0.82 | 0.82 | 0.82 | 0.82 | 0.82 | 0.82 | 0.82 | 0.82 | 0.82 | 0.82 | 0.82 | 0.82 | 0.82 | 0.81933 | 0.81867 | 0.818 | 0.81733 | 0.81667 | 0.816 | 0.81533 | 0.81467 | 0.814 | 0.81333 | 0.81267 | 0.812 | 0.81133 | 0.81067 | 0.81 | 0.80933 | 0.80867 | 0.808 | 0.80733 | 0.80667 | 0.806 | 0.80533 | 0.80467 | 0.804 | 0.80333 | 0.80267 | 0.802 | 0.80133 | 0.80067 | 0.8
0.17 | 0 | 0.027667 | 0.055333 | 0.083 | 0.11067 | 0.13833 | 0.166 | 0.19367 | 0.22133 | 0.249 | 0.27667 | 0.30827 | 0.33987 | 0.37147 | 0.40307 | 0.43467 | 0.44627 | 0.45787 | 0.46947 | 0.48107 | 0.49267 | 0.5018 | 0.51093 | 0.52007 | 0.5292 | 0.53833 | 0.54747 | 0.5566 | 0.56573 | 0.57487 | 0.584 | 0.58978 | 0.59556 | 0.60133 | 0.60711 | 0.61289 | 0.61867 | 0.62444 | 0.63022 | 0.636 | 0.64178 | 0.64756 | 0.65333 | 0.65911 | 0.66489 | 0.67067 | 0.67511 | 0.67956 | 0.684 | 0.68844 | 0.69289 | 0.69733 | 0.70178 | 0.70622 | 0.71067 | 0.71511 | 0.71956 | 0.724 | 0.72844 | 0.73289 | 0.73733 | 0.73853 | 0.73973 | 0.74093 | 0.74213 | 0.74333 | 0.74453 | 0.74573 | 0.74693 | 0.74813 | 0.74933 | 0.75053 | 0.75173 | 0.75293 | 0.75413 | 0.75533 | 0.75653 | 0.75773 | 0.75893 | 0.76013 | 0.76133 | 0.76253 | 0.76373 | 0.76493 | 0.76613 | 0.76733 | 0.76853 | 0.76973 | 0.77093 | 0.77213 | 0.77333 | 0.77369 | 0.77404 | 0.7744 | 0.77476 | 0.77511 | 0.77547 | 0.77582 | 0.77618 | 0.77653 | 0.77689 | 0.77724 | 0.7776 | 0.77796 | 0.77831 | 0.77867 | 0.77902 | 0.77938 | 0.77973 | 0.78009 | 0.78044 | 0.7808 | 0.78116 | 0.78151 | 0.78187 | 0.78222 | 0.78258 | 0.78293 | 0.78329 | 0.78364 | 0.784 | 0.784 | 0.784 | 0.784 | 0.784 | 0.784 | 0.784 | 0.784 | 0.784 | 0.784 | 0.784 | 0.784 | 0.784 | 0.784 | 0.784 | 0.784 | 0.784 | 0.784 | 0.784 | 0.784 | 0.784 | 0.784 | 0.784 | 0.784 | 0.784 | 0.784 | 0.784 | 0.784 | 0.784 | 0.784 | 0.784 | 0.78347 | 0.78293 | 0.7824 | 0.78187 | 0.78133 | 0.7808 | 0.78027 | 0.77973 | 0.7792 | 0.77867 | 0.77813 | 0.7776 | 0.77707 | 0.77653 | 0.776 | 0.77547 | 0.77493 | 0.7744 | 0.77387 | 0.77333 | 0.7728 | 0.77227 | 0.77173 | 0.7712 | 0.77067 | 0.77013 | 0.7696 | 0.76907 | 0.76853 | 0.768
0.2 | 0 | 0.026667 | 0.053333 | 0.08 | 0.10667 | 0.13333 | 0.16 | 0.18667 | 0.21333 | 0.24 | 0.26667 | 0.29467 | 0.32267 | 0.35067 | 0.37867 | 0.40667 | 0.42067 | 0.43467 | 0.44867 | 0.46267 | 0.47667 | 0.485 | 0.49333 | 0.50167 | 0.51 | 0.51833 | 0.52667 | 0.535 | 0.54333 | 0.55167 | 0.56 | 0.56511 | 0.57022 | 0.57533 | 0.58044 | 0.58556 | 0.59067 | 0.59578 | 0.60089 | 0.606 | 0.61111 | 0.61622 | 0.62133 | 0.62644 | 0.63156 | 0.63667 | 0.64044 | 0.64422 | 0.648 | 0.65178 | 0.65556 | 0.65933 | 0.66311 | 0.66689 | 0.67067 | 0.67444 | 0.67822 | 0.682 | 0.68578 | 0.68956 | 0.69333 | 0.69433 | 0.69533 | 0.69633 | 0.69733 | 0.69833 | 0.69933 | 0.70033 | 0.70133 | 0.70233 | 0.70333 | 0.70433 | 0.70533 | 0.70633 | 0.70733 | 0.70833 | 0.70933 | 0.71033 | 0.71133 | 0.71233 | 0.71333 | 0.71433 | 0.71533 | 0.71633 | 0.71733 | 0.71833 | 0.71933 | 0.72033 | 0.72133 | 0.72233 | 0.72333 | 0.72356 | 0.72378 | 0.724 | 0.72422 | 0.72444 | 0.72467 | 0.72489 | 0.72511 | 0.72533 | 0.72556 | 0.72578 | 0.726 | 0.72622 | 0.72644 | 0.72667 | 0.72689 | 0.72711 | 0.72733 | 0.72756 | 0.72778 | 0.728 | 0.72822 | 0.72844 | 0.72867 | 0.72889 | 0.72911 | 0.72933 | 0.72956 | 0.72978 | 0.73 | 0.73 | 0.73 | 0.73 | 0.73 | 0.73 | 0.73 | 0.73 | 0.73 | 0.73 | 0.73 | 0.73 | 0.73 | 0.73 | 0.73 | 0.73 | 0.73 | 0.73 | 0.73 | 0.73 | 0.73 | 0.73 | 0.73 | 0.73 | 0.73 | 0.73 | 0.73 | 0.73 | 0.73 | 0.73 | 0.73 | 0.72967 | 0.72933 | 0.729 | 0.72867 | 0.72833 | 0.728 | 0.72767 | 0.72733 | 0.727 | 0.72667 | 0.72633 | 0.726 | 0.72567 | 0.72533 | 0.725 | 0.72467 | 0.72433 | 0.724 | 0.72367 | 0.72333 | 0.723 | 0.72267 | 0.72233 | 0.722 | 0.72167 | 0.72133 | 0.721 | 0.72067 | 0.72033 | 0.72
0.25 | 0 | 0.025 | 0.05 | 0.075 | 0.1 | 0.125 | 0.15 | 0.175 | 0.2 | 0.225 | 0.25 | 0.272 | 0.294 | 0.316 | 0.338 | 0.36 | 0.378 | 0.396 | 0.414 | 0.432 | 0.45 | 0.457 | 0.464 | 0.471 | 0.478 | 0.485 | 0.492 | 0.499 | 0.506 | 0.513 | 0.52 | 0.524 | 0.528 | 0.532 | 0.536 | 0.54 | 0.544 | 0.548 | 0.552 | 0.556 | 0.56 | 0.564 | 0.568 | 0.572 | 0.576 | 0.58 | 0.58267 | 0.58533 | 0.588 | 0.59067 | 0.59333 | 0.596 | 0.59867 | 0.60133 | 0.604 | 0.60667 | 0.60933 | 0.612 | 0.61467 | 0.61733 | 0.62 | 0.62067 | 0.62133 | 0.622 | 0.62267 | 0.62333 | 0.624 | 0.62467 | 0.62533 | 0.626 | 0.62667 | 0.62733 | 0.628 | 0.62867 | 0.62933 | 0.63 | 0.63067 | 0.63133 | 0.632 | 0.63267 | 0.63333 | 0.634 | 0.63467 | 0.63533 | 0.636 | 0.63667 | 0.63733 | 0.638 | 0.63867 | 0.63933 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64
0.3 | 0 | 0.023 | 0.046 | 0.069 | 0.092 | 0.115 | 0.138 | 0.161 | 0.184 | 0.207 | 0.23 | 0.25 | 0.27 | 0.29 | 0.31 | 0.33 | 0.346 | 0.362 | 0.378 | 0.394 | 0.41 | 0.4166 | 0.4232 | 0.4298 | 0.4364 | 0.443 | 0.4496 | 0.4562 | 0.4628 | 0.4694 | 0.476 | 0.4796 | 0.4832 | 0.4868 | 0.4904 | 0.494 | 0.4976 | 0.5012 | 0.5048 | 0.5084 | 0.512 | 0.5156 | 0.5192 | 0.5228 | 0.5264 | 0.53 | 0.53213 | 0.53427 | 0.5364 | 0.53853 | 0.54067 | 0.5428 | 0.54493 | 0.54707 | 0.5492 | 0.55133 | 0.55347 | 0.5556 | 0.55773 | 0.55987 | 0.562 | 0.56253 | 0.56307 | 0.5636 | 0.56413 | 0.56467 | 0.5652 | 0.56573 | 0.56627 | 0.5668 | 0.56733 | 0.56787 | 0.5684 | 0.56893 | 0.56947 | 0.57 | 0.57053 | 0.57107 | 0.5716 | 0.57213 | 0.57267 | 0.5732 | 0.57373 | 0.57427 | 0.5748 | 0.57533 | 0.57587 | 0.5764 | 0.57693 | 0.57747 | 0.578 | 0.57793 | 0.57787 | 0.5778 | 0.57773 | 0.57767 | 0.5776 | 0.57753 | 0.57747 | 0.5774 | 0.57733 | 0.57727 | 0.5772 | 0.57713 | 0.57707 | 0.577 | 0.57693 | 0.57687 | 0.5768 | 0.57673 | 0.57667 | 0.5766 | 0.57653 | 0.57647 | 0.5764 | 0.57633 | 0.57627 | 0.5762 | 0.57613 | 0.57607 | 0.576 | 0.57593 | 0.57587 | 0.5758 | 0.57573 | 0.57567 | 0.5756 | 0.57553 | 0.57547 | 0.5754 | 0.57533 | 0.57527 | 0.5752 | 0.57513 | 0.57507 | 0.575 | 0.57493 | 0.57487 | 0.5748 | 0.57473 | 0.57467 | 0.5746 | 0.57453 | 0.57447 | 0.5744 | 0.57433 | 0.57427 | 0.5742 | 0.57413 | 0.57407 | 0.574 | 0.57393 | 0.57387 | 0.5738 | 0.57373 | 0.57367 | 0.5736 | 0.57353 | 0.57347 | 0.5734 | 0.57333 | 0.57327 | 0.5732 | 0.57313 | 0.57307 | 0.573 | 0.57293 | 0.57287 | 0.5728 | 0.57273 | 0.57267 | 0.5726 | 0.57253 | 0.57247 | 0.5724 | 0.57233 | 0.57227 | 0.5722 | 0.57213 | 0.57207 | 0.572
0.35 | 0 | 0.021 | 0.042 | 0.063 | 0.084 | 0.105 | 0.126 | 0.147 | 0.168 | 0.189 | 0.21 | 0.228 | 0.246 | 0.264 | 0.282 | 0.3 | 0.314 | 0.328 | 0.342 | 0.356 | 0.37 | 0.3762 | 0.3824 | 0.3886 | 0.3948 | 0.401 | 0.4072 | 0.4134 | 0.4196 | 0.4258 | 0.432 | 0.4352 | 0.4384 | 0.4416 | 0.4448 | 0.448 | 0.4512 | 0.4544 | 0.4576 | 0.4608 | 0.464 | 0.4672 | 0.4704 | 0.4736 | 0.4768 | 0.48 | 0.4816 | 0.4832 | 0.4848 | 0.4864 | 0.488 | 0.4896 | 0.4912 | 0.4928 | 0.4944 | 0.496 | 0.4976 | 0.4992 | 0.5008 | 0.5024 | 0.504 | 0.5044 | 0.5048 | 0.5052 | 0.5056 | 0.506 | 0.5064 | 0.5068 | 0.5072 | 0.5076 | 0.508 | 0.5084 | 0.5088 | 0.5092 | 0.5096 | 0.51 | 0.5104 | 0.5108 | 0.5112 | 0.5116 | 0.512 | 0.5124 | 0.5128 | 0.5132 | 0.5136 | 0.514 | 0.5144 | 0.5148 | 0.5152 | 0.5156 | 0.516 | 0.51587 | 0.51573 | 0.5156 | 0.51547 | 0.51533 | 0.5152 | 0.51507 | 0.51493 | 0.5148 | 0.51467 | 0.51453 | 0.5144 | 0.51427 | 0.51413 | 0.514 | 0.51387 | 0.51373 | 0.5136 | 0.51347 | 0.51333 | 0.5132 | 0.51307 | 0.51293 | 0.5128 | 0.51267 | 0.51253 | 0.5124 | 0.51227 | 0.51213 | 0.512 | 0.51187 | 0.51173 | 0.5116 | 0.51147 | 0.51133 | 0.5112 | 0.51107 | 0.51093 | 0.5108 | 0.51067 | 0.51053 | 0.5104 | 0.51027 | 0.51013 | 0.51 | 0.50987 | 0.50973 | 0.5096 | 0.50947 | 0.50933 | 0.5092 | 0.50907 | 0.50893 | 0.5088 | 0.50867 | 0.50853 | 0.5084 | 0.50827 | 0.50813 | 0.508 | 0.50787 | 0.50773 | 0.5076 | 0.50747 | 0.50733 | 0.5072 | 0.50707 | 0.50693 | 0.5068 | 0.50667 | 0.50653 | 0.5064 | 0.50627 | 0.50613 | 0.506 | 0.50587 | 0.50573 | 0.5056 | 0.50547 | 0.50533 | 0.5052 | 0.50507 | 0.50493 | 0.5048 | 0.50467 | 0.50453 | 0.5044 | 0.50427 | 0.50413 | 0.504
0.4 | 0 | 0.019 | 0.038 | 0.057 | 0.076 | 0.095 | 0.114 | 0.133 | 0.152 | 0.171 | 0.19 | 0.206 | 0.222 | 0.238 | 0.254 | 0.27 | 0.282 | 0.294 | 0.306 | 0.318 | 0.33 | 0.3358 | 0.3416 | 0.3474 | 0.3532 | 0.359 | 0.3648 | 0.3706 | 0.3764 | 0.3822 | 0.388 | 0.3908 | 0.3936 | 0.3964 | 0.3992 | 0.402 | 0.4048 | 0.4076 | 0.4104 | 0.4132 | 0.416 | 0.4188 | 0.4216 | 0.4244 | 0.4272 | 0.43 | 0.43107 | 0.43213 | 0.4332 | 0.43427 | 0.43533 | 0.4364 | 0.43747 | 0.43853 | 0.4396 | 0.44067 | 0.44173 | 0.4428 | 0.44387 | 0.44493 | 0.446 | 0.44627 | 0.44653 | 0.4468 | 0.44707 | 0.44733 | 0.4476 | 0.44787 | 0.44813 | 0.4484 | 0.44867 | 0.44893 | 0.4492 | 0.44947 | 0.44973 | 0.45 | 0.45027 | 0.45053 | 0.4508 | 0.45107 | 0.45133 | 0.4516 | 0.45187 | 0.45213 | 0.4524 | 0.45267 | 0.45293 | 0.4532 | 0.45347 | 0.45373 | 0.454 | 0.4538 | 0.4536 | 0.4534 | 0.4532 | 0.453 | 0.4528 | 0.4526 | 0.4524 | 0.4522 | 0.452 | 0.4518 | 0.4516 | 0.4514 | 0.4512 | 0.451 | 0.4508 | 0.4506 | 0.4504 | 0.4502 | 0.45 | 0.4498 | 0.4496 | 0.4494 | 0.4492 | 0.449 | 0.4488 | 0.4486 | 0.4484 | 0.4482 | 0.448 | 0.4478 | 0.4476 | 0.4474 | 0.4472 | 0.447 | 0.4468 | 0.4466 | 0.4464 | 0.4462 | 0.446 | 0.4458 | 0.4456 | 0.4454 | 0.4452 | 0.445 | 0.4448 | 0.4446 | 0.4444 | 0.4442 | 0.444 | 0.4438 | 0.4436 | 0.4434 | 0.4432 | 0.443 | 0.4428 | 0.4426 | 0.4424 | 0.4422 | 0.442 | 0.4418 | 0.4416 | 0.4414 | 0.4412 | 0.441 | 0.4408 | 0.4406 | 0.4404 | 0.4402 | 0.44 | 0.4398 | 0.4396 | 0.4394 | 0.4392 | 0.439 | 0.4388 | 0.4386 | 0.4384 | 0.4382 | 0.438 | 0.4378 | 0.4376 | 0.4374 | 0.4372 | 0.437 | 0.4368 | 0.4366 | 0.4364 | 0.4362 | 0.436
0.45 | 0 | 0.017 | 0.034 | 0.051 | 0.068 | 0.085 | 0.102 | 0.119 | 0.136 | 0.153 | 0.17 | 0.184 | 0.198 | 0.212 | 0.226 | 0.24 | 0.25 | 0.26 | 0.27 | 0.28 | 0.29 | 0.2954 | 0.3008 | 0.3062 | 0.3116 | 0.317 | 0.3224 | 0.3278 | 0.3332 | 0.3386 | 0.344 | 0.3464 | 0.3488 | 0.3512 | 0.3536 | 0.356 | 0.3584 | 0.3608 | 0.3632 | 0.3656 | 0.368 | 0.3704 | 0.3728 | 0.3752 | 0.3776 | 0.38 | 0.38053 | 0.38107 | 0.3816 | 0.38213 | 0.38267 | 0.3832 | 0.38373 | 0.38427 | 0.3848 | 0.38533 | 0.38587 | 0.3864 | 0.38693 | 0.38747 | 0.388 | 0.38813 | 0.38827 | 0.3884 | 0.38853 | 0.38867 | 0.3888 | 0.38893 | 0.38907 | 0.3892 | 0.38933 | 0.38947 | 0.3896 | 0.38973 | 0.38987 | 0.39 | 0.39013 | 0.39027 | 0.3904 | 0.39053 | 0.39067 | 0.3908 | 0.39093 | 0.39107 | 0.3912 | 0.39133 | 0.39147 | 0.3916 | 0.39173 | 0.39187 | 0.392 | 0.39173 | 0.39147 | 0.3912 | 0.39093 | 0.39067 | 0.3904 | 0.39013 | 0.38987 | 0.3896 | 0.38933 | 0.38907 | 0.3888 | 0.38853 | 0.38827 | 0.388 | 0.38773 | 0.38747 | 0.3872 | 0.38693 | 0.38667 | 0.3864 | 0.38613 | 0.38587 | 0.3856 | 0.38533 | 0.38507 | 0.3848 | 0.38453 | 0.38427 | 0.384 | 0.38373 | 0.38347 | 0.3832 | 0.38293 | 0.38267 | 0.3824 | 0.38213 | 0.38187 | 0.3816 | 0.38133 | 0.38107 | 0.3808 | 0.38053 | 0.38027 | 0.38 | 0.37973 | 0.37947 | 0.3792 | 0.37893 | 0.37867 | 0.3784 | 0.37813 | 0.37787 | 0.3776 | 0.37733 | 0.37707 | 0.3768 | 0.37653 | 0.37627 | 0.376 | 0.37573 | 0.37547 | 0.3752 | 0.37493 | 0.37467 | 0.3744 | 0.37413 | 0.37387 | 0.3736 | 0.37333 | 0.37307 | 0.3728 | 0.37253 | 0.37227 | 0.372 | 0.37173 | 0.37147 | 0.3712 | 0.37093 | 0.37067 | 0.3704 | 0.37013 | 0.36987 | 0.3696 | 0.36933 | 0.36907 | 0.3688 | 0.36853 | 0.36827 | 0.368
0.5 | 0 | 0.015 | 0.03 | 0.045 | 0.06 | 0.075 | 0.09 | 0.105 | 0.12 | 0.135 | 0.15 | 0.162 | 0.174 | 0.186 | 0.198 | 0.21 | 0.218 | 0.226 | 0.234 | 0.242 | 0.25 | 0.255 | 0.26 | 0.265 | 0.27 | 0.275 | 0.28 | 0.285 | 0.29 | 0.295 | 0.3 | 0.302 | 0.304 | 0.306 | 0.308 | 0.31 | 0.312 | 0.314 | 0.316 | 0.318 | 0.32 | 0.322 | 0.324 | 0.326 | 0.328 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.32967 | 0.32933 | 0.329 | 0.32867 | 0.32833 | 0.328 | 0.32767 | 0.32733 | 0.327 | 0.32667 | 0.32633 | 0.326 | 0.32567 | 0.32533 | 0.325 | 0.32467 | 0.32433 | 0.324 | 0.32367 | 0.32333 | 0.323 | 0.32267 | 0.32233 | 0.322 | 0.32167 | 0.32133 | 0.321 | 0.32067 | 0.32033 | 0.32 | 0.31967 | 0.31933 | 0.319 | 0.31867 | 0.31833 | 0.318 | 0.31767 | 0.31733 | 0.317 | 0.31667 | 0.31633 | 0.316 | 0.31567 | 0.31533 | 0.315 | 0.31467 | 0.31433 | 0.314 | 0.31367 | 0.31333 | 0.313 | 0.31267 | 0.31233 | 0.312 | 0.31167 | 0.31133 | 0.311 | 0.31067 | 0.31033 | 0.31 | 0.30967 | 0.30933 | 0.309 | 0.30867 | 0.30833 | 0.308 | 0.30767 | 0.30733 | 0.307 | 0.30667 | 0.30633 | 0.306 | 0.30567 | 0.30533 | 0.305 | 0.30467 | 0.30433 | 0.304 | 0.30367 | 0.30333 | 0.303 | 0.30267 | 0.30233 | 0.302 | 0.30167 | 0.30133 | 0.301 | 0.30067 | 0.30033 | 0.3
0.55 | 0 | 0.0135 | 0.027 | 0.0405 | 0.054 | 0.0675 | 0.081 | 0.0945 | 0.108 | 0.1215 | 0.135 | 0.1458 | 0.1566 | 0.1674 | 0.1782 | 0.189 | 0.1962 | 0.2034 | 0.2106 | 0.2178 | 0.225 | 0.2295 | 0.234 | 0.2385 | 0.243 | 0.2475 | 0.252 | 0.2565 | 0.261 | 0.2655 | 0.27 | 0.2718 | 0.2736 | 0.2754 | 0.2772 | 0.279 | 0.2808 | 0.2826 | 0.2844 | 0.2862 | 0.288 | 0.2898 | 0.2916 | 0.2934 | 0.2952 | 0.297 | 0.297 | 0.297 | 0.297 | 0.297 | 0.297 | 0.297 | 0.297 | 0.297 | 0.297 | 0.297 | 0.297 | 0.297 | 0.297 | 0.297 | 0.297 | 0.297 | 0.297 | 0.297 | 0.297 | 0.297 | 0.297 | 0.297 | 0.297 | 0.297 | 0.297 | 0.297 | 0.297 | 0.297 | 0.297 | 0.297 | 0.297 | 0.297 | 0.297 | 0.297 | 0.297 | 0.297 | 0.297 | 0.297 | 0.297 | 0.297 | 0.297 | 0.297 | 0.297 | 0.297 | 0.297 | 0.2967 | 0.2964 | 0.2961 | 0.2958 | 0.2955 | 0.2952 | 0.2949 | 0.2946 | 0.2943 | 0.294 | 0.2937 | 0.2934 | 0.2931 | 0.2928 | 0.2925 | 0.2922 | 0.2919 | 0.2916 | 0.2913 | 0.291 | 0.2907 | 0.2904 | 0.2901 | 0.2898 | 0.2895 | 0.2892 | 0.2889 | 0.2886 | 0.2883 | 0.288 | 0.2877 | 0.2874 | 0.2871 | 0.2868 | 0.2865 | 0.2862 | 0.2859 | 0.2856 | 0.2853 | 0.285 | 0.2847 | 0.2844 | 0.2841 | 0.2838 | 0.2835 | 0.2832 | 0.2829 | 0.2826 | 0.2823 | 0.282 | 0.2817 | 0.2814 | 0.2811 | 0.2808 | 0.2805 | 0.2802 | 0.2799 | 0.2796 | 0.2793 | 0.279 | 0.2787 | 0.2784 | 0.2781 | 0.2778 | 0.2775 | 0.2772 | 0.2769 | 0.2766 | 0.2763 | 0.276 | 0.2757 | 0.2754 | 0.2751 | 0.2748 | 0.2745 | 0.2742 | 0.2739 | 0.2736 | 0.2733 | 0.273 | 0.2727 | 0.2724 | 0.2721 | 0.2718 | 0.2715 | 0.2712 | 0.2709 | 0.2706 | 0.2703 | 0.27
0.6 | 0 | 0.012 | 0.024 | 0.036 | 0.048 | 0.06 | 0.072 | 0.084 | 0.096 | 0.108 | 0.12 | 0.1296 | 0.1392 | 0.1488 | 0.1584 | 0.168 | 0.1744 | 0.1808 | 0.1872 | 0.1936 | 0.2 | 0.204 | 0.208 | 0.212 | 0.216 | 0.22 | 0.224 | 0.228 | 0.232 | 0.236 | 0.24 | 0.2416 | 0.2432 | 0.2448 | 0.2464 | 0.248 | 0.2496 | 0.2512 | 0.2528 | 0.2544 | 0.256 | 0.2576 | 0.2592 | 0.2608 | 0.2624 | 0.264 | 0.264 | 0.264 | 0.264 | 0.264 | 0.264 | 0.264 | 0.264 | 0.264 | 0.264 | 0.264 | 0.264 | 0.264 | 0.264 | 0.264 | 0.264 | 0.264 | 0.264 | 0.264 | 0.264 | 0.264 | 0.264 | 0.264 | 0.264 | 0.264 | 0.264 | 0.264 | 0.264 | 0.264 | 0.264 | 0.264 | 0.264 | 0.264 | 0.264 | 0.264 | 0.264 | 0.264 | 0.264 | 0.264 | 0.264 | 0.264 | 0.264 | 0.264 | 0.264 | 0.264 | 0.264 | 0.26373 | 0.26347 | 0.2632 | 0.26293 | 0.26267 | 0.2624 | 0.26213 | 0.26187 | 0.2616 | 0.26133 | 0.26107 | 0.2608 | 0.26053 | 0.26027 | 0.26 | 0.25973 | 0.25947 | 0.2592 | 0.25893 | 0.25867 | 0.2584 | 0.25813 | 0.25787 | 0.2576 | 0.25733 | 0.25707 | 0.2568 | 0.25653 | 0.25627 | 0.256 | 0.25573 | 0.25547 | 0.2552 | 0.25493 | 0.25467 | 0.2544 | 0.25413 | 0.25387 | 0.2536 | 0.25333 | 0.25307 | 0.2528 | 0.25253 | 0.25227 | 0.252 | 0.25173 | 0.25147 | 0.2512 | 0.25093 | 0.25067 | 0.2504 | 0.25013 | 0.24987 | 0.2496 | 0.24933 | 0.24907 | 0.2488 | 0.24853 | 0.24827 | 0.248 | 0.24773 | 0.24747 | 0.2472 | 0.24693 | 0.24667 | 0.2464 | 0.24613 | 0.24587 | 0.2456 | 0.24533 | 0.24507 | 0.2448 | 0.24453 | 0.24427 | 0.244 | 0.24373 | 0.24347 | 0.2432 | 0.24293 | 0.24267 | 0.2424 | 0.24213 | 0.24187 | 0.2416 | 0.24133 | 0.24107 | 0.2408 | 0.24053 | 0.24027 | 0.24
0.65 | 0 | 0.0105 | 0.021 | 0.0315 | 0.042 | 0.0525 | 0.063 | 0.0735 | 0.084 | 0.0945 | 0.105 | 0.1134 | 0.1218 | 0.1302 | 0.1386 | 0.147 | 0.1526 | 0.1582 | 0.1638 | 0.1694 | 0.175 | 0.1785 | 0.182 | 0.1855 | 0.189 | 0.1925 | 0.196 | 0.1995 | 0.203 | 0.2065 | 0.21 | 0.2114 | 0.2128 | 0.2142 | 0.2156 | 0.217 | 0.2184 | 0.2198 | 0.2212 | 0.2226 | 0.224 | 0.2254 | 0.2268 | 0.2282 | 0.2296 | 0.231 | 0.231 | 0.231 | 0.231 | 0.231 | 0.231 | 0.231 | 0.231 | 0.231 | 0.231 | 0.231 | 0.231 | 0.231 | 0.231 | 0.231 | 0.231 | 0.231 | 0.231 | 0.231 | 0.231 | 0.231 | 0.231 | 0.231 | 0.231 | 0.231 | 0.231 | 0.231 | 0.231 | 0.231 | 0.231 | 0.231 | 0.231 | 0.231 | 0.231 | 0.231 | 0.231 | 0.231 | 0.231 | 0.231 | 0.231 | 0.231 | 0.231 | 0.231 | 0.231 | 0.231 | 0.231 | 0.23077 | 0.23053 | 0.2303 | 0.23007 | 0.22983 | 0.2296 | 0.22937 | 0.22913 | 0.2289 | 0.22867 | 0.22843 | 0.2282 | 0.22797 | 0.22773 | 0.2275 | 0.22727 | 0.22703 | 0.2268 | 0.22657 | 0.22633 | 0.2261 | 0.22587 | 0.22563 | 0.2254 | 0.22517 | 0.22493 | 0.2247 | 0.22447 | 0.22423 | 0.224 | 0.22377 | 0.22353 | 0.2233 | 0.22307 | 0.22283 | 0.2226 | 0.22237 | 0.22213 | 0.2219 | 0.22167 | 0.22143 | 0.2212 | 0.22097 | 0.22073 | 0.2205 | 0.22027 | 0.22003 | 0.2198 | 0.21957 | 0.21933 | 0.2191 | 0.21887 | 0.21863 | 0.2184 | 0.21817 | 0.21793 | 0.2177 | 0.21747 | 0.21723 | 0.217 | 0.21677 | 0.21653 | 0.2163 | 0.21607 | 0.21583 | 0.2156 | 0.21537 | 0.21513 | 0.2149 | 0.21467 | 0.21443 | 0.2142 | 0.21397 | 0.21373 | 0.2135 | 0.21327 | 0.21303 | 0.2128 | 0.21257 | 0.21233 | 0.2121 | 0.21187 | 0.21163 | 0.2114 | 0.21117 | 0.21093 | 0.2107 | 0.21047 | 0.21023 | 0.21
0.7 | 0 | 0.009 | 0.018 | 0.027 | 0.036 | 0.045 | 0.054 | 0.063 | 0.072 | 0.081 | 0.09 | 0.0972 | 0.1044 | 0.1116 | 0.1188 | 0.126 | 0.1308 | 0.1356 | 0.1404 | 0.1452 | 0.15 | 0.153 | 0.156 | 0.159 | 0.162 | 0.165 | 0.168 | 0.171 | 0.174 | 0.177 | 0.18 | 0.1812 | 0.1824 | 0.1836 | 0.1848 | 0.186 | 0.1872 | 0.1884 | 0.1896 | 0.1908 | 0.192 | 0.1932 | 0.1944 | 0.1956 | 0.1968 | 0.198 | 0.198 | 0.198 | 0.198 | 0.198 | 0.198 | 0.198 | 0.198 | 0.198 | 0.198 | 0.198 | 0.198 | 0.198 | 0.198 | 0.198 | 0.198 | 0.198 | 0.198 | 0.198 | 0.198 | 0.198 | 0.198 | 0.198 | 0.198 | 0.198 | 0.198 | 0.198 | 0.198 | 0.198 | 0.198 | 0.198 | 0.198 | 0.198 | 0.198 | 0.198 | 0.198 | 0.198 | 0.198 | 0.198 | 0.198 | 0.198 | 0.198 | 0.198 | 0.198 | 0.198 | 0.198 | 0.1978 | 0.1976 | 0.1974 | 0.1972 | 0.197 | 0.1968 | 0.1966 | 0.1964 | 0.1962 | 0.196 | 0.1958 | 0.1956 | 0.1954 | 0.1952 | 0.195 | 0.1948 | 0.1946 | 0.1944 | 0.1942 | 0.194 | 0.1938 | 0.1936 | 0.1934 | 0.1932 | 0.193 | 0.1928 | 0.1926 | 0.1924 | 0.1922 | 0.192 | 0.1918 | 0.1916 | 0.1914 | 0.1912 | 0.191 | 0.1908 | 0.1906 | 0.1904 | 0.1902 | 0.19 | 0.1898 | 0.1896 | 0.1894 | 0.1892 | 0.189 | 0.1888 | 0.1886 | 0.1884 | 0.1882 | 0.188 | 0.1878 | 0.1876 | 0.1874 | 0.1872 | 0.187 | 0.1868 | 0.1866 | 0.1864 | 0.1862 | 0.186 | 0.1858 | 0.1856 | 0.1854 | 0.1852 | 0.185 | 0.1848 | 0.1846 | 0.1844 | 0.1842 | 0.184 | 0.1838 | 0.1836 | 0.1834 | 0.1832 | 0.183 | 0.1828 | 0.1826 | 0.1824 | 0.1822 | 0.182 | 0.1818 | 0.1816 | 0.1814 | 0.1812 | 0.181 | 0.1808 | 0.1806 | 0.1804 | 0.1802 | 0.18
0.75 | 0 | 0.0075 | 0.015 | 0.0225 | 0.03 | 0.0375 | 0.045 | 0.0525 | 0.06 | 0.0675 | 0.075 | 0.081 | 0.087 | 0.093 | 0.099 | 0.105 | 0.109 | 0.113 | 0.117 | 0.121 | 0.125 | 0.1275 | 0.13 | 0.1325 | 0.135 | 0.1375 | 0.14 | 0.1425 | 0.145 | 0.1475 | 0.15 | 0.151 | 0.152 | 0.153 | 0.154 | 0.155 | 0.156 | 0.157 | 0.158 | 0.159 | 0.16 | 0.161 | 0.162 | 0.163 | 0.164 | 0.165 | 0.165 | 0.165 | 0.165 | 0.165 | 0.165 | 0.165 | 0.165 | 0.165 | 0.165 | 0.165 | 0.165 | 0.165 | 0.165 | 0.165 | 0.165 | 0.165 | 0.165 | 0.165 | 0.165 | 0.165 | 0.165 | 0.165 | 0.165 | 0.165 | 0.165 | 0.165 | 0.165 | 0.165 | 0.165 | 0.165 | 0.165 | 0.165 | 0.165 | 0.165 | 0.165 | 0.165 | 0.165 | 0.165 | 0.165 | 0.165 | 0.165 | 0.165 | 0.165 | 0.165 | 0.165 | 0.16483 | 0.16467 | 0.1645 | 0.16433 | 0.16417 | 0.164 | 0.16383 | 0.16367 | 0.1635 | 0.16333 | 0.16317 | 0.163 | 0.16283 | 0.16267 | 0.1625 | 0.16233 | 0.16217 | 0.162 | 0.16183 | 0.16167 | 0.1615 | 0.16133 | 0.16117 | 0.161 | 0.16083 | 0.16067 | 0.1605 | 0.16033 | 0.16017 | 0.16 | 0.15983 | 0.15967 | 0.1595 | 0.15933 | 0.15917 | 0.159 | 0.15883 | 0.15867 | 0.1585 | 0.15833 | 0.15817 | 0.158 | 0.15783 | 0.15767 | 0.1575 | 0.15733 | 0.15717 | 0.157 | 0.15683 | 0.15667 | 0.1565 | 0.15633 | 0.15617 | 0.156 | 0.15583 | 0.15567 | 0.1555 | 0.15533 | 0.15517 | 0.155 | 0.15483 | 0.15467 | 0.1545 | 0.15433 | 0.15417 | 0.154 | 0.15383 | 0.15367 | 0.1535 | 0.15333 | 0.15317 | 0.153 | 0.15283 | 0.15267 | 0.1525 | 0.15233 | 0.15217 | 0.152 | 0.15183 | 0.15167 | 0.1515 | 0.15133 | 0.15117 | 0.151 | 0.15083 | 0.15067 | 0.1505 | 0.15033 | 0.15017 | 0.15
0.8 | 0 | 0.006 | 0.012 | 0.018 | 0.024 | 0.03 | 0.036 | 0.042 | 0.048 | 0.054 | 0.06 | 0.0648 | 0.0696 | 0.0744 | 0.0792 | 0.084 | 0.0872 | 0.0904 | 0.0936 | 0.0968 | 0.1 | 0.102 | 0.104 | 0.106 | 0.108 | 0.11 | 0.112 | 0.114 | 0.116 | 0.118 | 0.12 | 0.1208 | 0.1216 | 0.1224 | 0.1232 | 0.124 | 0.1248 | 0.1256 | 0.1264 | 0.1272 | 0.128 | 0.1288 | 0.1296 | 0.1304 | 0.1312 | 0.132 | 0.132 | 0.132 | 0.132 | 0.132 | 0.132 | 0.132 | 0.132 | 0.132 | 0.132 | 0.132 | 0.132 | 0.132 | 0.132 | 0.132 | 0.132 | 0.132 | 0.132 | 0.132 | 0.132 | 0.132 | 0.132 | 0.132 | 0.132 | 0.132 | 0.132 | 0.132 | 0.132 | 0.132 | 0.132 | 0.132 | 0.132 | 0.132 | 0.132 | 0.132 | 0.132 | 0.132 | 0.132 | 0.132 | 0.132 | 0.132 | 0.132 | 0.132 | 0.132 | 0.132 | 0.132 | 0.13187 | 0.13173 | 0.1316 | 0.13147 | 0.13133 | 0.1312 | 0.13107 | 0.13093 | 0.1308 | 0.13067 | 0.13053 | 0.1304 | 0.13027 | 0.13013 | 0.13 | 0.12987 | 0.12973 | 0.1296 | 0.12947 | 0.12933 | 0.1292 | 0.12907 | 0.12893 | 0.1288 | 0.12867 | 0.12853 | 0.1284 | 0.12827 | 0.12813 | 0.128 | 0.12787 | 0.12773 | 0.1276 | 0.12747 | 0.12733 | 0.1272 | 0.12707 | 0.12693 | 0.1268 | 0.12667 | 0.12653 | 0.1264 | 0.12627 | 0.12613 | 0.126 | 0.12587 | 0.12573 | 0.1256 | 0.12547 | 0.12533 | 0.1252 | 0.12507 | 0.12493 | 0.1248 | 0.12467 | 0.12453 | 0.1244 | 0.12427 | 0.12413 | 0.124 | 0.12387 | 0.12373 | 0.1236 | 0.12347 | 0.12333 | 0.1232 | 0.12307 | 0.12293 | 0.1228 | 0.12267 | 0.12253 | 0.1224 | 0.12227 | 0.12213 | 0.122 | 0.12187 | 0.12173 | 0.1216 | 0.12147 | 0.12133 | 0.1212 | 0.12107 | 0.12093 | 0.1208 | 0.12067 | 0.12053 | 0.1204 | 0.12027 | 0.12013 | 0.12
0.85 | 0 | 0.0045 | 0.009 | 0.0135 | 0.018 | 0.0225 | 0.027 | 0.0315 | 0.036 | 0.0405 | 0.045 | 0.0486 | 0.0522 | 0.0558 | 0.0594 | 0.063 | 0.0654 | 0.0678 | 0.0702 | 0.0726 | 0.075 | 0.0765 | 0.078 | 0.0795 | 0.081 | 0.0825 | 0.084 | 0.0855 | 0.087 | 0.0885 | 0.09 | 0.0906 | 0.0912 | 0.0918 | 0.0924 | 0.093 | 0.0936 | 0.0942 | 0.0948 | 0.0954 | 0.096 | 0.0966 | 0.0972 | 0.0978 | 0.0984 | 0.099 | 0.099 | 0.099 | 0.099 | 0.099 | 0.099 | 0.099 | 0.099 | 0.099 | 0.099 | 0.099 | 0.099 | 0.099 | 0.099 | 0.099 | 0.099 | 0.099 | 0.099 | 0.099 | 0.099 | 0.099 | 0.099 | 0.099 | 0.099 | 0.099 | 0.099 | 0.099 | 0.099 | 0.099 | 0.099 | 0.099 | 0.099 | 0.099 | 0.099 | 0.099 | 0.099 | 0.099 | 0.099 | 0.099 | 0.099 | 0.099 | 0.099 | 0.099 | 0.099 | 0.099 | 0.099 | 0.0989 | 0.0988 | 0.0987 | 0.0986 | 0.0985 | 0.0984 | 0.0983 | 0.0982 | 0.0981 | 0.098 | 0.0979 | 0.0978 | 0.0977 | 0.0976 | 0.0975 | 0.0974 | 0.0973 | 0.0972 | 0.0971 | 0.097 | 0.0969 | 0.0968 | 0.0967 | 0.0966 | 0.0965 | 0.0964 | 0.0963 | 0.0962 | 0.0961 | 0.096 | 0.0959 | 0.0958 | 0.0957 | 0.0956 | 0.0955 | 0.0954 | 0.0953 | 0.0952 | 0.0951 | 0.095 | 0.0949 | 0.0948 | 0.0947 | 0.0946 | 0.0945 | 0.0944 | 0.0943 | 0.0942 | 0.0941 | 0.094 | 0.0939 | 0.0938 | 0.0937 | 0.0936 | 0.0935 | 0.0934 | 0.0933 | 0.0932 | 0.0931 | 0.093 | 0.0929 | 0.0928 | 0.0927 | 0.0926 | 0.0925 | 0.0924 | 0.0923 | 0.0922 | 0.0921 | 0.092 | 0.0919 | 0.0918 | 0.0917 | 0.0916 | 0.0915 | 0.0914 | 0.0913 | 0.0912 | 0.0911 | 0.091 | 0.0909 | 0.0908 | 0.0907 | 0.0906 | 0.0905 | 0.0904 | 0.0903 | 0.0902 | 0.0901 | 0.09
0.9 | 0 | 0.003 | 0.006 | 0.009 | 0.012 | 0.015 | 0.018 | 0.021 | 0.024 | 0.027 | 0.03 | 0.0324 | 0.0348 | 0.0372 | 0.0396 | 0.042 | 0.0436 | 0.0452 | 0.0468 | 0.0484 | 0.05 | 0.051 | 0.052 | 0.053 | 0.054 | 0.055 | 0.056 | 0.057 | 0.058 | 0.059 | 0.06 | 0.0604 | 0.0608 | 0.0612 | 0.0616 | 0.062 | 0.0624 | 0.0628 | 0.0632 | 0.0636 | 0.064 | 0.0644 | 0.0648 | 0.0652 | 0.0656 | 0.066 | 0.066 | 0.066 | 0.066 | 0.066 | 0.066 | 0.066 | 0.066 | 0.066 | 0.066 | 0.066 | 0.066 | 0.066 | 0.066 | 0.066 | 0.066 | 0.066 | 0.066 | 0.066 | 0.066 | 0.066 | 0.066 | 0.066 | 0.066 | 0.066 | 0.066 | 0.066 | 0.066 | 0.066 | 0.066 | 0.066 | 0.066 | 0.066 | 0.066 | 0.066 | 0.066 | 0.066 | 0.066 | 0.066 | 0.066 | 0.066 | 0.066 | 0.066 | 0.066 | 0.066 | 0.066 | 0.065933 | 0.065867 | 0.0658 | 0.065733 | 0.065667 | 0.0656 | 0.065533 | 0.065467 | 0.0654 | 0.065333 | 0.065267 | 0.0652 | 0.065133 | 0.065067 | 0.065 | 0.064933 | 0.064867 | 0.0648 | 0.064733 | 0.064667 | 0.0646 | 0.064533 | 0.064467 | 0.0644 | 0.064333 | 0.064267 | 0.0642 | 0.064133 | 0.064067 | 0.064 | 0.063933 | 0.063867 | 0.0638 | 0.063733 | 0.063667 | 0.0636 | 0.063533 | 0.063467 | 0.0634 | 0.063333 | 0.063267 | 0.0632 | 0.063133 | 0.063067 | 0.063 | 0.062933 | 0.062867 | 0.0628 | 0.062733 | 0.062667 | 0.0626 | 0.062533 | 0.062467 | 0.0624 | 0.062333 | 0.062267 | 0.0622 | 0.062133 | 0.062067 | 0.062 | 0.061933 | 0.061867 | 0.0618 | 0.061733 | 0.061667 | 0.0616 | 0.061533 | 0.061467 | 0.0614 | 0.061333 | 0.061267 | 0.0612 | 0.061133 | 0.061067 | 0.061 | 0.060933 | 0.060867 | 0.0608 | 0.060733 | 0.060667 | 0.0606 | 0.060533 | 0.060467 | 0.0604 | 0.060333 | 0.060267 | 0.0602 | 0.060133 | 0.060067 | 0.06
0.95 | 0 | 0.0015 | 0.003 | 0.0045 | 0.006 | 0.0075 | 0.009 | 0.0105 | 0.012 | 0.0135 | 0.015 | 0.0162 | 0.0174 | 0.0186 | 0.0198 | 0.021 | 0.0218 | 0.0226 | 0.0234 | 0.0242 | 0.025 | 0.0255 | 0.026 | 0.0265 | 0.027 | 0.0275 | 0.028 | 0.0285 | 0.029 | 0.0295 | 0.03 | 0.0302 | 0.0304 | 0.0306 | 0.0308 | 0.031 | 0.0312 | 0.0314 | 0.0316 | 0.0318 | 0.032 | 0.0322 | 0.0324 | 0.0326 | 0.0328 | 0.033 | 0.033 | 0.033 | 0.033 | 0.033 | 0.033 | 0.033 | 0.033 | 0.033 | 0.033 | 0.033 | 0.033 | 0.033 | 0.033 | 0.033 | 0.033 | 0.033 | 0.033 | 0.033 | 0.033 | 0.033 | 0.033 | 0.033 | 0.033 | 0.033 | 0.033 | 0.033 | 0.033 | 0.033 | 0.033 | 0.033 | 0.033 | 0.033 | 0.033 | 0.033 | 0.033 | 0.033 | 0.033 | 0.033 | 0.033 | 0.033 | 0.033 | 0.033 | 0.033 | 0.033 | 0.033 | 0.032967 | 0.032933 | 0.0329 | 0.032867 | 0.032833 | 0.0328 | 0.032767 | 0.032733 | 0.0327 | 0.032667 | 0.032633 | 0.0326 | 0.032567 | 0.032533 | 0.0325 | 0.032467 | 0.032433 | 0.0324 | 0.032367 | 0.032333 | 0.0323 | 0.032267 | 0.032233 | 0.0322 | 0.032167 | 0.032133 | 0.0321 | 0.032067 | 0.032033 | 0.032 | 0.031967 | 0.031933 | 0.0319 | 0.031867 | 0.031833 | 0.0318 | 0.031767 | 0.031733 | 0.0317 | 0.031667 | 0.031633 | 0.0316 | 0.031567 | 0.031533 | 0.0315 | 0.031467 | 0.031433 | 0.0314 | 0.031367 | 0.031333 | 0.0313 | 0.031267 | 0.031233 | 0.0312 | 0.031167 | 0.031133 | 0.0311 | 0.031067 | 0.031033 | 0.031 | 0.030967 | 0.030933 | 0.0309 | 0.030867 | 0.030833 | 0.0308 | 0.030767 | 0.030733 | 0.0307 | 0.030667 | 0.030633 | 0.0306 | 0.030567 | 0.030533 | 0.0305 | 0.030467 | 0.030433 | 0.0304 | 0.030367 | 0.030333 | 0.0303 | 0.030267 | 0.030233 | 0.0302 | 0.030167 | 0.030133 | 0.0301 | 0.030067 | 0.030033 | 0.03
1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1.05 | 0 | 0.0012 | 0.0024 | 0.0036 | 0.0048 | 0.006 | 0.0072 | 0.0084 | 0.0096 | 0.0108 | 0.012 | 0.0124 | 0.0128 | 0.0132 | 0.0136 | 0.014 | 0.0138 | 0.0136 | 0.0134 | 0.0132 | 0.013 | 0.0127 | 0.0124 | 0.0121 | 0.0118 | 0.0115 | 0.0112 | 0.0109 | 0.0106 | 0.0103 | 0.01 | 0.010067 | 0.010133 | 0.0102 | 0.010267 | 0.010333 | 0.0104 | 0.010467 | 0.010533 | 0.0106 | 0.010667 | 0.010733 | 0.0108 | 0.010867 | 0.010933 | 0.011 | 0.011067 | 0.011133 | 0.0112 | 0.011267 | 0.011333 | 0.0114 | 0.011467 | 0.011533 | 0.0116 | 0.011667 | 0.011733 | 0.0118 | 0.011867 | 0.011933 | 0.012 | 0.012417 | 0.012833 | 0.01325 | 0.013667 | 0.014083 | 0.0145 | 0.014917 | 0.015333 | 0.01575 | 0.016167 | 0.016583 | 0.017 | 0.017417 | 0.017833 | 0.01825 | 0.018667 | 0.019083 | 0.0195 | 0.019917 | 0.020333 | 0.02075 | 0.021167 | 0.021583 | 0.022 | 0.022417 | 0.022833 | 0.02325 | 0.023667 | 0.024083 | 0.0245 | 0.0249 | 0.0253 | 0.0257 | 0.0261 | 0.0265 | 0.0269 | 0.0273 | 0.0277 | 0.0281 | 0.0285 | 0.0289 | 0.0293 | 0.0297 | 0.0301 | 0.0305 | 0.0309 | 0.0313 | 0.0317 | 0.0321 | 0.0325 | 0.0329 | 0.0333 | 0.0337 | 0.0341 | 0.0345 | 0.0349 | 0.0353 | 0.0357 | 0.0361 | 0.0365 | 0.0369 | 0.0373 | 0.0377 | 0.0381 | 0.0385 | 0.0389 | 0.0393 | 0.0397 | 0.0401 | 0.0405 | 0.0409 | 0.0413 | 0.0417 | 0.0421 | 0.0425 | 0.0429 | 0.0433 | 0.0437 | 0.0441 | 0.0445 | 0.0449 | 0.0453 | 0.0457 | 0.0461 | 0.0465 | 0.0469 | 0.0473 | 0.0477 | 0.0481 | 0.0485 | 0.048617 | 0.048733 | 0.04885 | 0.048967 | 0.049083 | 0.0492 | 0.049317 | 0.049433 | 0.04955 | 0.049667 | 0.049783 | 0.0499 | 0.050017 | 0.050133 | 0.05025 | 0.050367 | 0.050483 | 0.0506 | 0.050717 | 0.050833 | 0.05095 | 0.051067 | 0.051183 | 0.0513 | 0.051417 | 0.051533 | 0.05165 | 0.051767 | 0.051883 | 0.052
1.1 | 0 | 0.0024 | 0.0048 | 0.0072 | 0.0096 | 0.012 | 0.0144 | 0.0168 | 0.0192 | 0.0216 | 0.024 | 0.0248 | 0.0256 | 0.0264 | 0.0272 | 0.028 | 0.0276 | 0.0272 | 0.0268 | 0.0264 | 0.026 | 0.0254 | 0.0248 | 0.0242 | 0.0236 | 0.023 | 0.0224 | 0.0218 | 0.0212 | 0.0206 | 0.02 | 0.020133 | 0.020267 | 0.0204 | 0.020533 | 0.020667 | 0.0208 | 0.020933 | 0.021067 | 0.0212 | 0.021333 | 0.021467 | 0.0216 | 0.021733 | 0.021867 | 0.022 | 0.022133 | 0.022267 | 0.0224 | 0.022533 | 0.022667 | 0.0228 | 0.022933 | 0.023067 | 0.0232 | 0.023333 | 0.023467 | 0.0236 | 0.023733 | 0.023867 | 0.024 | 0.024833 | 0.025667 | 0.0265 | 0.027333 | 0.028167 | 0.029 | 0.029833 | 0.030667 | 0.0315 | 0.032333 | 0.033167 | 0.034 | 0.034833 | 0.035667 | 0.0365 | 0.037333 | 0.038167 | 0.039 | 0.039833 | 0.040667 | 0.0415 | 0.042333 | 0.043167 | 0.044 | 0.044833 | 0.045667 | 0.0465 | 0.047333 | 0.048167 | 0.049 | 0.0498 | 0.0506 | 0.0514 | 0.0522 | 0.053 | 0.0538 | 0.0546 | 0.0554 | 0.0562 | 0.057 | 0.0578 | 0.0586 | 0.0594 | 0.0602 | 0.061 | 0.0618 | 0.0626 | 0.0634 | 0.0642 | 0.065 | 0.0658 | 0.0666 | 0.0674 | 0.0682 | 0.069 | 0.0698 | 0.0706 | 0.0714 | 0.0722 | 0.073 | 0.0738 | 0.0746 | 0.0754 | 0.0762 | 0.077 | 0.0778 | 0.0786 | 0.0794 | 0.0802 | 0.081 | 0.0818 | 0.0826 | 0.0834 | 0.0842 | 0.085 | 0.0858 | 0.0866 | 0.0874 | 0.0882 | 0.089 | 0.0898 | 0.0906 | 0.0914 | 0.0922 | 0.093 | 0.0938 | 0.0946 | 0.0954 | 0.0962 | 0.097 | 0.097233 | 0.097467 | 0.0977 | 0.097933 | 0.098167 | 0.0984 | 0.098633 | 0.098867 | 0.0991 | 0.099333 | 0.099567 | 0.0998 | 0.10003 | 0.10027 | 0.1005 | 0.10073 | 0.10097 | 0.1012 | 0.10143 | 0.10167 | 0.1019 | 0.10213 | 0.10237 | 0.1026 | 0.10283 | 0.10307 | 0.1033 | 0.10353 | 0.10377 | 0.104
1.15 | 0 | 0.0036 | 0.0072 | 0.0108 | 0.0144 | 0.018 | 0.0216 | 0.0252 | 0.0288 | 0.0324 | 0.036 | 0.0372 | 0.0384 | 0.0396 | 0.0408 | 0.042 | 0.0414 | 0.0408 | 0.0402 | 0.0396 | 0.039 | 0.0381 | 0.0372 | 0.0363 | 0.0354 | 0.0345 | 0.0336 | 0.0327 | 0.0318 | 0.0309 | 0.03 | 0.0302 | 0.0304 | 0.0306 | 0.0308 | 0.031 | 0.0312 | 0.0314 | 0.0316 | 0.0318 | 0.032 | 0.0322 | 0.0324 | 0.0326 | 0.0328 | 0.033 | 0.0332 | 0.0334 | 0.0336 | 0.0338 | 0.034 | 0.0342 | 0.0344 | 0.0346 | 0.0348 | 0.035 | 0.0352 | 0.0354 | 0.0356 | 0.0358 | 0.036 | 0.03725 | 0.0385 | 0.03975 | 0.041 | 0.04225 | 0.0435 | 0.04475 | 0.046 | 0.04725 | 0.0485 | 0.04975 | 0.051 | 0.05225 | 0.0535 | 0.05475 | 0.056 | 0.05725 | 0.0585 | 0.05975 | 0.061 | 0.06225 | 0.0635 | 0.06475 | 0.066 | 0.06725 | 0.0685 | 0.06975 | 0.071 | 0.07225 | 0.0735 | 0.0747 | 0.0759 | 0.0771 | 0.0783 | 0.0795 | 0.0807 | 0.0819 | 0.0831 | 0.0843 | 0.0855 | 0.0867 | 0.0879 | 0.0891 | 0.0903 | 0.0915 | 0.0927 | 0.0939 | 0.0951 | 0.0963 | 0.0975 | 0.0987 | 0.0999 | 0.1011 | 0.1023 | 0.1035 | 0.1047 | 0.1059 | 0.1071 | 0.1083 | 0.1095 | 0.1107 | 0.1119 | 0.1131 | 0.1143 | 0.1155 | 0.1167 | 0.1179 | 0.1191 | 0.1203 | 0.1215 | 0.1227 | 0.1239 | 0.1251 | 0.1263 | 0.1275 | 0.1287 | 0.1299 | 0.1311 | 0.1323 | 0.1335 | 0.1347 | 0.1359 | 0.1371 | 0.1383 | 0.1395 | 0.1407 | 0.1419 | 0.1431 | 0.1443 | 0.1455 | 0.14585 | 0.1462 | 0.14655 | 0.1469 | 0.14725 | 0.1476 | 0.14795 | 0.1483 | 0.14865 | 0.149 | 0.14935 | 0.1497 | 0.15005 | 0.1504 | 0.15075 | 0.1511 | 0.15145 | 0.1518 | 0.15215 | 0.1525 | 0.15285 | 0.1532 | 0.15355 | 0.1539 | 0.15425 | 0.1546 | 0.15495 | 0.1553 | 0.15565 | 0.156
1.2 | 0 | 0.0048 | 0.0096 | 0.0144 | 0.0192 | 0.024 | 0.0288 | 0.0336 | 0.0384 | 0.0432 | 0.048 | 0.0496 | 0.0512 | 0.0528 | 0.0544 | 0.056 | 0.0552 | 0.0544 | 0.0536 | 0.0528 | 0.052 | 0.0508 | 0.0496 | 0.0484 | 0.0472 | 0.046 | 0.0448 | 0.0436 | 0.0424 | 0.0412 | 0.04 | 0.040267 | 0.040533 | 0.0408 | 0.041067 | 0.041333 | 0.0416 | 0.041867 | 0.042133 | 0.0424 | 0.042667 | 0.042933 | 0.0432 | 0.043467 | 0.043733 | 0.044 | 0.044267 | 0.044533 | 0.0448 | 0.045067 | 0.045333 | 0.0456 | 0.045867 | 0.046133 | 0.0464 | 0.046667 | 0.046933 | 0.0472 | 0.047467 | 0.047733 | 0.048 | 0.049667 | 0.051333 | 0.053 | 0.054667 | 0.056333 | 0.058 | 0.059667 | 0.061333 | 0.063 | 0.064667 | 0.066333 | 0.068 | 0.069667 | 0.071333 | 0.073 | 0.074667 | 0.076333 | 0.078 | 0.079667 | 0.081333 | 0.083 | 0.084667 | 0.086333 | 0.088 | 0.089667 | 0.091333 | 0.093 | 0.094667 | 0.096333 | 0.098 | 0.0996 | 0.1012 | 0.1028 | 0.1044 | 0.106 | 0.1076 | 0.1092 | 0.1108 | 0.1124 | 0.114 | 0.1156 | 0.1172 | 0.1188 | 0.1204 | 0.122 | 0.1236 | 0.1252 | 0.1268 | 0.1284 | 0.13 | 0.1316 | 0.1332 | 0.1348 | 0.1364 | 0.138 | 0.1396 | 0.1412 | 0.1428 | 0.1444 | 0.146 | 0.1476 | 0.1492 | 0.1508 | 0.1524 | 0.154 | 0.1556 | 0.1572 | 0.1588 | 0.1604 | 0.162 | 0.1636 | 0.1652 | 0.1668 | 0.1684 | 0.17 | 0.1716 | 0.1732 | 0.1748 | 0.1764 | 0.178 | 0.1796 | 0.1812 | 0.1828 | 0.1844 | 0.186 | 0.1876 | 0.1892 | 0.1908 | 0.1924 | 0.194 | 0.19447 | 0.19493 | 0.1954 | 0.19587 | 0.19633 | 0.1968 | 0.19727 | 0.19773 | 0.1982 | 0.19867 | 0.19913 | 0.1996 | 0.20007 | 0.20053 | 0.201 | 0.20147 | 0.20193 | 0.2024 | 0.20287 | 0.20333 | 0.2038 | 0.20427 | 0.20473 | 0.2052 | 0.20567 | 0.20613 | 0.2066 | 0.20707 | 0.20753 | 0.208
1.25 | 0 | 0.006 | 0.012 | 0.018 | 0.024 | 0.03 | 0.036 | 0.042 | 0.048 | 0.054 | 0.06 | 0.062 | 0.064 | 0.066 | 0.068 | 0.07 | 0.069 | 0.068 | 0.067 | 0.066 | 0.065 | 0.0635 | 0.062 | 0.0605 | 0.059 | 0.0575 | 0.056 | 0.0545 | 0.053 | 0.0515 | 0.05 | 0.050333 | 0.050667 | 0.051 | 0.051333 | 0.051667 | 0.052 | 0.052333 | 0.052667 | 0.053 | 0.053333 | 0.053667 | 0.054 | 0.054333 | 0.054667 | 0.055 | 0.055333 | 0.055667 | 0.056 | 0.056333 | 0.056667 | 0.057 | 0.057333 | 0.057667 | 0.058 | 0.058333 | 0.058667 | 0.059 | 0.059333 | 0.059667 | 0.06 | 0.062083 | 0.064167 | 0.06625 | 0.068333 | 0.070417 | 0.0725 | 0.074583 | 0.076667 | 0.07875 | 0.080833 | 0.082917 | 0.085 | 0.087083 | 0.089167 | 0.09125 | 0.093333 | 0.095417 | 0.0975 | 0.099583 | 0.10167 | 0.10375 | 0.10583 | 0.10792 | 0.11 | 0.11208 | 0.11417 | 0.11625 | 0.11833 | 0.12042 | 0.1225 | 0.1245 | 0.1265 | 0.1285 | 0.1305 | 0.1325 | 0.1345 | 0.1365 | 0.1385 | 0.1405 | 0.1425 | 0.1445 | 0.1465 | 0.1485 | 0.1505 | 0.1525 | 0.1545 | 0.1565 | 0.1585 | 0.1605 | 0.1625 | 0.1645 | 0.1665 | 0.1685 | 0.1705 | 0.1725 | 0.1745 | 0.1765 | 0.1785 | 0.1805 | 0.1825 | 0.1845 | 0.1865 | 0.1885 | 0.1905 | 0.1925 | 0.1945 | 0.1965 | 0.1985 | 0.2005 | 0.2025 | 0.2045 | 0.2065 | 0.2085 | 0.2105 | 0.2125 | 0.2145 | 0.2165 | 0.2185 | 0.2205 | 0.2225 | 0.2245 | 0.2265 | 0.2285 | 0.2305 | 0.2325 | 0.2345 | 0.2365 | 0.2385 | 0.2405 | 0.2425 | 0.24308 | 0.24367 | 0.24425 | 0.24483 | 0.24542 | 0.246 | 0.24658 | 0.24717 | 0.24775 | 0.24833 | 0.24892 | 0.2495 | 0.25008 | 0.25067 | 0.25125 | 0.25183 | 0.25242 | 0.253 | 0.25358 | 0.25417 | 0.25475 | 0.25533 | 0.25592 | 0.2565 | 0.25708 | 0.25767 | 0.25825 | 0.25883 | 0.25942 | 0.26
1.3 | 0 | 0.0072 | 0.0144 | 0.0216 | 0.0288 | 0.036 | 0.0432 | 0.0504 | 0.0576 | 0.0648 | 0.072 | 0.0744 | 0.0768 | 0.0792 | 0.0816 | 0.084 | 0.0828 | 0.0816 | 0.0804 | 0.0792 | 0.078 | 0.0762 | 0.0744 | 0.0726 | 0.0708 | 0.069 | 0.0672 | 0.0654 | 0.0636 | 0.0618 | 0.06 | 0.0604 | 0.0608 | 0.0612 | 0.0616 | 0.062 | 0.0624 | 0.0628 | 0.0632 | 0.0636 | 0.064 | 0.0644 | 0.0648 | 0.0652 | 0.0656 | 0.066 | 0.0664 | 0.0668 | 0.0672 | 0.0676 | 0.068 | 0.0684 | 0.0688 | 0.0692 | 0.0696 | 0.07 | 0.0704 | 0.0708 | 0.0712 | 0.0716 | 0.072 | 0.0745 | 0.077 | 0.0795 | 0.082 | 0.0845 | 0.087 | 0.0895 | 0.092 | 0.0945 | 0.097 | 0.0995 | 0.102 | 0.1045 | 0.107 | 0.1095 | 0.112 | 0.1145 | 0.117 | 0.1195 | 0.122 | 0.1245 | 0.127 | 0.1295 | 0.132 | 0.1345 | 0.137 | 0.1395 | 0.142 | 0.1445 | 0.147 | 0.1494 | 0.1518 | 0.1542 | 0.1566 | 0.159 | 0.1614 | 0.1638 | 0.1662 | 0.1686 | 0.171 | 0.1734 | 0.1758 | 0.1782 | 0.1806 | 0.183 | 0.1854 | 0.1878 | 0.1902 | 0.1926 | 0.195 | 0.1974 | 0.1998 | 0.2022 | 0.2046 | 0.207 | 0.2094 | 0.2118 | 0.2142 | 0.2166 | 0.219 | 0.2214 | 0.2238 | 0.2262 | 0.2286 | 0.231 | 0.2334 | 0.2358 | 0.2382 | 0.2406 | 0.243 | 0.2454 | 0.2478 | 0.2502 | 0.2526 | 0.255 | 0.2574 | 0.2598 | 0.2622 | 0.2646 | 0.267 | 0.2694 | 0.2718 | 0.2742 | 0.2766 | 0.279 | 0.2814 | 0.2838 | 0.2862 | 0.2886 | 0.291 | 0.2917 | 0.2924 | 0.2931 | 0.2938 | 0.2945 | 0.2952 | 0.2959 | 0.2966 | 0.2973 | 0.298 | 0.2987 | 0.2994 | 0.3001 | 0.3008 | 0.3015 | 0.3022 | 0.3029 | 0.3036 | 0.3043 | 0.305 | 0.3057 | 0.3064 | 0.3071 | 0.3078 | 0.3085 | 0.3092 | 0.3099 | 0.3106 | 0.3113 | 0.312
1.35 | 0 | 0.0084 | 0.0168 | 0.0252 | 0.0336 | 0.042 | 0.0504 | 0.0588 | 0.0672 | 0.0756 | 0.084 | 0.0868 | 0.0896 | 0.0924 | 0.0952 | 0.098 | 0.0966 | 0.0952 | 0.0938 | 0.0924 | 0.091 | 0.0889 | 0.0868 | 0.0847 | 0.0826 | 0.0805 | 0.0784 | 0.0763 | 0.0742 | 0.0721 | 0.07 | 0.070467 | 0.070933 | 0.0714 | 0.071867 | 0.072333 | 0.0728 | 0.073267 | 0.073733 | 0.0742 | 0.074667 | 0.075133 | 0.0756 | 0.076067 | 0.076533 | 0.077 | 0.077467 | 0.077933 | 0.0784 | 0.078867 | 0.079333 | 0.0798 | 0.080267 | 0.080733 | 0.0812 | 0.081667 | 0.082133 | 0.0826 | 0.083067 | 0.083533 | 0.084 | 0.086917 | 0.089833 | 0.09275 | 0.095667 | 0.098583 | 0.1015 | 0.10442 | 0.10733 | 0.11025 | 0.11317 | 0.11608 | 0.119 | 0.12192 | 0.12483 | 0.12775 | 0.13067 | 0.13358 | 0.1365 | 0.13942 | 0.14233 | 0.14525 | 0.14817 | 0.15108 | 0.154 | 0.15692 | 0.15983 | 0.16275 | 0.16567 | 0.16858 | 0.1715 | 0.1743 | 0.1771 | 0.1799 | 0.1827 | 0.1855 | 0.1883 | 0.1911 | 0.1939 | 0.1967 | 0.1995 | 0.2023 | 0.2051 | 0.2079 | 0.2107 | 0.2135 | 0.2163 | 0.2191 | 0.2219 | 0.2247 | 0.2275 | 0.2303 | 0.2331 | 0.2359 | 0.2387 | 0.2415 | 0.2443 | 0.2471 | 0.2499 | 0.2527 | 0.2555 | 0.2583 | 0.2611 | 0.2639 | 0.2667 | 0.2695 | 0.2723 | 0.2751 | 0.2779 | 0.2807 | 0.2835 | 0.2863 | 0.2891 | 0.2919 | 0.2947 | 0.2975 | 0.3003 | 0.3031 | 0.3059 | 0.3087 | 0.3115 | 0.3143 | 0.3171 | 0.3199 | 0.3227 | 0.3255 | 0.3283 | 0.3311 | 0.3339 | 0.3367 | 0.3395 | 0.34032 | 0.34113 | 0.34195 | 0.34277 | 0.34358 | 0.3444 | 0.34522 | 0.34603 | 0.34685 | 0.34767 | 0.34848 | 0.3493 | 0.35012 | 0.35093 | 0.35175 | 0.35257 | 0.35338 | 0.3542 | 0.35502 | 0.35583 | 0.35665 | 0.35747 | 0.35828 | 0.3591 | 0.35992 | 0.36073 | 0.36155 | 0.36237 | 0.36318 | 0.364
1.4 | 0 | 0.0096 | 0.0192 | 0.0288 | 0.0384 | 0.048 | 0.0576 | 0.0672 | 0.0768 | 0.0864 | 0.096 | 0.0992 | 0.1024 | 0.1056 | 0.1088 | 0.112 | 0.1104 | 0.1088 | 0.1072 | 0.1056 | 0.104 | 0.1016 | 0.0992 | 0.0968 | 0.0944 | 0.092 | 0.0896 | 0.0872 | 0.0848 | 0.0824 | 0.08 | 0.080533 | 0.081067 | 0.0816 | 0.082133 | 0.082667 | 0.0832 | 0.083733 | 0.084267 | 0.0848 | 0.085333 | 0.085867 | 0.0864 | 0.086933 | 0.087467 | 0.088 | 0.088533 | 0.089067 | 0.0896 | 0.090133 | 0.090667 | 0.0912 | 0.091733 | 0.092267 | 0.0928 | 0.093333 | 0.093867 | 0.0944 | 0.094933 | 0.095467 | 0.096 | 0.099333 | 0.10267 | 0.106 | 0.10933 | 0.11267 | 0.116 | 0.11933 | 0.12267 | 0.126 | 0.12933 | 0.13267 | 0.136 | 0.13933 | 0.14267 | 0.146 | 0.14933 | 0.15267 | 0.156 | 0.15933 | 0.16267 | 0.166 | 0.16933 | 0.17267 | 0.176 | 0.17933 | 0.18267 | 0.186 | 0.18933 | 0.19267 | 0.196 | 0.1992 | 0.2024 | 0.2056 | 0.2088 | 0.212 | 0.2152 | 0.2184 | 0.2216 | 0.2248 | 0.228 | 0.2312 | 0.2344 | 0.2376 | 0.2408 | 0.244 | 0.2472 | 0.2504 | 0.2536 | 0.2568 | 0.26 | 0.2632 | 0.2664 | 0.2696 | 0.2728 | 0.276 | 0.2792 | 0.2824 | 0.2856 | 0.2888 | 0.292 | 0.2952 | 0.2984 | 0.3016 | 0.3048 | 0.308 | 0.3112 | 0.3144 | 0.3176 | 0.3208 | 0.324 | 0.3272 | 0.3304 | 0.3336 | 0.3368 | 0.34 | 0.3432 | 0.3464 | 0.3496 | 0.3528 | 0.356 | 0.3592 | 0.3624 | 0.3656 | 0.3688 | 0.372 | 0.3752 | 0.3784 | 0.3816 | 0.3848 | 0.388 | 0.38893 | 0.38987 | 0.3908 | 0.39173 | 0.39267 | 0.3936 | 0.39453 | 0.39547 | 0.3964 | 0.39733 | 0.39827 | 0.3992 | 0.40013 | 0.40107 | 0.402 | 0.40293 | 0.40387 | 0.4048 | 0.40573 | 0.40667 | 0.4076 | 0.40853 | 0.40947 | 0.4104 | 0.41133 | 0.41227 | 0.4132 | 0.41413 | 0.41507 | 0.416
1.45 | 0 | 0.0108 | 0.0216 | 0.0324 | 0.0432 | 0.054 | 0.0648 | 0.0756 | 0.0864 | 0.0972 | 0.108 | 0.1116 | 0.1152 | 0.1188 | 0.1224 | 0.126 | 0.1242 | 0.1224 | 0.1206 | 0.1188 | 0.117 | 0.1143 | 0.1116 | 0.1089 | 0.1062 | 0.1035 | 0.1008 | 0.0981 | 0.0954 | 0.0927 | 0.09 | 0.0906 | 0.0912 | 0.0918 | 0.0924 | 0.093 | 0.0936 | 0.0942 | 0.0948 | 0.0954 | 0.096 | 0.0966 | 0.0972 | 0.0978 | 0.0984 | 0.099 | 0.0996 | 0.1002 | 0.1008 | 0.1014 | 0.102 | 0.1026 | 0.1032 | 0.1038 | 0.1044 | 0.105 | 0.1056 | 0.1062 | 0.1068 | 0.1074 | 0.108 | 0.11175 | 0.1155 | 0.11925 | 0.123 | 0.12675 | 0.1305 | 0.13425 | 0.138 | 0.14175 | 0.1455 | 0.14925 | 0.153 | 0.15675 | 0.1605 | 0.16425 | 0.168 | 0.17175 | 0.1755 | 0.17925 | 0.183 | 0.18675 | 0.1905 | 0.19425 | 0.198 | 0.20175 | 0.2055 | 0.20925 | 0.213 | 0.21675 | 0.2205 | 0.2241 | 0.2277 | 0.2313 | 0.2349 | 0.2385 | 0.2421 | 0.2457 | 0.2493 | 0.2529 | 0.2565 | 0.2601 | 0.2637 | 0.2673 | 0.2709 | 0.2745 | 0.2781 | 0.2817 | 0.2853 | 0.2889 | 0.2925 | 0.2961 | 0.2997 | 0.3033 | 0.3069 | 0.3105 | 0.3141 | 0.3177 | 0.3213 | 0.3249 | 0.3285 | 0.3321 | 0.3357 | 0.3393 | 0.3429 | 0.3465 | 0.3501 | 0.3537 | 0.3573 | 0.3609 | 0.3645 | 0.3681 | 0.3717 | 0.3753 | 0.3789 | 0.3825 | 0.3861 | 0.3897 | 0.3933 | 0.3969 | 0.4005 | 0.4041 | 0.4077 | 0.4113 | 0.4149 | 0.4185 | 0.4221 | 0.4257 | 0.4293 | 0.4329 | 0.4365 | 0.43755 | 0.4386 | 0.43965 | 0.4407 | 0.44175 | 0.4428 | 0.44385 | 0.4449 | 0.44595 | 0.447 | 0.44805 | 0.4491 | 0.45015 | 0.4512 | 0.45225 | 0.4533 | 0.45435 | 0.4554 | 0.45645 | 0.4575 | 0.45855 | 0.4596 | 0.46065 | 0.4617 | 0.46275 | 0.4638 | 0.46485 | 0.4659 | 0.46695 | 0.468
1.5 | 0 | 0.012 | 0.024 | 0.036 | 0.048 | 0.06 | 0.072 | 0.084 | 0.096 | 0.108 | 0.12 | 0.124 | 0.128 | 0.132 | 0.136 | 0.14 | 0.138 | 0.136 | 0.134 | 0.132 | 0.13 | 0.127 | 0.124 | 0.121 | 0.118 | 0.115 | 0.112 | 0.109 | 0.106 | 0.103 | 0.1 | 0.10067 | 0.10133 | 0.102 | 0.10267 | 0.10333 | 0.104 | 0.10467 | 0.10533 | 0.106 | 0.10667 | 0.10733 | 0.108 | 0.10867 | 0.10933 | 0.11 | 0.11067 | 0.11133 | 0.112 | 0.11267 | 0.11333 | 0.114 | 0.11467 | 0.11533 | 0.116 | 0.11667 | 0.11733 | 0.118 | 0.11867 | 0.11933 | 0.12 | 0.12417 | 0.12833 | 0.1325 | 0.13667 | 0.14083 | 0.145 | 0.14917 | 0.15333 | 0.1575 | 0.16167 | 0.16583 | 0.17 | 0.17417 | 0.17833 | 0.1825 | 0.18667 | 0.19083 | 0.195 | 0.19917 | 0.20333 | 0.2075 | 0.21167 | 0.21583 | 0.22 | 0.22417 | 0.22833 | 0.2325 | 0.23667 | 0.24083 | 0.245 | 0.249 | 0.253 | 0.257 | 0.261 | 0.265 | 0.269 | 0.273 | 0.277 | 0.281 | 0.285 | 0.289 | 0.293 | 0.297 | 0.301 | 0.305 | 0.309 | 0.313 | 0.317 | 0.321 | 0.325 | 0.329 | 0.333 | 0.337 | 0.341 | 0.345 | 0.349 | 0.353 | 0.357 | 0.361 | 0.365 | 0.369 | 0.373 | 0.377 | 0.381 | 0.385 | 0.389 | 0.393 | 0.397 | 0.401 | 0.405 | 0.409 | 0.413 | 0.417 | 0.421 | 0.425 | 0.429 | 0.433 | 0.437 | 0.441 | 0.445 | 0.449 | 0.453 | 0.457 | 0.461 | 0.465 | 0.469 | 0.473 | 0.477 | 0.481 | 0.485 | 0.48617 | 0.48733 | 0.4885 | 0.48967 | 0.49083 | 0.492 | 0.49317 | 0.49433 | 0.4955 | 0.49667 | 0.49783 | 0.499 | 0.50017 | 0.50133 | 0.5025 | 0.50367 | 0.50483 | 0.506 | 0.50717 | 0.50833 | 0.5095 | 0.51067 | 0.51183 | 0.513 | 0.51417 | 0.51533 | 0.5165 | 0.51767 | 0.51883 | 0.52
1.55 | 0 | 0.0132 | 0.0264 | 0.0396 | 0.0528 | 0.066 | 0.0792 | 0.0924 | 0.1056 | 0.1188 | 0.132 | 0.1364 | 0.1408 | 0.1452 | 0.1496 | 0.154 | 0.1518 | 0.1496 | 0.1474 | 0.1452 | 0.143 | 0.1397 | 0.1364 | 0.1331 | 0.1298 | 0.1265 | 0.1232 | 0.1199 | 0.1166 | 0.1133 | 0.11 | 0.11073 | 0.11147 | 0.1122 | 0.11293 | 0.11367 | 0.1144 | 0.11513 | 0.11587 | 0.1166 | 0.11733 | 0.11807 | 0.1188 | 0.11953 | 0.12027 | 0.121 | 0.12173 | 0.12247 | 0.1232 | 0.12393 | 0.12467 | 0.1254 | 0.12613 | 0.12687 | 0.1276 | 0.12833 | 0.12907 | 0.1298 | 0.13053 | 0.13127 | 0.132 | 0.13658 | 0.14117 | 0.14575 | 0.15033 | 0.15492 | 0.1595 | 0.16408 | 0.16867 | 0.17325 | 0.17783 | 0.18242 | 0.187 | 0.19158 | 0.19617 | 0.20075 | 0.20533 | 0.20992 | 0.2145 | 0.21908 | 0.22367 | 0.22825 | 0.23283 | 0.23742 | 0.242 | 0.24658 | 0.25117 | 0.25575 | 0.26033 | 0.26492 | 0.2695 | 0.2739 | 0.2783 | 0.2827 | 0.2871 | 0.2915 | 0.2959 | 0.3003 | 0.3047 | 0.3091 | 0.3135 | 0.3179 | 0.3223 | 0.3267 | 0.3311 | 0.3355 | 0.3399 | 0.3443 | 0.3487 | 0.3531 | 0.3575 | 0.3619 | 0.3663 | 0.3707 | 0.3751 | 0.3795 | 0.3839 | 0.3883 | 0.3927 | 0.3971 | 0.4015 | 0.4059 | 0.4103 | 0.4147 | 0.4191 | 0.4235 | 0.4279 | 0.4323 | 0.4367 | 0.4411 | 0.4455 | 0.4499 | 0.4543 | 0.4587 | 0.4631 | 0.4675 | 0.4719 | 0.4763 | 0.4807 | 0.4851 | 0.4895 | 0.4939 | 0.4983 | 0.5027 | 0.5071 | 0.5115 | 0.5159 | 0.5203 | 0.5247 | 0.5291 | 0.5335 | 0.53478 | 0.53607 | 0.53735 | 0.53863 | 0.53992 | 0.5412 | 0.54248 | 0.54377 | 0.54505 | 0.54633 | 0.54762 | 0.5489 | 0.55018 | 0.55147 | 0.55275 | 0.55403 | 0.55532 | 0.5566 | 0.55788 | 0.55917 | 0.56045 | 0.56173 | 0.56302 | 0.5643 | 0.56558 | 0.56687 | 0.56815 | 0.56943 | 0.57072 | 0.572
1.6 | 0 | 0.0144 | 0.0288 | 0.0432 | 0.0576 | 0.072 | 0.0864 | 0.1008 | 0.1152 | 0.1296 | 0.144 | 0.1488 | 0.1536 | 0.1584 | 0.1632 | 0.168 | 0.1656 | 0.1632 | 0.1608 | 0.1584 | 0.156 | 0.1524 | 0.1488 | 0.1452 | 0.1416 | 0.138 | 0.1344 | 0.1308 | 0.1272 | 0.1236 | 0.12 | 0.1208 | 0.1216 | 0.1224 | 0.1232 | 0.124 | 0.1248 | 0.1256 | 0.1264 | 0.1272 | 0.128 | 0.1288 | 0.1296 | 0.1304 | 0.1312 | 0.132 | 0.1328 | 0.1336 | 0.1344 | 0.1352 | 0.136 | 0.1368 | 0.1376 | 0.1384 | 0.1392 | 0.14 | 0.1408 | 0.1416 | 0.1424 | 0.1432 | 0.144 | 0.149 | 0.154 | 0.159 | 0.164 | 0.169 | 0.174 | 0.179 | 0.184 | 0.189 | 0.194 | 0.199 | 0.204 | 0.209 | 0.214 | 0.219 | 0.224 | 0.229 | 0.234 | 0.239 | 0.244 | 0.249 | 0.254 | 0.259 | 0.264 | 0.269 | 0.274 | 0.279 | 0.284 | 0.289 | 0.294 | 0.2988 | 0.3036 | 0.3084 | 0.3132 | 0.318 | 0.3228 | 0.3276 | 0.3324 | 0.3372 | 0.342 | 0.3468 | 0.3516 | 0.3564 | 0.3612 | 0.366 | 0.3708 | 0.3756 | 0.3804 | 0.3852 | 0.39 | 0.3948 | 0.3996 | 0.4044 | 0.4092 | 0.414 | 0.4188 | 0.4236 | 0.4284 | 0.4332 | 0.438 | 0.4428 | 0.4476 | 0.4524 | 0.4572 | 0.462 | 0.4668 | 0.4716 | 0.4764 | 0.4812 | 0.486 | 0.4908 | 0.4956 | 0.5004 | 0.5052 | 0.51 | 0.5148 | 0.5196 | 0.5244 | 0.5292 | 0.534 | 0.5388 | 0.5436 | 0.5484 | 0.5532 | 0.558 | 0.5628 | 0.5676 | 0.5724 | 0.5772 | 0.582 | 0.5834 | 0.5848 | 0.5862 | 0.5876 | 0.589 | 0.5904 | 0.5918 | 0.5932 | 0.5946 | 0.596 | 0.5974 | 0.5988 | 0.6002 | 0.6016 | 0.603 | 0.6044 | 0.6058 | 0.6072 | 0.6086 | 0.61 | 0.6114 | 0.6128 | 0.6142 | 0.6156 | 0.617 | 0.6184 | 0.6198 | 0.6212 | 0.6226 | 0.624
1.65 | 0 | 0.0156 | 0.0312 | 0.0468 | 0.0624 | 0.078 | 0.0936 | 0.1092 | 0.1248 | 0.1404 | 0.156 | 0.1612 | 0.1664 | 0.1716 | 0.1768 | 0.182 | 0.1794 | 0.1768 | 0.1742 | 0.1716 | 0.169 | 0.1651 | 0.1612 | 0.1573 | 0.1534 | 0.1495 | 0.1456 | 0.1417 | 0.1378 | 0.1339 | 0.13 | 0.13087 | 0.13173 | 0.1326 | 0.13347 | 0.13433 | 0.1352 | 0.13607 | 0.13693 | 0.1378 | 0.13867 | 0.13953 | 0.1404 | 0.14127 | 0.14213 | 0.143 | 0.14387 | 0.14473 | 0.1456 | 0.14647 | 0.14733 | 0.1482 | 0.14907 | 0.14993 | 0.1508 | 0.15167 | 0.15253 | 0.1534 | 0.15427 | 0.15513 | 0.156 | 0.16142 | 0.16683 | 0.17225 | 0.17767 | 0.18308 | 0.1885 | 0.19392 | 0.19933 | 0.20475 | 0.21017 | 0.21558 | 0.221 | 0.22642 | 0.23183 | 0.23725 | 0.24267 | 0.24808 | 0.2535 | 0.25892 | 0.26433 | 0.26975 | 0.27517 | 0.28058 | 0.286 | 0.29142 | 0.29683 | 0.30225 | 0.30767 | 0.31308 | 0.3185 | 0.3237 | 0.3289 | 0.3341 | 0.3393 | 0.3445 | 0.3497 | 0.3549 | 0.3601 | 0.3653 | 0.3705 | 0.3757 | 0.3809 | 0.3861 | 0.3913 | 0.3965 | 0.4017 | 0.4069 | 0.4121 | 0.4173 | 0.4225 | 0.4277 | 0.4329 | 0.4381 | 0.4433 | 0.4485 | 0.4537 | 0.4589 | 0.4641 | 0.4693 | 0.4745 | 0.4797 | 0.4849 | 0.4901 | 0.4953 | 0.5005 | 0.5057 | 0.5109 | 0.5161 | 0.5213 | 0.5265 | 0.5317 | 0.5369 | 0.5421 | 0.5473 | 0.5525 | 0.5577 | 0.5629 | 0.5681 | 0.5733 | 0.5785 | 0.5837 | 0.5889 | 0.5941 | 0.5993 | 0.6045 | 0.6097 | 0.6149 | 0.6201 | 0.6253 | 0.6305 | 0.63202 | 0.63353 | 0.63505 | 0.63657 | 0.63808 | 0.6396 | 0.64112 | 0.64263 | 0.64415 | 0.64567 | 0.64718 | 0.6487 | 0.65022 | 0.65173 | 0.65325 | 0.65477 | 0.65628 | 0.6578 | 0.65932 | 0.66083 | 0.66235 | 0.66387 | 0.66538 | 0.6669 | 0.66842 | 0.66993 | 0.67145 | 0.67297 | 0.67448 | 0.676
1.7 | 0 | 0.0168 | 0.0336 | 0.0504 | 0.0672 | 0.084 | 0.1008 | 0.1176 | 0.1344 | 0.1512 | 0.168 | 0.1736 | 0.1792 | 0.1848 | 0.1904 | 0.196 | 0.1932 | 0.1904 | 0.1876 | 0.1848 | 0.182 | 0.1778 | 0.1736 | 0.1694 | 0.1652 | 0.161 | 0.1568 | 0.1526 | 0.1484 | 0.1442 | 0.14 | 0.14093 | 0.14187 | 0.1428 | 0.14373 | 0.14467 | 0.1456 | 0.14653 | 0.14747 | 0.1484 | 0.14933 | 0.15027 | 0.1512 | 0.15213 | 0.15307 | 0.154 | 0.15493 | 0.15587 | 0.1568 | 0.15773 | 0.15867 | 0.1596 | 0.16053 | 0.16147 | 0.1624 | 0.16333 | 0.16427 | 0.1652 | 0.16613 | 0.16707 | 0.168 | 0.17383 | 0.17967 | 0.1855 | 0.19133 | 0.19717 | 0.203 | 0.20883 | 0.21467 | 0.2205 | 0.22633 | 0.23217 | 0.238 | 0.24383 | 0.24967 | 0.2555 | 0.26133 | 0.26717 | 0.273 | 0.27883 | 0.28467 | 0.2905 | 0.29633 | 0.30217 | 0.308 | 0.31383 | 0.31967 | 0.3255 | 0.33133 | 0.33717 | 0.343 | 0.3486 | 0.3542 | 0.3598 | 0.3654 | 0.371 | 0.3766 | 0.3822 | 0.3878 | 0.3934 | 0.399 | 0.4046 | 0.4102 | 0.4158 | 0.4214 | 0.427 | 0.4326 | 0.4382 | 0.4438 | 0.4494 | 0.455 | 0.4606 | 0.4662 | 0.4718 | 0.4774 | 0.483 | 0.4886 | 0.4942 | 0.4998 | 0.5054 | 0.511 | 0.5166 | 0.5222 | 0.5278 | 0.5334 | 0.539 | 0.5446 | 0.5502 | 0.5558 | 0.5614 | 0.567 | 0.5726 | 0.5782 | 0.5838 | 0.5894 | 0.595 | 0.6006 | 0.6062 | 0.6118 | 0.6174 | 0.623 | 0.6286 | 0.6342 | 0.6398 | 0.6454 | 0.651 | 0.6566 | 0.6622 | 0.6678 | 0.6734 | 0.679 | 0.68063 | 0.68227 | 0.6839 | 0.68553 | 0.68717 | 0.6888 | 0.69043 | 0.69207 | 0.6937 | 0.69533 | 0.69697 | 0.6986 | 0.70023 | 0.70187 | 0.7035 | 0.70513 | 0.70677 | 0.7084 | 0.71003 | 0.71167 | 0.7133 | 0.71493 | 0.71657 | 0.7182 | 0.71983 | 0.72147 | 0.7231 | 0.72473 | 0.72637 | 0.728
1.75 | 0 | 0.018 | 0.036 | 0.054 | 0.072 | 0.09 | 0.108 | 0.126 | 0.144 | 0.162 | 0.18 | 0.186 | 0.192 | 0.198 | 0.204 | 0.21 | 0.207 | 0.204 | 0.201 | 0.198 | 0.195 | 0.1905 | 0.186 | 0.1815 | 0.177 | 0.1725 | 0.168 | 0.1635 | 0.159 | 0.1545 | 0.15 | 0.151 | 0.152 | 0.153 | 0.154 | 0.155 | 0.156 | 0.157 | 0.158 | 0.159 | 0.16 | 0.161 | 0.162 | 0.163 | 0.164 | 0.165 | 0.166 | 0.167 | 0.168 | 0.169 | 0.17 | 0.171 | 0.172 | 0.173 | 0.174 | 0.175 | 0.176 | 0.177 | 0.178 | 0.179 | 0.18 | 0.18625 | 0.1925 | 0.19875 | 0.205 | 0.21125 | 0.2175 | 0.22375 | 0.23 | 0.23625 | 0.2425 | 0.24875 | 0.255 | 0.26125 | 0.2675 | 0.27375 | 0.28 | 0.28625 | 0.2925 | 0.29875 | 0.305 | 0.31125 | 0.3175 | 0.32375 | 0.33 | 0.33625 | 0.3425 | 0.34875 | 0.355 | 0.36125 | 0.3675 | 0.3735 | 0.3795 | 0.3855 | 0.3915 | 0.3975 | 0.4035 | 0.4095 | 0.4155 | 0.4215 | 0.4275 | 0.4335 | 0.4395 | 0.4455 | 0.4515 | 0.4575 | 0.4635 | 0.4695 | 0.4755 | 0.4815 | 0.4875 | 0.4935 | 0.4995 | 0.5055 | 0.5115 | 0.5175 | 0.5235 | 0.5295 | 0.5355 | 0.5415 | 0.5475 | 0.5535 | 0.5595 | 0.5655 | 0.5715 | 0.5775 | 0.5835 | 0.5895 | 0.5955 | 0.6015 | 0.6075 | 0.6135 | 0.6195 | 0.6255 | 0.6315 | 0.6375 | 0.6435 | 0.6495 | 0.6555 | 0.6615 | 0.6675 | 0.6735 | 0.6795 | 0.6855 | 0.6915 | 0.6975 | 0.7035 | 0.7095 | 0.7155 | 0.7215 | 0.7275 | 0.72925 | 0.731 | 0.73275 | 0.7345 | 0.73625 | 0.738 | 0.73975 | 0.7415 | 0.74325 | 0.745 | 0.74675 | 0.7485 | 0.75025 | 0.752 | 0.75375 | 0.7555 | 0.75725 | 0.759 | 0.76075 | 0.7625 | 0.76425 | 0.766 | 0.76775 | 0.7695 | 0.77125 | 0.773 | 0.77475 | 0.7765 | 0.77825 | 0.78
1.8 | 0 | 0.0192 | 0.0384 | 0.0576 | 0.0768 | 0.096 | 0.1152 | 0.1344 | 0.1536 | 0.1728 | 0.192 | 0.1984 | 0.2048 | 0.2112 | 0.2176 | 0.224 | 0.2208 | 0.2176 | 0.2144 | 0.2112 | 0.208 | 0.2032 | 0.1984 | 0.1936 | 0.1888 | 0.184 | 0.1792 | 0.1744 | 0.1696 | 0.1648 | 0.16 | 0.16107 | 0.16213 | 0.1632 | 0.16427 | 0.16533 | 0.1664 | 0.16747 | 0.16853 | 0.1696 | 0.17067 | 0.17173 | 0.1728 | 0.17387 | 0.17493 | 0.176 | 0.17707 | 0.17813 | 0.1792 | 0.18027 | 0.18133 | 0.1824 | 0.18347 | 0.18453 | 0.1856 | 0.18667 | 0.18773 | 0.1888 | 0.18987 | 0.19093 | 0.192 | 0.19867 | 0.20533 | 0.212 | 0.21867 | 0.22533 | 0.232 | 0.23867 | 0.24533 | 0.252 | 0.25867 | 0.26533 | 0.272 | 0.27867 | 0.28533 | 0.292 | 0.29867 | 0.30533 | 0.312 | 0.31867 | 0.32533 | 0.332 | 0.33867 | 0.34533 | 0.352 | 0.35867 | 0.36533 | 0.372 | 0.37867 | 0.38533 | 0.392 | 0.3984 | 0.4048 | 0.4112 | 0.4176 | 0.424 | 0.4304 | 0.4368 | 0.4432 | 0.4496 | 0.456 | 0.4624 | 0.4688 | 0.4752 | 0.4816 | 0.488 | 0.4944 | 0.5008 | 0.5072 | 0.5136 | 0.52 | 0.5264 | 0.5328 | 0.5392 | 0.5456 | 0.552 | 0.5584 | 0.5648 | 0.5712 | 0.5776 | 0.584 | 0.5904 | 0.5968 | 0.6032 | 0.6096 | 0.616 | 0.6224 | 0.6288 | 0.6352 | 0.6416 | 0.648 | 0.6544 | 0.6608 | 0.6672 | 0.6736 | 0.68 | 0.6864 | 0.6928 | 0.6992 | 0.7056 | 0.712 | 0.7184 | 0.7248 | 0.7312 | 0.7376 | 0.744 | 0.7504 | 0.7568 | 0.7632 | 0.7696 | 0.776 | 0.77787 | 0.77973 | 0.7816 | 0.78347 | 0.78533 | 0.7872 | 0.78907 | 0.79093 | 0.7928 | 0.79467 | 0.79653 | 0.7984 | 0.80027 | 0.80213 | 0.804 | 0.80587 | 0.80773 | 0.8096 | 0.81147 | 0.81333 | 0.8152 | 0.81707 | 0.81893 | 0.8208 | 0.82267 | 0.82453 | 0.8264 | 0.82827 | 0.83013 | 0.832
1.85 | 0 | 0.0204 | 0.0408 | 0.0612 | 0.0816 | 0.102 | 0.1224 | 0.1428 | 0.1632 | 0.1836 | 0.204 | 0.2108 | 0.2176 | 0.2244 | 0.2312 | 0.238 | 0.2346 | 0.2312 | 0.2278 | 0.2244 | 0.221 | 0.2159 | 0.2108 | 0.2057 | 0.2006 | 0.1955 | 0.1904 | 0.1853 | 0.1802 | 0.1751 | 0.17 | 0.17113 | 0.17227 | 0.1734 | 0.17453 | 0.17567 | 0.1768 | 0.17793 | 0.17907 | 0.1802 | 0.18133 | 0.18247 | 0.1836 | 0.18473 | 0.18587 | 0.187 | 0.18813 | 0.18927 | 0.1904 | 0.19153 | 0.19267 | 0.1938 | 0.19493 | 0.19607 | 0.1972 | 0.19833 | 0.19947 | 0.2006 | 0.20173 | 0.20287 | 0.204 | 0.21108 | 0.21817 | 0.22525 | 0.23233 | 0.23942 | 0.2465 | 0.25358 | 0.26067 | 0.26775 | 0.27483 | 0.28192 | 0.289 | 0.29608 | 0.30317 | 0.31025 | 0.31733 | 0.32442 | 0.3315 | 0.33858 | 0.34567 | 0.35275 | 0.35983 | 0.36692 | 0.374 | 0.38108 | 0.38817 | 0.39525 | 0.40233 | 0.40942 | 0.4165 | 0.4233 | 0.4301 | 0.4369 | 0.4437 | 0.4505 | 0.4573 | 0.4641 | 0.4709 | 0.4777 | 0.4845 | 0.4913 | 0.4981 | 0.5049 | 0.5117 | 0.5185 | 0.5253 | 0.5321 | 0.5389 | 0.5457 | 0.5525 | 0.5593 | 0.5661 | 0.5729 | 0.5797 | 0.5865 | 0.5933 | 0.6001 | 0.6069 | 0.6137 | 0.6205 | 0.6273 | 0.6341 | 0.6409 | 0.6477 | 0.6545 | 0.6613 | 0.6681 | 0.6749 | 0.6817 | 0.6885 | 0.6953 | 0.7021 | 0.7089 | 0.7157 | 0.7225 | 0.7293 | 0.7361 | 0.7429 | 0.7497 | 0.7565 | 0.7633 | 0.7701 | 0.7769 | 0.7837 | 0.7905 | 0.7973 | 0.8041 | 0.8109 | 0.8177 | 0.8245 | 0.82648 | 0.82847 | 0.83045 | 0.83243 | 0.83442 | 0.8364 | 0.83838 | 0.84037 | 0.84235 | 0.84433 | 0.84632 | 0.8483 | 0.85028 | 0.85227 | 0.85425 | 0.85623 | 0.85822 | 0.8602 | 0.86218 | 0.86417 | 0.86615 | 0.86813 | 0.87012 | 0.8721 | 0.87408 | 0.87607 | 0.87805 | 0.88003 | 0.88202 | 0.884
1.9 | 0 | 0.0216 | 0.0432 | 0.0648 | 0.0864 | 0.108 | 0.1296 | 0.1512 | 0.1728 | 0.1944 | 0.216 | 0.2232 | 0.2304 | 0.2376 | 0.2448 | 0.252 | 0.2484 | 0.2448 | 0.2412 | 0.2376 | 0.234 | 0.2286 | 0.2232 | 0.2178 | 0.2124 | 0.207 | 0.2016 | 0.1962 | 0.1908 | 0.1854 | 0.18 | 0.1812 | 0.1824 | 0.1836 | 0.1848 | 0.186 | 0.1872 | 0.1884 | 0.1896 | 0.1908 | 0.192 | 0.1932 | 0.1944 | 0.1956 | 0.1968 | 0.198 | 0.1992 | 0.2004 | 0.2016 | 0.2028 | 0.204 | 0.2052 | 0.2064 | 0.2076 | 0.2088 | 0.21 | 0.2112 | 0.2124 | 0.2136 | 0.2148 | 0.216 | 0.2235 | 0.231 | 0.2385 | 0.246 | 0.2535 | 0.261 | 0.2685 | 0.276 | 0.2835 | 0.291 | 0.2985 | 0.306 | 0.3135 | 0.321 | 0.3285 | 0.336 | 0.3435 | 0.351 | 0.3585 | 0.366 | 0.3735 | 0.381 | 0.3885 | 0.396 | 0.4035 | 0.411 | 0.4185 | 0.426 | 0.4335 | 0.441 | 0.4482 | 0.4554 | 0.4626 | 0.4698 | 0.477 | 0.4842 | 0.4914 | 0.4986 | 0.5058 | 0.513 | 0.5202 | 0.5274 | 0.5346 | 0.5418 | 0.549 | 0.5562 | 0.5634 | 0.5706 | 0.5778 | 0.585 | 0.5922 | 0.5994 | 0.6066 | 0.6138 | 0.621 | 0.6282 | 0.6354 | 0.6426 | 0.6498 | 0.657 | 0.6642 | 0.6714 | 0.6786 | 0.6858 | 0.693 | 0.7002 | 0.7074 | 0.7146 | 0.7218 | 0.729 | 0.7362 | 0.7434 | 0.7506 | 0.7578 | 0.765 | 0.7722 | 0.7794 | 0.7866 | 0.7938 | 0.801 | 0.8082 | 0.8154 | 0.8226 | 0.8298 | 0.837 | 0.8442 | 0.8514 | 0.8586 | 0.8658 | 0.873 | 0.8751 | 0.8772 | 0.8793 | 0.8814 | 0.8835 | 0.8856 | 0.8877 | 0.8898 | 0.8919 | 0.894 | 0.8961 | 0.8982 | 0.9003 | 0.9024 | 0.9045 | 0.9066 | 0.9087 | 0.9108 | 0.9129 | 0.915 | 0.9171 | 0.9192 | 0.9213 | 0.9234 | 0.9255 | 0.9276 | 0.9297 | 0.9318 | 0.9339 | 0.936
1.95 | 0 | 0.0228 | 0.0456 | 0.0684 | 0.0912 | 0.114 | 0.1368 | 0.1596 | 0.1824 | 0.2052 | 0.228 | 0.2356 | 0.2432 | 0.2508 | 0.2584 | 0.266 | 0.2622 | 0.2584 | 0.2546 | 0.2508 | 0.247 | 0.2413 | 0.2356 | 0.2299 | 0.2242 | 0.2185 | 0.2128 | 0.2071 | 0.2014 | 0.1957 | 0.19 | 0.19127 | 0.19253 | 0.1938 | 0.19507 | 0.19633 | 0.1976 | 0.19887 | 0.20013 | 0.2014 | 0.20267 | 0.20393 | 0.2052 | 0.20647 | 0.20773 | 0.209 | 0.21027 | 0.21153 | 0.2128 | 0.21407 | 0.21533 | 0.2166 | 0.21787 | 0.21913 | 0.2204 | 0.22167 | 0.22293 | 0.2242 | 0.22547 | 0.22673 | 0.228 | 0.23592 | 0.24383 | 0.25175 | 0.25967 | 0.26758 | 0.2755 | 0.28342 | 0.29133 | 0.29925 | 0.30717 | 0.31508 | 0.323 | 0.33092 | 0.33883 | 0.34675 | 0.35467 | 0.36258 | 0.3705 | 0.37842 | 0.38633 | 0.39425 | 0.40217 | 0.41008 | 0.418 | 0.42592 | 0.43383 | 0.44175 | 0.44967 | 0.45758 | 0.4655 | 0.4731 | 0.4807 | 0.4883 | 0.4959 | 0.5035 | 0.5111 | 0.5187 | 0.5263 | 0.5339 | 0.5415 | 0.5491 | 0.5567 | 0.5643 | 0.5719 | 0.5795 | 0.5871 | 0.5947 | 0.6023 | 0.6099 | 0.6175 | 0.6251 | 0.6327 | 0.6403 | 0.6479 | 0.6555 | 0.6631 | 0.6707 | 0.6783 | 0.6859 | 0.6935 | 0.7011 | 0.7087 | 0.7163 | 0.7239 | 0.7315 | 0.7391 | 0.7467 | 0.7543 | 0.7619 | 0.7695 | 0.7771 | 0.7847 | 0.7923 | 0.7999 | 0.8075 | 0.8151 | 0.8227 | 0.8303 | 0.8379 | 0.8455 | 0.8531 | 0.8607 | 0.8683 | 0.8759 | 0.8835 | 0.8911 | 0.8987 | 0.9063 | 0.9139 | 0.9215 | 0.92372 | 0.92593 | 0.92815 | 0.93037 | 0.93258 | 0.9348 | 0.93702 | 0.93923 | 0.94145 | 0.94367 | 0.94588 | 0.9481 | 0.95032 | 0.95253 | 0.95475 | 0.95697 | 0.95918 | 0.9614 | 0.96362 | 0.96583 | 0.96805 | 0.97027 | 0.97248 | 0.9747 | 0.97692 | 0.97913 | 0.98135 | 0.98357 | 0.98578 | 0.988
2 | 0 | 0.024 | 0.048 | 0.072 | 0.096 | 0.12 | 0.144 | 0.168 | 0.192 | 0.216 | 0.24 | 0.248 | 0.256 | 0.264 | 0.272 | 0.28 | 0.276 | 0.272 | 0.268 | 0.264 | 0.26 | 0.254 | 0.248 | 0.242 | 0.236 | 0.23 | 0.224 | 0.218 | 0.212 | 0.206 | 0.2 | 0.20133 | 0.20267 | 0.204 | 0.20533 | 0.20667 | 0.208 | 0.20933 | 0.21067 | 0.212 | 0.21333 | 0.21467 | 0.216 | 0.21733 | 0.21867 | 0.22 | 0.22133 | 0.22267 | 0.224 | 0.22533 | 0.22667 | 0.228 | 0.22933 | 0.23067 | 0.232 | 0.23333 | 0.23467 | 0.236 | 0.23733 | 0.23867 | 0.24 | 0.24833 | 0.25667 | 0.265 | 0.27333 | 0.28167 | 0.29 | 0.29833 | 0.30667 | 0.315 | 0.32333 | 0.33167 | 0.34 | 0.34833 | 0.35667 | 0.365 | 0.37333 | 0.38167 | 0.39 | 0.39833 | 0.40667 | 0.415 | 0.42333 | 0.43167 | 0.44 | 0.44833 | 0.45667 | 0.465 | 0.47333 | 0.48167 | 0.49 | 0.498 | 0.506 | 0.514 | 0.522 | 0.53 | 0.538 | 0.546 | 0.554 | 0.562 | 0.57 | 0.578 | 0.586 | 0.594 | 0.602 | 0.61 | 0.618 | 0.626 | 0.634 | 0.642 | 0.65 | 0.658 | 0.666 | 0.674 | 0.682 | 0.69 | 0.698 | 0.706 | 0.714 | 0.722 | 0.73 | 0.738 | 0.746 | 0.754 | 0.762 | 0.77 | 0.778 | 0.786 | 0.794 | 0.802 | 0.81 | 0.818 | 0.826 | 0.834 | 0.842 | 0.85 | 0.858 | 0.866 | 0.874 | 0.882 | 0.89 | 0.898 | 0.906 | 0.914 | 0.922 | 0.93 | 0.938 | 0.946 | 0.954 | 0.962 | 0.97 | 0.97233 | 0.97467 | 0.977 | 0.97933 | 0.98167 | 0.984 | 0.98633 | 0.98867 | 0.991 | 0.99333 | 0.99567 | 0.998 | 1.0003 | 1.0027 | 1.005 | 1.0073 | 1.0097 | 1.012 | 1.0143 | 1.0167 | 1.019 | 1.0213 | 1.0237 | 1.026 | 1.0283 | 1.0307 | 1.033 | 1.0353 | 1.0377 | 1.04
2.05 | 0 | 0.025625 | 0.05125 | 0.076875 | 0.1025 | 0.12812 | 0.15375 | 0.17938 | 0.205 | 0.23062 | 0.25625 | 0.2635 | 0.27075 | 0.278 | 0.28525 | 0.2925 | 0.28865 | 0.2848 | 0.28095 | 0.2771 | 0.27325 | 0.26717 | 0.2611 | 0.25503 | 0.24895 | 0.24288 | 0.2368 | 0.23073 | 0.22465 | 0.21857 | 0.2125 | 0.2141 | 0.2157 | 0.2173 | 0.2189 | 0.2205 | 0.2221 | 0.2237 | 0.2253 | 0.2269 | 0.2285 | 0.2301 | 0.2317 | 0.2333 | 0.2349 | 0.2365 | 0.2382 | 0.2399 | 0.2416 | 0.2433 | 0.245 | 0.2467 | 0.2484 | 0.2501 | 0.2518 | 0.2535 | 0.2552 | 0.2569 | 0.2586 | 0.2603 | 0.262 | 0.27146 | 0.28092 | 0.29037 | 0.29983 | 0.30929 | 0.31875 | 0.32821 | 0.33767 | 0.34713 | 0.35658 | 0.36604 | 0.3755 | 0.38496 | 0.39442 | 0.40387 | 0.41333 | 0.42279 | 0.43225 | 0.44171 | 0.45117 | 0.46063 | 0.47008 | 0.47954 | 0.489 | 0.49846 | 0.50792 | 0.51737 | 0.52683 | 0.53629 | 0.54575 | 0.55489 | 0.56403 | 0.57317 | 0.58232 | 0.59146 | 0.6006 | 0.60974 | 0.61888 | 0.62803 | 0.63717 | 0.64631 | 0.65545 | 0.66459 | 0.67373 | 0.68288 | 0.69202 | 0.70116 | 0.7103 | 0.71944 | 0.72858 | 0.73772 | 0.74687 | 0.75601 | 0.76515 | 0.77429 | 0.78343 | 0.79258 | 0.80172 | 0.81086 | 0.82 | 0.82888 | 0.83775 | 0.84662 | 0.8555 | 0.86438 | 0.87325 | 0.88213 | 0.891 | 0.89987 | 0.90875 | 0.91763 | 0.9265 | 0.93537 | 0.94425 | 0.95312 | 0.962 | 0.97088 | 0.97975 | 0.98862 | 0.9975 | 1.0064 | 1.0152 | 1.0241 | 1.033 | 1.0419 | 1.0508 | 1.0596 | 1.0685 | 1.0774 | 1.0862 | 1.0893 | 1.0924 | 1.0955 | 1.0985 | 1.1016 | 1.1047 | 1.1078 | 1.1108 | 1.1139 | 1.117 | 1.1201 | 1.1232 | 1.1262 | 1.1293 | 1.1324 | 1.1355 | 1.1385 | 1.1416 | 1.1447 | 1.1478 | 1.1508 | 1.1539 | 1.157 | 1.1601 | 1.1631 | 1.1662 | 1.1693 | 1.1724 | 1.1754 | 1.1785
2.1 | 0 | 0.02725 | 0.0545 | 0.08175 | 0.109 | 0.13625 | 0.1635 | 0.19075 | 0.218 | 0.24525 | 0.2725 | 0.279 | 0.2855 | 0.292 | 0.2985 | 0.305 | 0.3013 | 0.2976 | 0.2939 | 0.2902 | 0.2865 | 0.28035 | 0.2742 | 0.26805 | 0.2619 | 0.25575 | 0.2496 | 0.24345 | 0.2373 | 0.23115 | 0.225 | 0.22687 | 0.22873 | 0.2306 | 0.23247 | 0.23433 | 0.2362 | 0.23807 | 0.23993 | 0.2418 | 0.24367 | 0.24553 | 0.2474 | 0.24927 | 0.25113 | 0.253 | 0.25507 | 0.25713 | 0.2592 | 0.26127 | 0.26333 | 0.2654 | 0.26747 | 0.26953 | 0.2716 | 0.27367 | 0.27573 | 0.2778 | 0.27987 | 0.28193 | 0.284 | 0.29458 | 0.30517 | 0.31575 | 0.32633 | 0.33692 | 0.3475 | 0.35808 | 0.36867 | 0.37925 | 0.38983 | 0.40042 | 0.411 | 0.42158 | 0.43217 | 0.44275 | 0.45333 | 0.46392 | 0.4745 | 0.48508 | 0.49567 | 0.50625 | 0.51683 | 0.52742 | 0.538 | 0.54858 | 0.55917 | 0.56975 | 0.58033 | 0.59092 | 0.6015 | 0.61178 | 0.62207 | 0.63235 | 0.64263 | 0.65292 | 0.6632 | 0.67348 | 0.68377 | 0.69405 | 0.70433 | 0.71462 | 0.7249 | 0.73518 | 0.74547 | 0.75575 | 0.76603 | 0.77632 | 0.7866 | 0.79688 | 0.80717 | 0.81745 | 0.82773 | 0.83802 | 0.8483 | 0.85858 | 0.86887 | 0.87915 | 0.88943 | 0.89972 | 0.91 | 0.91975 | 0.9295 | 0.93925 | 0.949 | 0.95875 | 0.9685 | 0.97825 | 0.988 | 0.99775 | 1.0075 | 1.0172 | 1.027 | 1.0368 | 1.0465 | 1.0562 | 1.066 | 1.0757 | 1.0855 | 1.0953 | 1.105 | 1.1147 | 1.1245 | 1.1342 | 1.144 | 1.1538 | 1.1635 | 1.1732 | 1.183 | 1.1927 | 1.2025 | 1.2063 | 1.2101 | 1.214 | 1.2178 | 1.2216 | 1.2254 | 1.2292 | 1.233 | 1.2369 | 1.2407 | 1.2445 | 1.2483 | 1.2521 | 1.2559 | 1.2597 | 1.2636 | 1.2674 | 1.2712 | 1.275 | 1.2788 | 1.2827 | 1.2865 | 1.2903 | 1.2941 | 1.2979 | 1.3017 | 1.3055 | 1.3094 | 1.3132 | 1.317
2.15 | 0 | 0.028875 | 0.05775 | 0.086625 | 0.1155 | 0.14438 | 0.17325 | 0.20212 | 0.231 | 0.25988 | 0.28875 | 0.2945 | 0.30025 | 0.306 | 0.31175 | 0.3175 | 0.31395 | 0.3104 | 0.30685 | 0.3033 | 0.29975 | 0.29352 | 0.2873 | 0.28108 | 0.27485 | 0.26863 | 0.2624 | 0.25617 | 0.24995 | 0.24372 | 0.2375 | 0.23963 | 0.24177 | 0.2439 | 0.24603 | 0.24817 | 0.2503 | 0.25243 | 0.25457 | 0.2567 | 0.25883 | 0.26097 | 0.2631 | 0.26523 | 0.26737 | 0.2695 | 0.27193 | 0.27437 | 0.2768 | 0.27923 | 0.28167 | 0.2841 | 0.28653 | 0.28897 | 0.2914 | 0.29383 | 0.29627 | 0.2987 | 0.30113 | 0.30357 | 0.306 | 0.31771 | 0.32942 | 0.34113 | 0.35283 | 0.36454 | 0.37625 | 0.38796 | 0.39967 | 0.41137 | 0.42308 | 0.43479 | 0.4465 | 0.45821 | 0.46992 | 0.48163 | 0.49333 | 0.50504 | 0.51675 | 0.52846 | 0.54017 | 0.55188 | 0.56358 | 0.57529 | 0.587 | 0.59871 | 0.61042 | 0.62213 | 0.63383 | 0.64554 | 0.65725 | 0.66868 | 0.6801 | 0.69152 | 0.70295 | 0.71437 | 0.7258 | 0.73723 | 0.74865 | 0.76007 | 0.7715 | 0.78292 | 0.79435 | 0.80578 | 0.8172 | 0.82862 | 0.84005 | 0.85147 | 0.8629 | 0.87433 | 0.88575 | 0.89717 | 0.9086 | 0.92002 | 0.93145 | 0.94288 | 0.9543 | 0.96572 | 0.97715 | 0.98857 | 1 | 1.0106 | 1.0212 | 1.0319 | 1.0425 | 1.0531 | 1.0637 | 1.0744 | 1.085 | 1.0956 | 1.1062 | 1.1169 | 1.1275 | 1.1381 | 1.1487 | 1.1594 | 1.17 | 1.1806 | 1.1912 | 1.2019 | 1.2125 | 1.2231 | 1.2337 | 1.2444 | 1.255 | 1.2656 | 1.2763 | 1.2869 | 1.2975 | 1.3081 | 1.3188 | 1.3233 | 1.3279 | 1.3324 | 1.337 | 1.3415 | 1.3461 | 1.3507 | 1.3552 | 1.3598 | 1.3643 | 1.3689 | 1.3735 | 1.378 | 1.3826 | 1.3871 | 1.3917 | 1.3962 | 1.4008 | 1.4054 | 1.4099 | 1.4145 | 1.419 | 1.4236 | 1.4282 | 1.4327 | 1.4373 | 1.4418 | 1.4464 | 1.4509 | 1.4555
2.2 | 0 | 0.0305 | 0.061 | 0.0915 | 0.122 | 0.1525 | 0.183 | 0.2135 | 0.244 | 0.2745 | 0.305 | 0.31 | 0.315 | 0.32 | 0.325 | 0.33 | 0.3266 | 0.3232 | 0.3198 | 0.3164 | 0.313 | 0.3067 | 0.3004 | 0.2941 | 0.2878 | 0.2815 | 0.2752 | 0.2689 | 0.2626 | 0.2563 | 0.25 | 0.2524 | 0.2548 | 0.2572 | 0.2596 | 0.262 | 0.2644 | 0.2668 | 0.2692 | 0.2716 | 0.274 | 0.2764 | 0.2788 | 0.2812 | 0.2836 | 0.286 | 0.2888 | 0.2916 | 0.2944 | 0.2972 | 0.3 | 0.3028 | 0.3056 | 0.3084 | 0.3112 | 0.314 | 0.3168 | 0.3196 | 0.3224 | 0.3252 | 0.328 | 0.34083 | 0.35367 | 0.3665 | 0.37933 | 0.39217 | 0.405 | 0.41783 | 0.43067 | 0.4435 | 0.45633 | 0.46917 | 0.482 | 0.49483 | 0.50767 | 0.5205 | 0.53333 | 0.54617 | 0.559 | 0.57183 | 0.58467 | 0.5975 | 0.61033 | 0.62317 | 0.636 | 0.64883 | 0.66167 | 0.6745 | 0.68733 | 0.70017 | 0.713 | 0.72557 | 0.73813 | 0.7507 | 0.76327 | 0.77583 | 0.7884 | 0.80097 | 0.81353 | 0.8261 | 0.83867 | 0.85123 | 0.8638 | 0.87637 | 0.88893 | 0.9015 | 0.91407 | 0.92663 | 0.9392 | 0.95177 | 0.96433 | 0.9769 | 0.98947 | 1.002 | 1.0146 | 1.0272 | 1.0397 | 1.0523 | 1.0649 | 1.0774 | 1.09 | 1.1015 | 1.113 | 1.1245 | 1.136 | 1.1475 | 1.159 | 1.1705 | 1.182 | 1.1935 | 1.205 | 1.2165 | 1.228 | 1.2395 | 1.251 | 1.2625 | 1.274 | 1.2855 | 1.297 | 1.3085 | 1.32 | 1.3315 | 1.343 | 1.3545 | 1.366 | 1.3775 | 1.389 | 1.4005 | 1.412 | 1.4235 | 1.435 | 1.4403 | 1.4456 | 1.4509 | 1.4562 | 1.4615 | 1.4668 | 1.4721 | 1.4774 | 1.4827 | 1.488 | 1.4933 | 1.4986 | 1.5039 | 1.5092 | 1.5145 | 1.5198 | 1.5251 | 1.5304 | 1.5357 | 1.541 | 1.5463 | 1.5516 | 1.5569 | 1.5622 | 1.5675 | 1.5728 | 1.5781 | 1.5834 | 1.5887 | 1.594
2.25 | 0 | 0.032125 | 0.06425 | 0.096375 | 0.1285 | 0.16062 | 0.19275 | 0.22487 | 0.257 | 0.28913 | 0.32125 | 0.3255 | 0.32975 | 0.334 | 0.33825 | 0.3425 | 0.33925 | 0.336 | 0.33275 | 0.3295 | 0.32625 | 0.31988 | 0.3135 | 0.30712 | 0.30075 | 0.29437 | 0.288 | 0.28163 | 0.27525 | 0.26887 | 0.2625 | 0.26517 | 0.26783 | 0.2705 | 0.27317 | 0.27583 | 0.2785 | 0.28117 | 0.28383 | 0.2865 | 0.28917 | 0.29183 | 0.2945 | 0.29717 | 0.29983 | 0.3025 | 0.30567 | 0.30883 | 0.312 | 0.31517 | 0.31833 | 0.3215 | 0.32467 | 0.32783 | 0.331 | 0.33417 | 0.33733 | 0.3405 | 0.34367 | 0.34683 | 0.35 | 0.36396 | 0.37792 | 0.39187 | 0.40583 | 0.41979 | 0.43375 | 0.44771 | 0.46167 | 0.47563 | 0.48958 | 0.50354 | 0.5175 | 0.53146 | 0.54542 | 0.55937 | 0.57333 | 0.58729 | 0.60125 | 0.61521 | 0.62917 | 0.64312 | 0.65708 | 0.67104 | 0.685 | 0.69896 | 0.71292 | 0.72688 | 0.74083 | 0.75479 | 0.76875 | 0.78246 | 0.79617 | 0.80988 | 0.82358 | 0.83729 | 0.851 | 0.86471 | 0.87842 | 0.89212 | 0.90583 | 0.91954 | 0.93325 | 0.94696 | 0.96067 | 0.97437 | 0.98808 | 1.0018 | 1.0155 | 1.0292 | 1.0429 | 1.0566 | 1.0703 | 1.084 | 1.0978 | 1.1115 | 1.1252 | 1.1389 | 1.1526 | 1.1663 | 1.18 | 1.1924 | 1.2047 | 1.2171 | 1.2295 | 1.2419 | 1.2543 | 1.2666 | 1.279 | 1.2914 | 1.3037 | 1.3161 | 1.3285 | 1.3409 | 1.3533 | 1.3656 | 1.378 | 1.3904 | 1.4027 | 1.4151 | 1.4275 | 1.4399 | 1.4523 | 1.4646 | 1.477 | 1.4894 | 1.5017 | 1.5141 | 1.5265 | 1.5389 | 1.5513 | 1.5573 | 1.5633 | 1.5694 | 1.5754 | 1.5815 | 1.5875 | 1.5935 | 1.5996 | 1.6056 | 1.6117 | 1.6177 | 1.6238 | 1.6298 | 1.6358 | 1.6419 | 1.6479 | 1.654 | 1.66 | 1.666 | 1.6721 | 1.6781 | 1.6842 | 1.6902 | 1.6963 | 1.7023 | 1.7083 | 1.7144 | 1.7204 | 1.7265 | 1.7325
2.3 | 0 | 0.03375 | 0.0675 | 0.10125 | 0.135 | 0.16875 | 0.2025 | 0.23625 | 0.27 | 0.30375 | 0.3375 | 0.341 | 0.3445 | 0.348 | 0.3515 | 0.355 | 0.3519 | 0.3488 | 0.3457 | 0.3426 | 0.3395 | 0.33305 | 0.3266 | 0.32015 | 0.3137 | 0.30725 | 0.3008 | 0.29435 | 0.2879 | 0.28145 | 0.275 | 0.27793 | 0.28087 | 0.2838 | 0.28673 | 0.28967 | 0.2926 | 0.29553 | 0.29847 | 0.3014 | 0.30433 | 0.30727 | 0.3102 | 0.31313 | 0.31607 | 0.319 | 0.32253 | 0.32607 | 0.3296 | 0.33313 | 0.33667 | 0.3402 | 0.34373 | 0.34727 | 0.3508 | 0.35433 | 0.35787 | 0.3614 | 0.36493 | 0.36847 | 0.372 | 0.38708 | 0.40217 | 0.41725 | 0.43233 | 0.44742 | 0.4625 | 0.47758 | 0.49267 | 0.50775 | 0.52283 | 0.53792 | 0.553 | 0.56808 | 0.58317 | 0.59825 | 0.61333 | 0.62842 | 0.6435 | 0.65858 | 0.67367 | 0.68875 | 0.70383 | 0.71892 | 0.734 | 0.74908 | 0.76417 | 0.77925 | 0.79433 | 0.80942 | 0.8245 | 0.83935 | 0.8542 | 0.86905 | 0.8839 | 0.89875 | 0.9136 | 0.92845 | 0.9433 | 0.95815 | 0.973 | 0.98785 | 1.0027 | 1.0175 | 1.0324 | 1.0473 | 1.0621 | 1.077 | 1.0918 | 1.1066 | 1.1215 | 1.1363 | 1.1512 | 1.1661 | 1.1809 | 1.1958 | 1.2106 | 1.2254 | 1.2403 | 1.2551 | 1.27 | 1.2833 | 1.2965 | 1.3097 | 1.323 | 1.3362 | 1.3495 | 1.3627 | 1.376 | 1.3893 | 1.4025 | 1.4158 | 1.429 | 1.4423 | 1.4555 | 1.4688 | 1.482 | 1.4952 | 1.5085 | 1.5217 | 1.535 | 1.5482 | 1.5615 | 1.5748 | 1.588 | 1.6013 | 1.6145 | 1.6278 | 1.641 | 1.6542 | 1.6675 | 1.6743 | 1.6811 | 1.6879 | 1.6946 | 1.7014 | 1.7082 | 1.715 | 1.7218 | 1.7286 | 1.7353 | 1.7421 | 1.7489 | 1.7557 | 1.7625 | 1.7692 | 1.776 | 1.7828 | 1.7896 | 1.7964 | 1.8032 | 1.8099 | 1.8167 | 1.8235 | 1.8303 | 1.8371 | 1.8439 | 1.8506 | 1.8574 | 1.8642 | 1.871
2.35 | 0 | 0.035375 | 0.07075 | 0.10612 | 0.1415 | 0.17688 | 0.21225 | 0.24763 | 0.283 | 0.31838 | 0.35375 | 0.3565 | 0.35925 | 0.362 | 0.36475 | 0.3675 | 0.36455 | 0.3616 | 0.35865 | 0.3557 | 0.35275 | 0.34623 | 0.3397 | 0.33317 | 0.32665 | 0.32012 | 0.3136 | 0.30707 | 0.30055 | 0.29402 | 0.2875 | 0.2907 | 0.2939 | 0.2971 | 0.3003 | 0.3035 | 0.3067 | 0.3099 | 0.3131 | 0.3163 | 0.3195 | 0.3227 | 0.3259 | 0.3291 | 0.3323 | 0.3355 | 0.3394 | 0.3433 | 0.3472 | 0.3511 | 0.355 | 0.3589 | 0.3628 | 0.3667 | 0.3706 | 0.3745 | 0.3784 | 0.3823 | 0.3862 | 0.3901 | 0.394 | 0.41021 | 0.42642 | 0.44262 | 0.45883 | 0.47504 | 0.49125 | 0.50746 | 0.52367 | 0.53987 | 0.55608 | 0.57229 | 0.5885 | 0.60471 | 0.62092 | 0.63713 | 0.65333 | 0.66954 | 0.68575 | 0.70196 | 0.71817 | 0.73438 | 0.75058 | 0.76679 | 0.783 | 0.79921 | 0.81542 | 0.83162 | 0.84783 | 0.86404 | 0.88025 | 0.89624 | 0.91223 | 0.92822 | 0.94422 | 0.96021 | 0.9762 | 0.99219 | 1.0082 | 1.0242 | 1.0402 | 1.0562 | 1.0721 | 1.0881 | 1.1041 | 1.1201 | 1.1361 | 1.1521 | 1.1681 | 1.1841 | 1.2001 | 1.2161 | 1.2321 | 1.2481 | 1.264 | 1.28 | 1.296 | 1.312 | 1.328 | 1.344 | 1.36 | 1.3741 | 1.3882 | 1.4024 | 1.4165 | 1.4306 | 1.4447 | 1.4589 | 1.473 | 1.4871 | 1.5012 | 1.5154 | 1.5295 | 1.5436 | 1.5577 | 1.5719 | 1.586 | 1.6001 | 1.6142 | 1.6284 | 1.6425 | 1.6566 | 1.6707 | 1.6849 | 1.699 | 1.7131 | 1.7272 | 1.7414 | 1.7555 | 1.7696 | 1.7837 | 1.7913 | 1.7988 | 1.8063 | 1.8138 | 1.8214 | 1.8289 | 1.8364 | 1.8439 | 1.8515 | 1.859 | 1.8665 | 1.874 | 1.8816 | 1.8891 | 1.8966 | 1.9042 | 1.9117 | 1.9192 | 1.9267 | 1.9343 | 1.9418 | 1.9493 | 1.9568 | 1.9644 | 1.9719 | 1.9794 | 1.9869 | 1.9945 | 2.002 | 2.0095
2.4 | 0 | 0.037 | 0.074 | 0.111 | 0.148 | 0.185 | 0.222 | 0.259 | 0.296 | 0.333 | 0.37 | 0.372 | 0.374 | 0.376 | 0.378 | 0.38 | 0.3772 | 0.3744 | 0.3716 | 0.3688 | 0.366 | 0.3594 | 0.3528 | 0.3462 | 0.3396 | 0.333 | 0.3264 | 0.3198 | 0.3132 | 0.3066 | 0.3 | 0.30347 | 0.30693 | 0.3104 | 0.31387 | 0.31733 | 0.3208 | 0.32427 | 0.32773 | 0.3312 | 0.33467 | 0.33813 | 0.3416 | 0.34507 | 0.34853 | 0.352 | 0.35627 | 0.36053 | 0.3648 | 0.36907 | 0.37333 | 0.3776 | 0.38187 | 0.38613 | 0.3904 | 0.39467 | 0.39893 | 0.4032 | 0.40747 | 0.41173 | 0.416 | 0.43333 | 0.45067 | 0.468 | 0.48533 | 0.50267 | 0.52 | 0.53733 | 0.55467 | 0.572 | 0.58933 | 0.60667 | 0.624 | 0.64133 | 0.65867 | 0.676 | 0.69333 | 0.71067 | 0.728 | 0.74533 | 0.76267 | 0.78 | 0.79733 | 0.81467 | 0.832 | 0.84933 | 0.86667 | 0.884 | 0.90133 | 0.91867 | 0.936 | 0.95313 | 0.97027 | 0.9874 | 1.0045 | 1.0217 | 1.0388 | 1.0559 | 1.0731 | 1.0902 | 1.1073 | 1.1245 | 1.1416 | 1.1587 | 1.1759 | 1.193 | 1.2101 | 1.2273 | 1.2444 | 1.2615 | 1.2787 | 1.2958 | 1.3129 | 1.3301 | 1.3472 | 1.3643 | 1.3815 | 1.3986 | 1.4157 | 1.4329 | 1.45 | 1.465 | 1.48 | 1.495 | 1.51 | 1.525 | 1.54 | 1.555 | 1.57 | 1.585 | 1.6 | 1.615 | 1.63 | 1.645 | 1.66 | 1.675 | 1.69 | 1.705 | 1.72 | 1.735 | 1.75 | 1.765 | 1.78 | 1.795 | 1.81 | 1.825 | 1.84 | 1.855 | 1.87 | 1.885 | 1.9 | 1.9083 | 1.9165 | 1.9248 | 1.9331 | 1.9413 | 1.9496 | 1.9579 | 1.9661 | 1.9744 | 1.9827 | 1.9909 | 1.9992 | 2.0075 | 2.0157 | 2.024 | 2.0323 | 2.0405 | 2.0488 | 2.0571 | 2.0653 | 2.0736 | 2.0819 | 2.0901 | 2.0984 | 2.1067 | 2.1149 | 2.1232 | 2.1315 | 2.1397 | 2.148
2.45 | 0 | 0.038625 | 0.07725 | 0.11588 | 0.1545 | 0.19312 | 0.23175 | 0.27037 | 0.309 | 0.34763 | 0.38625 | 0.3875 | 0.38875 | 0.39 | 0.39125 | 0.3925 | 0.38985 | 0.3872 | 0.38455 | 0.3819 | 0.37925 | 0.37257 | 0.3659 | 0.35923 | 0.35255 | 0.34587 | 0.3392 | 0.33253 | 0.32585 | 0.31917 | 0.3125 | 0.31623 | 0.31997 | 0.3237 | 0.32743 | 0.33117 | 0.3349 | 0.33863 | 0.34237 | 0.3461 | 0.34983 | 0.35357 | 0.3573 | 0.36103 | 0.36477 | 0.3685 | 0.37313 | 0.37777 | 0.3824 | 0.38703 | 0.39167 | 0.3963 | 0.40093 | 0.40557 | 0.4102 | 0.41483 | 0.41947 | 0.4241 | 0.42873 | 0.43337 | 0.438 | 0.45646 | 0.47492 | 0.49338 | 0.51183 | 0.53029 | 0.54875 | 0.56721 | 0.58567 | 0.60413 | 0.62258 | 0.64104 | 0.6595 | 0.67796 | 0.69642 | 0.71488 | 0.73333 | 0.75179 | 0.77025 | 0.78871 | 0.80717 | 0.82563 | 0.84408 | 0.86254 | 0.881 | 0.89946 | 0.91792 | 0.93637 | 0.95483 | 0.97329 | 0.99175 | 1.01 | 1.0283 | 1.0466 | 1.0649 | 1.0831 | 1.1014 | 1.1197 | 1.138 | 1.1562 | 1.1745 | 1.1928 | 1.211 | 1.2293 | 1.2476 | 1.2659 | 1.2841 | 1.3024 | 1.3207 | 1.339 | 1.3573 | 1.3755 | 1.3938 | 1.4121 | 1.4304 | 1.4486 | 1.4669 | 1.4852 | 1.5034 | 1.5217 | 1.54 | 1.5559 | 1.5717 | 1.5876 | 1.6035 | 1.6194 | 1.6353 | 1.6511 | 1.667 | 1.6829 | 1.6987 | 1.7146 | 1.7305 | 1.7464 | 1.7623 | 1.7781 | 1.794 | 1.8099 | 1.8257 | 1.8416 | 1.8575 | 1.8734 | 1.8893 | 1.9051 | 1.921 | 1.9369 | 1.9527 | 1.9686 | 1.9845 | 2.0004 | 2.0162 | 2.0253 | 2.0343 | 2.0433 | 2.0523 | 2.0613 | 2.0703 | 2.0793 | 2.0883 | 2.0973 | 2.1063 | 2.1153 | 2.1244 | 2.1334 | 2.1424 | 2.1514 | 2.1604 | 2.1694 | 2.1784 | 2.1874 | 2.1964 | 2.2054 | 2.2144 | 2.2234 | 2.2325 | 2.2415 | 2.2505 | 2.2595 | 2.2685 | 2.2775 | 2.2865
2.5 | 0 | 0.04025 | 0.0805 | 0.12075 | 0.161 | 0.20125 | 0.2415 | 0.28175 | 0.322 | 0.36225 | 0.4025 | 0.403 | 0.4035 | 0.404 | 0.4045 | 0.405 | 0.4025 | 0.4 | 0.3975 | 0.395 | 0.3925 | 0.38575 | 0.379 | 0.37225 | 0.3655 | 0.35875 | 0.352 | 0.34525 | 0.3385 | 0.33175 | 0.325 | 0.329 | 0.333 | 0.337 | 0.341 | 0.345 | 0.349 | 0.353 | 0.357 | 0.361 | 0.365 | 0.369 | 0.373 | 0.377 | 0.381 | 0.385 | 0.39 | 0.395 | 0.4 | 0.405 | 0.41 | 0.415 | 0.42 | 0.425 | 0.43 | 0.435 | 0.44 | 0.445 | 0.45 | 0.455 | 0.46 | 0.47958 | 0.49917 | 0.51875 | 0.53833 | 0.55792 | 0.5775 | 0.59708 | 0.61667 | 0.63625 | 0.65583 | 0.67542 | 0.695 | 0.71458 | 0.73417 | 0.75375 | 0.77333 | 0.79292 | 0.8125 | 0.83208 | 0.85167 | 0.87125 | 0.89083 | 0.91042 | 0.93 | 0.94958 | 0.96917 | 0.98875 | 1.0083 | 1.0279 | 1.0475 | 1.0669 | 1.0863 | 1.1058 | 1.1252 | 1.1446 | 1.164 | 1.1834 | 1.2028 | 1.2223 | 1.2417 | 1.2611 | 1.2805 | 1.2999 | 1.3193 | 1.3388 | 1.3582 | 1.3776 | 1.397 | 1.4164 | 1.4358 | 1.4552 | 1.4747 | 1.4941 | 1.5135 | 1.5329 | 1.5523 | 1.5717 | 1.5912 | 1.6106 | 1.63 | 1.6467 | 1.6635 | 1.6803 | 1.697 | 1.7138 | 1.7305 | 1.7472 | 1.764 | 1.7808 | 1.7975 | 1.8142 | 1.831 | 1.8478 | 1.8645 | 1.8813 | 1.898 | 1.9147 | 1.9315 | 1.9483 | 1.965 | 1.9817 | 1.9985 | 2.0152 | 2.032 | 2.0488 | 2.0655 | 2.0823 | 2.099 | 2.1157 | 2.1325 | 2.1423 | 2.152 | 2.1618 | 2.1715 | 2.1812 | 2.191 | 2.2008 | 2.2105 | 2.2203 | 2.23 | 2.2397 | 2.2495 | 2.2593 | 2.269 | 2.2788 | 2.2885 | 2.2982 | 2.308 | 2.3178 | 2.3275 | 2.3373 | 2.347 | 2.3567 | 2.3665 | 2.3763 | 2.386 | 2.3958 | 2.4055 | 2.4152 | 2.425
2.55 | 0 | 0.041875 | 0.08375 | 0.12562 | 0.1675 | 0.20938 | 0.25125 | 0.29313 | 0.335 | 0.37688 | 0.41875 | 0.4185 | 0.41825 | 0.418 | 0.41775 | 0.4175 | 0.41515 | 0.4128 | 0.41045 | 0.4081 | 0.40575 | 0.39892 | 0.3921 | 0.38527 | 0.37845 | 0.37162 | 0.3648 | 0.35797 | 0.35115 | 0.34432 | 0.3375 | 0.34177 | 0.34603 | 0.3503 | 0.35457 | 0.35883 | 0.3631 | 0.36737 | 0.37163 | 0.3759 | 0.38017 | 0.38443 | 0.3887 | 0.39297 | 0.39723 | 0.4015 | 0.40687 | 0.41223 | 0.4176 | 0.42297 | 0.42833 | 0.4337 | 0.43907 | 0.44443 | 0.4498 | 0.45517 | 0.46053 | 0.4659 | 0.47127 | 0.47663 | 0.482 | 0.50271 | 0.52342 | 0.54412 | 0.56483 | 0.58554 | 0.60625 | 0.62696 | 0.64767 | 0.66838 | 0.68908 | 0.70979 | 0.7305 | 0.75121 | 0.77192 | 0.79263 | 0.81333 | 0.83404 | 0.85475 | 0.87546 | 0.89617 | 0.91687 | 0.93758 | 0.95829 | 0.979 | 0.99971 | 1.0204 | 1.0411 | 1.0618 | 1.0825 | 1.1033 | 1.1238 | 1.1444 | 1.1649 | 1.1855 | 1.206 | 1.2266 | 1.2472 | 1.2677 | 1.2883 | 1.3088 | 1.3294 | 1.3499 | 1.3705 | 1.3911 | 1.4116 | 1.4322 | 1.4527 | 1.4733 | 1.4939 | 1.5144 | 1.535 | 1.5555 | 1.5761 | 1.5966 | 1.6172 | 1.6378 | 1.6583 | 1.6789 | 1.6994 | 1.72 | 1.7376 | 1.7552 | 1.7729 | 1.7905 | 1.8081 | 1.8257 | 1.8434 | 1.861 | 1.8786 | 1.8962 | 1.9139 | 1.9315 | 1.9491 | 1.9667 | 1.9844 | 2.002 | 2.0196 | 2.0372 | 2.0549 | 2.0725 | 2.0901 | 2.1077 | 2.1254 | 2.143 | 2.1606 | 2.1782 | 2.1959 | 2.2135 | 2.2311 | 2.2487 | 2.2592 | 2.2697 | 2.2802 | 2.2907 | 2.3012 | 2.3117 | 2.3222 | 2.3327 | 2.3432 | 2.3537 | 2.3642 | 2.3746 | 2.3851 | 2.3956 | 2.4061 | 2.4166 | 2.4271 | 2.4376 | 2.4481 | 2.4586 | 2.4691 | 2.4796 | 2.4901 | 2.5006 | 2.511 | 2.5215 | 2.532 | 2.5425 | 2.553 | 2.5635
2.6 | 0 | 0.0435 | 0.087 | 0.1305 | 0.174 | 0.2175 | 0.261 | 0.3045 | 0.348 | 0.3915 | 0.435 | 0.434 | 0.433 | 0.432 | 0.431 | 0.43 | 0.4278 | 0.4256 | 0.4234 | 0.4212 | 0.419 | 0.4121 | 0.4052 | 0.3983 | 0.3914 | 0.3845 | 0.3776 | 0.3707 | 0.3638 | 0.3569 | 0.35 | 0.35453 | 0.35907 | 0.3636 | 0.36813 | 0.37267 | 0.3772 | 0.38173 | 0.38627 | 0.3908 | 0.39533 | 0.39987 | 0.4044 | 0.40893 | 0.41347 | 0.418 | 0.42373 | 0.42947 | 0.4352 | 0.44093 | 0.44667 | 0.4524 | 0.45813 | 0.46387 | 0.4696 | 0.47533 | 0.48107 | 0.4868 | 0.49253 | 0.49827 | 0.504 | 0.52583 | 0.54767 | 0.5695 | 0.59133 | 0.61317 | 0.635 | 0.65683 | 0.67867 | 0.7005 | 0.72233 | 0.74417 | 0.766 | 0.78783 | 0.80967 | 0.8315 | 0.85333 | 0.87517 | 0.897 | 0.91883 | 0.94067 | 0.9625 | 0.98433 | 1.0062 | 1.028 | 1.0498 | 1.0717 | 1.0935 | 1.1153 | 1.1372 | 1.159 | 1.1807 | 1.2024 | 1.2241 | 1.2458 | 1.2675 | 1.2892 | 1.3109 | 1.3326 | 1.3543 | 1.376 | 1.3977 | 1.4194 | 1.4411 | 1.4628 | 1.4845 | 1.5062 | 1.5279 | 1.5496 | 1.5713 | 1.593 | 1.6147 | 1.6364 | 1.6581 | 1.6798 | 1.7015 | 1.7232 | 1.7449 | 1.7666 | 1.7883 | 1.81 | 1.8285 | 1.847 | 1.8655 | 1.884 | 1.9025 | 1.921 | 1.9395 | 1.958 | 1.9765 | 1.995 | 2.0135 | 2.032 | 2.0505 | 2.069 | 2.0875 | 2.106 | 2.1245 | 2.143 | 2.1615 | 2.18 | 2.1985 | 2.217 | 2.2355 | 2.254 | 2.2725 | 2.291 | 2.3095 | 2.328 | 2.3465 | 2.365 | 2.3762 | 2.3875 | 2.3987 | 2.4099 | 2.4212 | 2.4324 | 2.4436 | 2.4549 | 2.4661 | 2.4773 | 2.4886 | 2.4998 | 2.511 | 2.5223 | 2.5335 | 2.5447 | 2.556 | 2.5672 | 2.5784 | 2.5897 | 2.6009 | 2.6121 | 2.6234 | 2.6346 | 2.6458 | 2.6571 | 2.6683 | 2.6795 | 2.6908 | 2.702
2.65 | 0 | 0.045125 | 0.09025 | 0.13537 | 0.1805 | 0.22562 | 0.27075 | 0.31588 | 0.361 | 0.40613 | 0.45125 | 0.4495 | 0.44775 | 0.446 | 0.44425 | 0.4425 | 0.44045 | 0.4384 | 0.43635 | 0.4343 | 0.43225 | 0.42528 | 0.4183 | 0.41132 | 0.40435 | 0.39737 | 0.3904 | 0.38343 | 0.37645 | 0.36947 | 0.3625 | 0.3673 | 0.3721 | 0.3769 | 0.3817 | 0.3865 | 0.3913 | 0.3961 | 0.4009 | 0.4057 | 0.4105 | 0.4153 | 0.4201 | 0.4249 | 0.4297 | 0.4345 | 0.4406 | 0.4467 | 0.4528 | 0.4589 | 0.465 | 0.4711 | 0.4772 | 0.4833 | 0.4894 | 0.4955 | 0.5016 | 0.5077 | 0.5138 | 0.5199 | 0.526 | 0.54896 | 0.57192 | 0.59488 | 0.61783 | 0.64079 | 0.66375 | 0.68671 | 0.70967 | 0.73262 | 0.75558 | 0.77854 | 0.8015 | 0.82446 | 0.84742 | 0.87038 | 0.89333 | 0.91629 | 0.93925 | 0.96221 | 0.98517 | 1.0081 | 1.0311 | 1.054 | 1.077 | 1.1 | 1.1229 | 1.1459 | 1.1688 | 1.1918 | 1.2147 | 1.2376 | 1.2604 | 1.2833 | 1.3061 | 1.329 | 1.3518 | 1.3746 | 1.3975 | 1.4203 | 1.4432 | 1.466 | 1.4889 | 1.5117 | 1.5345 | 1.5574 | 1.5802 | 1.6031 | 1.6259 | 1.6487 | 1.6716 | 1.6944 | 1.7173 | 1.7401 | 1.763 | 1.7858 | 1.8086 | 1.8315 | 1.8543 | 1.8772 | 1.9 | 1.9194 | 1.9387 | 1.9581 | 1.9775 | 1.9969 | 2.0162 | 2.0356 | 2.055 | 2.0744 | 2.0938 | 2.1131 | 2.1325 | 2.1519 | 2.1713 | 2.1906 | 2.21 | 2.2294 | 2.2487 | 2.2681 | 2.2875 | 2.3069 | 2.3262 | 2.3456 | 2.365 | 2.3844 | 2.4038 | 2.4231 | 2.4425 | 2.4619 | 2.4813 | 2.4932 | 2.5052 | 2.5172 | 2.5292 | 2.5411 | 2.5531 | 2.5651 | 2.577 | 2.589 | 2.601 | 2.613 | 2.625 | 2.6369 | 2.6489 | 2.6609 | 2.6728 | 2.6848 | 2.6968 | 2.7088 | 2.7207 | 2.7327 | 2.7447 | 2.7567 | 2.7687 | 2.7806 | 2.7926 | 2.8046 | 2.8165 | 2.8285 | 2.8405
2.7 | 0 | 0.04675 | 0.0935 | 0.14025 | 0.187 | 0.23375 | 0.2805 | 0.32725 | 0.374 | 0.42075 | 0.4675 | 0.465 | 0.4625 | 0.46 | 0.4575 | 0.455 | 0.4531 | 0.4512 | 0.4493 | 0.4474 | 0.4455 | 0.43845 | 0.4314 | 0.42435 | 0.4173 | 0.41025 | 0.4032 | 0.39615 | 0.3891 | 0.38205 | 0.375 | 0.38007 | 0.38513 | 0.3902 | 0.39527 | 0.40033 | 0.4054 | 0.41047 | 0.41553 | 0.4206 | 0.42567 | 0.43073 | 0.4358 | 0.44087 | 0.44593 | 0.451 | 0.45747 | 0.46393 | 0.4704 | 0.47687 | 0.48333 | 0.4898 | 0.49627 | 0.50273 | 0.5092 | 0.51567 | 0.52213 | 0.5286 | 0.53507 | 0.54153 | 0.548 | 0.57208 | 0.59617 | 0.62025 | 0.64433 | 0.66842 | 0.6925 | 0.71658 | 0.74067 | 0.76475 | 0.78883 | 0.81292 | 0.837 | 0.86108 | 0.88517 | 0.90925 | 0.93333 | 0.95742 | 0.9815 | 1.0056 | 1.0297 | 1.0537 | 1.0778 | 1.1019 | 1.126 | 1.1501 | 1.1742 | 1.1983 | 1.2223 | 1.2464 | 1.2705 | 1.2945 | 1.3185 | 1.3424 | 1.3664 | 1.3904 | 1.4144 | 1.4384 | 1.4624 | 1.4864 | 1.5103 | 1.5343 | 1.5583 | 1.5823 | 1.6063 | 1.6302 | 1.6542 | 1.6782 | 1.7022 | 1.7262 | 1.7502 | 1.7741 | 1.7981 | 1.8221 | 1.8461 | 1.8701 | 1.8941 | 1.9181 | 1.942 | 1.966 | 1.99 | 2.0103 | 2.0305 | 2.0507 | 2.071 | 2.0913 | 2.1115 | 2.1317 | 2.152 | 2.1723 | 2.1925 | 2.2128 | 2.233 | 2.2532 | 2.2735 | 2.2938 | 2.314 | 2.3342 | 2.3545 | 2.3748 | 2.395 | 2.4152 | 2.4355 | 2.4558 | 2.476 | 2.4962 | 2.5165 | 2.5368 | 2.557 | 2.5772 | 2.5975 | 2.6102 | 2.6229 | 2.6357 | 2.6484 | 2.6611 | 2.6738 | 2.6865 | 2.6992 | 2.7119 | 2.7247 | 2.7374 | 2.7501 | 2.7628 | 2.7755 | 2.7883 | 2.801 | 2.8137 | 2.8264 | 2.8391 | 2.8518 | 2.8645 | 2.8773 | 2.89 | 2.9027 | 2.9154 | 2.9281 | 2.9409 | 2.9536 | 2.9663 | 2.979
2.75 | 0 | 0.048375 | 0.09675 | 0.14513 | 0.1935 | 0.24188 | 0.29025 | 0.33863 | 0.387 | 0.43538 | 0.48375 | 0.4805 | 0.47725 | 0.474 | 0.47075 | 0.4675 | 0.46575 | 0.464 | 0.46225 | 0.4605 | 0.45875 | 0.45162 | 0.4445 | 0.43738 | 0.43025 | 0.42312 | 0.416 | 0.40887 | 0.40175 | 0.39463 | 0.3875 | 0.39283 | 0.39817 | 0.4035 | 0.40883 | 0.41417 | 0.4195 | 0.42483 | 0.43017 | 0.4355 | 0.44083 | 0.44617 | 0.4515 | 0.45683 | 0.46217 | 0.4675 | 0.47433 | 0.48117 | 0.488 | 0.49483 | 0.50167 | 0.5085 | 0.51533 | 0.52217 | 0.529 | 0.53583 | 0.54267 | 0.5495 | 0.55633 | 0.56317 | 0.57 | 0.59521 | 0.62042 | 0.64563 | 0.67083 | 0.69604 | 0.72125 | 0.74646 | 0.77167 | 0.79688 | 0.82208 | 0.84729 | 0.8725 | 0.89771 | 0.92292 | 0.94812 | 0.97333 | 0.99854 | 1.0237 | 1.049 | 1.0742 | 1.0994 | 1.1246 | 1.1498 | 1.175 | 1.2002 | 1.2254 | 1.2506 | 1.2758 | 1.301 | 1.3262 | 1.3514 | 1.3765 | 1.4016 | 1.4267 | 1.4519 | 1.477 | 1.5021 | 1.5272 | 1.5524 | 1.5775 | 1.6026 | 1.6278 | 1.6529 | 1.678 | 1.7031 | 1.7283 | 1.7534 | 1.7785 | 1.8036 | 1.8288 | 1.8539 | 1.879 | 1.9041 | 1.9292 | 1.9544 | 1.9795 | 2.0046 | 2.0297 | 2.0549 | 2.08 | 2.1011 | 2.1223 | 2.1434 | 2.1645 | 2.1856 | 2.2067 | 2.2279 | 2.249 | 2.2701 | 2.2912 | 2.3124 | 2.3335 | 2.3546 | 2.3758 | 2.3969 | 2.418 | 2.4391 | 2.4602 | 2.4814 | 2.5025 | 2.5236 | 2.5448 | 2.5659 | 2.587 | 2.6081 | 2.6292 | 2.6504 | 2.6715 | 2.6926 | 2.7138 | 2.7272 | 2.7407 | 2.7541 | 2.7676 | 2.781 | 2.7945 | 2.808 | 2.8214 | 2.8349 | 2.8483 | 2.8618 | 2.8752 | 2.8887 | 2.9022 | 2.9156 | 2.9291 | 2.9425 | 2.956 | 2.9695 | 2.9829 | 2.9964 | 3.0098 | 3.0233 | 3.0368 | 3.0502 | 3.0637 | 3.0771 | 3.0906 | 3.104 | 3.1175
2.8 | 0 | 0.05 | 0.1 | 0.15 | 0.2 | 0.25 | 0.3 | 0.35 | 0.4 | 0.45 | 0.5 | 0.496 | 0.492 | 0.488 | 0.484 | 0.48 | 0.4784 | 0.4768 | 0.4752 | 0.4736 | 0.472 | 0.4648 | 0.4576 | 0.4504 | 0.4432 | 0.436 | 0.4288 | 0.4216 | 0.4144 | 0.4072 | 0.4 | 0.4056 | 0.4112 | 0.4168 | 0.4224 | 0.428 | 0.4336 | 0.4392 | 0.4448 | 0.4504 | 0.456 | 0.4616 | 0.4672 | 0.4728 | 0.4784 | 0.484 | 0.4912 | 0.4984 | 0.5056 | 0.5128 | 0.52 | 0.5272 | 0.5344 | 0.5416 | 0.5488 | 0.556 | 0.5632 | 0.5704 | 0.5776 | 0.5848 | 0.592 | 0.61833 | 0.64467 | 0.671 | 0.69733 | 0.72367 | 0.75 | 0.77633 | 0.80267 | 0.829 | 0.85533 | 0.88167 | 0.908 | 0.93433 | 0.96067 | 0.987 | 1.0133 | 1.0397 | 1.066 | 1.0923 | 1.1187 | 1.145 | 1.1713 | 1.1977 | 1.224 | 1.2503 | 1.2767 | 1.303 | 1.3293 | 1.3557 | 1.382 | 1.4083 | 1.4345 | 1.4608 | 1.4871 | 1.5133 | 1.5396 | 1.5659 | 1.5921 | 1.6184 | 1.6447 | 1.6709 | 1.6972 | 1.7235 | 1.7497 | 1.776 | 1.8023 | 1.8285 | 1.8548 | 1.8811 | 1.9073 | 1.9336 | 1.9599 | 1.9861 | 2.0124 | 2.0387 | 2.0649 | 2.0912 | 2.1175 | 2.1437 | 2.17 | 2.192 | 2.214 | 2.236 | 2.258 | 2.28 | 2.302 | 2.324 | 2.346 | 2.368 | 2.39 | 2.412 | 2.434 | 2.456 | 2.478 | 2.5 | 2.522 | 2.544 | 2.566 | 2.588 | 2.61 | 2.632 | 2.654 | 2.676 | 2.698 | 2.72 | 2.742 | 2.764 | 2.786 | 2.808 | 2.83 | 2.8442 | 2.8584 | 2.8726 | 2.8868 | 2.901 | 2.9152 | 2.9294 | 2.9436 | 2.9578 | 2.972 | 2.9862 | 3.0004 | 3.0146 | 3.0288 | 3.043 | 3.0572 | 3.0714 | 3.0856 | 3.0998 | 3.114 | 3.1282 | 3.1424 | 3.1566 | 3.1708 | 3.185 | 3.1992 | 3.2134 | 3.2276 | 3.2418 | 3.256
2.85 | 0 | 0.051625 | 0.10325 | 0.15488 | 0.2065 | 0.25812 | 0.30975 | 0.36138 | 0.413 | 0.46463 | 0.51625 | 0.5115 | 0.50675 | 0.502 | 0.49725 | 0.4925 | 0.49105 | 0.4896 | 0.48815 | 0.4867 | 0.48525 | 0.47797 | 0.4707 | 0.46342 | 0.45615 | 0.44888 | 0.4416 | 0.43433 | 0.42705 | 0.41978 | 0.4125 | 0.41837 | 0.42423 | 0.4301 | 0.43597 | 0.44183 | 0.4477 | 0.45357 | 0.45943 | 0.4653 | 0.47117 | 0.47703 | 0.4829 | 0.48877 | 0.49463 | 0.5005 | 0.50807 | 0.51563 | 0.5232 | 0.53077 | 0.53833 | 0.5459 | 0.55347 | 0.56103 | 0.5686 | 0.57617 | 0.58373 | 0.5913 | 0.59887 | 0.60643 | 0.614 | 0.64146 | 0.66892 | 0.69637 | 0.72383 | 0.75129 | 0.77875 | 0.80621 | 0.83367 | 0.86113 | 0.88858 | 0.91604 | 0.9435 | 0.97096 | 0.99842 | 1.0259 | 1.0533 | 1.0808 | 1.1082 | 1.1357 | 1.1632 | 1.1906 | 1.2181 | 1.2455 | 1.273 | 1.3005 | 1.3279 | 1.3554 | 1.3828 | 1.4103 | 1.4378 | 1.4652 | 1.4926 | 1.52 | 1.5474 | 1.5748 | 1.6022 | 1.6296 | 1.657 | 1.6844 | 1.7118 | 1.7392 | 1.7667 | 1.7941 | 1.8215 | 1.8489 | 1.8763 | 1.9037 | 1.9311 | 1.9585 | 1.9859 | 2.0133 | 2.0407 | 2.0681 | 2.0955 | 2.123 | 2.1504 | 2.1778 | 2.2052 | 2.2326 | 2.26 | 2.2829 | 2.3058 | 2.3286 | 2.3515 | 2.3744 | 2.3973 | 2.4201 | 2.443 | 2.4659 | 2.4888 | 2.5116 | 2.5345 | 2.5574 | 2.5802 | 2.6031 | 2.626 | 2.6489 | 2.6717 | 2.6946 | 2.7175 | 2.7404 | 2.7633 | 2.7861 | 2.809 | 2.8319 | 2.8548 | 2.8776 | 2.9005 | 2.9234 | 2.9463 | 2.9612 | 2.9761 | 2.9911 | 3.006 | 3.021 | 3.0359 | 3.0508 | 3.0658 | 3.0807 | 3.0957 | 3.1106 | 3.1256 | 3.1405 | 3.1554 | 3.1704 | 3.1853 | 3.2003 | 3.2152 | 3.2301 | 3.2451 | 3.26 | 3.275 | 3.2899 | 3.3049 | 3.3198 | 3.3347 | 3.3497 | 3.3646 | 3.3796 | 3.3945
2.9 | 0 | 0.05325 | 0.1065 | 0.15975 | 0.213 | 0.26625 | 0.3195 | 0.37275 | 0.426 | 0.47925 | 0.5325 | 0.527 | 0.5215 | 0.516 | 0.5105 | 0.505 | 0.5037 | 0.5024 | 0.5011 | 0.4998 | 0.4985 | 0.49115 | 0.4838 | 0.47645 | 0.4691 | 0.46175 | 0.4544 | 0.44705 | 0.4397 | 0.43235 | 0.425 | 0.43113 | 0.43727 | 0.4434 | 0.44953 | 0.45567 | 0.4618 | 0.46793 | 0.47407 | 0.4802 | 0.48633 | 0.49247 | 0.4986 | 0.50473 | 0.51087 | 0.517 | 0.52493 | 0.53287 | 0.5408 | 0.54873 | 0.55667 | 0.5646 | 0.57253 | 0.58047 | 0.5884 | 0.59633 | 0.60427 | 0.6122 | 0.62013 | 0.62807 | 0.636 | 0.66458 | 0.69317 | 0.72175 | 0.75033 | 0.77892 | 0.8075 | 0.83608 | 0.86467 | 0.89325 | 0.92183 | 0.95042 | 0.979 | 1.0076 | 1.0362 | 1.0648 | 1.0933 | 1.1219 | 1.1505 | 1.1791 | 1.2077 | 1.2363 | 1.2648 | 1.2934 | 1.322 | 1.3506 | 1.3792 | 1.4078 | 1.4363 | 1.4649 | 1.4935 | 1.522 | 1.5506 | 1.5792 | 1.6077 | 1.6362 | 1.6648 | 1.6933 | 1.7219 | 1.7505 | 1.779 | 1.8075 | 1.8361 | 1.8646 | 1.8932 | 1.9218 | 1.9503 | 1.9788 | 2.0074 | 2.036 | 2.0645 | 2.093 | 2.1216 | 2.1502 | 2.1787 | 2.2073 | 2.2358 | 2.2643 | 2.2929 | 2.3215 | 2.35 | 2.3737 | 2.3975 | 2.4213 | 2.445 | 2.4688 | 2.4925 | 2.5162 | 2.54 | 2.5638 | 2.5875 | 2.6113 | 2.635 | 2.6587 | 2.6825 | 2.7062 | 2.73 | 2.7538 | 2.7775 | 2.8013 | 2.825 | 2.8487 | 2.8725 | 2.8963 | 2.92 | 2.9438 | 2.9675 | 2.9912 | 3.015 | 3.0387 | 3.0625 | 3.0782 | 3.0939 | 3.1096 | 3.1252 | 3.1409 | 3.1566 | 3.1723 | 3.188 | 3.2037 | 3.2193 | 3.235 | 3.2507 | 3.2664 | 3.2821 | 3.2978 | 3.3134 | 3.3291 | 3.3448 | 3.3605 | 3.3762 | 3.3918 | 3.4075 | 3.4232 | 3.4389 | 3.4546 | 3.4703 | 3.4859 | 3.5016 | 3.5173 | 3.533
2.95 | 0 | 0.054875 | 0.10975 | 0.16462 | 0.2195 | 0.27437 | 0.32925 | 0.38412 | 0.439 | 0.49388 | 0.54875 | 0.5425 | 0.53625 | 0.53 | 0.52375 | 0.5175 | 0.51635 | 0.5152 | 0.51405 | 0.5129 | 0.51175 | 0.50433 | 0.4969 | 0.48947 | 0.48205 | 0.47463 | 0.4672 | 0.45977 | 0.45235 | 0.44493 | 0.4375 | 0.4439 | 0.4503 | 0.4567 | 0.4631 | 0.4695 | 0.4759 | 0.4823 | 0.4887 | 0.4951 | 0.5015 | 0.5079 | 0.5143 | 0.5207 | 0.5271 | 0.5335 | 0.5418 | 0.5501 | 0.5584 | 0.5667 | 0.575 | 0.5833 | 0.5916 | 0.5999 | 0.6082 | 0.6165 | 0.6248 | 0.6331 | 0.6414 | 0.6497 | 0.658 | 0.68771 | 0.71742 | 0.74713 | 0.77683 | 0.80654 | 0.83625 | 0.86596 | 0.89567 | 0.92537 | 0.95508 | 0.98479 | 1.0145 | 1.0442 | 1.0739 | 1.1036 | 1.1333 | 1.163 | 1.1927 | 1.2225 | 1.2522 | 1.2819 | 1.3116 | 1.3413 | 1.371 | 1.4007 | 1.4304 | 1.4601 | 1.4898 | 1.5195 | 1.5493 | 1.5789 | 1.6086 | 1.6383 | 1.668 | 1.6977 | 1.7274 | 1.7571 | 1.7868 | 1.8165 | 1.8462 | 1.8759 | 1.9056 | 1.9352 | 1.9649 | 1.9946 | 2.0243 | 2.054 | 2.0837 | 2.1134 | 2.1431 | 2.1728 | 2.2025 | 2.2322 | 2.2618 | 2.2915 | 2.3212 | 2.3509 | 2.3806 | 2.4103 | 2.44 | 2.4646 | 2.4893 | 2.5139 | 2.5385 | 2.5631 | 2.5878 | 2.6124 | 2.637 | 2.6616 | 2.6862 | 2.7109 | 2.7355 | 2.7601 | 2.7847 | 2.8094 | 2.834 | 2.8586 | 2.8832 | 2.9079 | 2.9325 | 2.9571 | 2.9817 | 3.0064 | 3.031 | 3.0556 | 3.0802 | 3.1049 | 3.1295 | 3.1541 | 3.1787 | 3.1952 | 3.2116 | 3.228 | 3.2445 | 3.2609 | 3.2773 | 3.2937 | 3.3102 | 3.3266 | 3.343 | 3.3594 | 3.3758 | 3.3923 | 3.4087 | 3.4251 | 3.4415 | 3.458 | 3.4744 | 3.4908 | 3.5072 | 3.5237 | 3.5401 | 3.5565 | 3.573 | 3.5894 | 3.6058 | 3.6222 | 3.6387 | 3.6551 | 3.6715
3 | 0 | 0.0565 | 0.113 | 0.1695 | 0.226 | 0.2825 | 0.339 | 0.3955 | 0.452 | 0.5085 | 0.565 | 0.558 | 0.551 | 0.544 | 0.537 | 0.53 | 0.529 | 0.528 | 0.527 | 0.526 | 0.525 | 0.5175 | 0.51 | 0.5025 | 0.495 | 0.4875 | 0.48 | 0.4725 | 0.465 | 0.4575 | 0.45 | 0.45667 | 0.46333 | 0.47 | 0.47667 | 0.48333 | 0.49 | 0.49667 | 0.50333 | 0.51 | 0.51667 | 0.52333 | 0.53 | 0.53667 | 0.54333 | 0.55 | 0.55867 | 0.56733 | 0.576 | 0.58467 | 0.59333 | 0.602 | 0.61067 | 0.61933 | 0.628 | 0.63667 | 0.64533 | 0.654 | 0.66267 | 0.67133 | 0.68 | 0.71083 | 0.74167 | 0.7725 | 0.80333 | 0.83417 | 0.865 | 0.89583 | 0.92667 | 0.9575 | 0.98833 | 1.0192 | 1.05 | 1.0808 | 1.1117 | 1.1425 | 1.1733 | 1.2042 | 1.235 | 1.2658 | 1.2967 | 1.3275 | 1.3583 | 1.3892 | 1.42 | 1.4508 | 1.4817 | 1.5125 | 1.5433 | 1.5742 | 1.605 | 1.6358 | 1.6667 | 1.6975 | 1.7283 | 1.7592 | 1.79 | 1.8208 | 1.8517 | 1.8825 | 1.9133 | 1.9442 | 1.975 | 2.0058 | 2.0367 | 2.0675 | 2.0983 | 2.1292 | 2.16 | 2.1908 | 2.2217 | 2.2525 | 2.2833 | 2.3142 | 2.345 | 2.3758 | 2.4067 | 2.4375 | 2.4683 | 2.4992 | 2.53 | 2.5555 | 2.581 | 2.6065 | 2.632 | 2.6575 | 2.683 | 2.7085 | 2.734 | 2.7595 | 2.785 | 2.8105 | 2.836 | 2.8615 | 2.887 | 2.9125 | 2.938 | 2.9635 | 2.989 | 3.0145 | 3.04 | 3.0655 | 3.091 | 3.1165 | 3.142 | 3.1675 | 3.193 | 3.2185 | 3.244 | 3.2695 | 3.295 | 3.3122 | 3.3293 | 3.3465 | 3.3637 | 3.3808 | 3.398 | 3.4152 | 3.4323 | 3.4495 | 3.4667 | 3.4838 | 3.501 | 3.5182 | 3.5353 | 3.5525 | 3.5697 | 3.5868 | 3.604 | 3.6212 | 3.6383 | 3.6555 | 3.6727 | 3.6898 | 3.707 | 3.7242 | 3.7413 | 3.7585 | 3.7757 | 3.7928 | 3.81
3.05 | 0 | 0.058125 | 0.11625 | 0.17438 | 0.2325 | 0.29063 | 0.34875 | 0.40687 | 0.465 | 0.52312 | 0.58125 | 0.5735 | 0.56575 | 0.558 | 0.55025 | 0.5425 | 0.54165 | 0.5408 | 0.53995 | 0.5391 | 0.53825 | 0.53068 | 0.5231 | 0.51553 | 0.50795 | 0.50038 | 0.4928 | 0.48523 | 0.47765 | 0.47008 | 0.4625 | 0.46943 | 0.47637 | 0.4833 | 0.49023 | 0.49717 | 0.5041 | 0.51103 | 0.51797 | 0.5249 | 0.53183 | 0.53877 | 0.5457 | 0.55263 | 0.55957 | 0.5665 | 0.57553 | 0.58457 | 0.5936 | 0.60263 | 0.61167 | 0.6207 | 0.62973 | 0.63877 | 0.6478 | 0.65683 | 0.66587 | 0.6749 | 0.68393 | 0.69297 | 0.702 | 0.73396 | 0.76592 | 0.79788 | 0.82983 | 0.86179 | 0.89375 | 0.92571 | 0.95767 | 0.98962 | 1.0216 | 1.0535 | 1.0855 | 1.1175 | 1.1494 | 1.1814 | 1.2133 | 1.2453 | 1.2772 | 1.3092 | 1.3412 | 1.3731 | 1.4051 | 1.437 | 1.469 | 1.501 | 1.5329 | 1.5649 | 1.5968 | 1.6288 | 1.6607 | 1.6927 | 1.7247 | 1.7567 | 1.7887 | 1.8206 | 1.8526 | 1.8846 | 1.9165 | 1.9485 | 1.9805 | 2.0125 | 2.0444 | 2.0764 | 2.1084 | 2.1404 | 2.1723 | 2.2043 | 2.2363 | 2.2683 | 2.3003 | 2.3322 | 2.3642 | 2.3962 | 2.4282 | 2.4601 | 2.4921 | 2.5241 | 2.556 | 2.588 | 2.62 | 2.6464 | 2.6728 | 2.6991 | 2.7255 | 2.7519 | 2.7782 | 2.8046 | 2.831 | 2.8574 | 2.8838 | 2.9101 | 2.9365 | 2.9629 | 2.9893 | 3.0156 | 3.042 | 3.0684 | 3.0947 | 3.1211 | 3.1475 | 3.1739 | 3.2003 | 3.2266 | 3.253 | 3.2794 | 3.3058 | 3.3321 | 3.3585 | 3.3849 | 3.4112 | 3.4292 | 3.4471 | 3.465 | 3.4829 | 3.5008 | 3.5187 | 3.5366 | 3.5545 | 3.5724 | 3.5903 | 3.6082 | 3.6261 | 3.6441 | 3.662 | 3.6799 | 3.6978 | 3.7157 | 3.7336 | 3.7515 | 3.7694 | 3.7873 | 3.8052 | 3.8231 | 3.8411 | 3.859 | 3.8769 | 3.8948 | 3.9127 | 3.9306 | 3.9485
3.1 | 0 | 0.05975 | 0.1195 | 0.17925 | 0.239 | 0.29875 | 0.3585 | 0.41825 | 0.478 | 0.53775 | 0.5975 | 0.589 | 0.5805 | 0.572 | 0.5635 | 0.555 | 0.5543 | 0.5536 | 0.5529 | 0.5522 | 0.5515 | 0.54385 | 0.5362 | 0.52855 | 0.5209 | 0.51325 | 0.5056 | 0.49795 | 0.4903 | 0.48265 | 0.475 | 0.4822 | 0.4894 | 0.4966 | 0.5038 | 0.511 | 0.5182 | 0.5254 | 0.5326 | 0.5398 | 0.547 | 0.5542 | 0.5614 | 0.5686 | 0.5758 | 0.583 | 0.5924 | 0.6018 | 0.6112 | 0.6206 | 0.63 | 0.6394 | 0.6488 | 0.6582 | 0.6676 | 0.677 | 0.6864 | 0.6958 | 0.7052 | 0.7146 | 0.724 | 0.75708 | 0.79017 | 0.82325 | 0.85633 | 0.88942 | 0.9225 | 0.95558 | 0.98867 | 1.0217 | 1.0548 | 1.0879 | 1.121 | 1.1541 | 1.1872 | 1.2203 | 1.2533 | 1.2864 | 1.3195 | 1.3526 | 1.3857 | 1.4187 | 1.4518 | 1.4849 | 1.518 | 1.5511 | 1.5842 | 1.6173 | 1.6503 | 1.6834 | 1.7165 | 1.7496 | 1.7827 | 1.8158 | 1.849 | 1.8821 | 1.9152 | 1.9483 | 1.9814 | 2.0145 | 2.0477 | 2.0808 | 2.1139 | 2.147 | 2.1801 | 2.2132 | 2.2464 | 2.2795 | 2.3126 | 2.3457 | 2.3788 | 2.412 | 2.4451 | 2.4782 | 2.5113 | 2.5444 | 2.5775 | 2.6107 | 2.6438 | 2.6769 | 2.71 | 2.7372 | 2.7645 | 2.7917 | 2.819 | 2.8462 | 2.8735 | 2.9007 | 2.928 | 2.9552 | 2.9825 | 3.0097 | 3.037 | 3.0642 | 3.0915 | 3.1187 | 3.146 | 3.1732 | 3.2005 | 3.2277 | 3.255 | 3.2822 | 3.3095 | 3.3367 | 3.364 | 3.3912 | 3.4185 | 3.4457 | 3.473 | 3.5002 | 3.5275 | 3.5461 | 3.5648 | 3.5835 | 3.6021 | 3.6208 | 3.6394 | 3.658 | 3.6767 | 3.6953 | 3.714 | 3.7327 | 3.7513 | 3.77 | 3.7886 | 3.8072 | 3.8259 | 3.8445 | 3.8632 | 3.8819 | 3.9005 | 3.9192 | 3.9378 | 3.9564 | 3.9751 | 3.9937 | 4.0124 | 4.031 | 4.0497 | 4.0683 | 4.087
3.15 | 0 | 0.061375 | 0.12275 | 0.18413 | 0.2455 | 0.30688 | 0.36825 | 0.42962 | 0.491 | 0.55237 | 0.61375 | 0.6045 | 0.59525 | 0.586 | 0.57675 | 0.5675 | 0.56695 | 0.5664 | 0.56585 | 0.5653 | 0.56475 | 0.55702 | 0.5493 | 0.54158 | 0.53385 | 0.52612 | 0.5184 | 0.51067 | 0.50295 | 0.49523 | 0.4875 | 0.49497 | 0.50243 | 0.5099 | 0.51737 | 0.52483 | 0.5323 | 0.53977 | 0.54723 | 0.5547 | 0.56217 | 0.56963 | 0.5771 | 0.58457 | 0.59203 | 0.5995 | 0.60927 | 0.61903 | 0.6288 | 0.63857 | 0.64833 | 0.6581 | 0.66787 | 0.67763 | 0.6874 | 0.69717 | 0.70693 | 0.7167 | 0.72647 | 0.73623 | 0.746 | 0.78021 | 0.81442 | 0.84862 | 0.88283 | 0.91704 | 0.95125 | 0.98546 | 1.0197 | 1.0539 | 1.0881 | 1.1223 | 1.1565 | 1.1907 | 1.2249 | 1.2591 | 1.2933 | 1.3275 | 1.3618 | 1.396 | 1.4302 | 1.4644 | 1.4986 | 1.5328 | 1.567 | 1.6012 | 1.6354 | 1.6696 | 1.7038 | 1.738 | 1.7723 | 1.8065 | 1.8408 | 1.875 | 1.9093 | 1.9435 | 1.9778 | 2.0121 | 2.0463 | 2.0806 | 2.1148 | 2.1491 | 2.1833 | 2.2176 | 2.2519 | 2.2861 | 2.3204 | 2.3546 | 2.3889 | 2.4232 | 2.4574 | 2.4917 | 2.5259 | 2.5602 | 2.5945 | 2.6287 | 2.663 | 2.6972 | 2.7315 | 2.7657 | 2.8 | 2.8281 | 2.8563 | 2.8844 | 2.9125 | 2.9406 | 2.9688 | 2.9969 | 3.025 | 3.0531 | 3.0812 | 3.1094 | 3.1375 | 3.1656 | 3.1938 | 3.2219 | 3.25 | 3.2781 | 3.3062 | 3.3344 | 3.3625 | 3.3906 | 3.4188 | 3.4469 | 3.475 | 3.5031 | 3.5312 | 3.5594 | 3.5875 | 3.6156 | 3.6437 | 3.6631 | 3.6825 | 3.7019 | 3.7213 | 3.7407 | 3.7601 | 3.7795 | 3.7989 | 3.8183 | 3.8377 | 3.8571 | 3.8765 | 3.8958 | 3.9152 | 3.9346 | 3.954 | 3.9734 | 3.9928 | 4.0122 | 4.0316 | 4.051 | 4.0704 | 4.0898 | 4.1091 | 4.1285 | 4.1479 | 4.1673 | 4.1867 | 4.2061 | 4.2255
3.2 | 0 | 0.063 | 0.126 | 0.189 | 0.252 | 0.315 | 0.378 | 0.441 | 0.504 | 0.567 | 0.63 | 0.62 | 0.61 | 0.6 | 0.59 | 0.58 | 0.5796 | 0.5792 | 0.5788 | 0.5784 | 0.578 | 0.5702 | 0.5624 | 0.5546 | 0.5468 | 0.539 | 0.5312 | 0.5234 | 0.5156 | 0.5078 | 0.5 | 0.50773 | 0.51547 | 0.5232 | 0.53093 | 0.53867 | 0.5464 | 0.55413 | 0.56187 | 0.5696 | 0.57733 | 0.58507 | 0.5928 | 0.60053 | 0.60827 | 0.616 | 0.62613 | 0.63627 | 0.6464 | 0.65653 | 0.66667 | 0.6768 | 0.68693 | 0.69707 | 0.7072 | 0.71733 | 0.72747 | 0.7376 | 0.74773 | 0.75787 | 0.768 | 0.80333 | 0.83867 | 0.874 | 0.90933 | 0.94467 | 0.98 | 1.0153 | 1.0507 | 1.086 | 1.1213 | 1.1567 | 1.192 | 1.2273 | 1.2627 | 1.298 | 1.3333 | 1.3687 | 1.404 | 1.4393 | 1.4747 | 1.51 | 1.5453 | 1.5807 | 1.616 | 1.6513 | 1.6867 | 1.722 | 1.7573 | 1.7927 | 1.828 | 1.8634 | 1.8988 | 1.9342 | 1.9696 | 2.005 | 2.0404 | 2.0758 | 2.1112 | 2.1466 | 2.182 | 2.2174 | 2.2528 | 2.2882 | 2.3236 | 2.359 | 2.3944 | 2.4298 | 2.4652 | 2.5006 | 2.536 | 2.5714 | 2.6068 | 2.6422 | 2.6776 | 2.713 | 2.7484 | 2.7838 | 2.8192 | 2.8546 | 2.89 | 2.919 | 2.948 | 2.977 | 3.006 | 3.035 | 3.064 | 3.093 | 3.122 | 3.151 | 3.18 | 3.209 | 3.238 | 3.267 | 3.296 | 3.325 | 3.354 | 3.383 | 3.412 | 3.441 | 3.47 | 3.499 | 3.528 | 3.557 | 3.586 | 3.615 | 3.644 | 3.673 | 3.702 | 3.731 | 3.76 | 3.7801 | 3.8003 | 3.8204 | 3.8405 | 3.8607 | 3.8808 | 3.9009 | 3.9211 | 3.9412 | 3.9613 | 3.9815 | 4.0016 | 4.0217 | 4.0419 | 4.062 | 4.0821 | 4.1023 | 4.1224 | 4.1425 | 4.1627 | 4.1828 | 4.2029 | 4.2231 | 4.2432 | 4.2633 | 4.2835 | 4.3036 | 4.3237 | 4.3439 | 4.364
3.25 | 0 | 0.064625 | 0.12925 | 0.19387 | 0.2585 | 0.32312 | 0.38775 | 0.45238 | 0.517 | 0.58162 | 0.64625 | 0.6355 | 0.62475 | 0.614 | 0.60325 | 0.5925 | 0.59225 | 0.592 | 0.59175 | 0.5915 | 0.59125 | 0.58337 | 0.5755 | 0.56763 | 0.55975 | 0.55188 | 0.544 | 0.53612 | 0.52825 | 0.52038 | 0.5125 | 0.5205 | 0.5285 | 0.5365 | 0.5445 | 0.5525 | 0.5605 | 0.5685 | 0.5765 | 0.5845 | 0.5925 | 0.6005 | 0.6085 | 0.6165 | 0.6245 | 0.6325 | 0.643 | 0.6535 | 0.664 | 0.6745 | 0.685 | 0.6955 | 0.706 | 0.7165 | 0.727 | 0.7375 | 0.748 | 0.7585 | 0.769 | 0.7795 | 0.79 | 0.82646 | 0.86292 | 0.89938 | 0.93583 | 0.97229 | 1.0088 | 1.0452 | 1.0817 | 1.1181 | 1.1546 | 1.191 | 1.2275 | 1.264 | 1.3004 | 1.3369 | 1.3733 | 1.4098 | 1.4463 | 1.4827 | 1.5192 | 1.5556 | 1.5921 | 1.6285 | 1.665 | 1.7015 | 1.7379 | 1.7744 | 1.8108 | 1.8473 | 1.8838 | 1.9203 | 1.9568 | 1.9934 | 2.0299 | 2.0665 | 2.103 | 2.1395 | 2.1761 | 2.2126 | 2.2492 | 2.2857 | 2.3222 | 2.3588 | 2.3953 | 2.4319 | 2.4684 | 2.505 | 2.5415 | 2.578 | 2.6146 | 2.6511 | 2.6877 | 2.7242 | 2.7607 | 2.7973 | 2.8338 | 2.8704 | 2.9069 | 2.9435 | 2.98 | 3.0099 | 3.0398 | 3.0696 | 3.0995 | 3.1294 | 3.1593 | 3.1891 | 3.219 | 3.2489 | 3.2788 | 3.3086 | 3.3385 | 3.3684 | 3.3982 | 3.4281 | 3.458 | 3.4879 | 3.5177 | 3.5476 | 3.5775 | 3.6074 | 3.6372 | 3.6671 | 3.697 | 3.7269 | 3.7567 | 3.7866 | 3.8165 | 3.8464 | 3.8763 | 3.8971 | 3.918 | 3.9389 | 3.9598 | 3.9806 | 4.0015 | 4.0224 | 4.0432 | 4.0641 | 4.085 | 4.1059 | 4.1268 | 4.1476 | 4.1685 | 4.1894 | 4.2103 | 4.2311 | 4.252 | 4.2729 | 4.2938 | 4.3146 | 4.3355 | 4.3564 | 4.3773 | 4.3981 | 4.419 | 4.4399 | 4.4607 | 4.4816 | 4.5025
3.3 | 0 | 0.06625 | 0.1325 | 0.19875 | 0.265 | 0.33125 | 0.3975 | 0.46375 | 0.53 | 0.59625 | 0.6625 | 0.651 | 0.6395 | 0.628 | 0.6165 | 0.605 | 0.6049 | 0.6048 | 0.6047 | 0.6046 | 0.6045 | 0.59655 | 0.5886 | 0.58065 | 0.5727 | 0.56475 | 0.5568 | 0.54885 | 0.5409 | 0.53295 | 0.525 | 0.53327 | 0.54153 | 0.5498 | 0.55807 | 0.56633 | 0.5746 | 0.58287 | 0.59113 | 0.5994 | 0.60767 | 0.61593 | 0.6242 | 0.63247 | 0.64073 | 0.649 | 0.65987 | 0.67073 | 0.6816 | 0.69247 | 0.70333 | 0.7142 | 0.72507 | 0.73593 | 0.7468 | 0.75767 | 0.76853 | 0.7794 | 0.79027 | 0.80113 | 0.812 | 0.84958 | 0.88717 | 0.92475 | 0.96233 | 0.99992 | 1.0375 | 1.0751 | 1.1127 | 1.1502 | 1.1878 | 1.2254 | 1.263 | 1.3006 | 1.3382 | 1.3758 | 1.4133 | 1.4509 | 1.4885 | 1.5261 | 1.5637 | 1.6013 | 1.6388 | 1.6764 | 1.714 | 1.7516 | 1.7892 | 1.8268 | 1.8643 | 1.9019 | 1.9395 | 1.9772 | 2.0149 | 2.0526 | 2.0902 | 2.1279 | 2.1656 | 2.2033 | 2.241 | 2.2786 | 2.3163 | 2.354 | 2.3917 | 2.4294 | 2.4671 | 2.5048 | 2.5424 | 2.5801 | 2.6178 | 2.6555 | 2.6932 | 2.7309 | 2.7685 | 2.8062 | 2.8439 | 2.8816 | 2.9193 | 2.9569 | 2.9946 | 3.0323 | 3.07 | 3.1008 | 3.1315 | 3.1622 | 3.193 | 3.2237 | 3.2545 | 3.2853 | 3.316 | 3.3468 | 3.3775 | 3.4082 | 3.439 | 3.4697 | 3.5005 | 3.5312 | 3.562 | 3.5928 | 3.6235 | 3.6543 | 3.685 | 3.7157 | 3.7465 | 3.7772 | 3.808 | 3.8388 | 3.8695 | 3.9003 | 3.931 | 3.9617 | 3.9925 | 4.0141 | 4.0357 | 4.0573 | 4.079 | 4.1006 | 4.1222 | 4.1438 | 4.1654 | 4.1871 | 4.2087 | 4.2303 | 4.2519 | 4.2735 | 4.2951 | 4.3167 | 4.3384 | 4.36 | 4.3816 | 4.4032 | 4.4248 | 4.4464 | 4.4681 | 4.4897 | 4.5113 | 4.5329 | 4.5545 | 4.5762 | 4.5978 | 4.6194 | 4.641
3.35 | 0 | 0.067875 | 0.13575 | 0.20363 | 0.2715 | 0.33937 | 0.40725 | 0.47513 | 0.543 | 0.61087 | 0.67875 | 0.6665 | 0.65425 | 0.642 | 0.62975 | 0.6175 | 0.61755 | 0.6176 | 0.61765 | 0.6177 | 0.61775 | 0.60972 | 0.6017 | 0.59367 | 0.58565 | 0.57763 | 0.5696 | 0.56158 | 0.55355 | 0.54553 | 0.5375 | 0.54603 | 0.55457 | 0.5631 | 0.57163 | 0.58017 | 0.5887 | 0.59723 | 0.60577 | 0.6143 | 0.62283 | 0.63137 | 0.6399 | 0.64843 | 0.65697 | 0.6655 | 0.67673 | 0.68797 | 0.6992 | 0.71043 | 0.72167 | 0.7329 | 0.74413 | 0.75537 | 0.7666 | 0.77783 | 0.78907 | 0.8003 | 0.81153 | 0.82277 | 0.834 | 0.87271 | 0.91142 | 0.95012 | 0.98883 | 1.0275 | 1.0662 | 1.105 | 1.1437 | 1.1824 | 1.2211 | 1.2598 | 1.2985 | 1.3372 | 1.3759 | 1.4146 | 1.4533 | 1.492 | 1.5308 | 1.5695 | 1.6082 | 1.6469 | 1.6856 | 1.7243 | 1.763 | 1.8017 | 1.8404 | 1.8791 | 1.9178 | 1.9565 | 1.9952 | 2.0341 | 2.0729 | 2.1117 | 2.1505 | 2.1894 | 2.2282 | 2.267 | 2.3058 | 2.3447 | 2.3835 | 2.4223 | 2.4611 | 2.5 | 2.5388 | 2.5776 | 2.6164 | 2.6553 | 2.6941 | 2.7329 | 2.7717 | 2.8106 | 2.8494 | 2.8882 | 2.927 | 2.9659 | 3.0047 | 3.0435 | 3.0823 | 3.1212 | 3.16 | 3.1916 | 3.2233 | 3.2549 | 3.2865 | 3.3181 | 3.3497 | 3.3814 | 3.413 | 3.4446 | 3.4762 | 3.5079 | 3.5395 | 3.5711 | 3.6027 | 3.6344 | 3.666 | 3.6976 | 3.7292 | 3.7609 | 3.7925 | 3.8241 | 3.8558 | 3.8874 | 3.919 | 3.9506 | 3.9823 | 4.0139 | 4.0455 | 4.0771 | 4.1087 | 4.1311 | 4.1535 | 4.1758 | 4.1982 | 4.2205 | 4.2429 | 4.2653 | 4.2876 | 4.31 | 4.3323 | 4.3547 | 4.377 | 4.3994 | 4.4218 | 4.4441 | 4.4665 | 4.4888 | 4.5112 | 4.5336 | 4.5559 | 4.5783 | 4.6006 | 4.623 | 4.6453 | 4.6677 | 4.6901 | 4.7124 | 4.7348 | 4.7571 | 4.7795
3.4 | 0 | 0.0695 | 0.139 | 0.2085 | 0.278 | 0.3475 | 0.417 | 0.4865 | 0.556 | 0.6255 | 0.695 | 0.682 | 0.669 | 0.656 | 0.643 | 0.63 | 0.6302 | 0.6304 | 0.6306 | 0.6308 | 0.631 | 0.6229 | 0.6148 | 0.6067 | 0.5986 | 0.5905 | 0.5824 | 0.5743 | 0.5662 | 0.5581 | 0.55 | 0.5588 | 0.5676 | 0.5764 | 0.5852 | 0.594 | 0.6028 | 0.6116 | 0.6204 | 0.6292 | 0.638 | 0.6468 | 0.6556 | 0.6644 | 0.6732 | 0.682 | 0.6936 | 0.7052 | 0.7168 | 0.7284 | 0.74 | 0.7516 | 0.7632 | 0.7748 | 0.7864 | 0.798 | 0.8096 | 0.8212 | 0.8328 | 0.8444 | 0.856 | 0.89583 | 0.93567 | 0.9755 | 1.0153 | 1.0552 | 1.095 | 1.1348 | 1.1747 | 1.2145 | 1.2543 | 1.2942 | 1.334 | 1.3738 | 1.4137 | 1.4535 | 1.4933 | 1.5332 | 1.573 | 1.6128 | 1.6527 | 1.6925 | 1.7323 | 1.7722 | 1.812 | 1.8518 | 1.8917 | 1.9315 | 1.9713 | 2.0112 | 2.051 | 2.091 | 2.1309 | 2.1709 | 2.2109 | 2.2508 | 2.2908 | 2.3308 | 2.3707 | 2.4107 | 2.4507 | 2.4906 | 2.5306 | 2.5706 | 2.6105 | 2.6505 | 2.6905 | 2.7304 | 2.7704 | 2.8104 | 2.8503 | 2.8903 | 2.9303 | 2.9702 | 3.0102 | 3.0502 | 3.0901 | 3.1301 | 3.1701 | 3.21 | 3.25 | 3.2825 | 3.315 | 3.3475 | 3.38 | 3.4125 | 3.445 | 3.4775 | 3.51 | 3.5425 | 3.575 | 3.6075 | 3.64 | 3.6725 | 3.705 | 3.7375 | 3.77 | 3.8025 | 3.835 | 3.8675 | 3.9 | 3.9325 | 3.965 | 3.9975 | 4.03 | 4.0625 | 4.095 | 4.1275 | 4.16 | 4.1925 | 4.225 | 4.2481 | 4.2712 | 4.2943 | 4.3174 | 4.3405 | 4.3636 | 4.3867 | 4.4098 | 4.4329 | 4.456 | 4.4791 | 4.5022 | 4.5253 | 4.5484 | 4.5715 | 4.5946 | 4.6177 | 4.6408 | 4.6639 | 4.687 | 4.7101 | 4.7332 | 4.7563 | 4.7794 | 4.8025 | 4.8256 | 4.8487 | 4.8718 | 4.8949 | 4.918
3.45 | 0 | 0.071125 | 0.14225 | 0.21338 | 0.2845 | 0.35563 | 0.42675 | 0.49788 | 0.569 | 0.64013 | 0.71125 | 0.6975 | 0.68375 | 0.67 | 0.65625 | 0.6425 | 0.64285 | 0.6432 | 0.64355 | 0.6439 | 0.64425 | 0.63607 | 0.6279 | 0.61972 | 0.61155 | 0.60337 | 0.5952 | 0.58703 | 0.57885 | 0.57068 | 0.5625 | 0.57157 | 0.58063 | 0.5897 | 0.59877 | 0.60783 | 0.6169 | 0.62597 | 0.63503 | 0.6441 | 0.65317 | 0.66223 | 0.6713 | 0.68037 | 0.68943 | 0.6985 | 0.71047 | 0.72243 | 0.7344 | 0.74637 | 0.75833 | 0.7703 | 0.78227 | 0.79423 | 0.8062 | 0.81817 | 0.83013 | 0.8421 | 0.85407 | 0.86603 | 0.878 | 0.91896 | 0.95992 | 1.0009 | 1.0418 | 1.0828 | 1.1238 | 1.1647 | 1.2057 | 1.2466 | 1.2876 | 1.3285 | 1.3695 | 1.4105 | 1.4514 | 1.4924 | 1.5333 | 1.5743 | 1.6153 | 1.6562 | 1.6972 | 1.7381 | 1.7791 | 1.82 | 1.861 | 1.902 | 1.9429 | 1.9839 | 2.0248 | 2.0658 | 2.1067 | 2.1479 | 2.189 | 2.2301 | 2.2712 | 2.3123 | 2.3534 | 2.3945 | 2.4356 | 2.4767 | 2.5178 | 2.5589 | 2.6 | 2.6412 | 2.6823 | 2.7234 | 2.7645 | 2.8056 | 2.8467 | 2.8878 | 2.9289 | 2.97 | 3.0111 | 3.0522 | 3.0934 | 3.1345 | 3.1756 | 3.2167 | 3.2578 | 3.2989 | 3.34 | 3.3734 | 3.4068 | 3.4401 | 3.4735 | 3.5069 | 3.5402 | 3.5736 | 3.607 | 3.6404 | 3.6738 | 3.7071 | 3.7405 | 3.7739 | 3.8072 | 3.8406 | 3.874 | 3.9074 | 3.9407 | 3.9741 | 4.0075 | 4.0409 | 4.0743 | 4.1076 | 4.141 | 4.1744 | 4.2077 | 4.2411 | 4.2745 | 4.3079 | 4.3412 | 4.3651 | 4.3889 | 4.4128 | 4.4366 | 4.4605 | 4.4843 | 4.5081 | 4.532 | 4.5558 | 4.5797 | 4.6035 | 4.6273 | 4.6512 | 4.675 | 4.6989 | 4.7227 | 4.7466 | 4.7704 | 4.7942 | 4.8181 | 4.8419 | 4.8658 | 4.8896 | 4.9135 | 4.9373 | 4.9611 | 4.985 | 5.0088 | 5.0327 | 5.0565
3.5 | 0 | 0.07275 | 0.1455 | 0.21825 | 0.291 | 0.36375 | 0.4365 | 0.50925 | 0.582 | 0.65475 | 0.7275 | 0.713 | 0.6985 | 0.684 | 0.6695 | 0.655 | 0.6555 | 0.656 | 0.6565 | 0.657 | 0.6575 | 0.64925 | 0.641 | 0.63275 | 0.6245 | 0.61625 | 0.608 | 0.59975 | 0.5915 | 0.58325 | 0.575 | 0.58433 | 0.59367 | 0.603 | 0.61233 | 0.62167 | 0.631 | 0.64033 | 0.64967 | 0.659 | 0.66833 | 0.67767 | 0.687 | 0.69633 | 0.70567 | 0.715 | 0.72733 | 0.73967 | 0.752 | 0.76433 | 0.77667 | 0.789 | 0.80133 | 0.81367 | 0.826 | 0.83833 | 0.85067 | 0.863 | 0.87533 | 0.88767 | 0.9 | 0.94208 | 0.98417 | 1.0263 | 1.0683 | 1.1104 | 1.1525 | 1.1946 | 1.2367 | 1.2788 | 1.3208 | 1.3629 | 1.405 | 1.4471 | 1.4892 | 1.5312 | 1.5733 | 1.6154 | 1.6575 | 1.6996 | 1.7417 | 1.7837 | 1.8258 | 1.8679 | 1.91 | 1.9521 | 1.9942 | 2.0362 | 2.0783 | 2.1204 | 2.1625 | 2.2048 | 2.247 | 2.2893 | 2.3315 | 2.3737 | 2.416 | 2.4583 | 2.5005 | 2.5427 | 2.585 | 2.6273 | 2.6695 | 2.7117 | 2.754 | 2.7963 | 2.8385 | 2.8807 | 2.923 | 2.9653 | 3.0075 | 3.0497 | 3.092 | 3.1343 | 3.1765 | 3.2188 | 3.261 | 3.3032 | 3.3455 | 3.3878 | 3.43 | 3.4642 | 3.4985 | 3.5328 | 3.567 | 3.6012 | 3.6355 | 3.6698 | 3.704 | 3.7382 | 3.7725 | 3.8068 | 3.841 | 3.8752 | 3.9095 | 3.9438 | 3.978 | 4.0122 | 4.0465 | 4.0808 | 4.115 | 4.1493 | 4.1835 | 4.2177 | 4.252 | 4.2862 | 4.3205 | 4.3548 | 4.389 | 4.4233 | 4.4575 | 4.4821 | 4.5067 | 4.5312 | 4.5558 | 4.5804 | 4.605 | 4.6296 | 4.6542 | 4.6787 | 4.7033 | 4.7279 | 4.7525 | 4.7771 | 4.8017 | 4.8262 | 4.8508 | 4.8754 | 4.9 | 4.9246 | 4.9492 | 4.9737 | 4.9983 | 5.0229 | 5.0475 | 5.0721 | 5.0967 | 5.1212 | 5.1458 | 5.1704 | 5.195
3.55 | 0 | 0.074375 | 0.14875 | 0.22312 | 0.2975 | 0.37188 | 0.44625 | 0.52063 | 0.595 | 0.66938 | 0.74375 | 0.7285 | 0.71325 | 0.698 | 0.68275 | 0.6675 | 0.66815 | 0.6688 | 0.66945 | 0.6701 | 0.67075 | 0.66243 | 0.6541 | 0.64577 | 0.63745 | 0.62913 | 0.6208 | 0.61247 | 0.60415 | 0.59583 | 0.5875 | 0.5971 | 0.6067 | 0.6163 | 0.6259 | 0.6355 | 0.6451 | 0.6547 | 0.6643 | 0.6739 | 0.6835 | 0.6931 | 0.7027 | 0.7123 | 0.7219 | 0.7315 | 0.7442 | 0.7569 | 0.7696 | 0.7823 | 0.795 | 0.8077 | 0.8204 | 0.8331 | 0.8458 | 0.8585 | 0.8712 | 0.8839 | 0.8966 | 0.9093 | 0.922 | 0.96521 | 1.0084 | 1.0516 | 1.0948 | 1.138 | 1.1812 | 1.2245 | 1.2677 | 1.3109 | 1.3541 | 1.3973 | 1.4405 | 1.4837 | 1.5269 | 1.5701 | 1.6133 | 1.6565 | 1.6998 | 1.743 | 1.7862 | 1.8294 | 1.8726 | 1.9158 | 1.959 | 2.0022 | 2.0454 | 2.0886 | 2.1318 | 2.175 | 2.2182 | 2.2616 | 2.305 | 2.3484 | 2.3918 | 2.4352 | 2.4786 | 2.522 | 2.5654 | 2.6088 | 2.6522 | 2.6956 | 2.7389 | 2.7823 | 2.8257 | 2.8691 | 2.9125 | 2.9559 | 2.9993 | 3.0427 | 3.0861 | 3.1295 | 3.1729 | 3.2163 | 3.2597 | 3.303 | 3.3464 | 3.3898 | 3.4332 | 3.4766 | 3.52 | 3.5551 | 3.5903 | 3.6254 | 3.6605 | 3.6956 | 3.7308 | 3.7659 | 3.801 | 3.8361 | 3.8712 | 3.9064 | 3.9415 | 3.9766 | 4.0118 | 4.0469 | 4.082 | 4.1171 | 4.1523 | 4.1874 | 4.2225 | 4.2576 | 4.2927 | 4.3279 | 4.363 | 4.3981 | 4.4333 | 4.4684 | 4.5035 | 4.5386 | 4.5738 | 4.5991 | 4.6244 | 4.6497 | 4.675 | 4.7004 | 4.7257 | 4.751 | 4.7763 | 4.8017 | 4.827 | 4.8523 | 4.8777 | 4.903 | 4.9283 | 4.9536 | 4.979 | 5.0043 | 5.0296 | 5.0549 | 5.0803 | 5.1056 | 5.1309 | 5.1562 | 5.1815 | 5.2069 | 5.2322 | 5.2575 | 5.2828 | 5.3082 | 5.3335
3.6 | 0 | 0.076 | 0.152 | 0.228 | 0.304 | 0.38 | 0.456 | 0.532 | 0.608 | 0.684 | 0.76 | 0.744 | 0.728 | 0.712 | 0.696 | 0.68 | 0.6808 | 0.6816 | 0.6824 | 0.6832 | 0.684 | 0.6756 | 0.6672 | 0.6588 | 0.6504 | 0.642 | 0.6336 | 0.6252 | 0.6168 | 0.6084 | 0.6 | 0.60987 | 0.61973 | 0.6296 | 0.63947 | 0.64933 | 0.6592 | 0.66907 | 0.67893 | 0.6888 | 0.69867 | 0.70853 | 0.7184 | 0.72827 | 0.73813 | 0.748 | 0.76107 | 0.77413 | 0.7872 | 0.80027 | 0.81333 | 0.8264 | 0.83947 | 0.85253 | 0.8656 | 0.87867 | 0.89173 | 0.9048 | 0.91787 | 0.93093 | 0.944 | 0.98833 | 1.0327 | 1.077 | 1.1213 | 1.1657 | 1.21 | 1.2543 | 1.2987 | 1.343 | 1.3873 | 1.4317 | 1.476 | 1.5203 | 1.5647 | 1.609 | 1.6533 | 1.6977 | 1.742 | 1.7863 | 1.8307 | 1.875 | 1.9193 | 1.9637 | 2.008 | 2.0523 | 2.0967 | 2.141 | 2.1853 | 2.2297 | 2.274 | 2.3185 | 2.3631 | 2.4076 | 2.4521 | 2.4967 | 2.5412 | 2.5857 | 2.6303 | 2.6748 | 2.7193 | 2.7639 | 2.8084 | 2.8529 | 2.8975 | 2.942 | 2.9865 | 3.0311 | 3.0756 | 3.1201 | 3.1647 | 3.2092 | 3.2537 | 3.2983 | 3.3428 | 3.3873 | 3.4319 | 3.4764 | 3.5209 | 3.5655 | 3.61 | 3.646 | 3.682 | 3.718 | 3.754 | 3.79 | 3.826 | 3.862 | 3.898 | 3.934 | 3.97 | 4.006 | 4.042 | 4.078 | 4.114 | 4.15 | 4.186 | 4.222 | 4.258 | 4.294 | 4.33 | 4.366 | 4.402 | 4.438 | 4.474 | 4.51 | 4.546 | 4.582 | 4.618 | 4.654 | 4.69 | 4.7161 | 4.7421 | 4.7682 | 4.7943 | 4.8203 | 4.8464 | 4.8725 | 4.8985 | 4.9246 | 4.9507 | 4.9767 | 5.0028 | 5.0289 | 5.0549 | 5.081 | 5.1071 | 5.1331 | 5.1592 | 5.1853 | 5.2113 | 5.2374 | 5.2635 | 5.2895 | 5.3156 | 5.3417 | 5.3677 | 5.3938 | 5.4199 | 5.4459 | 5.472
3.65 | 0 | 0.077625 | 0.15525 | 0.23287 | 0.3105 | 0.38812 | 0.46575 | 0.54338 | 0.621 | 0.69863 | 0.77625 | 0.7595 | 0.74275 | 0.726 | 0.70925 | 0.6925 | 0.69345 | 0.6944 | 0.69535 | 0.6963 | 0.69725 | 0.68878 | 0.6803 | 0.67183 | 0.66335 | 0.65487 | 0.6464 | 0.63792 | 0.62945 | 0.62098 | 0.6125 | 0.62263 | 0.63277 | 0.6429 | 0.65303 | 0.66317 | 0.6733 | 0.68343 | 0.69357 | 0.7037 | 0.71383 | 0.72397 | 0.7341 | 0.74423 | 0.75437 | 0.7645 | 0.77793 | 0.79137 | 0.8048 | 0.81823 | 0.83167 | 0.8451 | 0.85853 | 0.87197 | 0.8854 | 0.89883 | 0.91227 | 0.9257 | 0.93913 | 0.95257 | 0.966 | 1.0115 | 1.0569 | 1.1024 | 1.1478 | 1.1933 | 1.2388 | 1.2842 | 1.3297 | 1.3751 | 1.4206 | 1.466 | 1.5115 | 1.557 | 1.6024 | 1.6479 | 1.6933 | 1.7388 | 1.7842 | 1.8297 | 1.8752 | 1.9206 | 1.9661 | 2.0115 | 2.057 | 2.1025 | 2.1479 | 2.1934 | 2.2388 | 2.2843 | 2.3298 | 2.3754 | 2.4211 | 2.4668 | 2.5124 | 2.5581 | 2.6038 | 2.6495 | 2.6951 | 2.7408 | 2.7865 | 2.8322 | 2.8779 | 2.9235 | 2.9692 | 3.0149 | 3.0606 | 3.1062 | 3.1519 | 3.1976 | 3.2433 | 3.2889 | 3.3346 | 3.3803 | 3.4259 | 3.4716 | 3.5173 | 3.563 | 3.6086 | 3.6543 | 3.7 | 3.7369 | 3.7738 | 3.8106 | 3.8475 | 3.8844 | 3.9213 | 3.9581 | 3.995 | 4.0319 | 4.0687 | 4.1056 | 4.1425 | 4.1794 | 4.2162 | 4.2531 | 4.29 | 4.3269 | 4.3637 | 4.4006 | 4.4375 | 4.4744 | 4.5113 | 4.5481 | 4.585 | 4.6219 | 4.6588 | 4.6956 | 4.7325 | 4.7694 | 4.8063 | 4.8331 | 4.8599 | 4.8867 | 4.9135 | 4.9403 | 4.9671 | 4.9939 | 5.0207 | 5.0475 | 5.0743 | 5.1011 | 5.128 | 5.1548 | 5.1816 | 5.2084 | 5.2352 | 5.262 | 5.2888 | 5.3156 | 5.3424 | 5.3692 | 5.396 | 5.4228 | 5.4497 | 5.4765 | 5.5033 | 5.5301 | 5.5569 | 5.5837 | 5.6105
3.7 | 0 | 0.07925 | 0.1585 | 0.23775 | 0.317 | 0.39625 | 0.4755 | 0.55475 | 0.634 | 0.71325 | 0.7925 | 0.775 | 0.7575 | 0.74 | 0.7225 | 0.705 | 0.7061 | 0.7072 | 0.7083 | 0.7094 | 0.7105 | 0.70195 | 0.6934 | 0.68485 | 0.6763 | 0.66775 | 0.6592 | 0.65065 | 0.6421 | 0.63355 | 0.625 | 0.6354 | 0.6458 | 0.6562 | 0.6666 | 0.677 | 0.6874 | 0.6978 | 0.7082 | 0.7186 | 0.729 | 0.7394 | 0.7498 | 0.7602 | 0.7706 | 0.781 | 0.7948 | 0.8086 | 0.8224 | 0.8362 | 0.85 | 0.8638 | 0.8776 | 0.8914 | 0.9052 | 0.919 | 0.9328 | 0.9466 | 0.9604 | 0.9742 | 0.988 | 1.0346 | 1.0812 | 1.1278 | 1.1743 | 1.2209 | 1.2675 | 1.3141 | 1.3607 | 1.4072 | 1.4538 | 1.5004 | 1.547 | 1.5936 | 1.6402 | 1.6867 | 1.7333 | 1.7799 | 1.8265 | 1.8731 | 1.9197 | 1.9663 | 2.0128 | 2.0594 | 2.106 | 2.1526 | 2.1992 | 2.2458 | 2.2923 | 2.3389 | 2.3855 | 2.4323 | 2.4791 | 2.5259 | 2.5728 | 2.6196 | 2.6664 | 2.7132 | 2.76 | 2.8068 | 2.8537 | 2.9005 | 2.9473 | 2.9941 | 3.0409 | 3.0878 | 3.1346 | 3.1814 | 3.2282 | 3.275 | 3.3218 | 3.3687 | 3.4155 | 3.4623 | 3.5091 | 3.5559 | 3.6027 | 3.6496 | 3.6964 | 3.7432 | 3.79 | 3.8277 | 3.8655 | 3.9032 | 3.941 | 3.9787 | 4.0165 | 4.0542 | 4.092 | 4.1297 | 4.1675 | 4.2053 | 4.243 | 4.2808 | 4.3185 | 4.3563 | 4.394 | 4.4318 | 4.4695 | 4.5072 | 4.545 | 4.5827 | 4.6205 | 4.6582 | 4.696 | 4.7337 | 4.7715 | 4.8092 | 4.847 | 4.8848 | 4.9225 | 4.9501 | 4.9776 | 5.0052 | 5.0327 | 5.0602 | 5.0878 | 5.1154 | 5.1429 | 5.1704 | 5.198 | 5.2256 | 5.2531 | 5.2806 | 5.3082 | 5.3357 | 5.3633 | 5.3909 | 5.4184 | 5.4459 | 5.4735 | 5.5011 | 5.5286 | 5.5561 | 5.5837 | 5.6113 | 5.6388 | 5.6664 | 5.6939 | 5.7214 | 5.749
3.75 | 0 | 0.080875 | 0.16175 | 0.24263 | 0.3235 | 0.40437 | 0.48525 | 0.56612 | 0.647 | 0.72788 | 0.80875 | 0.7905 | 0.77225 | 0.754 | 0.73575 | 0.7175 | 0.71875 | 0.72 | 0.72125 | 0.7225 | 0.72375 | 0.71513 | 0.7065 | 0.69788 | 0.68925 | 0.68063 | 0.672 | 0.66338 | 0.65475 | 0.64612 | 0.6375 | 0.64817 | 0.65883 | 0.6695 | 0.68017 | 0.69083 | 0.7015 | 0.71217 | 0.72283 | 0.7335 | 0.74417 | 0.75483 | 0.7655 | 0.77617 | 0.78683 | 0.7975 | 0.81167 | 0.82583 | 0.84 | 0.85417 | 0.86833 | 0.8825 | 0.89667 | 0.91083 | 0.925 | 0.93917 | 0.95333 | 0.9675 | 0.98167 | 0.99583 | 1.01 | 1.0577 | 1.1054 | 1.1531 | 1.2008 | 1.2485 | 1.2962 | 1.344 | 1.3917 | 1.4394 | 1.4871 | 1.5348 | 1.5825 | 1.6302 | 1.6779 | 1.7256 | 1.7733 | 1.821 | 1.8687 | 1.9165 | 1.9642 | 2.0119 | 2.0596 | 2.1073 | 2.155 | 2.2027 | 2.2504 | 2.2981 | 2.3458 | 2.3935 | 2.4413 | 2.4892 | 2.5372 | 2.5851 | 2.6331 | 2.681 | 2.729 | 2.777 | 2.8249 | 2.8729 | 2.9208 | 2.9688 | 3.0168 | 3.0647 | 3.1127 | 3.1606 | 3.2086 | 3.2565 | 3.3045 | 3.3525 | 3.4004 | 3.4484 | 3.4963 | 3.5443 | 3.5922 | 3.6402 | 3.6882 | 3.7361 | 3.7841 | 3.832 | 3.88 | 3.9186 | 3.9573 | 3.9959 | 4.0345 | 4.0731 | 4.1117 | 4.1504 | 4.189 | 4.2276 | 4.2663 | 4.3049 | 4.3435 | 4.3821 | 4.4207 | 4.4594 | 4.498 | 4.5366 | 4.5752 | 4.6139 | 4.6525 | 4.6911 | 4.7298 | 4.7684 | 4.807 | 4.8456 | 4.8842 | 4.9229 | 4.9615 | 5.0001 | 5.0388 | 5.067 | 5.0953 | 5.1236 | 5.1519 | 5.1802 | 5.2085 | 5.2368 | 5.2651 | 5.2934 | 5.3217 | 5.35 | 5.3783 | 5.4065 | 5.4348 | 5.4631 | 5.4914 | 5.5197 | 5.548 | 5.5763 | 5.6046 | 5.6329 | 5.6612 | 5.6895 | 5.7177 | 5.746 | 5.7743 | 5.8026 | 5.8309 | 5.8592 | 5.8875
3.8 | 0 | 0.0825 | 0.165 | 0.2475 | 0.33 | 0.4125 | 0.495 | 0.5775 | 0.66 | 0.7425 | 0.825 | 0.806 | 0.787 | 0.768 | 0.749 | 0.73 | 0.7314 | 0.7328 | 0.7342 | 0.7356 | 0.737 | 0.7283 | 0.7196 | 0.7109 | 0.7022 | 0.6935 | 0.6848 | 0.6761 | 0.6674 | 0.6587 | 0.65 | 0.66093 | 0.67187 | 0.6828 | 0.69373 | 0.70467 | 0.7156 | 0.72653 | 0.73747 | 0.7484 | 0.75933 | 0.77027 | 0.7812 | 0.79213 | 0.80307 | 0.814 | 0.82853 | 0.84307 | 0.8576 | 0.87213 | 0.88667 | 0.9012 | 0.91573 | 0.93027 | 0.9448 | 0.95933 | 0.97387 | 0.9884 | 1.0029 | 1.0175 | 1.032 | 1.0808 | 1.1297 | 1.1785 | 1.2273 | 1.2762 | 1.325 | 1.3738 | 1.4227 | 1.4715 | 1.5203 | 1.5692 | 1.618 | 1.6668 | 1.7157 | 1.7645 | 1.8133 | 1.8622 | 1.911 | 1.9598 | 2.0087 | 2.0575 | 2.1063 | 2.1552 | 2.204 | 2.2528 | 2.3017 | 2.3505 | 2.3993 | 2.4482 | 2.497 | 2.5461 | 2.5952 | 2.6443 | 2.6934 | 2.7425 | 2.7916 | 2.8407 | 2.8898 | 2.9389 | 2.988 | 3.0371 | 3.0862 | 3.1353 | 3.1844 | 3.2335 | 3.2826 | 3.3317 | 3.3808 | 3.4299 | 3.479 | 3.5281 | 3.5772 | 3.6263 | 3.6754 | 3.7245 | 3.7736 | 3.8227 | 3.8718 | 3.9209 | 3.97 | 4.0095 | 4.049 | 4.0885 | 4.128 | 4.1675 | 4.207 | 4.2465 | 4.286 | 4.3255 | 4.365 | 4.4045 | 4.444 | 4.4835 | 4.523 | 4.5625 | 4.602 | 4.6415 | 4.681 | 4.7205 | 4.76 | 4.7995 | 4.839 | 4.8785 | 4.918 | 4.9575 | 4.997 | 5.0365 | 5.076 | 5.1155 | 5.155 | 5.184 | 5.2131 | 5.2421 | 5.2711 | 5.3002 | 5.3292 | 5.3582 | 5.3873 | 5.4163 | 5.4453 | 5.4744 | 5.5034 | 5.5324 | 5.5615 | 5.5905 | 5.6195 | 5.6486 | 5.6776 | 5.7066 | 5.7357 | 5.7647 | 5.7937 | 5.8228 | 5.8518 | 5.8808 | 5.9099 | 5.9389 | 5.9679 | 5.997 | 6.026
3.85 | 0 | 0.084125 | 0.16825 | 0.25238 | 0.3365 | 0.42063 | 0.50475 | 0.58888 | 0.673 | 0.75713 | 0.84125 | 0.8215 | 0.80175 | 0.782 | 0.76225 | 0.7425 | 0.74405 | 0.7456 | 0.74715 | 0.7487 | 0.75025 | 0.74147 | 0.7327 | 0.72393 | 0.71515 | 0.70637 | 0.6976 | 0.68883 | 0.68005 | 0.67127 | 0.6625 | 0.6737 | 0.6849 | 0.6961 | 0.7073 | 0.7185 | 0.7297 | 0.7409 | 0.7521 | 0.7633 | 0.7745 | 0.7857 | 0.7969 | 0.8081 | 0.8193 | 0.8305 | 0.8454 | 0.8603 | 0.8752 | 0.8901 | 0.905 | 0.9199 | 0.9348 | 0.9497 | 0.9646 | 0.9795 | 0.9944 | 1.0093 | 1.0242 | 1.0391 | 1.054 | 1.104 | 1.1539 | 1.2039 | 1.2538 | 1.3038 | 1.3538 | 1.4037 | 1.4537 | 1.5036 | 1.5536 | 1.6035 | 1.6535 | 1.7035 | 1.7534 | 1.8034 | 1.8533 | 1.9033 | 1.9532 | 2.0032 | 2.0532 | 2.1031 | 2.1531 | 2.203 | 2.253 | 2.303 | 2.3529 | 2.4029 | 2.4528 | 2.5028 | 2.5528 | 2.603 | 2.6532 | 2.7035 | 2.7537 | 2.804 | 2.8542 | 2.9044 | 2.9547 | 3.0049 | 3.0552 | 3.1054 | 3.1557 | 3.2059 | 3.2561 | 3.3064 | 3.3566 | 3.4069 | 3.4571 | 3.5073 | 3.5576 | 3.6078 | 3.6581 | 3.7083 | 3.7586 | 3.8088 | 3.859 | 3.9093 | 3.9595 | 4.0098 | 4.06 | 4.1004 | 4.1407 | 4.1811 | 4.2215 | 4.2619 | 4.3022 | 4.3426 | 4.383 | 4.4234 | 4.4638 | 4.5041 | 4.5445 | 4.5849 | 4.6253 | 4.6656 | 4.706 | 4.7464 | 4.7867 | 4.8271 | 4.8675 | 4.9079 | 4.9482 | 4.9886 | 5.029 | 5.0694 | 5.1098 | 5.1501 | 5.1905 | 5.2309 | 5.2713 | 5.301 | 5.3308 | 5.3606 | 5.3903 | 5.4201 | 5.4499 | 5.4797 | 5.5095 | 5.5392 | 5.569 | 5.5988 | 5.6285 | 5.6583 | 5.6881 | 5.7179 | 5.7477 | 5.7774 | 5.8072 | 5.837 | 5.8667 | 5.8965 | 5.9263 | 5.9561 | 5.9859 | 6.0156 | 6.0454 | 6.0752 | 6.1049 | 6.1347 | 6.1645
3.9 | 0 | 0.08575 | 0.1715 | 0.25725 | 0.343 | 0.42875 | 0.5145 | 0.60025 | 0.686 | 0.77175 | 0.8575 | 0.837 | 0.8165 | 0.796 | 0.7755 | 0.755 | 0.7567 | 0.7584 | 0.7601 | 0.7618 | 0.7635 | 0.75465 | 0.7458 | 0.73695 | 0.7281 | 0.71925 | 0.7104 | 0.70155 | 0.6927 | 0.68385 | 0.675 | 0.68647 | 0.69793 | 0.7094 | 0.72087 | 0.73233 | 0.7438 | 0.75527 | 0.76673 | 0.7782 | 0.78967 | 0.80113 | 0.8126 | 0.82407 | 0.83553 | 0.847 | 0.86227 | 0.87753 | 0.8928 | 0.90807 | 0.92333 | 0.9386 | 0.95387 | 0.96913 | 0.9844 | 0.99967 | 1.0149 | 1.0302 | 1.0455 | 1.0607 | 1.076 | 1.1271 | 1.1782 | 1.2292 | 1.2803 | 1.3314 | 1.3825 | 1.4336 | 1.4847 | 1.5357 | 1.5868 | 1.6379 | 1.689 | 1.7401 | 1.7912 | 1.8422 | 1.8933 | 1.9444 | 1.9955 | 2.0466 | 2.0977 | 2.1488 | 2.1998 | 2.2509 | 2.302 | 2.3531 | 2.4042 | 2.4552 | 2.5063 | 2.5574 | 2.6085 | 2.6599 | 2.7113 | 2.7626 | 2.814 | 2.8654 | 2.9168 | 2.9682 | 3.0196 | 3.0709 | 3.1223 | 3.1737 | 3.2251 | 3.2765 | 3.3279 | 3.3792 | 3.4306 | 3.482 | 3.5334 | 3.5848 | 3.6362 | 3.6875 | 3.7389 | 3.7903 | 3.8417 | 3.8931 | 3.9445 | 3.9958 | 4.0472 | 4.0986 | 4.15 | 4.1913 | 4.2325 | 4.2737 | 4.315 | 4.3563 | 4.3975 | 4.4387 | 4.48 | 4.5213 | 4.5625 | 4.6037 | 4.645 | 4.6863 | 4.7275 | 4.7687 | 4.81 | 4.8513 | 4.8925 | 4.9337 | 4.975 | 5.0163 | 5.0575 | 5.0987 | 5.14 | 5.1813 | 5.2225 | 5.2637 | 5.305 | 5.3463 | 5.3875 | 5.418 | 5.4485 | 5.479 | 5.5096 | 5.5401 | 5.5706 | 5.6011 | 5.6316 | 5.6621 | 5.6927 | 5.7232 | 5.7537 | 5.7842 | 5.8147 | 5.8453 | 5.8758 | 5.9063 | 5.9368 | 5.9673 | 5.9978 | 6.0283 | 6.0589 | 6.0894 | 6.1199 | 6.1504 | 6.1809 | 6.2115 | 6.242 | 6.2725 | 6.303
3.95 | 0 | 0.087375 | 0.17475 | 0.26212 | 0.3495 | 0.43688 | 0.52425 | 0.61162 | 0.699 | 0.78638 | 0.87375 | 0.8525 | 0.83125 | 0.81 | 0.78875 | 0.7675 | 0.76935 | 0.7712 | 0.77305 | 0.7749 | 0.77675 | 0.76782 | 0.7589 | 0.74997 | 0.74105 | 0.73213 | 0.7232 | 0.71427 | 0.70535 | 0.69642 | 0.6875 | 0.69923 | 0.71097 | 0.7227 | 0.73443 | 0.74617 | 0.7579 | 0.76963 | 0.78137 | 0.7931 | 0.80483 | 0.81657 | 0.8283 | 0.84003 | 0.85177 | 0.8635 | 0.87913 | 0.89477 | 0.9104 | 0.92603 | 0.94167 | 0.9573 | 0.97293 | 0.98857 | 1.0042 | 1.0198 | 1.0355 | 1.0511 | 1.0667 | 1.0824 | 1.098 | 1.1502 | 1.2024 | 1.2546 | 1.3068 | 1.359 | 1.4112 | 1.4635 | 1.5157 | 1.5679 | 1.6201 | 1.6723 | 1.7245 | 1.7767 | 1.8289 | 1.8811 | 1.9333 | 1.9855 | 2.0377 | 2.09 | 2.1422 | 2.1944 | 2.2466 | 2.2988 | 2.351 | 2.4032 | 2.4554 | 2.5076 | 2.5598 | 2.612 | 2.6643 | 2.7168 | 2.7693 | 2.8218 | 2.8744 | 2.9269 | 2.9794 | 3.0319 | 3.0844 | 3.137 | 3.1895 | 3.242 | 3.2946 | 3.3471 | 3.3996 | 3.4521 | 3.5046 | 3.5572 | 3.6097 | 3.6622 | 3.7147 | 3.7673 | 3.8198 | 3.8723 | 3.9249 | 3.9774 | 4.0299 | 4.0824 | 4.1349 | 4.1875 | 4.24 | 4.2821 | 4.3243 | 4.3664 | 4.4085 | 4.4506 | 4.4928 | 4.5349 | 4.577 | 4.6191 | 4.6612 | 4.7034 | 4.7455 | 4.7876 | 4.8297 | 4.8719 | 4.914 | 4.9561 | 4.9982 | 5.0404 | 5.0825 | 5.1246 | 5.1668 | 5.2089 | 5.251 | 5.2931 | 5.3353 | 5.3774 | 5.4195 | 5.4616 | 5.5038 | 5.535 | 5.5663 | 5.5975 | 5.6288 | 5.66 | 5.6913 | 5.7226 | 5.7538 | 5.7851 | 5.8163 | 5.8476 | 5.8788 | 5.9101 | 5.9414 | 5.9726 | 6.0039 | 6.0351 | 6.0664 | 6.0977 | 6.1289 | 6.1602 | 6.1914 | 6.2227 | 6.2539 | 6.2852 | 6.3165 | 6.3477 | 6.379 | 6.4102 | 6.4415
4 | 0 | 0.089 | 0.178 | 0.267 | 0.356 | 0.445 | 0.534 | 0.623 | 0.712 | 0.801 | 0.89 | 0.868 | 0.846 | 0.824 | 0.802 | 0.78 | 0.782 | 0.784 | 0.786 | 0.788 | 0.79 | 0.781 | 0.772 | 0.763 | 0.754 | 0.745 | 0.736 | 0.727 | 0.718 | 0.709 | 0.7 | 0.712 | 0.724 | 0.736 | 0.748 | 0.76 | 0.772 | 0.784 | 0.796 | 0.808 | 0.82 | 0.832 | 0.844 | 0.856 | 0.868 | 0.88 | 0.896 | 0.912 | 0.928 | 0.944 | 0.96 | 0.976 | 0.992 | 1.008 | 1.024 | 1.04 | 1.056 | 1.072 | 1.088 | 1.104 | 1.12 | 1.1733 | 1.2267 | 1.28 | 1.3333 | 1.3867 | 1.44 | 1.4933 | 1.5467 | 1.6 | 1.6533 | 1.7067 | 1.76 | 1.8133 | 1.8667 | 1.92 | 1.9733 | 2.0267 | 2.08 | 2.1333 | 2.1867 | 2.24 | 2.2933 | 2.3467 | 2.4 | 2.4533 | 2.5067 | 2.56 | 2.6133 | 2.6667 | 2.72 | 2.7737 | 2.8273 | 2.881 | 2.9347 | 2.9883 | 3.042 | 3.0957 | 3.1493 | 3.203 | 3.2567 | 3.3103 | 3.364 | 3.4177 | 3.4713 | 3.525 | 3.5787 | 3.6323 | 3.686 | 3.7397 | 3.7933 | 3.847 | 3.9007 | 3.9543 | 4.008 | 4.0617 | 4.1153 | 4.169 | 4.2227 | 4.2763 | 4.33 | 4.373 | 4.416 | 4.459 | 4.502 | 4.545 | 4.588 | 4.631 | 4.674 | 4.717 | 4.76 | 4.803 | 4.846 | 4.889 | 4.932 | 4.975 | 5.018 | 5.061 | 5.104 | 5.147 | 5.19 | 5.233 | 5.276 | 5.319 | 5.362 | 5.405 | 5.448 | 5.491 | 5.534 | 5.577 | 5.62 | 5.652 | 5.684 | 5.716 | 5.748 | 5.78 | 5.812 | 5.844 | 5.876 | 5.908 | 5.94 | 5.972 | 6.004 | 6.036 | 6.068 | 6.1 | 6.132 | 6.164 | 6.196 | 6.228 | 6.26 | 6.292 | 6.324 | 6.356 | 6.388 | 6.42 | 6.452 | 6.484 | 6.516 | 6.548 | 6.58
4.05 | 0 | 0.0915 | 0.183 | 0.2745 | 0.366 | 0.4575 | 0.549 | 0.6405 | 0.732 | 0.8235 | 0.915 | 0.89245 | 0.8699 | 0.84735 | 0.8248 | 0.80225 | 0.8038 | 0.80535 | 0.8069 | 0.80845 | 0.81 | 0.80097 | 0.79195 | 0.78292 | 0.7739 | 0.76487 | 0.75585 | 0.74682 | 0.7378 | 0.72877 | 0.71975 | 0.73227 | 0.74478 | 0.7573 | 0.76982 | 0.78233 | 0.79485 | 0.80737 | 0.81988 | 0.8324 | 0.84492 | 0.85743 | 0.86995 | 0.88247 | 0.89498 | 0.9075 | 0.924 | 0.9405 | 0.957 | 0.9735 | 0.99 | 1.0065 | 1.023 | 1.0395 | 1.056 | 1.0725 | 1.089 | 1.1055 | 1.122 | 1.1385 | 1.155 | 1.2103 | 1.2656 | 1.321 | 1.3763 | 1.4316 | 1.4869 | 1.5423 | 1.5976 | 1.6529 | 1.7083 | 1.7636 | 1.8189 | 1.8742 | 1.9296 | 1.9849 | 2.0402 | 2.0955 | 2.1509 | 2.2062 | 2.2615 | 2.3168 | 2.3721 | 2.4275 | 2.4828 | 2.5381 | 2.5934 | 2.6488 | 2.7041 | 2.7594 | 2.8148 | 2.8701 | 2.9255 | 2.9808 | 3.0362 | 3.0915 | 3.1469 | 3.2022 | 3.2576 | 3.3129 | 3.3683 | 3.4236 | 3.479 | 3.5343 | 3.5896 | 3.645 | 3.7003 | 3.7557 | 3.811 | 3.8664 | 3.9217 | 3.9771 | 4.0324 | 4.0878 | 4.1432 | 4.1985 | 4.2538 | 4.3092 | 4.3646 | 4.4199 | 4.4752 | 4.5196 | 4.564 | 4.6083 | 4.6527 | 4.697 | 4.7413 | 4.7857 | 4.83 | 4.8744 | 4.9188 | 4.9631 | 5.0075 | 5.0518 | 5.0961 | 5.1405 | 5.1848 | 5.2292 | 5.2736 | 5.3179 | 5.3623 | 5.4066 | 5.4509 | 5.4953 | 5.5396 | 5.584 | 5.6284 | 5.6727 | 5.7171 | 5.7614 | 5.8057 | 5.8387 | 5.8716 | 5.9046 | 5.9375 | 5.9705 | 6.0034 | 6.0363 | 6.0693 | 6.1022 | 6.1352 | 6.1681 | 6.2011 | 6.234 | 6.2669 | 6.2999 | 6.3328 | 6.3658 | 6.3987 | 6.4316 | 6.4646 | 6.4975 | 6.5305 | 6.5634 | 6.5964 | 6.6293 | 6.6622 | 6.6952 | 6.7281 | 6.7611 | 6.794
4.1 | 0 | 0.094 | 0.188 | 0.282 | 0.376 | 0.47 | 0.564 | 0.658 | 0.752 | 0.846 | 0.94 | 0.9169 | 0.8938 | 0.8707 | 0.8476 | 0.8245 | 0.8256 | 0.8267 | 0.8278 | 0.8289 | 0.83 | 0.82095 | 0.8119 | 0.80285 | 0.7938 | 0.78475 | 0.7757 | 0.76665 | 0.7576 | 0.74855 | 0.7395 | 0.75253 | 0.76557 | 0.7786 | 0.79163 | 0.80467 | 0.8177 | 0.83073 | 0.84377 | 0.8568 | 0.86983 | 0.88287 | 0.8959 | 0.90893 | 0.92197 | 0.935 | 0.952 | 0.969 | 0.986 | 1.003 | 1.02 | 1.037 | 1.054 | 1.071 | 1.088 | 1.105 | 1.122 | 1.139 | 1.156 | 1.173 | 1.19 | 1.2473 | 1.3046 | 1.3619 | 1.4193 | 1.4766 | 1.5339 | 1.5912 | 1.6485 | 1.7059 | 1.7632 | 1.8205 | 1.8778 | 1.9351 | 1.9924 | 2.0497 | 2.1071 | 2.1644 | 2.2217 | 2.279 | 2.3363 | 2.3937 | 2.451 | 2.5083 | 2.5656 | 2.6229 | 2.6802 | 2.7376 | 2.7949 | 2.8522 | 2.9095 | 2.9665 | 3.0236 | 3.0806 | 3.1376 | 3.1947 | 3.2517 | 3.3087 | 3.3658 | 3.4228 | 3.4798 | 3.5369 | 3.5939 | 3.6509 | 3.708 | 3.765 | 3.822 | 3.8791 | 3.9361 | 3.9931 | 4.0502 | 4.1072 | 4.1642 | 4.2213 | 4.2783 | 4.3353 | 4.3924 | 4.4494 | 4.5064 | 4.5635 | 4.6205 | 4.6662 | 4.7119 | 4.7576 | 4.8033 | 4.849 | 4.8947 | 4.9404 | 4.9861 | 5.0318 | 5.0775 | 5.1232 | 5.1689 | 5.2146 | 5.2603 | 5.306 | 5.3517 | 5.3974 | 5.4431 | 5.4888 | 5.5345 | 5.5802 | 5.6259 | 5.6716 | 5.7173 | 5.763 | 5.8087 | 5.8544 | 5.9001 | 5.9458 | 5.9915 | 6.0254 | 6.0593 | 6.0931 | 6.127 | 6.1609 | 6.1948 | 6.2287 | 6.2626 | 6.2965 | 6.3303 | 6.3642 | 6.3981 | 6.432 | 6.4659 | 6.4997 | 6.5336 | 6.5675 | 6.6014 | 6.6353 | 6.6692 | 6.7031 | 6.7369 | 6.7708 | 6.8047 | 6.8386 | 6.8725 | 6.9063 | 6.9402 | 6.9741 | 7.008
4.15 | 0 | 0.0965 | 0.193 | 0.2895 | 0.386 | 0.4825 | 0.579 | 0.6755 | 0.772 | 0.8685 | 0.965 | 0.94135 | 0.9177 | 0.89405 | 0.8704 | 0.84675 | 0.8474 | 0.84805 | 0.8487 | 0.84935 | 0.85 | 0.84093 | 0.83185 | 0.82278 | 0.8137 | 0.80463 | 0.79555 | 0.78648 | 0.7774 | 0.76833 | 0.75925 | 0.7728 | 0.78635 | 0.7999 | 0.81345 | 0.827 | 0.84055 | 0.8541 | 0.86765 | 0.8812 | 0.89475 | 0.9083 | 0.92185 | 0.9354 | 0.94895 | 0.9625 | 0.98 | 0.9975 | 1.015 | 1.0325 | 1.05 | 1.0675 | 1.085 | 1.1025 | 1.12 | 1.1375 | 1.155 | 1.1725 | 1.19 | 1.2075 | 1.225 | 1.2843 | 1.3436 | 1.4029 | 1.4622 | 1.5215 | 1.5809 | 1.6402 | 1.6995 | 1.7588 | 1.8181 | 1.8774 | 1.9367 | 1.996 | 2.0553 | 2.1146 | 2.1739 | 2.2332 | 2.2925 | 2.3519 | 2.4112 | 2.4705 | 2.5298 | 2.5891 | 2.6484 | 2.7077 | 2.767 | 2.8263 | 2.8856 | 2.9449 | 3.0042 | 3.063 | 3.1217 | 3.1804 | 3.2391 | 3.2978 | 3.3565 | 3.4153 | 3.474 | 3.5327 | 3.5914 | 3.6501 | 3.7088 | 3.7676 | 3.8263 | 3.885 | 3.9437 | 4.0024 | 4.0611 | 4.1199 | 4.1786 | 4.2373 | 4.296 | 4.3547 | 4.4135 | 4.4722 | 4.5309 | 4.5896 | 4.6483 | 4.707 | 4.7657 | 4.8128 | 4.8598 | 4.9069 | 4.9539 | 5.001 | 5.048 | 5.0951 | 5.1421 | 5.1892 | 5.2363 | 5.2833 | 5.3304 | 5.3774 | 5.4245 | 5.4715 | 5.5186 | 5.5656 | 5.6127 | 5.6597 | 5.7068 | 5.7538 | 5.8008 | 5.8479 | 5.8949 | 5.942 | 5.989 | 6.0361 | 6.0831 | 6.1302 | 6.1772 | 6.2121 | 6.2469 | 6.2817 | 6.3166 | 6.3514 | 6.3862 | 6.421 | 6.4558 | 6.4907 | 6.5255 | 6.5603 | 6.5952 | 6.63 | 6.6648 | 6.6996 | 6.7344 | 6.7693 | 6.8041 | 6.8389 | 6.8738 | 6.9086 | 6.9434 | 6.9782 | 7.013 | 7.0479 | 7.0827 | 7.1175 | 7.1524 | 7.1872 | 7.222
4.2 | 0 | 0.099 | 0.198 | 0.297 | 0.396 | 0.495 | 0.594 | 0.693 | 0.792 | 0.891 | 0.99 | 0.9658 | 0.9416 | 0.9174 | 0.8932 | 0.869 | 0.8692 | 0.8694 | 0.8696 | 0.8698 | 0.87 | 0.8609 | 0.8518 | 0.8427 | 0.8336 | 0.8245 | 0.8154 | 0.8063 | 0.7972 | 0.7881 | 0.779 | 0.79307 | 0.80713 | 0.8212 | 0.83527 | 0.84933 | 0.8634 | 0.87747 | 0.89153 | 0.9056 | 0.91967 | 0.93373 | 0.9478 | 0.96187 | 0.97593 | 0.99 | 1.008 | 1.026 | 1.044 | 1.062 | 1.08 | 1.098 | 1.116 | 1.134 | 1.152 | 1.17 | 1.188 | 1.206 | 1.224 | 1.242 | 1.26 | 1.3213 | 1.3826 | 1.4439 | 1.5052 | 1.5665 | 1.6278 | 1.6891 | 1.7504 | 1.8117 | 1.873 | 1.9343 | 1.9956 | 2.0569 | 2.1182 | 2.1795 | 2.2408 | 2.3021 | 2.3634 | 2.4247 | 2.486 | 2.5473 | 2.6086 | 2.6699 | 2.7312 | 2.7925 | 2.8538 | 2.9151 | 2.9764 | 3.0377 | 3.099 | 3.1594 | 3.2198 | 3.2802 | 3.3406 | 3.401 | 3.4614 | 3.5218 | 3.5822 | 3.6426 | 3.703 | 3.7634 | 3.8238 | 3.8842 | 3.9446 | 4.005 | 4.0654 | 4.1258 | 4.1862 | 4.2466 | 4.307 | 4.3674 | 4.4278 | 4.4882 | 4.5486 | 4.609 | 4.6694 | 4.7298 | 4.7902 | 4.8506 | 4.911 | 4.9594 | 5.0078 | 5.0562 | 5.1046 | 5.153 | 5.2014 | 5.2498 | 5.2982 | 5.3466 | 5.395 | 5.4434 | 5.4918 | 5.5402 | 5.5886 | 5.637 | 5.6854 | 5.7338 | 5.7822 | 5.8306 | 5.879 | 5.9274 | 5.9758 | 6.0242 | 6.0726 | 6.121 | 6.1694 | 6.2178 | 6.2662 | 6.3146 | 6.363 | 6.3988 | 6.4345 | 6.4703 | 6.5061 | 6.5418 | 6.5776 | 6.6134 | 6.6491 | 6.6849 | 6.7207 | 6.7564 | 6.7922 | 6.828 | 6.8637 | 6.8995 | 6.9353 | 6.971 | 7.0068 | 7.0426 | 7.0783 | 7.1141 | 7.1499 | 7.1856 | 7.2214 | 7.2572 | 7.2929 | 7.3287 | 7.3645 | 7.4002 | 7.436
4.25 | 0 | 0.1015 | 0.203 | 0.3045 | 0.406 | 0.5075 | 0.609 | 0.7105 | 0.812 | 0.9135 | 1.015 | 0.99025 | 0.9655 | 0.94075 | 0.916 | 0.89125 | 0.891 | 0.89075 | 0.8905 | 0.89025 | 0.89 | 0.88087 | 0.87175 | 0.86262 | 0.8535 | 0.84437 | 0.83525 | 0.82612 | 0.817 | 0.80788 | 0.79875 | 0.81333 | 0.82792 | 0.8425 | 0.85708 | 0.87167 | 0.88625 | 0.90083 | 0.91542 | 0.93 | 0.94458 | 0.95917 | 0.97375 | 0.98833 | 1.0029 | 1.0175 | 1.036 | 1.0545 | 1.073 | 1.0915 | 1.11 | 1.1285 | 1.147 | 1.1655 | 1.184 | 1.2025 | 1.221 | 1.2395 | 1.258 | 1.2765 | 1.295 | 1.3583 | 1.4216 | 1.4849 | 1.5482 | 1.6115 | 1.6747 | 1.738 | 1.8013 | 1.8646 | 1.9279 | 1.9912 | 2.0545 | 2.1178 | 2.1811 | 2.2444 | 2.3077 | 2.371 | 2.4343 | 2.4975 | 2.5608 | 2.6241 | 2.6874 | 2.7507 | 2.814 | 2.8773 | 2.9406 | 3.0039 | 3.0672 | 3.1305 | 3.1938 | 3.2558 | 3.3179 | 3.38 | 3.4421 | 3.5042 | 3.5663 | 3.6283 | 3.6904 | 3.7525 | 3.8146 | 3.8767 | 3.9388 | 4.0008 | 4.0629 | 4.125 | 4.1871 | 4.2492 | 4.3113 | 4.3733 | 4.4354 | 4.4975 | 4.5596 | 4.6217 | 4.6837 | 4.7458 | 4.8079 | 4.87 | 4.9321 | 4.9942 | 5.0563 | 5.106 | 5.1558 | 5.2055 | 5.2553 | 5.305 | 5.3548 | 5.4045 | 5.4543 | 5.504 | 5.5537 | 5.6035 | 5.6532 | 5.703 | 5.7527 | 5.8025 | 5.8522 | 5.902 | 5.9517 | 6.0015 | 6.0512 | 6.101 | 6.1508 | 6.2005 | 6.2503 | 6.3 | 6.3498 | 6.3995 | 6.4493 | 6.499 | 6.5488 | 6.5855 | 6.6222 | 6.6589 | 6.6956 | 6.7323 | 6.769 | 6.8057 | 6.8424 | 6.8791 | 6.9158 | 6.9525 | 6.9893 | 7.026 | 7.0627 | 7.0994 | 7.1361 | 7.1728 | 7.2095 | 7.2462 | 7.2829 | 7.3196 | 7.3563 | 7.393 | 7.4298 | 7.4665 | 7.5032 | 7.5399 | 7.5766 | 7.6133 | 7.65
4.3 | 0 | 0.104 | 0.208 | 0.312 | 0.416 | 0.52 | 0.624 | 0.728 | 0.832 | 0.936 | 1.04 | 1.0147 | 0.9894 | 0.9641 | 0.9388 | 0.9135 | 0.9128 | 0.9121 | 0.9114 | 0.9107 | 0.91 | 0.90085 | 0.8917 | 0.88255 | 0.8734 | 0.86425 | 0.8551 | 0.84595 | 0.8368 | 0.82765 | 0.8185 | 0.8336 | 0.8487 | 0.8638 | 0.8789 | 0.894 | 0.9091 | 0.9242 | 0.9393 | 0.9544 | 0.9695 | 0.9846 | 0.9997 | 1.0148 | 1.0299 | 1.045 | 1.064 | 1.083 | 1.102 | 1.121 | 1.14 | 1.159 | 1.178 | 1.197 | 1.216 | 1.235 | 1.254 | 1.273 | 1.292 | 1.311 | 1.33 | 1.3953 | 1.4606 | 1.5258 | 1.5911 | 1.6564 | 1.7217 | 1.787 | 1.8523 | 1.9176 | 1.9828 | 2.0481 | 2.1134 | 2.1787 | 2.244 | 2.3093 | 2.3745 | 2.4398 | 2.5051 | 2.5704 | 2.6357 | 2.701 | 2.7662 | 2.8315 | 2.8968 | 2.9621 | 3.0274 | 3.0926 | 3.1579 | 3.2232 | 3.2885 | 3.3523 | 3.416 | 3.4798 | 3.5436 | 3.6073 | 3.6711 | 3.7349 | 3.7986 | 3.8624 | 3.9262 | 3.9899 | 4.0537 | 4.1175 | 4.1812 | 4.245 | 4.3088 | 4.3725 | 4.4363 | 4.5001 | 4.5638 | 4.6276 | 4.6914 | 4.7551 | 4.8189 | 4.8827 | 4.9464 | 5.0102 | 5.074 | 5.1377 | 5.2015 | 5.2526 | 5.3037 | 5.3548 | 5.4059 | 5.457 | 5.5081 | 5.5592 | 5.6103 | 5.6614 | 5.7125 | 5.7636 | 5.8147 | 5.8658 | 5.9169 | 5.968 | 6.0191 | 6.0702 | 6.1213 | 6.1724 | 6.2235 | 6.2746 | 6.3257 | 6.3768 | 6.4279 | 6.479 | 6.5301 | 6.5812 | 6.6323 | 6.6834 | 6.7345 | 6.7721 | 6.8098 | 6.8475 | 6.8851 | 6.9227 | 6.9604 | 6.9981 | 7.0357 | 7.0733 | 7.111 | 7.1486 | 7.1863 | 7.224 | 7.2616 | 7.2992 | 7.3369 | 7.3746 | 7.4122 | 7.4498 | 7.4875 | 7.5252 | 7.5628 | 7.6005 | 7.6381 | 7.6757 | 7.7134 | 7.7511 | 7.7887 | 7.8263 | 7.864
4.35 | 0 | 0.1065 | 0.213 | 0.3195 | 0.426 | 0.5325 | 0.639 | 0.7455 | 0.852 | 0.9585 | 1.065 | 1.0392 | 1.0133 | 0.98745 | 0.9616 | 0.93575 | 0.9346 | 0.93345 | 0.9323 | 0.93115 | 0.93 | 0.92083 | 0.91165 | 0.90248 | 0.8933 | 0.88413 | 0.87495 | 0.86577 | 0.8566 | 0.84742 | 0.83825 | 0.85387 | 0.86948 | 0.8851 | 0.90072 | 0.91633 | 0.93195 | 0.94757 | 0.96318 | 0.9788 | 0.99442 | 1.01 | 1.0256 | 1.0413 | 1.0569 | 1.0725 | 1.092 | 1.1115 | 1.131 | 1.1505 | 1.17 | 1.1895 | 1.209 | 1.2285 | 1.248 | 1.2675 | 1.287 | 1.3065 | 1.326 | 1.3455 | 1.365 | 1.4323 | 1.4995 | 1.5668 | 1.6341 | 1.7014 | 1.7687 | 1.8359 | 1.9032 | 1.9705 | 2.0377 | 2.105 | 2.1723 | 2.2396 | 2.3068 | 2.3741 | 2.4414 | 2.5087 | 2.576 | 2.6432 | 2.7105 | 2.7778 | 2.8451 | 2.9123 | 2.9796 | 3.0469 | 3.1141 | 3.1814 | 3.2487 | 3.316 | 3.3832 | 3.4487 | 3.5141 | 3.5796 | 3.645 | 3.7105 | 3.7759 | 3.8414 | 3.9068 | 3.9723 | 4.0377 | 4.1032 | 4.1687 | 4.2341 | 4.2995 | 4.365 | 4.4305 | 4.4959 | 4.5614 | 4.6268 | 4.6922 | 4.7577 | 4.8232 | 4.8886 | 4.954 | 5.0195 | 5.085 | 5.1504 | 5.2158 | 5.2813 | 5.3468 | 5.3992 | 5.4516 | 5.5041 | 5.5565 | 5.609 | 5.6615 | 5.7139 | 5.7664 | 5.8188 | 5.8712 | 5.9237 | 5.9761 | 6.0286 | 6.0811 | 6.1335 | 6.186 | 6.2384 | 6.2908 | 6.3433 | 6.3957 | 6.4482 | 6.5007 | 6.5531 | 6.6056 | 6.658 | 6.7104 | 6.7629 | 6.8153 | 6.8678 | 6.9203 | 6.9588 | 6.9974 | 7.036 | 7.0746 | 7.1132 | 7.1518 | 7.1904 | 7.229 | 7.2676 | 7.3062 | 7.3448 | 7.3834 | 7.4219 | 7.4605 | 7.4991 | 7.5377 | 7.5763 | 7.6149 | 7.6535 | 7.6921 | 7.7307 | 7.7693 | 7.8079 | 7.8464 | 7.885 | 7.9236 | 7.9622 | 8.0008 | 8.0394 | 8.078
4.4 | 0 | 0.109 | 0.218 | 0.327 | 0.436 | 0.545 | 0.654 | 0.763 | 0.872 | 0.981 | 1.09 | 1.0636 | 1.0372 | 1.0108 | 0.9844 | 0.958 | 0.9564 | 0.9548 | 0.9532 | 0.9516 | 0.95 | 0.9408 | 0.9316 | 0.9224 | 0.9132 | 0.904 | 0.8948 | 0.8856 | 0.8764 | 0.8672 | 0.858 | 0.87413 | 0.89027 | 0.9064 | 0.92253 | 0.93867 | 0.9548 | 0.97093 | 0.98707 | 1.0032 | 1.0193 | 1.0355 | 1.0516 | 1.0677 | 1.0839 | 1.1 | 1.12 | 1.14 | 1.16 | 1.18 | 1.2 | 1.22 | 1.24 | 1.26 | 1.28 | 1.3 | 1.32 | 1.34 | 1.36 | 1.38 | 1.4 | 1.4693 | 1.5385 | 1.6078 | 1.6771 | 1.7463 | 1.8156 | 1.8849 | 1.9541 | 2.0234 | 2.0927 | 2.1619 | 2.2312 | 2.3005 | 2.3697 | 2.439 | 2.5083 | 2.5775 | 2.6468 | 2.7161 | 2.7853 | 2.8546 | 2.9239 | 2.9931 | 3.0624 | 3.1317 | 3.2009 | 3.2702 | 3.3395 | 3.4087 | 3.478 | 3.5451 | 3.6123 | 3.6794 | 3.7465 | 3.8137 | 3.8808 | 3.9479 | 4.0151 | 4.0822 | 4.1493 | 4.2165 | 4.2836 | 4.3507 | 4.4179 | 4.485 | 4.5521 | 4.6193 | 4.6864 | 4.7535 | 4.8207 | 4.8878 | 4.9549 | 5.0221 | 5.0892 | 5.1563 | 5.2235 | 5.2906 | 5.3577 | 5.4249 | 5.492 | 5.5458 | 5.5996 | 5.6534 | 5.7072 | 5.761 | 5.8148 | 5.8686 | 5.9224 | 5.9762 | 6.03 | 6.0838 | 6.1376 | 6.1914 | 6.2452 | 6.299 | 6.3528 | 6.4066 | 6.4604 | 6.5142 | 6.568 | 6.6218 | 6.6756 | 6.7294 | 6.7832 | 6.837 | 6.8908 | 6.9446 | 6.9984 | 7.0522 | 7.106 | 7.1455 | 7.1851 | 7.2246 | 7.2641 | 7.3037 | 7.3432 | 7.3827 | 7.4223 | 7.4618 | 7.5013 | 7.5409 | 7.5804 | 7.6199 | 7.6595 | 7.699 | 7.7385 | 7.7781 | 7.8176 | 7.8571 | 7.8967 | 7.9362 | 7.9757 | 8.0153 | 8.0548 | 8.0943 | 8.1339 | 8.1734 | 8.2129 | 8.2525 | 8.292
4.45 | 0 | 0.1115 | 0.223 | 0.3345 | 0.446 | 0.5575 | 0.669 | 0.7805 | 0.892 | 1.0035 | 1.115 | 1.088 | 1.0611 | 1.0341 | 1.0072 | 0.98025 | 0.9782 | 0.97615 | 0.9741 | 0.97205 | 0.97 | 0.96078 | 0.95155 | 0.94232 | 0.9331 | 0.92388 | 0.91465 | 0.90543 | 0.8962 | 0.88697 | 0.87775 | 0.8944 | 0.91105 | 0.9277 | 0.94435 | 0.961 | 0.97765 | 0.9943 | 1.011 | 1.0276 | 1.0442 | 1.0609 | 1.0776 | 1.0942 | 1.1108 | 1.1275 | 1.148 | 1.1685 | 1.189 | 1.2095 | 1.23 | 1.2505 | 1.271 | 1.2915 | 1.312 | 1.3325 | 1.353 | 1.3735 | 1.394 | 1.4145 | 1.435 | 1.5063 | 1.5775 | 1.6488 | 1.72 | 1.7913 | 1.8625 | 1.9338 | 2.0051 | 2.0763 | 2.1476 | 2.2188 | 2.2901 | 2.3614 | 2.4326 | 2.5039 | 2.5751 | 2.6464 | 2.7176 | 2.7889 | 2.8602 | 2.9314 | 3.0027 | 3.0739 | 3.1452 | 3.2165 | 3.2877 | 3.359 | 3.4302 | 3.5015 | 3.5728 | 3.6416 | 3.7104 | 3.7792 | 3.848 | 3.9168 | 3.9857 | 4.0545 | 4.1233 | 4.1921 | 4.2609 | 4.3297 | 4.3986 | 4.4674 | 4.5362 | 4.605 | 4.6738 | 4.7426 | 4.8114 | 4.8803 | 4.9491 | 5.0179 | 5.0867 | 5.1555 | 5.2244 | 5.2932 | 5.362 | 5.4308 | 5.4996 | 5.5684 | 5.6372 | 5.6924 | 5.7476 | 5.8027 | 5.8579 | 5.913 | 5.9681 | 6.0233 | 6.0785 | 6.1336 | 6.1887 | 6.2439 | 6.2991 | 6.3542 | 6.4093 | 6.4645 | 6.5197 | 6.5748 | 6.63 | 6.6851 | 6.7402 | 6.7954 | 6.8506 | 6.9057 | 6.9608 | 7.016 | 7.0712 | 7.1263 | 7.1814 | 7.2366 | 7.2918 | 7.3322 | 7.3727 | 7.4132 | 7.4536 | 7.4941 | 7.5346 | 7.5751 | 7.6155 | 7.656 | 7.6965 | 7.737 | 7.7774 | 7.8179 | 7.8584 | 7.8989 | 7.9394 | 7.9798 | 8.0203 | 8.0608 | 8.1013 | 8.1417 | 8.1822 | 8.2227 | 8.2631 | 8.3036 | 8.3441 | 8.3846 | 8.4251 | 8.4655 | 8.506
4.5 | 0 | 0.114 | 0.228 | 0.342 | 0.456 | 0.57 | 0.684 | 0.798 | 0.912 | 1.026 | 1.14 | 1.1125 | 1.085 | 1.0575 | 1.03 | 1.0025 | 1 | 0.9975 | 0.995 | 0.9925 | 0.99 | 0.98075 | 0.9715 | 0.96225 | 0.953 | 0.94375 | 0.9345 | 0.92525 | 0.916 | 0.90675 | 0.8975 | 0.91467 | 0.93183 | 0.949 | 0.96617 | 0.98333 | 1.0005 | 1.0177 | 1.0348 | 1.052 | 1.0692 | 1.0863 | 1.1035 | 1.1207 | 1.1378 | 1.155 | 1.176 | 1.197 | 1.218 | 1.239 | 1.26 | 1.281 | 1.302 | 1.323 | 1.344 | 1.365 | 1.386 | 1.407 | 1.428 | 1.449 | 1.47 | 1.5433 | 1.6165 | 1.6898 | 1.763 | 1.8362 | 1.9095 | 1.9828 | 2.056 | 2.1292 | 2.2025 | 2.2757 | 2.349 | 2.4223 | 2.4955 | 2.5688 | 2.642 | 2.7153 | 2.7885 | 2.8617 | 2.935 | 3.0082 | 3.0815 | 3.1547 | 3.228 | 3.3013 | 3.3745 | 3.4478 | 3.521 | 3.5943 | 3.6675 | 3.738 | 3.8085 | 3.879 | 3.9495 | 4.02 | 4.0905 | 4.161 | 4.2315 | 4.302 | 4.3725 | 4.443 | 4.5135 | 4.584 | 4.6545 | 4.725 | 4.7955 | 4.866 | 4.9365 | 5.007 | 5.0775 | 5.148 | 5.2185 | 5.289 | 5.3595 | 5.43 | 5.5005 | 5.571 | 5.6415 | 5.712 | 5.7825 | 5.839 | 5.8955 | 5.952 | 6.0085 | 6.065 | 6.1215 | 6.178 | 6.2345 | 6.291 | 6.3475 | 6.404 | 6.4605 | 6.517 | 6.5735 | 6.63 | 6.6865 | 6.743 | 6.7995 | 6.856 | 6.9125 | 6.969 | 7.0255 | 7.082 | 7.1385 | 7.195 | 7.2515 | 7.308 | 7.3645 | 7.421 | 7.4775 | 7.5189 | 7.5603 | 7.6018 | 7.6432 | 7.6846 | 7.726 | 7.7674 | 7.8088 | 7.8502 | 7.8917 | 7.9331 | 7.9745 | 8.0159 | 8.0573 | 8.0988 | 8.1402 | 8.1816 | 8.223 | 8.2644 | 8.3058 | 8.3473 | 8.3887 | 8.4301 | 8.4715 | 8.5129 | 8.5543 | 8.5958 | 8.6372 | 8.6786 | 8.72
4.55 | 0 | 0.1165 | 0.233 | 0.3495 | 0.466 | 0.5825 | 0.699 | 0.8155 | 0.932 | 1.0485 | 1.165 | 1.1369 | 1.1089 | 1.0809 | 1.0528 | 1.0248 | 1.0218 | 1.0189 | 1.0159 | 1.013 | 1.01 | 1.0007 | 0.99145 | 0.98218 | 0.9729 | 0.96362 | 0.95435 | 0.94507 | 0.9358 | 0.92653 | 0.91725 | 0.93493 | 0.95262 | 0.9703 | 0.98798 | 1.0057 | 1.0233 | 1.041 | 1.0587 | 1.0764 | 1.0941 | 1.1118 | 1.1295 | 1.1471 | 1.1648 | 1.1825 | 1.204 | 1.2255 | 1.247 | 1.2685 | 1.29 | 1.3115 | 1.333 | 1.3545 | 1.376 | 1.3975 | 1.419 | 1.4405 | 1.462 | 1.4835 | 1.505 | 1.5802 | 1.6555 | 1.7307 | 1.806 | 1.8812 | 1.9565 | 2.0317 | 2.1069 | 2.1822 | 2.2574 | 2.3327 | 2.4079 | 2.4831 | 2.5584 | 2.6336 | 2.7089 | 2.7841 | 2.8594 | 2.9346 | 3.0098 | 3.0851 | 3.1603 | 3.2356 | 3.3108 | 3.386 | 3.4613 | 3.5365 | 3.6118 | 3.687 | 3.7622 | 3.8344 | 3.9066 | 3.9788 | 4.051 | 4.1232 | 4.1954 | 4.2675 | 4.3397 | 4.4119 | 4.4841 | 4.5563 | 4.6284 | 4.7006 | 4.7728 | 4.845 | 4.9172 | 4.9894 | 5.0616 | 5.1337 | 5.2059 | 5.2781 | 5.3503 | 5.4225 | 5.4947 | 5.5668 | 5.639 | 5.7112 | 5.7834 | 5.8556 | 5.9277 | 5.9856 | 6.0434 | 6.1013 | 6.1592 | 6.217 | 6.2748 | 6.3327 | 6.3906 | 6.4484 | 6.5062 | 6.5641 | 6.622 | 6.6798 | 6.7377 | 6.7955 | 6.8533 | 6.9112 | 6.9691 | 7.0269 | 7.0847 | 7.1426 | 7.2005 | 7.2583 | 7.3162 | 7.374 | 7.4318 | 7.4897 | 7.5476 | 7.6054 | 7.6632 | 7.7056 | 7.748 | 7.7903 | 7.8327 | 7.875 | 7.9174 | 7.9598 | 8.0021 | 8.0445 | 8.0868 | 8.1292 | 8.1715 | 8.2139 | 8.2563 | 8.2986 | 8.341 | 8.3833 | 8.4257 | 8.4681 | 8.5104 | 8.5528 | 8.5951 | 8.6375 | 8.6799 | 8.7222 | 8.7646 | 8.8069 | 8.8493 | 8.8916 | 8.934
4.6 | 0 | 0.119 | 0.238 | 0.357 | 0.476 | 0.595 | 0.714 | 0.833 | 0.952 | 1.071 | 1.19 | 1.1614 | 1.1328 | 1.1042 | 1.0756 | 1.047 | 1.0436 | 1.0402 | 1.0368 | 1.0334 | 1.03 | 1.0207 | 1.0114 | 1.0021 | 0.9928 | 0.9835 | 0.9742 | 0.9649 | 0.9556 | 0.9463 | 0.937 | 0.9552 | 0.9734 | 0.9916 | 1.0098 | 1.028 | 1.0462 | 1.0644 | 1.0826 | 1.1008 | 1.119 | 1.1372 | 1.1554 | 1.1736 | 1.1918 | 1.21 | 1.232 | 1.254 | 1.276 | 1.298 | 1.32 | 1.342 | 1.364 | 1.386 | 1.408 | 1.43 | 1.452 | 1.474 | 1.496 | 1.518 | 1.54 | 1.6172 | 1.6945 | 1.7717 | 1.8489 | 1.9262 | 2.0034 | 2.0806 | 2.1579 | 2.2351 | 2.3123 | 2.3896 | 2.4668 | 2.544 | 2.6213 | 2.6985 | 2.7757 | 2.853 | 2.9302 | 3.0074 | 3.0847 | 3.1619 | 3.2391 | 3.3164 | 3.3936 | 3.4708 | 3.5481 | 3.6253 | 3.7025 | 3.7798 | 3.857 | 3.9309 | 4.0047 | 4.0786 | 4.1525 | 4.2263 | 4.3002 | 4.3741 | 4.4479 | 4.5218 | 4.5957 | 4.6695 | 4.7434 | 4.8173 | 4.8911 | 4.965 | 5.0389 | 5.1127 | 5.1866 | 5.2605 | 5.3343 | 5.4082 | 5.4821 | 5.5559 | 5.6298 | 5.7037 | 5.7775 | 5.8514 | 5.9253 | 5.9991 | 6.073 | 6.1322 | 6.1914 | 6.2506 | 6.3098 | 6.369 | 6.4282 | 6.4874 | 6.5466 | 6.6058 | 6.665 | 6.7242 | 6.7834 | 6.8426 | 6.9018 | 6.961 | 7.0202 | 7.0794 | 7.1386 | 7.1978 | 7.257 | 7.3162 | 7.3754 | 7.4346 | 7.4938 | 7.553 | 7.6122 | 7.6714 | 7.7306 | 7.7898 | 7.849 | 7.8923 | 7.9356 | 7.9789 | 8.0222 | 8.0655 | 8.1088 | 8.1521 | 8.1954 | 8.2387 | 8.282 | 8.3253 | 8.3686 | 8.4119 | 8.4552 | 8.4985 | 8.5418 | 8.5851 | 8.6284 | 8.6717 | 8.715 | 8.7583 | 8.8016 | 8.8449 | 8.8882 | 8.9315 | 8.9748 | 9.0181 | 9.0614 | 9.1047 | 9.148
4.65 | 0 | 0.1215 | 0.243 | 0.3645 | 0.486 | 0.6075 | 0.729 | 0.8505 | 0.972 | 1.0935 | 1.215 | 1.1859 | 1.1567 | 1.1276 | 1.0984 | 1.0693 | 1.0654 | 1.0615 | 1.0577 | 1.0538 | 1.05 | 1.0407 | 1.0313 | 1.022 | 1.0127 | 1.0034 | 0.99405 | 0.98472 | 0.9754 | 0.96608 | 0.95675 | 0.97547 | 0.99418 | 1.0129 | 1.0316 | 1.0503 | 1.0691 | 1.0878 | 1.1065 | 1.1252 | 1.1439 | 1.1626 | 1.1813 | 1.2001 | 1.2188 | 1.2375 | 1.26 | 1.2825 | 1.305 | 1.3275 | 1.35 | 1.3725 | 1.395 | 1.4175 | 1.44 | 1.4625 | 1.485 | 1.5075 | 1.53 | 1.5525 | 1.575 | 1.6542 | 1.7334 | 1.8127 | 1.8919 | 1.9711 | 2.0503 | 2.1296 | 2.2088 | 2.288 | 2.3672 | 2.4465 | 2.5257 | 2.6049 | 2.6841 | 2.7634 | 2.8426 | 2.9218 | 3.0011 | 3.0803 | 3.1595 | 3.2387 | 3.318 | 3.3972 | 3.4764 | 3.5556 | 3.6349 | 3.7141 | 3.7933 | 3.8725 | 3.9518 | 4.0273 | 4.1029 | 4.1784 | 4.2539 | 4.3295 | 4.4051 | 4.4806 | 4.5561 | 4.6317 | 4.7073 | 4.7828 | 4.8583 | 4.9339 | 5.0095 | 5.085 | 5.1605 | 5.2361 | 5.3117 | 5.3872 | 5.4627 | 5.5383 | 5.6139 | 5.6894 | 5.7649 | 5.8405 | 5.9161 | 5.9916 | 6.0671 | 6.1427 | 6.2183 | 6.2788 | 6.3393 | 6.3999 | 6.4604 | 6.521 | 6.5816 | 6.6421 | 6.7027 | 6.7632 | 6.8238 | 6.8843 | 6.9448 | 7.0054 | 7.0659 | 7.1265 | 7.1871 | 7.2476 | 7.3082 | 7.3687 | 7.4292 | 7.4898 | 7.5503 | 7.6109 | 7.6715 | 7.732 | 7.7926 | 7.8531 | 7.9136 | 7.9742 | 8.0348 | 8.079 | 8.1232 | 8.1675 | 8.2117 | 8.256 | 8.3002 | 8.3444 | 8.3887 | 8.4329 | 8.4772 | 8.5214 | 8.5656 | 8.6099 | 8.6541 | 8.6984 | 8.7426 | 8.7869 | 8.8311 | 8.8753 | 8.9196 | 8.9638 | 9.0081 | 9.0523 | 9.0966 | 9.1408 | 9.185 | 9.2293 | 9.2735 | 9.3178 | 9.362
4.7 | 0 | 0.124 | 0.248 | 0.372 | 0.496 | 0.62 | 0.744 | 0.868 | 0.992 | 1.116 | 1.24 | 1.2103 | 1.1806 | 1.1509 | 1.1212 | 1.0915 | 1.0872 | 1.0829 | 1.0786 | 1.0743 | 1.07 | 1.0607 | 1.0513 | 1.0419 | 1.0326 | 1.0232 | 1.0139 | 1.0046 | 0.9952 | 0.98585 | 0.9765 | 0.99573 | 1.015 | 1.0342 | 1.0534 | 1.0727 | 1.0919 | 1.1111 | 1.1304 | 1.1496 | 1.1688 | 1.1881 | 1.2073 | 1.2265 | 1.2458 | 1.265 | 1.288 | 1.311 | 1.334 | 1.357 | 1.38 | 1.403 | 1.426 | 1.449 | 1.472 | 1.495 | 1.518 | 1.541 | 1.564 | 1.587 | 1.61 | 1.6912 | 1.7724 | 1.8537 | 1.9349 | 2.0161 | 2.0973 | 2.1785 | 2.2597 | 2.3409 | 2.4222 | 2.5034 | 2.5846 | 2.6658 | 2.747 | 2.8283 | 2.9095 | 2.9907 | 3.0719 | 3.1531 | 3.2343 | 3.3155 | 3.3968 | 3.478 | 3.5592 | 3.6404 | 3.7216 | 3.8028 | 3.8841 | 3.9653 | 4.0465 | 4.1237 | 4.201 | 4.2782 | 4.3554 | 4.4327 | 4.5099 | 4.5871 | 4.6644 | 4.7416 | 4.8188 | 4.8961 | 4.9733 | 5.0505 | 5.1278 | 5.205 | 5.2822 | 5.3595 | 5.4367 | 5.5139 | 5.5912 | 5.6684 | 5.7456 | 5.8229 | 5.9001 | 5.9773 | 6.0546 | 6.1318 | 6.209 | 6.2863 | 6.3635 | 6.4254 | 6.4873 | 6.5492 | 6.6111 | 6.673 | 6.7349 | 6.7968 | 6.8587 | 6.9206 | 6.9825 | 7.0444 | 7.1063 | 7.1682 | 7.2301 | 7.292 | 7.3539 | 7.4158 | 7.4777 | 7.5396 | 7.6015 | 7.6634 | 7.7253 | 7.7872 | 7.8491 | 7.911 | 7.9729 | 8.0348 | 8.0967 | 8.1586 | 8.2205 | 8.2657 | 8.3109 | 8.356 | 8.4012 | 8.4464 | 8.4916 | 8.5368 | 8.582 | 8.6272 | 8.6723 | 8.7175 | 8.7627 | 8.8079 | 8.8531 | 8.8983 | 8.9434 | 8.9886 | 9.0338 | 9.079 | 9.1242 | 9.1693 | 9.2145 | 9.2597 | 9.3049 | 9.3501 | 9.3953 | 9.4405 | 9.4856 | 9.5308 | 9.576
4.75 | 0 | 0.1265 | 0.253 | 0.3795 | 0.506 | 0.6325 | 0.759 | 0.8855 | 1.012 | 1.1385 | 1.265 | 1.2348 | 1.2045 | 1.1743 | 1.144 | 1.1138 | 1.109 | 1.1042 | 1.0995 | 1.0947 | 1.09 | 1.0806 | 1.0713 | 1.0619 | 1.0525 | 1.0431 | 1.0337 | 1.0244 | 1.015 | 1.0056 | 0.99625 | 1.016 | 1.0357 | 1.0555 | 1.0753 | 1.095 | 1.1147 | 1.1345 | 1.1542 | 1.174 | 1.1938 | 1.2135 | 1.2332 | 1.253 | 1.2728 | 1.2925 | 1.316 | 1.3395 | 1.363 | 1.3865 | 1.41 | 1.4335 | 1.457 | 1.4805 | 1.504 | 1.5275 | 1.551 | 1.5745 | 1.598 | 1.6215 | 1.645 | 1.7282 | 1.8114 | 1.8946 | 1.9778 | 2.061 | 2.1442 | 2.2275 | 2.3107 | 2.3939 | 2.4771 | 2.5603 | 2.6435 | 2.7267 | 2.8099 | 2.8931 | 2.9763 | 3.0595 | 3.1427 | 3.226 | 3.3092 | 3.3924 | 3.4756 | 3.5588 | 3.642 | 3.7252 | 3.8084 | 3.8916 | 3.9748 | 4.058 | 4.1413 | 4.2202 | 4.2991 | 4.378 | 4.4569 | 4.5358 | 4.6147 | 4.6937 | 4.7726 | 4.8515 | 4.9304 | 5.0093 | 5.0883 | 5.1672 | 5.2461 | 5.325 | 5.4039 | 5.4828 | 5.5617 | 5.6407 | 5.7196 | 5.7985 | 5.8774 | 5.9563 | 6.0352 | 6.1142 | 6.1931 | 6.272 | 6.3509 | 6.4298 | 6.5088 | 6.572 | 6.6353 | 6.6985 | 6.7618 | 6.825 | 6.8883 | 6.9515 | 7.0148 | 7.078 | 7.1413 | 7.2045 | 7.2678 | 7.331 | 7.3943 | 7.4575 | 7.5207 | 7.584 | 7.6472 | 7.7105 | 7.7737 | 7.837 | 7.9002 | 7.9635 | 8.0267 | 8.09 | 8.1532 | 8.2165 | 8.2797 | 8.343 | 8.4062 | 8.4524 | 8.4985 | 8.5446 | 8.5907 | 8.6369 | 8.683 | 8.7291 | 8.7752 | 8.8214 | 8.8675 | 8.9136 | 8.9597 | 9.0059 | 9.052 | 9.0981 | 9.1442 | 9.1904 | 9.2365 | 9.2826 | 9.3287 | 9.3749 | 9.421 | 9.4671 | 9.5132 | 9.5594 | 9.6055 | 9.6516 | 9.6977 | 9.7439 | 9.79
4.8 | 0 | 0.129 | 0.258 | 0.387 | 0.516 | 0.645 | 0.774 | 0.903 | 1.032 | 1.161 | 1.29 | 1.2592 | 1.2284 | 1.1976 | 1.1668 | 1.136 | 1.1308 | 1.1256 | 1.1204 | 1.1152 | 1.11 | 1.1006 | 1.0912 | 1.0818 | 1.0724 | 1.063 | 1.0536 | 1.0442 | 1.0348 | 1.0254 | 1.016 | 1.0363 | 1.0565 | 1.0768 | 1.0971 | 1.1173 | 1.1376 | 1.1579 | 1.1781 | 1.1984 | 1.2187 | 1.2389 | 1.2592 | 1.2795 | 1.2997 | 1.32 | 1.344 | 1.368 | 1.392 | 1.416 | 1.44 | 1.464 | 1.488 | 1.512 | 1.536 | 1.56 | 1.584 | 1.608 | 1.632 | 1.656 | 1.68 | 1.7652 | 1.8504 | 1.9356 | 2.0208 | 2.106 | 2.1912 | 2.2764 | 2.3616 | 2.4468 | 2.532 | 2.6172 | 2.7024 | 2.7876 | 2.8728 | 2.958 | 3.0432 | 3.1284 | 3.2136 | 3.2988 | 3.384 | 3.4692 | 3.5544 | 3.6396 | 3.7248 | 3.81 | 3.8952 | 3.9804 | 4.0656 | 4.1508 | 4.236 | 4.3166 | 4.3972 | 4.4778 | 4.5584 | 4.639 | 4.7196 | 4.8002 | 4.8808 | 4.9614 | 5.042 | 5.1226 | 5.2032 | 5.2838 | 5.3644 | 5.445 | 5.5256 | 5.6062 | 5.6868 | 5.7674 | 5.848 | 5.9286 | 6.0092 | 6.0898 | 6.1704 | 6.251 | 6.3316 | 6.4122 | 6.4928 | 6.5734 | 6.654 | 6.7186 | 6.7832 | 6.8478 | 6.9124 | 6.977 | 7.0416 | 7.1062 | 7.1708 | 7.2354 | 7.3 | 7.3646 | 7.4292 | 7.4938 | 7.5584 | 7.623 | 7.6876 | 7.7522 | 7.8168 | 7.8814 | 7.946 | 8.0106 | 8.0752 | 8.1398 | 8.2044 | 8.269 | 8.3336 | 8.3982 | 8.4628 | 8.5274 | 8.592 | 8.6391 | 8.6861 | 8.7332 | 8.7803 | 8.8273 | 8.8744 | 8.9215 | 8.9685 | 9.0156 | 9.0627 | 9.1097 | 9.1568 | 9.2039 | 9.2509 | 9.298 | 9.3451 | 9.3921 | 9.4392 | 9.4863 | 9.5333 | 9.5804 | 9.6275 | 9.6745 | 9.7216 | 9.7687 | 9.8157 | 9.8628 | 9.9099 | 9.9569 | 10.004
4.85 | 0 | 0.1315 | 0.263 | 0.3945 | 0.526 | 0.6575 | 0.789 | 0.9205 | 1.052 | 1.1835 | 1.315 | 1.2836 | 1.2523 | 1.2209 | 1.1896 | 1.1583 | 1.1526 | 1.1469 | 1.1413 | 1.1357 | 1.13 | 1.1206 | 1.1112 | 1.1017 | 1.0923 | 1.0829 | 1.0735 | 1.064 | 1.0546 | 1.0452 | 1.0357 | 1.0565 | 1.0773 | 1.0981 | 1.1189 | 1.1397 | 1.1604 | 1.1812 | 1.202 | 1.2228 | 1.2436 | 1.2644 | 1.2852 | 1.3059 | 1.3267 | 1.3475 | 1.372 | 1.3965 | 1.421 | 1.4455 | 1.47 | 1.4945 | 1.519 | 1.5435 | 1.568 | 1.5925 | 1.617 | 1.6415 | 1.666 | 1.6905 | 1.715 | 1.8022 | 1.8894 | 1.9766 | 2.0638 | 2.151 | 2.2382 | 2.3253 | 2.4125 | 2.4997 | 2.5869 | 2.6741 | 2.7613 | 2.8485 | 2.9357 | 3.0229 | 3.1101 | 3.1973 | 3.2845 | 3.3716 | 3.4588 | 3.546 | 3.6332 | 3.7204 | 3.8076 | 3.8948 | 3.982 | 4.0692 | 4.1564 | 4.2436 | 4.3308 | 4.413 | 4.4953 | 4.5776 | 4.6599 | 4.7422 | 4.8244 | 4.9067 | 4.989 | 5.0713 | 5.1536 | 5.2359 | 5.3182 | 5.4004 | 5.4827 | 5.565 | 5.6473 | 5.7296 | 5.8118 | 5.8941 | 5.9764 | 6.0587 | 6.141 | 6.2233 | 6.3056 | 6.3878 | 6.4701 | 6.5524 | 6.6347 | 6.717 | 6.7992 | 6.8652 | 6.9311 | 6.9971 | 7.063 | 7.129 | 7.195 | 7.2609 | 7.3269 | 7.3928 | 7.4588 | 7.5247 | 7.5907 | 7.6566 | 7.7226 | 7.7885 | 7.8544 | 7.9204 | 7.9863 | 8.0523 | 8.1182 | 8.1842 | 8.2501 | 8.3161 | 8.382 | 8.448 | 8.5139 | 8.5799 | 8.6458 | 8.7118 | 8.7777 | 8.8258 | 8.8738 | 8.9218 | 8.9698 | 9.0178 | 9.0658 | 9.1138 | 9.1618 | 9.2098 | 9.2578 | 9.3058 | 9.3538 | 9.4019 | 9.4499 | 9.4979 | 9.5459 | 9.5939 | 9.6419 | 9.6899 | 9.7379 | 9.7859 | 9.8339 | 9.8819 | 9.9299 | 9.978 | 10.026 | 10.074 | 10.122 | 10.17 | 10.218
4.9 | 0 | 0.134 | 0.268 | 0.402 | 0.536 | 0.67 | 0.804 | 0.938 | 1.072 | 1.206 | 1.34 | 1.3081 | 1.2762 | 1.2443 | 1.2124 | 1.1805 | 1.1744 | 1.1683 | 1.1622 | 1.1561 | 1.15 | 1.1405 | 1.1311 | 1.1217 | 1.1122 | 1.1027 | 1.0933 | 1.0838 | 1.0744 | 1.065 | 1.0555 | 1.0768 | 1.0981 | 1.1194 | 1.1407 | 1.162 | 1.1833 | 1.2046 | 1.2259 | 1.2472 | 1.2685 | 1.2898 | 1.3111 | 1.3324 | 1.3537 | 1.375 | 1.4 | 1.425 | 1.45 | 1.475 | 1.5 | 1.525 | 1.55 | 1.575 | 1.6 | 1.625 | 1.65 | 1.675 | 1.7 | 1.725 | 1.75 | 1.8392 | 1.9284 | 2.0175 | 2.1067 | 2.1959 | 2.2851 | 2.3743 | 2.4635 | 2.5526 | 2.6418 | 2.731 | 2.8202 | 2.9094 | 2.9986 | 3.0878 | 3.1769 | 3.2661 | 3.3553 | 3.4445 | 3.5337 | 3.6229 | 3.712 | 3.8012 | 3.8904 | 3.9796 | 4.0688 | 4.1579 | 4.2471 | 4.3363 | 4.4255 | 4.5095 | 4.5934 | 4.6774 | 4.7614 | 4.8453 | 4.9293 | 5.0133 | 5.0972 | 5.1812 | 5.2652 | 5.3491 | 5.4331 | 5.5171 | 5.601 | 5.685 | 5.769 | 5.8529 | 5.9369 | 6.0209 | 6.1048 | 6.1888 | 6.2728 | 6.3567 | 6.4407 | 6.5247 | 6.6086 | 6.6926 | 6.7766 | 6.8605 | 6.9445 | 7.0118 | 7.0791 | 7.1464 | 7.2137 | 7.281 | 7.3483 | 7.4156 | 7.4829 | 7.5502 | 7.6175 | 7.6848 | 7.7521 | 7.8194 | 7.8867 | 7.954 | 8.0213 | 8.0886 | 8.1559 | 8.2232 | 8.2905 | 8.3578 | 8.4251 | 8.4924 | 8.5597 | 8.627 | 8.6943 | 8.7616 | 8.8289 | 8.8962 | 8.9635 | 9.0124 | 9.0614 | 9.1104 | 9.1593 | 9.2082 | 9.2572 | 9.3062 | 9.3551 | 9.404 | 9.453 | 9.502 | 9.5509 | 9.5998 | 9.6488 | 9.6977 | 9.7467 | 9.7957 | 9.8446 | 9.8935 | 9.9425 | 9.9915 | 10.0404 | 10.0893 | 10.1383 | 10.1873 | 10.2362 | 10.2851 | 10.3341 | 10.3831 | 10.432
4.95 | 0 | 0.1365 | 0.273 | 0.4095 | 0.546 | 0.6825 | 0.819 | 0.9555 | 1.092 | 1.2285 | 1.365 | 1.3325 | 1.3001 | 1.2676 | 1.2352 | 1.2027 | 1.1962 | 1.1897 | 1.1831 | 1.1765 | 1.17 | 1.1605 | 1.151 | 1.1416 | 1.1321 | 1.1226 | 1.1132 | 1.1037 | 1.0942 | 1.0847 | 1.0753 | 1.0971 | 1.1189 | 1.1407 | 1.1625 | 1.1843 | 1.2062 | 1.228 | 1.2498 | 1.2716 | 1.2934 | 1.3152 | 1.3371 | 1.3589 | 1.3807 | 1.4025 | 1.428 | 1.4535 | 1.479 | 1.5045 | 1.53 | 1.5555 | 1.581 | 1.6065 | 1.632 | 1.6575 | 1.683 | 1.7085 | 1.734 | 1.7595 | 1.785 | 1.8762 | 1.9673 | 2.0585 | 2.1497 | 2.2409 | 2.3321 | 2.4232 | 2.5144 | 2.6056 | 2.6968 | 2.7879 | 2.8791 | 2.9703 | 3.0614 | 3.1526 | 3.2438 | 3.335 | 3.4261 | 3.5173 | 3.6085 | 3.6997 | 3.7908 | 3.882 | 3.9732 | 4.0644 | 4.1555 | 4.2467 | 4.3379 | 4.4291 | 4.5202 | 4.6059 | 4.6916 | 4.7772 | 4.8628 | 4.9485 | 5.0342 | 5.1198 | 5.2054 | 5.2911 | 5.3768 | 5.4624 | 5.548 | 5.6337 | 5.7194 | 5.805 | 5.8906 | 5.9763 | 6.062 | 6.1476 | 6.2332 | 6.3189 | 6.4046 | 6.4902 | 6.5758 | 6.6615 | 6.7472 | 6.8328 | 6.9184 | 7.0041 | 7.0898 | 7.1584 | 7.2271 | 7.2957 | 7.3643 | 7.433 | 7.5016 | 7.5703 | 7.639 | 7.7076 | 7.7763 | 7.8449 | 7.9135 | 7.9822 | 8.0509 | 8.1195 | 8.1882 | 8.2568 | 8.3255 | 8.3941 | 8.4627 | 8.5314 | 8.6 | 8.6687 | 8.7373 | 8.806 | 8.8747 | 8.9433 | 9.012 | 9.0806 | 9.1493 | 9.1991 | 9.249 | 9.2989 | 9.3488 | 9.3987 | 9.4486 | 9.4985 | 9.5484 | 9.5983 | 9.6482 | 9.6981 | 9.7479 | 9.7978 | 9.8477 | 9.8976 | 9.9475 | 9.9974 | 10.0473 | 10.0972 | 10.1471 | 10.197 | 10.2469 | 10.2968 | 10.3467 | 10.3965 | 10.4464 | 10.4963 | 10.5462 | 10.5961 | 10.646
5 | 0 | 0.139 | 0.278 | 0.417 | 0.556 | 0.695 | 0.834 | 0.973 | 1.112 | 1.251 | 1.39 | 1.357 | 1.324 | 1.291 | 1.258 | 1.225 | 1.218 | 1.211 | 1.204 | 1.197 | 1.19 | 1.1805 | 1.171 | 1.1615 | 1.152 | 1.1425 | 1.133 | 1.1235 | 1.114 | 1.1045 | 1.095 | 1.1173 | 1.1397 | 1.162 | 1.1843 | 1.2067 | 1.229 | 1.2513 | 1.2737 | 1.296 | 1.3183 | 1.3407 | 1.363 | 1.3853 | 1.4077 | 1.43 | 1.456 | 1.482 | 1.508 | 1.534 | 1.56 | 1.586 | 1.612 | 1.638 | 1.664 | 1.69 | 1.716 | 1.742 | 1.768 | 1.794 | 1.82 | 1.9132 | 2.0063 | 2.0995 | 2.1927 | 2.2858 | 2.379 | 2.4722 | 2.5653 | 2.6585 | 2.7517 | 2.8448 | 2.938 | 3.0312 | 3.1243 | 3.2175 | 3.3107 | 3.4038 | 3.497 | 3.5902 | 3.6833 | 3.7765 | 3.8697 | 3.9628 | 4.056 | 4.1492 | 4.2423 | 4.3355 | 4.4287 | 4.5218 | 4.615 | 4.7023 | 4.7897 | 4.877 | 4.9643 | 5.0517 | 5.139 | 5.2263 | 5.3137 | 5.401 | 5.4883 | 5.5757 | 5.663 | 5.7503 | 5.8377 | 5.925 | 6.0123 | 6.0997 | 6.187 | 6.2743 | 6.3617 | 6.449 | 6.5363 | 6.6237 | 6.711 | 6.7983 | 6.8857 | 6.973 | 7.0603 | 7.1477 | 7.235 | 7.305 | 7.375 | 7.445 | 7.515 | 7.585 | 7.655 | 7.725 | 7.795 | 7.865 | 7.935 | 8.005 | 8.075 | 8.145 | 8.215 | 8.285 | 8.355 | 8.425 | 8.495 | 8.565 | 8.635 | 8.705 | 8.775 | 8.845 | 8.915 | 8.985 | 9.055 | 9.125 | 9.195 | 9.265 | 9.335 | 9.3858 | 9.4367 | 9.4875 | 9.5383 | 9.5892 | 9.64 | 9.6908 | 9.7417 | 9.7925 | 9.8433 | 9.8942 | 9.945 | 9.9958 | 10.0467 | 10.0975 | 10.1483 | 10.1992 | 10.25 | 10.3008 | 10.3517 | 10.4025 | 10.4533 | 10.5042 | 10.555 | 10.6058 | 10.6567 | 10.7075 | 10.7583 | 10.8092 | 10.86
5.05 | 0 | 0.1415 | 0.283 | 0.4245 | 0.566 | 0.7075 | 0.849 | 0.9905 | 1.132 | 1.2735 | 1.415 | 1.3815 | 1.3479 | 1.3143 | 1.2808 | 1.2472 | 1.2398 | 1.2324 | 1.2249 | 1.2174 | 1.21 | 1.2005 | 1.1909 | 1.1814 | 1.1719 | 1.1624 | 1.1528 | 1.1433 | 1.1338 | 1.1243 | 1.1147 | 1.1376 | 1.1604 | 1.1833 | 1.2062 | 1.229 | 1.2518 | 1.2747 | 1.2975 | 1.3204 | 1.3433 | 1.3661 | 1.3889 | 1.4118 | 1.4346 | 1.4575 | 1.484 | 1.5105 | 1.537 | 1.5635 | 1.59 | 1.6165 | 1.643 | 1.6695 | 1.696 | 1.7225 | 1.749 | 1.7755 | 1.802 | 1.8285 | 1.855 | 1.9502 | 2.0453 | 2.1405 | 2.2356 | 2.3308 | 2.4259 | 2.5211 | 2.6163 | 2.7114 | 2.8066 | 2.9017 | 2.9969 | 3.0921 | 3.1872 | 3.2824 | 3.3775 | 3.4727 | 3.5678 | 3.663 | 3.7582 | 3.8533 | 3.9485 | 4.0436 | 4.1388 | 4.234 | 4.3291 | 4.4243 | 4.5194 | 4.6146 | 4.7097 | 4.7988 | 4.8878 | 4.9768 | 5.0658 | 5.1548 | 5.2439 | 5.3329 | 5.4219 | 5.5109 | 5.5999 | 5.6889 | 5.7779 | 5.867 | 5.956 | 6.045 | 6.134 | 6.223 | 6.3121 | 6.4011 | 6.4901 | 6.5791 | 6.6681 | 6.7571 | 6.8461 | 6.9352 | 7.0242 | 7.1132 | 7.2022 | 7.2912 | 7.3803 | 7.4516 | 7.5229 | 7.5943 | 7.6657 | 7.737 | 7.8083 | 7.8797 | 7.9511 | 8.0224 | 8.0938 | 8.1651 | 8.2364 | 8.3078 | 8.3791 | 8.4505 | 8.5219 | 8.5932 | 8.6646 | 8.7359 | 8.8072 | 8.8786 | 8.9499 | 9.0213 | 9.0927 | 9.164 | 9.2354 | 9.3067 | 9.378 | 9.4494 | 9.5207 | 9.5725 | 9.6243 | 9.6761 | 9.7279 | 9.7796 | 9.8314 | 9.8832 | 9.935 | 9.9867 | 10.0385 | 10.0903 | 10.142 | 10.1938 | 10.2456 | 10.2974 | 10.3491 | 10.4009 | 10.4527 | 10.5045 | 10.5563 | 10.608 | 10.6598 | 10.7116 | 10.7634 | 10.8151 | 10.8669 | 10.9187 | 10.9704 | 11.0222 | 11.074
5.1 | 0 | 0.144 | 0.288 | 0.432 | 0.576 | 0.72 | 0.864 | 1.008 | 1.152 | 1.296 | 1.44 | 1.4059 | 1.3718 | 1.3377 | 1.3036 | 1.2695 | 1.2616 | 1.2537 | 1.2458 | 1.2379 | 1.23 | 1.2205 | 1.2109 | 1.2013 | 1.1918 | 1.1823 | 1.1727 | 1.1631 | 1.1536 | 1.1441 | 1.1345 | 1.1579 | 1.1812 | 1.2046 | 1.228 | 1.2513 | 1.2747 | 1.2981 | 1.3214 | 1.3448 | 1.3682 | 1.3915 | 1.4149 | 1.4383 | 1.4616 | 1.485 | 1.512 | 1.539 | 1.566 | 1.593 | 1.62 | 1.647 | 1.674 | 1.701 | 1.728 | 1.755 | 1.782 | 1.809 | 1.836 | 1.863 | 1.89 | 1.9871 | 2.0843 | 2.1814 | 2.2786 | 2.3758 | 2.4729 | 2.5701 | 2.6672 | 2.7643 | 2.8615 | 2.9587 | 3.0558 | 3.153 | 3.2501 | 3.3472 | 3.4444 | 3.5415 | 3.6387 | 3.7359 | 3.833 | 3.9301 | 4.0273 | 4.1245 | 4.2216 | 4.3187 | 4.4159 | 4.513 | 4.6102 | 4.7073 | 4.8045 | 4.8952 | 4.9859 | 5.0766 | 5.1673 | 5.258 | 5.3487 | 5.4394 | 5.5301 | 5.6208 | 5.7115 | 5.8022 | 5.8929 | 5.9836 | 6.0743 | 6.165 | 6.2557 | 6.3464 | 6.4371 | 6.5278 | 6.6185 | 6.7092 | 6.7999 | 6.8906 | 6.9813 | 7.072 | 7.1627 | 7.2534 | 7.3441 | 7.4348 | 7.5255 | 7.5982 | 7.6709 | 7.7436 | 7.8163 | 7.889 | 7.9617 | 8.0344 | 8.1071 | 8.1798 | 8.2525 | 8.3252 | 8.3979 | 8.4706 | 8.5433 | 8.616 | 8.6887 | 8.7614 | 8.8341 | 8.9068 | 8.9795 | 9.0522 | 9.1249 | 9.1976 | 9.2703 | 9.343 | 9.4157 | 9.4884 | 9.5611 | 9.6338 | 9.7065 | 9.7592 | 9.8119 | 9.8646 | 9.9174 | 9.9701 | 10.0228 | 10.0755 | 10.1282 | 10.1809 | 10.2337 | 10.2864 | 10.3391 | 10.3918 | 10.4445 | 10.4972 | 10.55 | 10.6027 | 10.6554 | 10.7081 | 10.7608 | 10.8135 | 10.8663 | 10.919 | 10.9717 | 11.0244 | 11.0771 | 11.1298 | 11.1826 | 11.2353 | 11.288
5.15 | 0 | 0.1465 | 0.293 | 0.4395 | 0.586 | 0.7325 | 0.879 | 1.0255 | 1.172 | 1.3185 | 1.465 | 1.4304 | 1.3957 | 1.3611 | 1.3264 | 1.2917 | 1.2834 | 1.2751 | 1.2667 | 1.2584 | 1.25 | 1.2404 | 1.2308 | 1.2213 | 1.2117 | 1.2021 | 1.1925 | 1.183 | 1.1734 | 1.1638 | 1.1542 | 1.1781 | 1.202 | 1.2259 | 1.2498 | 1.2737 | 1.2975 | 1.3214 | 1.3453 | 1.3692 | 1.3931 | 1.417 | 1.4408 | 1.4647 | 1.4886 | 1.5125 | 1.54 | 1.5675 | 1.595 | 1.6225 | 1.65 | 1.6775 | 1.705 | 1.7325 | 1.76 | 1.7875 | 1.815 | 1.8425 | 1.87 | 1.8975 | 1.925 | 2.0241 | 2.1233 | 2.2224 | 2.3216 | 2.4207 | 2.5198 | 2.619 | 2.7181 | 2.8173 | 2.9164 | 3.0156 | 3.1147 | 3.2138 | 3.313 | 3.4121 | 3.5113 | 3.6104 | 3.7096 | 3.8087 | 3.9078 | 4.007 | 4.1061 | 4.2053 | 4.3044 | 4.4035 | 4.5027 | 4.6018 | 4.701 | 4.8001 | 4.8993 | 4.9916 | 5.084 | 5.1764 | 5.2688 | 5.3612 | 5.4535 | 5.5459 | 5.6383 | 5.7307 | 5.8231 | 5.9155 | 6.0079 | 6.1002 | 6.1926 | 6.285 | 6.3774 | 6.4698 | 6.5621 | 6.6545 | 6.7469 | 6.8393 | 6.9317 | 7.0241 | 7.1165 | 7.2088 | 7.3012 | 7.3936 | 7.486 | 7.5784 | 7.6707 | 7.7448 | 7.8189 | 7.8929 | 7.9669 | 8.041 | 8.1151 | 8.1891 | 8.2631 | 8.3372 | 8.4113 | 8.4853 | 8.5594 | 8.6334 | 8.7074 | 8.7815 | 8.8555 | 8.9296 | 9.0037 | 9.0777 | 9.1517 | 9.2258 | 9.2998 | 9.3739 | 9.448 | 9.522 | 9.596 | 9.6701 | 9.7441 | 9.8182 | 9.8923 | 9.9459 | 9.9996 | 10.0532 | 10.1069 | 10.1605 | 10.2142 | 10.2679 | 10.3215 | 10.3752 | 10.4288 | 10.4825 | 10.5361 | 10.5898 | 10.6435 | 10.6971 | 10.7508 | 10.8044 | 10.8581 | 10.9118 | 10.9654 | 11.0191 | 11.0727 | 11.1264 | 11.18 | 11.2337 | 11.2874 | 11.341 | 11.3947 | 11.4483 | 11.502
5.2 | 0 | 0.149 | 0.298 | 0.447 | 0.596 | 0.745 | 0.894 | 1.043 | 1.192 | 1.341 | 1.49 | 1.4548 | 1.4196 | 1.3844 | 1.3492 | 1.314 | 1.3052 | 1.2964 | 1.2876 | 1.2788 | 1.27 | 1.2604 | 1.2508 | 1.2412 | 1.2316 | 1.222 | 1.2124 | 1.2028 | 1.1932 | 1.1836 | 1.174 | 1.1984 | 1.2228 | 1.2472 | 1.2716 | 1.296 | 1.3204 | 1.3448 | 1.3692 | 1.3936 | 1.418 | 1.4424 | 1.4668 | 1.4912 | 1.5156 | 1.54 | 1.568 | 1.596 | 1.624 | 1.652 | 1.68 | 1.708 | 1.736 | 1.764 | 1.792 | 1.82 | 1.848 | 1.876 | 1.904 | 1.932 | 1.96 | 2.0611 | 2.1623 | 2.2634 | 2.3645 | 2.4657 | 2.5668 | 2.6679 | 2.7691 | 2.8702 | 2.9713 | 3.0725 | 3.1736 | 3.2747 | 3.3759 | 3.477 | 3.5781 | 3.6793 | 3.7804 | 3.8815 | 3.9827 | 4.0838 | 4.1849 | 4.2861 | 4.3872 | 4.4883 | 4.5895 | 4.6906 | 4.7917 | 4.8929 | 4.994 | 5.0881 | 5.1821 | 5.2762 | 5.3703 | 5.4643 | 5.5584 | 5.6525 | 5.7465 | 5.8406 | 5.9347 | 6.0287 | 6.1228 | 6.2169 | 6.3109 | 6.405 | 6.4991 | 6.5931 | 6.6872 | 6.7813 | 6.8753 | 6.9694 | 7.0635 | 7.1575 | 7.2516 | 7.3457 | 7.4397 | 7.5338 | 7.6279 | 7.7219 | 7.816 | 7.8914 | 7.9668 | 8.0422 | 8.1176 | 8.193 | 8.2684 | 8.3438 | 8.4192 | 8.4946 | 8.57 | 8.6454 | 8.7208 | 8.7962 | 8.8716 | 8.947 | 9.0224 | 9.0978 | 9.1732 | 9.2486 | 9.324 | 9.3994 | 9.4748 | 9.5502 | 9.6256 | 9.701 | 9.7764 | 9.8518 | 9.9272 | 10.0026 | 10.078 | 10.1326 | 10.1872 | 10.2418 | 10.2964 | 10.351 | 10.4056 | 10.4602 | 10.5148 | 10.5694 | 10.624 | 10.6786 | 10.7332 | 10.7878 | 10.8424 | 10.897 | 10.9516 | 11.0062 | 11.0608 | 11.1154 | 11.17 | 11.2246 | 11.2792 | 11.3338 | 11.3884 | 11.443 | 11.4976 | 11.5522 | 11.6068 | 11.6614 | 11.716
5.25 | 0 | 0.1515 | 0.303 | 0.4545 | 0.606 | 0.7575 | 0.909 | 1.0605 | 1.212 | 1.3635 | 1.515 | 1.4792 | 1.4435 | 1.4078 | 1.372 | 1.3362 | 1.327 | 1.3177 | 1.3085 | 1.2993 | 1.29 | 1.2804 | 1.2708 | 1.2611 | 1.2515 | 1.2419 | 1.2323 | 1.2226 | 1.213 | 1.2034 | 1.1938 | 1.2187 | 1.2436 | 1.2685 | 1.2934 | 1.3183 | 1.3433 | 1.3682 | 1.3931 | 1.418 | 1.4429 | 1.4678 | 1.4928 | 1.5177 | 1.5426 | 1.5675 | 1.596 | 1.6245 | 1.653 | 1.6815 | 1.71 | 1.7385 | 1.767 | 1.7955 | 1.824 | 1.8525 | 1.881 | 1.9095 | 1.938 | 1.9665 | 1.995 | 2.0981 | 2.2012 | 2.3044 | 2.4075 | 2.5106 | 2.6138 | 2.7169 | 2.82 | 2.9231 | 3.0263 | 3.1294 | 3.2325 | 3.3356 | 3.4388 | 3.5419 | 3.645 | 3.7481 | 3.8512 | 3.9544 | 4.0575 | 4.1606 | 4.2637 | 4.3669 | 4.47 | 4.5731 | 4.6762 | 4.7794 | 4.8825 | 4.9856 | 5.0888 | 5.1845 | 5.2802 | 5.376 | 5.4718 | 5.5675 | 5.6632 | 5.759 | 5.8548 | 5.9505 | 6.0462 | 6.142 | 6.2378 | 6.3335 | 6.4292 | 6.525 | 6.6208 | 6.7165 | 6.8122 | 6.908 | 7.0038 | 7.0995 | 7.1952 | 7.291 | 7.3868 | 7.4825 | 7.5782 | 7.674 | 7.7698 | 7.8655 | 7.9612 | 8.038 | 8.1148 | 8.1915 | 8.2683 | 8.345 | 8.4217 | 8.4985 | 8.5753 | 8.652 | 8.7287 | 8.8055 | 8.8823 | 8.959 | 9.0358 | 9.1125 | 9.1892 | 9.266 | 9.3428 | 9.4195 | 9.4962 | 9.573 | 9.6497 | 9.7265 | 9.8033 | 9.88 | 9.9567 | 10.0335 | 10.1103 | 10.187 | 10.2637 | 10.3193 | 10.3748 | 10.4304 | 10.4859 | 10.5415 | 10.597 | 10.6525 | 10.7081 | 10.7636 | 10.8192 | 10.8747 | 10.9302 | 10.9858 | 11.0413 | 11.0969 | 11.1524 | 11.208 | 11.2635 | 11.319 | 11.3746 | 11.4301 | 11.4857 | 11.5412 | 11.5968 | 11.6523 | 11.7078 | 11.7634 | 11.8189 | 11.8745 | 11.93
5.3 | 0 | 0.154 | 0.308 | 0.462 | 0.616 | 0.77 | 0.924 | 1.078 | 1.232 | 1.386 | 1.54 | 1.5037 | 1.4674 | 1.4311 | 1.3948 | 1.3585 | 1.3488 | 1.3391 | 1.3294 | 1.3197 | 1.31 | 1.3003 | 1.2907 | 1.2811 | 1.2714 | 1.2617 | 1.2521 | 1.2425 | 1.2328 | 1.2231 | 1.2135 | 1.2389 | 1.2644 | 1.2898 | 1.3152 | 1.3407 | 1.3661 | 1.3915 | 1.417 | 1.4424 | 1.4678 | 1.4933 | 1.5187 | 1.5441 | 1.5696 | 1.595 | 1.624 | 1.653 | 1.682 | 1.711 | 1.74 | 1.769 | 1.798 | 1.827 | 1.856 | 1.885 | 1.914 | 1.943 | 1.972 | 2.001 | 2.03 | 2.1351 | 2.2402 | 2.3453 | 2.4505 | 2.5556 | 2.6607 | 2.7658 | 2.8709 | 2.976 | 3.0812 | 3.1863 | 3.2914 | 3.3965 | 3.5016 | 3.6067 | 3.7119 | 3.817 | 3.9221 | 4.0272 | 4.1323 | 4.2374 | 4.3426 | 4.4477 | 4.5528 | 4.6579 | 4.763 | 4.8681 | 4.9733 | 5.0784 | 5.1835 | 5.2809 | 5.3784 | 5.4758 | 5.5732 | 5.6707 | 5.7681 | 5.8655 | 5.963 | 6.0604 | 6.1578 | 6.2553 | 6.3527 | 6.4501 | 6.5476 | 6.645 | 6.7424 | 6.8399 | 6.9373 | 7.0347 | 7.1322 | 7.2296 | 7.327 | 7.4245 | 7.5219 | 7.6193 | 7.7168 | 7.8142 | 7.9116 | 8.0091 | 8.1065 | 8.1846 | 8.2627 | 8.3408 | 8.4189 | 8.497 | 8.5751 | 8.6532 | 8.7313 | 8.8094 | 8.8875 | 8.9656 | 9.0437 | 9.1218 | 9.1999 | 9.278 | 9.3561 | 9.4342 | 9.5123 | 9.5904 | 9.6685 | 9.7466 | 9.8247 | 9.9028 | 9.9809 | 10.059 | 10.1371 | 10.2152 | 10.2933 | 10.3714 | 10.4495 | 10.506 | 10.5625 | 10.6189 | 10.6754 | 10.7319 | 10.7884 | 10.8449 | 10.9014 | 10.9579 | 11.0143 | 11.0708 | 11.1273 | 11.1838 | 11.2403 | 11.2967 | 11.3532 | 11.4097 | 11.4662 | 11.5227 | 11.5792 | 11.6357 | 11.6921 | 11.7486 | 11.8051 | 11.8616 | 11.9181 | 11.9746 | 12.031 | 12.0875 | 12.144
5.35 | 0 | 0.1565 | 0.313 | 0.4695 | 0.626 | 0.7825 | 0.939 | 1.0955 | 1.252 | 1.4085 | 1.565 | 1.5281 | 1.4913 | 1.4545 | 1.4176 | 1.3807 | 1.3706 | 1.3604 | 1.3503 | 1.3401 | 1.33 | 1.3203 | 1.3107 | 1.301 | 1.2913 | 1.2816 | 1.2719 | 1.2623 | 1.2526 | 1.2429 | 1.2332 | 1.2592 | 1.2852 | 1.3111 | 1.3371 | 1.363 | 1.3889 | 1.4149 | 1.4408 | 1.4668 | 1.4928 | 1.5187 | 1.5447 | 1.5706 | 1.5965 | 1.6225 | 1.652 | 1.6815 | 1.711 | 1.7405 | 1.77 | 1.7995 | 1.829 | 1.8585 | 1.888 | 1.9175 | 1.947 | 1.9765 | 2.006 | 2.0355 | 2.065 | 2.1721 | 2.2792 | 2.3863 | 2.4934 | 2.6005 | 2.7077 | 2.8148 | 2.9219 | 3.029 | 3.1361 | 3.2432 | 3.3503 | 3.4574 | 3.5645 | 3.6716 | 3.7787 | 3.8858 | 3.9929 | 4.1001 | 4.2072 | 4.3143 | 4.4214 | 4.5285 | 4.6356 | 4.7427 | 4.8498 | 4.9569 | 5.064 | 5.1711 | 5.2782 | 5.3774 | 5.4765 | 5.5756 | 5.6747 | 5.7738 | 5.873 | 5.9721 | 6.0712 | 6.1703 | 6.2694 | 6.3685 | 6.4676 | 6.5668 | 6.6659 | 6.765 | 6.8641 | 6.9632 | 7.0624 | 7.1615 | 7.2606 | 7.3597 | 7.4588 | 7.5579 | 7.657 | 7.7562 | 7.8553 | 7.9544 | 8.0535 | 8.1526 | 8.2517 | 8.3312 | 8.4107 | 8.4901 | 8.5695 | 8.649 | 8.7285 | 8.8079 | 8.8873 | 8.9668 | 9.0463 | 9.1257 | 9.2051 | 9.2846 | 9.3641 | 9.4435 | 9.5229 | 9.6024 | 9.6819 | 9.7613 | 9.8407 | 9.9202 | 9.9997 | 10.0791 | 10.1585 | 10.238 | 10.3174 | 10.3969 | 10.4764 | 10.5558 | 10.6352 | 10.6927 | 10.7501 | 10.8075 | 10.865 | 10.9224 | 10.9798 | 11.0372 | 11.0946 | 11.1521 | 11.2095 | 11.2669 | 11.3244 | 11.3818 | 11.4392 | 11.4966 | 11.5541 | 11.6115 | 11.6689 | 11.7263 | 11.7837 | 11.8412 | 11.8986 | 11.956 | 12.0135 | 12.0709 | 12.1283 | 12.1857 | 12.2431 | 12.3006 | 12.358
5.4 | 0 | 0.159 | 0.318 | 0.477 | 0.636 | 0.795 | 0.954 | 1.113 | 1.272 | 1.431 | 1.59 | 1.5526 | 1.5152 | 1.4778 | 1.4404 | 1.403 | 1.3924 | 1.3818 | 1.3712 | 1.3606 | 1.35 | 1.3403 | 1.3306 | 1.3209 | 1.3112 | 1.3015 | 1.2918 | 1.2821 | 1.2724 | 1.2627 | 1.253 | 1.2795 | 1.3059 | 1.3324 | 1.3589 | 1.3853 | 1.4118 | 1.4383 | 1.4647 | 1.4912 | 1.5177 | 1.5441 | 1.5706 | 1.5971 | 1.6235 | 1.65 | 1.68 | 1.71 | 1.74 | 1.77 | 1.8 | 1.83 | 1.86 | 1.89 | 1.92 | 1.95 | 1.98 | 2.01 | 2.04 | 2.07 | 2.1 | 2.2091 | 2.3182 | 2.4273 | 2.5364 | 2.6455 | 2.7546 | 2.8637 | 2.9728 | 3.0819 | 3.191 | 3.3001 | 3.4092 | 3.5183 | 3.6274 | 3.7365 | 3.8456 | 3.9547 | 4.0638 | 4.1729 | 4.282 | 4.3911 | 4.5002 | 4.6093 | 4.7184 | 4.8275 | 4.9366 | 5.0457 | 5.1548 | 5.2639 | 5.373 | 5.4738 | 5.5746 | 5.6754 | 5.7762 | 5.877 | 5.9778 | 6.0786 | 6.1794 | 6.2802 | 6.381 | 6.4818 | 6.5826 | 6.6834 | 6.7842 | 6.885 | 6.9858 | 7.0866 | 7.1874 | 7.2882 | 7.389 | 7.4898 | 7.5906 | 7.6914 | 7.7922 | 7.893 | 7.9938 | 8.0946 | 8.1954 | 8.2962 | 8.397 | 8.4778 | 8.5586 | 8.6394 | 8.7202 | 8.801 | 8.8818 | 8.9626 | 9.0434 | 9.1242 | 9.205 | 9.2858 | 9.3666 | 9.4474 | 9.5282 | 9.609 | 9.6898 | 9.7706 | 9.8514 | 9.9322 | 10.013 | 10.0938 | 10.1746 | 10.2554 | 10.3362 | 10.417 | 10.4978 | 10.5786 | 10.6594 | 10.7402 | 10.821 | 10.8794 | 10.9377 | 10.9961 | 11.0545 | 11.1128 | 11.1712 | 11.2296 | 11.2879 | 11.3463 | 11.4047 | 11.463 | 11.5214 | 11.5798 | 11.6381 | 11.6965 | 11.7549 | 11.8132 | 11.8716 | 11.93 | 11.9883 | 12.0467 | 12.1051 | 12.1634 | 12.2218 | 12.2802 | 12.3385 | 12.3969 | 12.4553 | 12.5136 | 12.572
5.45 | 0 | 0.1615 | 0.323 | 0.4845 | 0.646 | 0.8075 | 0.969 | 1.1305 | 1.292 | 1.4535 | 1.615 | 1.5771 | 1.5391 | 1.5011 | 1.4632 | 1.4252 | 1.4142 | 1.4031 | 1.3921 | 1.3811 | 1.37 | 1.3603 | 1.3505 | 1.3408 | 1.3311 | 1.3214 | 1.3116 | 1.3019 | 1.2922 | 1.2825 | 1.2728 | 1.2997 | 1.3267 | 1.3537 | 1.3807 | 1.4077 | 1.4346 | 1.4616 | 1.4886 | 1.5156 | 1.5426 | 1.5696 | 1.5965 | 1.6235 | 1.6505 | 1.6775 | 1.708 | 1.7385 | 1.769 | 1.7995 | 1.83 | 1.8605 | 1.891 | 1.9215 | 1.952 | 1.9825 | 2.013 | 2.0435 | 2.074 | 2.1045 | 2.135 | 2.2461 | 2.3572 | 2.4683 | 2.5794 | 2.6905 | 2.8016 | 2.9126 | 3.0237 | 3.1348 | 3.2459 | 3.357 | 3.4681 | 3.5792 | 3.6903 | 3.8014 | 3.9125 | 4.0236 | 4.1346 | 4.2457 | 4.3568 | 4.4679 | 4.579 | 4.6901 | 4.8012 | 4.9123 | 5.0234 | 5.1345 | 5.2456 | 5.3567 | 5.4677 | 5.5702 | 5.6727 | 5.7752 | 5.8777 | 5.9802 | 6.0827 | 6.1851 | 6.2876 | 6.3901 | 6.4926 | 6.5951 | 6.6975 | 6.8 | 6.9025 | 7.005 | 7.1075 | 7.21 | 7.3125 | 7.4149 | 7.5174 | 7.6199 | 7.7224 | 7.8249 | 7.9273 | 8.0298 | 8.1323 | 8.2348 | 8.3373 | 8.4398 | 8.5422 | 8.6244 | 8.7066 | 8.7887 | 8.8709 | 8.953 | 9.0351 | 9.1173 | 9.1995 | 9.2816 | 9.3637 | 9.4459 | 9.5281 | 9.6102 | 9.6923 | 9.7745 | 9.8567 | 9.9388 | 10.0209 | 10.1031 | 10.1852 | 10.2674 | 10.3496 | 10.4317 | 10.5138 | 10.596 | 10.6782 | 10.7603 | 10.8424 | 10.9246 | 11.0068 | 11.0661 | 11.1254 | 11.1847 | 11.244 | 11.3033 | 11.3626 | 11.4219 | 11.4812 | 11.5405 | 11.5998 | 11.6591 | 11.7185 | 11.7778 | 11.8371 | 11.8964 | 11.9557 | 12.015 | 12.0743 | 12.1336 | 12.1929 | 12.2522 | 12.3115 | 12.3708 | 12.4301 | 12.4895 | 12.5488 | 12.6081 | 12.6674 | 12.7267 | 12.786
5.5 | 0 | 0.164 | 0.328 | 0.492 | 0.656 | 0.82 | 0.984 | 1.148 | 1.312 | 1.476 | 1.64 | 1.6015 | 1.563 | 1.5245 | 1.486 | 1.4475 | 1.436 | 1.4245 | 1.413 | 1.4015 | 1.39 | 1.3802 | 1.3705 | 1.3607 | 1.351 | 1.3413 | 1.3315 | 1.3217 | 1.312 | 1.3022 | 1.2925 | 1.32 | 1.3475 | 1.375 | 1.4025 | 1.43 | 1.4575 | 1.485 | 1.5125 | 1.54 | 1.5675 | 1.595 | 1.6225 | 1.65 | 1.6775 | 1.705 | 1.736 | 1.767 | 1.798 | 1.829 | 1.86 | 1.891 | 1.922 | 1.953 | 1.984 | 2.015 | 2.046 | 2.077 | 2.108 | 2.139 | 2.17 | 2.2831 | 2.3962 | 2.5093 | 2.6223 | 2.7354 | 2.8485 | 2.9616 | 3.0747 | 3.1877 | 3.3008 | 3.4139 | 3.527 | 3.6401 | 3.7532 | 3.8662 | 3.9793 | 4.0924 | 4.2055 | 4.3186 | 4.4317 | 4.5447 | 4.6578 | 4.7709 | 4.884 | 4.9971 | 5.1102 | 5.2233 | 5.3363 | 5.4494 | 5.5625 | 5.6667 | 5.7708 | 5.875 | 5.9792 | 6.0833 | 6.1875 | 6.2917 | 6.3958 | 6.5 | 6.6042 | 6.7083 | 6.8125 | 6.9167 | 7.0208 | 7.125 | 7.2292 | 7.3333 | 7.4375 | 7.5417 | 7.6458 | 7.75 | 7.8542 | 7.9583 | 8.0625 | 8.1667 | 8.2708 | 8.375 | 8.4792 | 8.5833 | 8.6875 | 8.771 | 8.8545 | 8.938 | 9.0215 | 9.105 | 9.1885 | 9.272 | 9.3555 | 9.439 | 9.5225 | 9.606 | 9.6895 | 9.773 | 9.8565 | 9.94 | 10.0235 | 10.107 | 10.1905 | 10.274 | 10.3575 | 10.441 | 10.5245 | 10.608 | 10.6915 | 10.775 | 10.8585 | 10.942 | 11.0255 | 11.109 | 11.1925 | 11.2528 | 11.313 | 11.3733 | 11.4335 | 11.4938 | 11.554 | 11.6143 | 11.6745 | 11.7348 | 11.795 | 11.8552 | 11.9155 | 11.9757 | 12.036 | 12.0962 | 12.1565 | 12.2167 | 12.277 | 12.3372 | 12.3975 | 12.4578 | 12.518 | 12.5783 | 12.6385 | 12.6988 | 12.759 | 12.8193 | 12.8795 | 12.9398 | 13
5.55 | 0 | 0.1665 | 0.333 | 0.4995 | 0.666 | 0.8325 | 0.999 | 1.1655 | 1.332 | 1.4985 | 1.665 | 1.626 | 1.5869 | 1.5478 | 1.5088 | 1.4697 | 1.4578 | 1.4459 | 1.4339 | 1.422 | 1.41 | 1.4002 | 1.3904 | 1.3807 | 1.3709 | 1.3611 | 1.3514 | 1.3416 | 1.3318 | 1.322 | 1.3122 | 1.3403 | 1.3683 | 1.3963 | 1.4243 | 1.4523 | 1.4804 | 1.5084 | 1.5364 | 1.5644 | 1.5924 | 1.6204 | 1.6484 | 1.6765 | 1.7045 | 1.7325 | 1.764 | 1.7955 | 1.827 | 1.8585 | 1.89 | 1.9215 | 1.953 | 1.9845 | 2.016 | 2.0475 | 2.079 | 2.1105 | 2.142 | 2.1735 | 2.205 | 2.3201 | 2.4352 | 2.5502 | 2.6653 | 2.7804 | 2.8954 | 3.0105 | 3.1256 | 3.2407 | 3.3558 | 3.4708 | 3.5859 | 3.701 | 3.8161 | 3.9311 | 4.0462 | 4.1613 | 4.2763 | 4.3914 | 4.5065 | 4.6216 | 4.7367 | 4.8517 | 4.9668 | 5.0819 | 5.197 | 5.312 | 5.4271 | 5.5422 | 5.6573 | 5.7631 | 5.8689 | 5.9748 | 6.0807 | 6.1865 | 6.2923 | 6.3982 | 6.5041 | 6.6099 | 6.7157 | 6.8216 | 6.9275 | 7.0333 | 7.1391 | 7.245 | 7.3509 | 7.4567 | 7.5625 | 7.6684 | 7.7743 | 7.8801 | 7.9859 | 8.0918 | 8.1976 | 8.3035 | 8.4093 | 8.5152 | 8.6211 | 8.7269 | 8.8328 | 8.9176 | 9.0024 | 9.0873 | 9.1722 | 9.257 | 9.3419 | 9.4267 | 9.5115 | 9.5964 | 9.6813 | 9.7661 | 9.8509 | 9.9358 | 10.0206 | 10.1055 | 10.1904 | 10.2752 | 10.36 | 10.4449 | 10.5297 | 10.6146 | 10.6995 | 10.7843 | 10.8691 | 10.954 | 11.0389 | 11.1237 | 11.2086 | 11.2934 | 11.3782 | 11.4394 | 11.5006 | 11.5618 | 11.623 | 11.6842 | 11.7454 | 11.8066 | 11.8678 | 11.929 | 11.9902 | 12.0514 | 12.1126 | 12.1737 | 12.2349 | 12.2961 | 12.3573 | 12.4185 | 12.4797 | 12.5409 | 12.6021 | 12.6633 | 12.7245 | 12.7857 | 12.8468 | 12.908 | 12.9692 | 13.0304 | 13.0916 | 13.1528 | 13.214
5.6 | 0 | 0.169 | 0.338 | 0.507 | 0.676 | 0.845 | 1.014 | 1.183 | 1.352 | 1.521 | 1.69 | 1.6504 | 1.6108 | 1.5712 | 1.5316 | 1.492 | 1.4796 | 1.4672 | 1.4548 | 1.4424 | 1.43 | 1.4202 | 1.4104 | 1.4006 | 1.3908 | 1.381 | 1.3712 | 1.3614 | 1.3516 | 1.3418 | 1.332 | 1.3605 | 1.3891 | 1.4176 | 1.4461 | 1.4747 | 1.5032 | 1.5317 | 1.5603 | 1.5888 | 1.6173 | 1.6459 | 1.6744 | 1.7029 | 1.7315 | 1.76 | 1.792 | 1.824 | 1.856 | 1.888 | 1.92 | 1.952 | 1.984 | 2.016 | 2.048 | 2.08 | 2.112 | 2.144 | 2.176 | 2.208 | 2.24 | 2.3571 | 2.4741 | 2.5912 | 2.7083 | 2.8253 | 2.9424 | 3.0595 | 3.1765 | 3.2936 | 3.4107 | 3.5277 | 3.6448 | 3.7619 | 3.8789 | 3.996 | 4.1131 | 4.2301 | 4.3472 | 4.4643 | 4.5813 | 4.6984 | 4.8155 | 4.9325 | 5.0496 | 5.1667 | 5.2837 | 5.4008 | 5.5179 | 5.6349 | 5.752 | 5.8595 | 5.9671 | 6.0746 | 6.1821 | 6.2897 | 6.3972 | 6.5047 | 6.6123 | 6.7198 | 6.8273 | 6.9349 | 7.0424 | 7.1499 | 7.2575 | 7.365 | 7.4725 | 7.5801 | 7.6876 | 7.7951 | 7.9027 | 8.0102 | 8.1177 | 8.2253 | 8.3328 | 8.4403 | 8.5479 | 8.6554 | 8.7629 | 8.8705 | 8.978 | 9.0642 | 9.1504 | 9.2366 | 9.3228 | 9.409 | 9.4952 | 9.5814 | 9.6676 | 9.7538 | 9.84 | 9.9262 | 10.0124 | 10.0986 | 10.1848 | 10.271 | 10.3572 | 10.4434 | 10.5296 | 10.6158 | 10.702 | 10.7882 | 10.8744 | 10.9606 | 11.0468 | 11.133 | 11.2192 | 11.3054 | 11.3916 | 11.4778 | 11.564 | 11.6261 | 11.6883 | 11.7504 | 11.8125 | 11.8747 | 11.9368 | 11.9989 | 12.0611 | 12.1232 | 12.1853 | 12.2475 | 12.3096 | 12.3717 | 12.4339 | 12.496 | 12.5581 | 12.6203 | 12.6824 | 12.7445 | 12.8067 | 12.8688 | 12.9309 | 12.9931 | 13.0552 | 13.1173 | 13.1795 | 13.2416 | 13.3037 | 13.3659 | 13.428
5.65 | 0 | 0.1715 | 0.343 | 0.5145 | 0.686 | 0.8575 | 1.029 | 1.2005 | 1.372 | 1.5435 | 1.715 | 1.6748 | 1.6347 | 1.5945 | 1.5544 | 1.5143 | 1.5014 | 1.4886 | 1.4757 | 1.4628 | 1.45 | 1.4402 | 1.4304 | 1.4205 | 1.4107 | 1.4009 | 1.391 | 1.3812 | 1.3714 | 1.3616 | 1.3518 | 1.3808 | 1.4099 | 1.4389 | 1.468 | 1.497 | 1.526 | 1.5551 | 1.5841 | 1.6132 | 1.6422 | 1.6713 | 1.7004 | 1.7294 | 1.7585 | 1.7875 | 1.82 | 1.8525 | 1.885 | 1.9175 | 1.95 | 1.9825 | 2.015 | 2.0475 | 2.08 | 2.1125 | 2.145 | 2.1775 | 2.21 | 2.2425 | 2.275 | 2.3941 | 2.5131 | 2.6322 | 2.7512 | 2.8703 | 2.9893 | 3.1084 | 3.2275 | 3.3465 | 3.4656 | 3.5846 | 3.7037 | 3.8228 | 3.9418 | 4.0609 | 4.1799 | 4.299 | 4.4181 | 4.5371 | 4.6562 | 4.7752 | 4.8943 | 5.0133 | 5.1324 | 5.2515 | 5.3705 | 5.4896 | 5.6086 | 5.7277 | 5.8468 | 5.956 | 6.0652 | 6.1744 | 6.2836 | 6.3928 | 6.502 | 6.6113 | 6.7205 | 6.8297 | 6.9389 | 7.0481 | 7.1574 | 7.2666 | 7.3758 | 7.485 | 7.5942 | 7.7034 | 7.8126 | 7.9219 | 8.0311 | 8.1403 | 8.2495 | 8.3587 | 8.468 | 8.5772 | 8.6864 | 8.7956 | 8.9048 | 9.014 | 9.1233 | 9.2108 | 9.2983 | 9.3859 | 9.4734 | 9.561 | 9.6486 | 9.7361 | 9.8237 | 9.9112 | 9.9987 | 10.0863 | 10.1738 | 10.2614 | 10.349 | 10.4365 | 10.5241 | 10.6116 | 10.6991 | 10.7867 | 10.8742 | 10.9618 | 11.0494 | 11.1369 | 11.2244 | 11.312 | 11.3995 | 11.4871 | 11.5747 | 11.6622 | 11.7498 | 11.8128 | 11.8759 | 11.939 | 12.0021 | 12.0651 | 12.1282 | 12.1913 | 12.2544 | 12.3174 | 12.3805 | 12.4436 | 12.5067 | 12.5697 | 12.6328 | 12.6959 | 12.759 | 12.822 | 12.8851 | 12.9482 | 13.0113 | 13.0743 | 13.1374 | 13.2005 | 13.2636 | 13.3266 | 13.3897 | 13.4528 | 13.5159 | 13.5789 | 13.642
5.7 | 0 | 0.174 | 0.348 | 0.522 | 0.696 | 0.87 | 1.044 | 1.218 | 1.392 | 1.566 | 1.74 | 1.6993 | 1.6586 | 1.6179 | 1.5772 | 1.5365 | 1.5232 | 1.5099 | 1.4966 | 1.4833 | 1.47 | 1.4602 | 1.4503 | 1.4405 | 1.4306 | 1.4207 | 1.4109 | 1.401 | 1.3912 | 1.3814 | 1.3715 | 1.4011 | 1.4306 | 1.4602 | 1.4898 | 1.5193 | 1.5489 | 1.5785 | 1.608 | 1.6376 | 1.6672 | 1.6967 | 1.7263 | 1.7559 | 1.7854 | 1.815 | 1.848 | 1.881 | 1.914 | 1.947 | 1.98 | 2.013 | 2.046 | 2.079 | 2.112 | 2.145 | 2.178 | 2.211 | 2.244 | 2.277 | 2.31 | 2.431 | 2.5521 | 2.6732 | 2.7942 | 2.9152 | 3.0363 | 3.1574 | 3.2784 | 3.3994 | 3.5205 | 3.6416 | 3.7626 | 3.8836 | 4.0047 | 4.1258 | 4.2468 | 4.3678 | 4.4889 | 4.61 | 4.731 | 4.8521 | 4.9731 | 5.0941 | 5.2152 | 5.3362 | 5.4573 | 5.5784 | 5.6994 | 5.8205 | 5.9415 | 6.0524 | 6.1633 | 6.2742 | 6.3851 | 6.496 | 6.6069 | 6.7178 | 6.8287 | 6.9396 | 7.0505 | 7.1614 | 7.2723 | 7.3832 | 7.4941 | 7.605 | 7.7159 | 7.8268 | 7.9377 | 8.0486 | 8.1595 | 8.2704 | 8.3813 | 8.4922 | 8.6031 | 8.714 | 8.8249 | 8.9358 | 9.0467 | 9.1576 | 9.2685 | 9.3574 | 9.4463 | 9.5352 | 9.6241 | 9.713 | 9.8019 | 9.8908 | 9.9797 | 10.0686 | 10.1575 | 10.2464 | 10.3353 | 10.4242 | 10.5131 | 10.602 | 10.6909 | 10.7798 | 10.8687 | 10.9576 | 11.0465 | 11.1354 | 11.2243 | 11.3132 | 11.4021 | 11.491 | 11.5799 | 11.6688 | 11.7577 | 11.8466 | 11.9355 | 11.9995 | 12.0635 | 12.1275 | 12.1916 | 12.2556 | 12.3196 | 12.3836 | 12.4476 | 12.5116 | 12.5757 | 12.6397 | 12.7037 | 12.7677 | 12.8317 | 12.8957 | 12.9598 | 13.0238 | 13.0878 | 13.1518 | 13.2158 | 13.2798 | 13.3439 | 13.4079 | 13.4719 | 13.5359 | 13.5999 | 13.6639 | 13.728 | 13.792 | 13.856
5.75 | 0 | 0.1765 | 0.353 | 0.5295 | 0.706 | 0.8825 | 1.059 | 1.2355 | 1.412 | 1.5885 | 1.765 | 1.7237 | 1.6825 | 1.6413 | 1.6 | 1.5588 | 1.545 | 1.5312 | 1.5175 | 1.5037 | 1.49 | 1.4801 | 1.4703 | 1.4604 | 1.4505 | 1.4406 | 1.4307 | 1.4209 | 1.411 | 1.4011 | 1.3913 | 1.4213 | 1.4514 | 1.4815 | 1.5116 | 1.5417 | 1.5717 | 1.6018 | 1.6319 | 1.662 | 1.6921 | 1.7222 | 1.7523 | 1.7823 | 1.8124 | 1.8425 | 1.876 | 1.9095 | 1.943 | 1.9765 | 2.01 | 2.0435 | 2.077 | 2.1105 | 2.144 | 2.1775 | 2.211 | 2.2445 | 2.278 | 2.3115 | 2.345 | 2.468 | 2.5911 | 2.7141 | 2.8372 | 2.9602 | 3.0833 | 3.2063 | 3.3293 | 3.4524 | 3.5754 | 3.6985 | 3.8215 | 3.9445 | 4.0676 | 4.1906 | 4.3137 | 4.4367 | 4.5598 | 4.6828 | 4.8058 | 4.9289 | 5.0519 | 5.175 | 5.298 | 5.421 | 5.5441 | 5.6671 | 5.7902 | 5.9132 | 6.0362 | 6.1488 | 6.2614 | 6.374 | 6.4866 | 6.5992 | 6.7118 | 6.8243 | 6.9369 | 7.0495 | 7.1621 | 7.2747 | 7.3872 | 7.4998 | 7.6124 | 7.725 | 7.8376 | 7.9502 | 8.0627 | 8.1753 | 8.2879 | 8.4005 | 8.5131 | 8.6257 | 8.7383 | 8.8508 | 8.9634 | 9.076 | 9.1886 | 9.3012 | 9.4138 | 9.504 | 9.5943 | 9.6845 | 9.7747 | 9.865 | 9.9552 | 10.0455 | 10.1357 | 10.226 | 10.3163 | 10.4065 | 10.4968 | 10.587 | 10.6773 | 10.7675 | 10.8577 | 10.948 | 11.0382 | 11.1285 | 11.2188 | 11.309 | 11.3993 | 11.4895 | 11.5798 | 11.67 | 11.7602 | 11.8505 | 11.9407 | 12.031 | 12.1212 | 12.1862 | 12.2512 | 12.3161 | 12.3811 | 12.446 | 12.511 | 12.576 | 12.6409 | 12.7059 | 12.7708 | 12.8358 | 12.9008 | 12.9657 | 13.0307 | 13.0956 | 13.1606 | 13.2255 | 13.2905 | 13.3555 | 13.4204 | 13.4854 | 13.5503 | 13.6153 | 13.6802 | 13.7452 | 13.8102 | 13.8751 | 13.9401 | 14.005 | 14.07
5.8 | 0 | 0.179 | 0.358 | 0.537 | 0.716 | 0.895 | 1.074 | 1.253 | 1.432 | 1.611 | 1.79 | 1.7482 | 1.7064 | 1.6646 | 1.6228 | 1.581 | 1.5668 | 1.5526 | 1.5384 | 1.5242 | 1.51 | 1.5001 | 1.4902 | 1.4803 | 1.4704 | 1.4605 | 1.4506 | 1.4407 | 1.4308 | 1.4209 | 1.411 | 1.4416 | 1.4722 | 1.5028 | 1.5334 | 1.564 | 1.5946 | 1.6252 | 1.6558 | 1.6864 | 1.717 | 1.7476 | 1.7782 | 1.8088 | 1.8394 | 1.87 | 1.904 | 1.938 | 1.972 | 2.006 | 2.04 | 2.074 | 2.108 | 2.142 | 2.176 | 2.21 | 2.244 | 2.278 | 2.312 | 2.346 | 2.38 | 2.505 | 2.6301 | 2.7551 | 2.8801 | 3.0052 | 3.1302 | 3.2552 | 3.3803 | 3.5053 | 3.6303 | 3.7554 | 3.8804 | 4.0054 | 4.1305 | 4.2555 | 4.3805 | 4.5056 | 4.6306 | 4.7556 | 4.8807 | 5.0057 | 5.1307 | 5.2558 | 5.3808 | 5.5058 | 5.6309 | 5.7559 | 5.8809 | 6.006 | 6.131 | 6.2453 | 6.3595 | 6.4738 | 6.5881 | 6.7023 | 6.8166 | 6.9309 | 7.0451 | 7.1594 | 7.2737 | 7.3879 | 7.5022 | 7.6165 | 7.7307 | 7.845 | 7.9593 | 8.0735 | 8.1878 | 8.3021 | 8.4163 | 8.5306 | 8.6449 | 8.7591 | 8.8734 | 8.9877 | 9.1019 | 9.2162 | 9.3305 | 9.4447 | 9.559 | 9.6506 | 9.7422 | 9.8338 | 9.9254 | 10.017 | 10.1086 | 10.2002 | 10.2918 | 10.3834 | 10.475 | 10.5666 | 10.6582 | 10.7498 | 10.8414 | 10.933 | 11.0246 | 11.1162 | 11.2078 | 11.2994 | 11.391 | 11.4826 | 11.5742 | 11.6658 | 11.7574 | 11.849 | 11.9406 | 12.0322 | 12.1238 | 12.2154 | 12.307 | 12.3729 | 12.4388 | 12.5047 | 12.5706 | 12.6365 | 12.7024 | 12.7683 | 12.8342 | 12.9001 | 12.966 | 13.0319 | 13.0978 | 13.1637 | 13.2296 | 13.2955 | 13.3614 | 13.4273 | 13.4932 | 13.5591 | 13.625 | 13.6909 | 13.7568 | 13.8227 | 13.8886 | 13.9545 | 14.0204 | 14.0863 | 14.1522 | 14.2181 | 14.284
5.85 | 0 | 0.1815 | 0.363 | 0.5445 | 0.726 | 0.9075 | 1.089 | 1.2705 | 1.452 | 1.6335 | 1.815 | 1.7727 | 1.7303 | 1.688 | 1.6456 | 1.6033 | 1.5886 | 1.5739 | 1.5593 | 1.5447 | 1.53 | 1.5201 | 1.5102 | 1.5002 | 1.4903 | 1.4804 | 1.4705 | 1.4605 | 1.4506 | 1.4407 | 1.4307 | 1.4619 | 1.493 | 1.5241 | 1.5552 | 1.5863 | 1.6175 | 1.6486 | 1.6797 | 1.7108 | 1.7419 | 1.773 | 1.8041 | 1.8353 | 1.8664 | 1.8975 | 1.932 | 1.9665 | 2.001 | 2.0355 | 2.07 | 2.1045 | 2.139 | 2.1735 | 2.208 | 2.2425 | 2.277 | 2.3115 | 2.346 | 2.3805 | 2.415 | 2.542 | 2.669 | 2.7961 | 2.9231 | 3.0501 | 3.1772 | 3.3042 | 3.4312 | 3.5582 | 3.6852 | 3.8123 | 3.9393 | 4.0663 | 4.1933 | 4.3204 | 4.4474 | 4.5744 | 4.7015 | 4.8285 | 4.9555 | 5.0825 | 5.2096 | 5.3366 | 5.4636 | 5.5906 | 5.7176 | 5.8447 | 5.9717 | 6.0987 | 6.2257 | 6.3417 | 6.4577 | 6.5736 | 6.6895 | 6.8055 | 6.9215 | 7.0374 | 7.1533 | 7.2693 | 7.3853 | 7.5012 | 7.6171 | 7.7331 | 7.8491 | 7.965 | 8.0809 | 8.1969 | 8.3128 | 8.4288 | 8.5448 | 8.6607 | 8.7767 | 8.8926 | 9.0085 | 9.1245 | 9.2404 | 9.3564 | 9.4724 | 9.5883 | 9.7043 | 9.7972 | 9.8902 | 9.9831 | 10.0761 | 10.169 | 10.262 | 10.3549 | 10.4479 | 10.5408 | 10.6337 | 10.7267 | 10.8196 | 10.9126 | 11.0055 | 11.0985 | 11.1914 | 11.2844 | 11.3773 | 11.4703 | 11.5633 | 11.6562 | 11.7492 | 11.8421 | 11.9351 | 12.028 | 12.121 | 12.2139 | 12.3069 | 12.3998 | 12.4927 | 12.5596 | 12.6264 | 12.6933 | 12.7601 | 12.827 | 12.8938 | 12.9606 | 13.0275 | 13.0943 | 13.1612 | 13.228 | 13.2949 | 13.3617 | 13.4285 | 13.4954 | 13.5622 | 13.6291 | 13.6959 | 13.7627 | 13.8296 | 13.8964 | 13.9633 | 14.0301 | 14.0969 | 14.1638 | 14.2306 | 14.2975 | 14.3643 | 14.4312 | 14.498
5.9 | 0 | 0.184 | 0.368 | 0.552 | 0.736 | 0.92 | 1.104 | 1.288 | 1.472 | 1.656 | 1.84 | 1.7971 | 1.7542 | 1.7113 | 1.6684 | 1.6255 | 1.6104 | 1.5953 | 1.5802 | 1.5651 | 1.55 | 1.54 | 1.5301 | 1.5201 | 1.5102 | 1.5003 | 1.4903 | 1.4804 | 1.4704 | 1.4605 | 1.4505 | 1.4821 | 1.5138 | 1.5454 | 1.577 | 1.6087 | 1.6403 | 1.6719 | 1.7036 | 1.7352 | 1.7668 | 1.7985 | 1.8301 | 1.8617 | 1.8934 | 1.925 | 1.96 | 1.995 | 2.03 | 2.065 | 2.1 | 2.135 | 2.17 | 2.205 | 2.24 | 2.275 | 2.31 | 2.345 | 2.38 | 2.415 | 2.45 | 2.579 | 2.708 | 2.8371 | 2.9661 | 3.0951 | 3.2241 | 3.3531 | 3.4821 | 3.6111 | 3.7402 | 3.8692 | 3.9982 | 4.1272 | 4.2562 | 4.3853 | 4.5143 | 4.6433 | 4.7723 | 4.9013 | 5.0303 | 5.1593 | 5.2884 | 5.4174 | 5.5464 | 5.6754 | 5.8044 | 5.9334 | 6.0625 | 6.1915 | 6.3205 | 6.4381 | 6.5558 | 6.6734 | 6.791 | 6.9087 | 7.0263 | 7.1439 | 7.2616 | 7.3792 | 7.4968 | 7.6145 | 7.7321 | 7.8497 | 7.9674 | 8.085 | 8.2026 | 8.3203 | 8.4379 | 8.5555 | 8.6732 | 8.7908 | 8.9084 | 9.0261 | 9.1437 | 9.2613 | 9.379 | 9.4966 | 9.6142 | 9.7319 | 9.8495 | 9.9438 | 10.0381 | 10.1324 | 10.2267 | 10.321 | 10.4153 | 10.5096 | 10.6039 | 10.6982 | 10.7925 | 10.8868 | 10.9811 | 11.0754 | 11.1697 | 11.264 | 11.3583 | 11.4526 | 11.5469 | 11.6412 | 11.7355 | 11.8298 | 11.9241 | 12.0184 | 12.1127 | 12.207 | 12.3013 | 12.3956 | 12.4899 | 12.5842 | 12.6785 | 12.7463 | 12.8141 | 12.8819 | 12.9496 | 13.0174 | 13.0852 | 13.153 | 13.2208 | 13.2886 | 13.3563 | 13.4241 | 13.4919 | 13.5597 | 13.6275 | 13.6952 | 13.763 | 13.8308 | 13.8986 | 13.9664 | 14.0342 | 14.102 | 14.1697 | 14.2375 | 14.3053 | 14.3731 | 14.4409 | 14.5086 | 14.5764 | 14.6442 | 14.712
5.95 | 0 | 0.1865 | 0.373 | 0.5595 | 0.746 | 0.9325 | 1.119 | 1.3055 | 1.492 | 1.6785 | 1.865 | 1.8216 | 1.7781 | 1.7347 | 1.6912 | 1.6478 | 1.6322 | 1.6166 | 1.6011 | 1.5856 | 1.57 | 1.56 | 1.55 | 1.5401 | 1.5301 | 1.5201 | 1.5102 | 1.5002 | 1.4902 | 1.4802 | 1.4703 | 1.5024 | 1.5346 | 1.5667 | 1.5989 | 1.631 | 1.6631 | 1.6953 | 1.7274 | 1.7596 | 1.7917 | 1.8239 | 1.856 | 1.8882 | 1.9204 | 1.9525 | 1.988 | 2.0235 | 2.059 | 2.0945 | 2.13 | 2.1655 | 2.201 | 2.2365 | 2.272 | 2.3075 | 2.343 | 2.3785 | 2.414 | 2.4495 | 2.485 | 2.616 | 2.747 | 2.878 | 3.009 | 3.14 | 3.271 | 3.4021 | 3.5331 | 3.6641 | 3.7951 | 3.9261 | 4.0571 | 4.1881 | 4.3191 | 4.4501 | 4.5811 | 4.7121 | 4.8431 | 4.9742 | 5.1052 | 5.2362 | 5.3672 | 5.4982 | 5.6292 | 5.7602 | 5.8912 | 6.0222 | 6.1532 | 6.2842 | 6.4153 | 6.5346 | 6.6539 | 6.7732 | 6.8925 | 7.0118 | 7.1311 | 7.2505 | 7.3698 | 7.4891 | 7.6084 | 7.7277 | 7.8471 | 7.9664 | 8.0857 | 8.205 | 8.3243 | 8.4436 | 8.563 | 8.6823 | 8.8016 | 8.9209 | 9.0402 | 9.1595 | 9.2789 | 9.3982 | 9.5175 | 9.6368 | 9.7561 | 9.8754 | 9.9947 | 10.0904 | 10.186 | 10.2817 | 10.3773 | 10.473 | 10.5686 | 10.6643 | 10.7599 | 10.8556 | 10.9512 | 11.0469 | 11.1425 | 11.2382 | 11.3338 | 11.4295 | 11.5252 | 11.6208 | 11.7165 | 11.8121 | 11.9078 | 12.0034 | 12.0991 | 12.1947 | 12.2904 | 12.386 | 12.4817 | 12.5773 | 12.673 | 12.7686 | 12.8643 | 12.933 | 13.0017 | 13.0704 | 13.1392 | 13.2079 | 13.2766 | 13.3453 | 13.414 | 13.4828 | 13.5515 | 13.6202 | 13.689 | 13.7577 | 13.8264 | 13.8951 | 13.9639 | 14.0326 | 14.1013 | 14.17 | 14.2387 | 14.3075 | 14.3762 | 14.4449 | 14.5137 | 14.5824 | 14.6511 | 14.7198 | 14.7886 | 14.8573 | 14.926
6 | 0 | 0.189 | 0.378 | 0.567 | 0.756 | 0.945 | 1.134 | 1.323 | 1.512 | 1.701 | 1.89 | 1.846 | 1.802 | 1.758 | 1.714 | 1.67 | 1.654 | 1.638 | 1.622 | 1.606 | 1.59 | 1.58 | 1.57 | 1.56 | 1.55 | 1.54 | 1.53 | 1.52 | 1.51 | 1.5 | 1.49 | 1.5227 | 1.5553 | 1.588 | 1.6207 | 1.6533 | 1.686 | 1.7187 | 1.7513 | 1.784 | 1.8167 | 1.8493 | 1.882 | 1.9147 | 1.9473 | 1.98 | 2.016 | 2.052 | 2.088 | 2.124 | 2.16 | 2.196 | 2.232 | 2.268 | 2.304 | 2.34 | 2.376 | 2.412 | 2.448 | 2.484 | 2.52 | 2.653 | 2.786 | 2.919 | 3.052 | 3.185 | 3.318 | 3.451 | 3.584 | 3.717 | 3.85 | 3.983 | 4.116 | 4.249 | 4.382 | 4.515 | 4.648 | 4.781 | 4.914 | 5.047 | 5.18 | 5.313 | 5.446 | 5.579 | 5.712 | 5.845 | 5.978 | 6.111 | 6.244 | 6.377 | 6.51 | 6.631 | 6.752 | 6.873 | 6.994 | 7.115 | 7.236 | 7.357 | 7.478 | 7.599 | 7.72 | 7.841 | 7.962 | 8.083 | 8.204 | 8.325 | 8.446 | 8.567 | 8.688 | 8.809 | 8.93 | 9.051 | 9.172 | 9.293 | 9.414 | 9.535 | 9.656 | 9.777 | 9.898 | 10.019 | 10.14 | 10.237 | 10.334 | 10.431 | 10.528 | 10.625 | 10.722 | 10.819 | 10.916 | 11.013 | 11.11 | 11.207 | 11.304 | 11.401 | 11.498 | 11.595 | 11.692 | 11.789 | 11.886 | 11.983 | 12.08 | 12.177 | 12.274 | 12.371 | 12.468 | 12.565 | 12.662 | 12.759 | 12.856 | 12.953 | 13.05 | 13.1197 | 13.1893 | 13.259 | 13.3287 | 13.3983 | 13.468 | 13.5377 | 13.6073 | 13.677 | 13.7467 | 13.8163 | 13.886 | 13.9557 | 14.0253 | 14.095 | 14.1647 | 14.2343 | 14.304 | 14.3737 | 14.4433 | 14.513 | 14.5827 | 14.6523 | 14.722 | 14.7917 | 14.8613 | 14.931 | 15.0007 | 15.0703 | 15.14
6.05 | 0 | 0.193 | 0.386 | 0.579 | 0.772 | 0.965 | 1.158 | 1.351 | 1.544 | 1.737 | 1.93 | 1.8871 | 1.8442 | 1.8014 | 1.7585 | 1.7156 | 1.6994 | 1.6832 | 1.6669 | 1.6507 | 1.6345 | 1.6245 | 1.6145 | 1.6045 | 1.5945 | 1.5845 | 1.5745 | 1.5645 | 1.5545 | 1.5445 | 1.5345 | 1.568 | 1.6014 | 1.6349 | 1.6684 | 1.7018 | 1.7353 | 1.7688 | 1.8022 | 1.8357 | 1.8692 | 1.9026 | 1.9361 | 1.9696 | 2.003 | 2.0365 | 2.0733 | 2.1102 | 2.147 | 2.1839 | 2.2207 | 2.2576 | 2.2944 | 2.3312 | 2.3681 | 2.4049 | 2.4418 | 2.4786 | 2.5154 | 2.5523 | 2.5891 | 2.725 | 2.861 | 2.9969 | 3.1328 | 3.2687 | 3.4047 | 3.5406 | 3.6765 | 3.8125 | 3.9484 | 4.0843 | 4.2202 | 4.3562 | 4.4921 | 4.628 | 4.7639 | 4.8998 | 5.0358 | 5.1717 | 5.3076 | 5.4436 | 5.5795 | 5.7154 | 5.8513 | 5.9873 | 6.1232 | 6.2591 | 6.395 | 6.5309 | 6.6669 | 6.7905 | 6.9142 | 7.0378 | 7.1615 | 7.2852 | 7.4088 | 7.5325 | 7.6561 | 7.7798 | 7.9035 | 8.0271 | 8.1508 | 8.2744 | 8.3981 | 8.5218 | 8.6454 | 8.7691 | 8.8927 | 9.0164 | 9.14 | 9.2637 | 9.3874 | 9.511 | 9.6347 | 9.7583 | 9.882 | 10.0056 | 10.1293 | 10.253 | 10.3766 | 10.4757 | 10.5749 | 10.674 | 10.7731 | 10.8722 | 10.9714 | 11.0705 | 11.1696 | 11.2688 | 11.3679 | 11.467 | 11.5661 | 11.6653 | 11.7644 | 11.8635 | 11.9626 | 12.0617 | 12.1609 | 12.26 | 12.3591 | 12.4582 | 12.5574 | 12.6565 | 12.7556 | 12.8547 | 12.9539 | 13.053 | 13.1521 | 13.2513 | 13.3504 | 13.4217 | 13.4929 | 13.5642 | 13.6355 | 13.7068 | 13.7781 | 13.8494 | 13.9206 | 13.9919 | 14.0632 | 14.1345 | 14.2058 | 14.2771 | 14.3483 | 14.4196 | 14.4909 | 14.5622 | 14.6335 | 14.7048 | 14.776 | 14.8473 | 14.9186 | 14.9899 | 15.0612 | 15.1325 | 15.2037 | 15.275 | 15.3463 | 15.4176 | 15.4889
6.1 | 0 | 0.197 | 0.394 | 0.591 | 0.788 | 0.985 | 1.182 | 1.379 | 1.576 | 1.773 | 1.97 | 1.9283 | 1.8865 | 1.8447 | 1.803 | 1.7612 | 1.7448 | 1.7284 | 1.7119 | 1.6954 | 1.679 | 1.669 | 1.659 | 1.649 | 1.639 | 1.629 | 1.619 | 1.609 | 1.599 | 1.589 | 1.579 | 1.6133 | 1.6475 | 1.6818 | 1.7161 | 1.7503 | 1.7846 | 1.8189 | 1.8531 | 1.8874 | 1.9217 | 1.9559 | 1.9902 | 2.0245 | 2.0587 | 2.093 | 2.1307 | 2.1684 | 2.206 | 2.2437 | 2.2814 | 2.3191 | 2.3568 | 2.3945 | 2.4322 | 2.4698 | 2.5075 | 2.5452 | 2.5829 | 2.6206 | 2.6582 | 2.7971 | 2.936 | 3.0748 | 3.2136 | 3.3525 | 3.4914 | 3.6302 | 3.7691 | 3.9079 | 4.0468 | 4.1856 | 4.3244 | 4.4633 | 4.6021 | 4.741 | 4.8799 | 5.0187 | 5.1575 | 5.2964 | 5.4352 | 5.5741 | 5.713 | 5.8518 | 5.9906 | 6.1295 | 6.2683 | 6.4072 | 6.5461 | 6.6849 | 6.8238 | 6.9501 | 7.0764 | 7.2027 | 7.329 | 7.4553 | 7.5816 | 7.708 | 7.8343 | 7.9606 | 8.0869 | 8.2132 | 8.3395 | 8.4659 | 8.5922 | 8.7185 | 8.8448 | 8.9711 | 9.0975 | 9.2238 | 9.3501 | 9.4764 | 9.6027 | 9.729 | 9.8553 | 9.9817 | 10.108 | 10.2343 | 10.3606 | 10.4869 | 10.6133 | 10.7145 | 10.8157 | 10.917 | 11.0183 | 11.1195 | 11.2208 | 11.322 | 11.4232 | 11.5245 | 11.6258 | 11.727 | 11.8283 | 11.9295 | 12.0307 | 12.132 | 12.2332 | 12.3345 | 12.4358 | 12.537 | 12.6382 | 12.7395 | 12.8407 | 12.942 | 13.0433 | 13.1445 | 13.2457 | 13.347 | 13.4482 | 13.5495 | 13.6508 | 13.7236 | 13.7965 | 13.8695 | 13.9423 | 14.0152 | 14.0882 | 14.161 | 14.234 | 14.3069 | 14.3797 | 14.4527 | 14.5256 | 14.5984 | 14.6714 | 14.7442 | 14.8171 | 14.8901 | 14.9629 | 15.0358 | 15.1088 | 15.1816 | 15.2546 | 15.3275 | 15.4003 | 15.4733 | 15.5462 | 15.619 | 15.692 | 15.7648 | 15.8377
6.15 | 0 | 0.201 | 0.402 | 0.603 | 0.804 | 1.005 | 1.206 | 1.407 | 1.608 | 1.809 | 2.01 | 1.9694 | 1.9287 | 1.8881 | 1.8475 | 1.8069 | 1.7902 | 1.7735 | 1.7569 | 1.7402 | 1.7235 | 1.7135 | 1.7035 | 1.6935 | 1.6835 | 1.6735 | 1.6635 | 1.6535 | 1.6435 | 1.6335 | 1.6235 | 1.6586 | 1.6936 | 1.7287 | 1.7638 | 1.7988 | 1.8339 | 1.869 | 1.904 | 1.9391 | 1.9742 | 2.0092 | 2.0443 | 2.0794 | 2.1144 | 2.1495 | 2.188 | 2.2266 | 2.2651 | 2.3036 | 2.3421 | 2.3807 | 2.4192 | 2.4577 | 2.4962 | 2.5347 | 2.5733 | 2.6118 | 2.6503 | 2.6888 | 2.7274 | 2.8691 | 3.0109 | 3.1527 | 3.2945 | 3.4362 | 3.578 | 3.7198 | 3.8616 | 4.0034 | 4.1451 | 4.2869 | 4.4287 | 4.5705 | 4.7122 | 4.854 | 4.9958 | 5.1376 | 5.2793 | 5.4211 | 5.5629 | 5.7046 | 5.8464 | 5.9882 | 6.13 | 6.2717 | 6.4135 | 6.5553 | 6.6971 | 6.8388 | 6.9806 | 7.1096 | 7.2386 | 7.3675 | 7.4965 | 7.6255 | 7.7545 | 7.8834 | 8.0124 | 8.1414 | 8.2704 | 8.3994 | 8.5283 | 8.6573 | 8.7863 | 8.9153 | 9.0442 | 9.1732 | 9.3022 | 9.4312 | 9.5601 | 9.6891 | 9.8181 | 9.9471 | 10.076 | 10.205 | 10.334 | 10.4629 | 10.5919 | 10.7209 | 10.8499 | 10.9533 | 11.0566 | 11.16 | 11.2634 | 11.3667 | 11.4701 | 11.5735 | 11.6769 | 11.7803 | 11.8836 | 11.987 | 12.0904 | 12.1937 | 12.2971 | 12.4005 | 12.5039 | 12.6073 | 12.7106 | 12.814 | 12.9174 | 13.0207 | 13.1241 | 13.2275 | 13.3309 | 13.4343 | 13.5376 | 13.641 | 13.7444 | 13.8477 | 13.9511 | 14.0256 | 14.1002 | 14.1747 | 14.2492 | 14.3237 | 14.3982 | 14.4727 | 14.5473 | 14.6218 | 14.6963 | 14.7708 | 14.8453 | 14.9198 | 14.9944 | 15.0689 | 15.1434 | 15.2179 | 15.2924 | 15.3669 | 15.4415 | 15.516 | 15.5905 | 15.665 | 15.7395 | 15.814 | 15.8886 | 15.9631 | 16.0376 | 16.1121 | 16.1866
6.2 | 0 | 0.205 | 0.41 | 0.615 | 0.82 | 1.025 | 1.23 | 1.435 | 1.64 | 1.845 | 2.05 | 2.0105 | 1.971 | 1.9315 | 1.892 | 1.8525 | 1.8356 | 1.8187 | 1.8018 | 1.7849 | 1.768 | 1.758 | 1.748 | 1.738 | 1.728 | 1.718 | 1.708 | 1.698 | 1.688 | 1.678 | 1.668 | 1.7039 | 1.7397 | 1.7756 | 1.8115 | 1.8473 | 1.8832 | 1.9191 | 1.9549 | 1.9908 | 2.0267 | 2.0625 | 2.0984 | 2.1343 | 2.1701 | 2.206 | 2.2454 | 2.2847 | 2.3241 | 2.3635 | 2.4028 | 2.4422 | 2.4816 | 2.5209 | 2.5603 | 2.5997 | 2.639 | 2.6784 | 2.7178 | 2.7571 | 2.7965 | 2.9412 | 3.0859 | 3.2306 | 3.3753 | 3.52 | 3.6647 | 3.8094 | 3.9541 | 4.0988 | 4.2435 | 4.3882 | 4.5329 | 4.6776 | 4.8223 | 4.967 | 5.1117 | 5.2564 | 5.4011 | 5.5458 | 5.6905 | 5.8352 | 5.9799 | 6.1246 | 6.2693 | 6.414 | 6.5587 | 6.7034 | 6.8481 | 6.9928 | 7.1375 | 7.2691 | 7.4008 | 7.5324 | 7.664 | 7.7957 | 7.9273 | 8.0589 | 8.1906 | 8.3222 | 8.4538 | 8.5855 | 8.7171 | 8.8487 | 8.9804 | 9.112 | 9.2436 | 9.3753 | 9.5069 | 9.6385 | 9.7702 | 9.9018 | 10.0334 | 10.1651 | 10.2967 | 10.4283 | 10.56 | 10.6916 | 10.8232 | 10.9549 | 11.0865 | 11.192 | 11.2975 | 11.403 | 11.5085 | 11.614 | 11.7195 | 11.825 | 11.9305 | 12.036 | 12.1415 | 12.247 | 12.3525 | 12.458 | 12.5635 | 12.669 | 12.7745 | 12.88 | 12.9855 | 13.091 | 13.1965 | 13.302 | 13.4075 | 13.513 | 13.6185 | 13.724 | 13.8295 | 13.935 | 14.0405 | 14.146 | 14.2515 | 14.3276 | 14.4038 | 14.4799 | 14.556 | 14.6322 | 14.7083 | 14.7844 | 14.8606 | 14.9367 | 15.0128 | 15.089 | 15.1651 | 15.2412 | 15.3174 | 15.3935 | 15.4696 | 15.5458 | 15.6219 | 15.698 | 15.7742 | 15.8503 | 15.9264 | 16.0026 | 16.0787 | 16.1548 | 16.231 | 16.3071 | 16.3832 | 16.4594 | 16.5355
6.25 | 0 | 0.209 | 0.418 | 0.627 | 0.836 | 1.045 | 1.254 | 1.463 | 1.672 | 1.881 | 2.09 | 2.0516 | 2.0133 | 1.9749 | 1.9365 | 1.8981 | 1.881 | 1.8639 | 1.8467 | 1.8296 | 1.8125 | 1.8025 | 1.7925 | 1.7825 | 1.7725 | 1.7625 | 1.7525 | 1.7425 | 1.7325 | 1.7225 | 1.7125 | 1.7492 | 1.7858 | 1.8225 | 1.8592 | 1.8958 | 1.9325 | 1.9692 | 2.0058 | 2.0425 | 2.0792 | 2.1158 | 2.1525 | 2.1892 | 2.2258 | 2.2625 | 2.3027 | 2.3429 | 2.3831 | 2.4233 | 2.4635 | 2.5038 | 2.544 | 2.5842 | 2.6244 | 2.6646 | 2.7048 | 2.745 | 2.7852 | 2.8254 | 2.8656 | 3.0133 | 3.1609 | 3.3085 | 3.4561 | 3.6037 | 3.7514 | 3.899 | 4.0466 | 4.1943 | 4.3419 | 4.4895 | 4.6371 | 4.7847 | 4.9324 | 5.08 | 5.2276 | 5.3753 | 5.5229 | 5.6705 | 5.8181 | 5.9657 | 6.1134 | 6.261 | 6.4086 | 6.5563 | 6.7039 | 6.8515 | 6.9991 | 7.1467 | 7.2944 | 7.4287 | 7.563 | 7.6973 | 7.8315 | 7.9658 | 8.1001 | 8.2344 | 8.3687 | 8.503 | 8.6373 | 8.7716 | 8.9059 | 9.0402 | 9.1745 | 9.3087 | 9.443 | 9.5773 | 9.7116 | 9.8459 | 9.9802 | 10.1145 | 10.2488 | 10.3831 | 10.5174 | 10.6517 | 10.786 | 10.9202 | 11.0545 | 11.1888 | 11.3231 | 11.4307 | 11.5384 | 11.646 | 11.7536 | 11.8613 | 11.9689 | 12.0765 | 12.1841 | 12.2918 | 12.3994 | 12.507 | 12.6146 | 12.7223 | 12.8299 | 12.9375 | 13.0451 | 13.1527 | 13.2604 | 13.368 | 13.4756 | 13.5832 | 13.6909 | 13.7985 | 13.9061 | 14.0137 | 14.1214 | 14.229 | 14.3366 | 14.4443 | 14.5519 | 14.6296 | 14.7074 | 14.7851 | 14.8629 | 14.9406 | 15.0184 | 15.0961 | 15.1739 | 15.2516 | 15.3294 | 15.4071 | 15.4849 | 15.5626 | 15.6404 | 15.7181 | 15.7959 | 15.8736 | 15.9514 | 16.0291 | 16.1069 | 16.1846 | 16.2624 | 16.3401 | 16.4179 | 16.4956 | 16.5734 | 16.6511 | 16.7289 | 16.8066 | 16.8844
6.3 | 0 | 0.213 | 0.426 | 0.639 | 0.852 | 1.065 | 1.278 | 1.491 | 1.704 | 1.917 | 2.13 | 2.0928 | 2.0555 | 2.0183 | 1.981 | 1.9438 | 1.9264 | 1.909 | 1.8917 | 1.8743 | 1.857 | 1.847 | 1.837 | 1.827 | 1.817 | 1.807 | 1.797 | 1.787 | 1.777 | 1.767 | 1.757 | 1.7945 | 1.8319 | 1.8694 | 1.9069 | 1.9443 | 1.9818 | 2.0193 | 2.0567 | 2.0942 | 2.1317 | 2.1691 | 2.2066 | 2.2441 | 2.2815 | 2.319 | 2.3601 | 2.4011 | 2.4421 | 2.4832 | 2.5242 | 2.5653 | 2.6063 | 2.6474 | 2.6885 | 2.7295 | 2.7706 | 2.8116 | 2.8527 | 2.8937 | 2.9348 | 3.0853 | 3.2359 | 3.3864 | 3.537 | 3.6875 | 3.838 | 3.9886 | 4.1391 | 4.2897 | 4.4402 | 4.5908 | 4.7413 | 4.8919 | 5.0424 | 5.193 | 5.3435 | 5.4941 | 5.6447 | 5.7952 | 5.9458 | 6.0963 | 6.2469 | 6.3974 | 6.548 | 6.6985 | 6.8491 | 6.9996 | 7.1502 | 7.3007 | 7.4512 | 7.5882 | 7.7252 | 7.8621 | 7.9991 | 8.136 | 8.2729 | 8.4099 | 8.5468 | 8.6838 | 8.8208 | 8.9577 | 9.0946 | 9.2316 | 9.3686 | 9.5055 | 9.6425 | 9.7794 | 9.9163 | 10.0533 | 10.1903 | 10.3272 | 10.4642 | 10.6011 | 10.738 | 10.875 | 11.012 | 11.1489 | 11.2858 | 11.4228 | 11.5597 | 11.6695 | 11.7792 | 11.889 | 11.9987 | 12.1085 | 12.2182 | 12.328 | 12.4377 | 12.5475 | 12.6572 | 12.767 | 12.8767 | 12.9865 | 13.0962 | 13.206 | 13.3157 | 13.4255 | 13.5352 | 13.645 | 13.7547 | 13.8645 | 13.9742 | 14.084 | 14.1937 | 14.3035 | 14.4132 | 14.523 | 14.6327 | 14.7425 | 14.8522 | 14.9316 | 15.011 | 15.0904 | 15.1697 | 15.2491 | 15.3285 | 15.4078 | 15.4872 | 15.5665 | 15.6459 | 15.7253 | 15.8047 | 15.884 | 15.9634 | 16.0428 | 16.1221 | 16.2015 | 16.2809 | 16.3602 | 16.4396 | 16.519 | 16.5983 | 16.6777 | 16.757 | 16.8364 | 16.9158 | 16.9951 | 17.0745 | 17.1539 | 17.2332
6.35 | 0 | 0.217 | 0.434 | 0.651 | 0.868 | 1.085 | 1.302 | 1.519 | 1.736 | 1.953 | 2.17 | 2.1339 | 2.0978 | 2.0616 | 2.0255 | 1.9894 | 1.9718 | 1.9542 | 1.9366 | 1.9191 | 1.9015 | 1.8915 | 1.8815 | 1.8715 | 1.8615 | 1.8515 | 1.8415 | 1.8315 | 1.8215 | 1.8115 | 1.8015 | 1.8398 | 1.878 | 1.9163 | 1.9546 | 1.9928 | 2.0311 | 2.0694 | 2.1076 | 2.1459 | 2.1842 | 2.2224 | 2.2607 | 2.299 | 2.3372 | 2.3755 | 2.4174 | 2.4593 | 2.5012 | 2.5431 | 2.585 | 2.6269 | 2.6687 | 2.7106 | 2.7525 | 2.7944 | 2.8363 | 2.8782 | 2.9201 | 2.962 | 3.0039 | 3.1574 | 3.3108 | 3.4643 | 3.6178 | 3.7713 | 3.9247 | 4.0782 | 4.2317 | 4.3852 | 4.5386 | 4.6921 | 4.8456 | 4.9991 | 5.1525 | 5.306 | 5.4595 | 5.6129 | 5.7664 | 5.9199 | 6.0734 | 6.2268 | 6.3803 | 6.5338 | 6.6873 | 6.8407 | 6.9942 | 7.1477 | 7.3012 | 7.4546 | 7.6081 | 7.7477 | 7.8873 | 8.0269 | 8.1666 | 8.3062 | 8.4458 | 8.5854 | 8.725 | 8.8646 | 9.0042 | 9.1438 | 9.2834 | 9.423 | 9.5626 | 9.7022 | 9.8419 | 9.9815 | 10.1211 | 10.2607 | 10.4003 | 10.5399 | 10.6795 | 10.8191 | 10.9587 | 11.0983 | 11.2379 | 11.3775 | 11.5172 | 11.6568 | 11.7964 | 11.9083 | 12.0201 | 12.132 | 12.2439 | 12.3558 | 12.4676 | 12.5795 | 12.6914 | 12.8033 | 12.9151 | 13.027 | 13.1389 | 13.2508 | 13.3626 | 13.4745 | 13.5864 | 13.6982 | 13.8101 | 13.922 | 14.0339 | 14.1457 | 14.2576 | 14.3695 | 14.4814 | 14.5932 | 14.7051 | 14.817 | 14.9289 | 15.0407 | 15.1526 | 15.2336 | 15.3146 | 15.3956 | 15.4766 | 15.5575 | 15.6385 | 15.7195 | 15.8005 | 15.8815 | 15.9625 | 16.0434 | 16.1244 | 16.2054 | 16.2864 | 16.3674 | 16.4484 | 16.5293 | 16.6103 | 16.6913 | 16.7723 | 16.8533 | 16.9343 | 17.0152 | 17.0962 | 17.1772 | 17.2582 | 17.3392 | 17.4202 | 17.5011 | 17.5821
6.4 | 0 | 0.221 | 0.442 | 0.663 | 0.884 | 1.105 | 1.326 | 1.547 | 1.768 | 1.989 | 2.21 | 2.175 | 2.14 | 2.105 | 2.07 | 2.035 | 2.0172 | 1.9994 | 1.9816 | 1.9638 | 1.946 | 1.936 | 1.926 | 1.916 | 1.906 | 1.896 | 1.886 | 1.876 | 1.866 | 1.856 | 1.846 | 1.8851 | 1.9241 | 1.9632 | 2.0023 | 2.0413 | 2.0804 | 2.1195 | 2.1585 | 2.1976 | 2.2367 | 2.2757 | 2.3148 | 2.3539 | 2.3929 | 2.432 | 2.4747 | 2.5175 | 2.5602 | 2.6029 | 2.6457 | 2.6884 | 2.7311 | 2.7739 | 2.8166 | 2.8593 | 2.9021 | 2.9448 | 2.9875 | 3.0303 | 3.073 | 3.2294 | 3.3858 | 3.5422 | 3.6986 | 3.855 | 4.0114 | 4.1678 | 4.3242 | 4.4806 | 4.637 | 4.7934 | 4.9498 | 5.1062 | 5.2626 | 5.419 | 5.5754 | 5.7318 | 5.8882 | 6.0446 | 6.201 | 6.3574 | 6.5138 | 6.6702 | 6.8266 | 6.983 | 7.1394 | 7.2958 | 7.4522 | 7.6086 | 7.765 | 7.9073 | 8.0495 | 8.1918 | 8.3341 | 8.4763 | 8.6186 | 8.7609 | 8.9031 | 9.0454 | 9.1877 | 9.3299 | 9.4722 | 9.6145 | 9.7567 | 9.899 | 10.0413 | 10.1835 | 10.3258 | 10.4681 | 10.6103 | 10.7526 | 10.8949 | 11.0371 | 11.1794 | 11.3217 | 11.4639 | 11.6062 | 11.7485 | 11.8907 | 12.033 | 12.147 | 12.261 | 12.375 | 12.489 | 12.603 | 12.717 | 12.831 | 12.945 | 13.059 | 13.173 | 13.287 | 13.401 | 13.515 | 13.629 | 13.743 | 13.857 | 13.971 | 14.085 | 14.199 | 14.313 | 14.427 | 14.541 | 14.655 | 14.769 | 14.883 | 14.997 | 15.111 | 15.225 | 15.339 | 15.453 | 15.5356 | 15.6182 | 15.7008 | 15.7834 | 15.866 | 15.9486 | 16.0312 | 16.1138 | 16.1964 | 16.279 | 16.3616 | 16.4442 | 16.5268 | 16.6094 | 16.692 | 16.7746 | 16.8572 | 16.9398 | 17.0224 | 17.105 | 17.1876 | 17.2702 | 17.3528 | 17.4354 | 17.518 | 17.6006 | 17.6832 | 17.7658 | 17.8484 | 17.931
6.45 | 0 | 0.225 | 0.45 | 0.675 | 0.9 | 1.125 | 1.35 | 1.575 | 1.8 | 2.025 | 2.25 | 2.2161 | 2.1822 | 2.1484 | 2.1145 | 2.0806 | 2.0626 | 2.0446 | 2.0265 | 2.0085 | 1.9905 | 1.9805 | 1.9705 | 1.9605 | 1.9505 | 1.9405 | 1.9305 | 1.9205 | 1.9105 | 1.9005 | 1.8905 | 1.9304 | 1.9702 | 2.0101 | 2.05 | 2.0898 | 2.1297 | 2.1696 | 2.2094 | 2.2493 | 2.2892 | 2.329 | 2.3689 | 2.4088 | 2.4486 | 2.4885 | 2.5321 | 2.5756 | 2.6192 | 2.6628 | 2.7064 | 2.75 | 2.7935 | 2.8371 | 2.8807 | 2.9242 | 2.9678 | 3.0114 | 3.055 | 3.0985 | 3.1421 | 3.3014 | 3.4608 | 3.6201 | 3.7794 | 3.9388 | 4.0981 | 4.2574 | 4.4167 | 4.5761 | 4.7354 | 4.8947 | 5.054 | 5.2134 | 5.3727 | 5.532 | 5.6913 | 5.8506 | 6.01 | 6.1693 | 6.3286 | 6.4879 | 6.6473 | 6.8066 | 6.9659 | 7.1253 | 7.2846 | 7.4439 | 7.6032 | 7.7626 | 7.9219 | 8.0668 | 8.2117 | 8.3567 | 8.5016 | 8.6465 | 8.7914 | 8.9363 | 9.0813 | 9.2262 | 9.3711 | 9.516 | 9.661 | 9.8059 | 9.9508 | 10.0958 | 10.2407 | 10.3856 | 10.5305 | 10.6754 | 10.8204 | 10.9653 | 11.1102 | 11.2552 | 11.4001 | 11.545 | 11.6899 | 11.8348 | 11.9798 | 12.1247 | 12.2696 | 12.3857 | 12.5019 | 12.618 | 12.7341 | 12.8503 | 12.9664 | 13.0825 | 13.1986 | 13.3148 | 13.4309 | 13.547 | 13.6631 | 13.7792 | 13.8954 | 14.0115 | 14.1276 | 14.2438 | 14.3599 | 14.476 | 14.5921 | 14.7082 | 14.8244 | 14.9405 | 15.0566 | 15.1728 | 15.2889 | 15.405 | 15.5211 | 15.6372 | 15.7534 | 15.8376 | 15.9218 | 16.006 | 16.0902 | 16.1745 | 16.2587 | 16.3429 | 16.4271 | 16.5113 | 16.5955 | 16.6798 | 16.764 | 16.8482 | 16.9324 | 17.0166 | 17.1008 | 17.1851 | 17.2693 | 17.3535 | 17.4377 | 17.5219 | 17.6061 | 17.6904 | 17.7746 | 17.8588 | 17.943 | 18.0272 | 18.1114 | 18.1957 | 18.2799
6.5 | 0 | 0.229 | 0.458 | 0.687 | 0.916 | 1.145 | 1.374 | 1.603 | 1.832 | 2.061 | 2.29 | 2.2572 | 2.2245 | 2.1917 | 2.159 | 2.1263 | 2.108 | 2.0897 | 2.0715 | 2.0532 | 2.035 | 2.025 | 2.015 | 2.005 | 1.995 | 1.985 | 1.975 | 1.965 | 1.955 | 1.945 | 1.935 | 1.9757 | 2.0163 | 2.057 | 2.0977 | 2.1383 | 2.179 | 2.2197 | 2.2603 | 2.301 | 2.3417 | 2.3823 | 2.423 | 2.4637 | 2.5043 | 2.545 | 2.5894 | 2.6338 | 2.6782 | 2.7227 | 2.7671 | 2.8115 | 2.8559 | 2.9003 | 2.9447 | 2.9892 | 3.0336 | 3.078 | 3.1224 | 3.1668 | 3.2113 | 3.3735 | 3.5358 | 3.698 | 3.8603 | 4.0225 | 4.1848 | 4.347 | 4.5092 | 4.6715 | 4.8338 | 4.996 | 5.1582 | 5.3205 | 5.4828 | 5.645 | 5.8072 | 5.9695 | 6.1318 | 6.294 | 6.4562 | 6.6185 | 6.7808 | 6.943 | 7.1052 | 7.2675 | 7.4298 | 7.592 | 7.7542 | 7.9165 | 8.0787 | 8.2263 | 8.3739 | 8.5215 | 8.6691 | 8.8167 | 8.9642 | 9.1118 | 9.2594 | 9.407 | 9.5546 | 9.7022 | 9.8498 | 9.9973 | 10.1449 | 10.2925 | 10.4401 | 10.5877 | 10.7353 | 10.8828 | 11.0304 | 11.178 | 11.3256 | 11.4732 | 11.6207 | 11.7683 | 11.9159 | 12.0635 | 12.2111 | 12.3587 | 12.5062 | 12.6245 | 12.7427 | 12.861 | 12.9793 | 13.0975 | 13.2157 | 13.334 | 13.4522 | 13.5705 | 13.6888 | 13.807 | 13.9253 | 14.0435 | 14.1617 | 14.28 | 14.3983 | 14.5165 | 14.6348 | 14.753 | 14.8712 | 14.9895 | 15.1077 | 15.226 | 15.3443 | 15.4625 | 15.5808 | 15.699 | 15.8172 | 15.9355 | 16.0538 | 16.1396 | 16.2254 | 16.3113 | 16.3971 | 16.4829 | 16.5688 | 16.6546 | 16.7404 | 16.8263 | 16.9121 | 16.9979 | 17.0837 | 17.1696 | 17.2554 | 17.3412 | 17.4271 | 17.5129 | 17.5987 | 17.6846 | 17.7704 | 17.8562 | 17.9421 | 18.0279 | 18.1137 | 18.1996 | 18.2854 | 18.3712 | 18.4571 | 18.5429 | 18.6287
6.55 | 0 | 0.233 | 0.466 | 0.699 | 0.932 | 1.165 | 1.398 | 1.631 | 1.864 | 2.097 | 2.33 | 2.2984 | 2.2668 | 2.2351 | 2.2035 | 2.1719 | 2.1534 | 2.1349 | 2.1164 | 2.098 | 2.0795 | 2.0695 | 2.0595 | 2.0495 | 2.0395 | 2.0295 | 2.0195 | 2.0095 | 1.9995 | 1.9895 | 1.9795 | 2.021 | 2.0624 | 2.1039 | 2.1454 | 2.1868 | 2.2283 | 2.2698 | 2.3112 | 2.3527 | 2.3942 | 2.4356 | 2.4771 | 2.5186 | 2.56 | 2.6015 | 2.6468 | 2.692 | 2.7373 | 2.7825 | 2.8278 | 2.8731 | 2.9183 | 2.9636 | 3.0088 | 3.0541 | 3.0993 | 3.1446 | 3.1899 | 3.2351 | 3.2804 | 3.4455 | 3.6107 | 3.7759 | 3.9411 | 4.1063 | 4.2714 | 4.4366 | 4.6018 | 4.7669 | 4.9321 | 5.0973 | 5.2625 | 5.4276 | 5.5928 | 5.758 | 5.9232 | 6.0884 | 6.2535 | 6.4187 | 6.5839 | 6.7491 | 6.9142 | 7.0794 | 7.2446 | 7.4097 | 7.5749 | 7.7401 | 7.9053 | 8.0704 | 8.2356 | 8.3859 | 8.5361 | 8.6863 | 8.8366 | 8.9868 | 9.1371 | 9.2873 | 9.4376 | 9.5878 | 9.738 | 9.8883 | 10.0385 | 10.1888 | 10.339 | 10.4893 | 10.6395 | 10.7897 | 10.94 | 11.0902 | 11.2405 | 11.3907 | 11.5409 | 11.6912 | 11.8414 | 11.9917 | 12.1419 | 12.2921 | 12.4424 | 12.5926 | 12.7429 | 12.8633 | 12.9836 | 13.104 | 13.2244 | 13.3447 | 13.4651 | 13.5855 | 13.7059 | 13.8262 | 13.9466 | 14.067 | 14.1874 | 14.3078 | 14.4281 | 14.5485 | 14.6689 | 14.7892 | 14.9096 | 15.03 | 15.1504 | 15.2707 | 15.3911 | 15.5115 | 15.6319 | 15.7523 | 15.8726 | 15.993 | 16.1134 | 16.2338 | 16.3541 | 16.4416 | 16.529 | 16.6165 | 16.7039 | 16.7914 | 16.8788 | 16.9663 | 17.0537 | 17.1412 | 17.2286 | 17.3161 | 17.4035 | 17.491 | 17.5784 | 17.6659 | 17.7533 | 17.8408 | 17.9282 | 18.0157 | 18.1031 | 18.1906 | 18.278 | 18.3655 | 18.4529 | 18.5404 | 18.6278 | 18.7153 | 18.8027 | 18.8902 | 18.9776
6.6 | 0 | 0.237 | 0.474 | 0.711 | 0.948 | 1.185 | 1.422 | 1.659 | 1.896 | 2.133 | 2.37 | 2.3395 | 2.309 | 2.2785 | 2.248 | 2.2175 | 2.1988 | 2.1801 | 2.1614 | 2.1427 | 2.124 | 2.114 | 2.104 | 2.094 | 2.084 | 2.074 | 2.064 | 2.054 | 2.044 | 2.034 | 2.024 | 2.0663 | 2.1085 | 2.1508 | 2.1931 | 2.2353 | 2.2776 | 2.3199 | 2.3621 | 2.4044 | 2.4467 | 2.4889 | 2.5312 | 2.5735 | 2.6157 | 2.658 | 2.7041 | 2.7502 | 2.7963 | 2.8424 | 2.8885 | 2.9346 | 2.9807 | 3.0268 | 3.0729 | 3.119 | 3.1651 | 3.2112 | 3.2573 | 3.3034 | 3.3495 | 3.5176 | 3.6857 | 3.8538 | 4.0219 | 4.19 | 4.3581 | 4.5262 | 4.6943 | 4.8624 | 5.0305 | 5.1986 | 5.3667 | 5.5348 | 5.7029 | 5.871 | 6.0391 | 6.2072 | 6.3753 | 6.5434 | 6.7115 | 6.8796 | 7.0477 | 7.2158 | 7.3839 | 7.552 | 7.7201 | 7.8882 | 8.0563 | 8.2244 | 8.3925 | 8.5454 | 8.6983 | 8.8512 | 9.0041 | 9.157 | 9.3099 | 9.4628 | 9.6157 | 9.7686 | 9.9215 | 10.0744 | 10.2273 | 10.3802 | 10.5331 | 10.686 | 10.8389 | 10.9918 | 11.1447 | 11.2976 | 11.4505 | 11.6034 | 11.7563 | 11.9092 | 12.0621 | 12.215 | 12.3679 | 12.5208 | 12.6737 | 12.8266 | 12.9795 | 13.102 | 13.2245 | 13.347 | 13.4695 | 13.592 | 13.7145 | 13.837 | 13.9595 | 14.082 | 14.2045 | 14.327 | 14.4495 | 14.572 | 14.6945 | 14.817 | 14.9395 | 15.062 | 15.1845 | 15.307 | 15.4295 | 15.552 | 15.6745 | 15.797 | 15.9195 | 16.042 | 16.1645 | 16.287 | 16.4095 | 16.532 | 16.6545 | 16.7436 | 16.8326 | 16.9217 | 17.0108 | 17.0998 | 17.1889 | 17.278 | 17.367 | 17.4561 | 17.5452 | 17.6342 | 17.7233 | 17.8124 | 17.9014 | 17.9905 | 18.0796 | 18.1686 | 18.2577 | 18.3468 | 18.4358 | 18.5249 | 18.614 | 18.703 | 18.7921 | 18.8812 | 18.9702 | 19.0593 | 19.1484 | 19.2374 | 19.3265
6.65 | 0 | 0.241 | 0.482 | 0.723 | 0.964 | 1.205 | 1.446 | 1.687 | 1.928 | 2.169 | 2.41 | 2.3806 | 2.3512 | 2.3219 | 2.2925 | 2.2631 | 2.2442 | 2.2253 | 2.2064 | 2.1874 | 2.1685 | 2.1585 | 2.1485 | 2.1385 | 2.1285 | 2.1185 | 2.1085 | 2.0985 | 2.0885 | 2.0785 | 2.0685 | 2.1116 | 2.1546 | 2.1977 | 2.2408 | 2.2838 | 2.3269 | 2.37 | 2.413 | 2.4561 | 2.4992 | 2.5422 | 2.5853 | 2.6284 | 2.6714 | 2.7145 | 2.7614 | 2.8084 | 2.8553 | 2.9023 | 2.9492 | 2.9962 | 3.0431 | 3.09 | 3.137 | 3.1839 | 3.2309 | 3.2778 | 3.3247 | 3.3717 | 3.4186 | 3.5896 | 3.7607 | 3.9317 | 4.1027 | 4.2737 | 4.4448 | 4.6158 | 4.7868 | 4.9578 | 5.1289 | 5.2999 | 5.4709 | 5.6419 | 5.813 | 5.984 | 6.155 | 6.3261 | 6.4971 | 6.6681 | 6.8391 | 7.0102 | 7.1812 | 7.3522 | 7.5232 | 7.6943 | 7.8653 | 8.0363 | 8.2073 | 8.3783 | 8.5494 | 8.7049 | 8.8605 | 9.016 | 9.1716 | 9.3272 | 9.4827 | 9.6383 | 9.7938 | 9.9494 | 10.105 | 10.2605 | 10.4161 | 10.5716 | 10.7272 | 10.8827 | 11.0383 | 11.1939 | 11.3494 | 11.505 | 11.6605 | 11.8161 | 11.9717 | 12.1272 | 12.2828 | 12.4383 | 12.5939 | 12.7494 | 12.905 | 13.0606 | 13.2161 | 13.3407 | 13.4654 | 13.59 | 13.7146 | 13.8392 | 13.9639 | 14.0885 | 14.2131 | 14.3377 | 14.4624 | 14.587 | 14.7116 | 14.8362 | 14.9609 | 15.0855 | 15.2101 | 15.3347 | 15.4594 | 15.584 | 15.7086 | 15.8332 | 15.9579 | 16.0825 | 16.2071 | 16.3317 | 16.4564 | 16.581 | 16.7056 | 16.8302 | 16.9549 | 17.0456 | 17.1362 | 17.2269 | 17.3176 | 17.4083 | 17.499 | 17.5897 | 17.6803 | 17.771 | 17.8617 | 17.9524 | 18.0431 | 18.1338 | 18.2244 | 18.3151 | 18.4058 | 18.4965 | 18.5872 | 18.6779 | 18.7685 | 18.8592 | 18.9499 | 19.0406 | 19.1313 | 19.222 | 19.3126 | 19.4033 | 19.494 | 19.5847 | 19.6754
6.7 | 0 | 0.245 | 0.49 | 0.735 | 0.98 | 1.225 | 1.47 | 1.715 | 1.96 | 2.205 | 2.45 | 2.4217 | 2.3935 | 2.3653 | 2.337 | 2.3087 | 2.2896 | 2.2704 | 2.2513 | 2.2321 | 2.213 | 2.203 | 2.193 | 2.183 | 2.173 | 2.163 | 2.153 | 2.143 | 2.133 | 2.123 | 2.113 | 2.1569 | 2.2007 | 2.2446 | 2.2885 | 2.3323 | 2.3762 | 2.4201 | 2.4639 | 2.5078 | 2.5517 | 2.5955 | 2.6394 | 2.6833 | 2.7271 | 2.771 | 2.8188 | 2.8666 | 2.9144 | 2.9621 | 3.0099 | 3.0577 | 3.1055 | 3.1533 | 3.201 | 3.2488 | 3.2966 | 3.3444 | 3.3922 | 3.44 | 3.4878 | 3.6617 | 3.8356 | 4.0096 | 4.1836 | 4.3575 | 4.5315 | 4.7054 | 4.8793 | 5.0533 | 5.2272 | 5.4012 | 5.5751 | 5.7491 | 5.923 | 6.097 | 6.271 | 6.4449 | 6.6189 | 6.7928 | 6.9668 | 7.1407 | 7.3147 | 7.4886 | 7.6626 | 7.8365 | 8.0105 | 8.1844 | 8.3583 | 8.5323 | 8.7063 | 8.8645 | 9.0227 | 9.1809 | 9.3391 | 9.4973 | 9.6555 | 9.8138 | 9.972 | 10.1302 | 10.2884 | 10.4466 | 10.6049 | 10.7631 | 10.9213 | 11.0795 | 11.2377 | 11.3959 | 11.5541 | 11.7124 | 11.8706 | 12.0288 | 12.187 | 12.3452 | 12.5035 | 12.6617 | 12.8199 | 12.9781 | 13.1363 | 13.2945 | 13.4527 | 13.5795 | 13.7063 | 13.833 | 13.9597 | 14.0865 | 14.2133 | 14.34 | 14.4667 | 14.5935 | 14.7203 | 14.847 | 14.9738 | 15.1005 | 15.2272 | 15.354 | 15.4808 | 15.6075 | 15.7342 | 15.861 | 15.9878 | 16.1145 | 16.2413 | 16.368 | 16.4947 | 16.6215 | 16.7482 | 16.875 | 17.0018 | 17.1285 | 17.2553 | 17.3475 | 17.4398 | 17.5322 | 17.6244 | 17.7168 | 17.809 | 17.9014 | 17.9936 | 18.086 | 18.1782 | 18.2706 | 18.3629 | 18.4551 | 18.5475 | 18.6397 | 18.7321 | 18.8243 | 18.9167 | 19.0089 | 19.1013 | 19.1935 | 19.2858 | 19.3782 | 19.4704 | 19.5628 | 19.655 | 19.7474 | 19.8396 | 19.932 | 20.0242
6.75 | 0 | 0.249 | 0.498 | 0.747 | 0.996 | 1.245 | 1.494 | 1.743 | 1.992 | 2.241 | 2.49 | 2.4629 | 2.4358 | 2.4086 | 2.3815 | 2.3544 | 2.335 | 2.3156 | 2.2963 | 2.2769 | 2.2575 | 2.2475 | 2.2375 | 2.2275 | 2.2175 | 2.2075 | 2.1975 | 2.1875 | 2.1775 | 2.1675 | 2.1575 | 2.2022 | 2.2468 | 2.2915 | 2.3362 | 2.3808 | 2.4255 | 2.4702 | 2.5148 | 2.5595 | 2.6042 | 2.6488 | 2.6935 | 2.7382 | 2.7828 | 2.8275 | 2.8761 | 2.9247 | 2.9734 | 3.022 | 3.0706 | 3.1193 | 3.1679 | 3.2165 | 3.2651 | 3.3138 | 3.3624 | 3.411 | 3.4596 | 3.5082 | 3.5569 | 3.7338 | 3.9106 | 4.0875 | 4.2644 | 4.4413 | 4.6181 | 4.795 | 4.9719 | 5.1487 | 5.3256 | 5.5025 | 5.6794 | 5.8563 | 6.0331 | 6.21 | 6.3869 | 6.5637 | 6.7406 | 6.9175 | 7.0944 | 7.2713 | 7.4481 | 7.625 | 7.8019 | 7.9787 | 8.1556 | 8.3325 | 8.5094 | 8.6862 | 8.8631 | 9.024 | 9.1849 | 9.3458 | 9.5066 | 9.6675 | 9.8284 | 9.9893 | 10.1501 | 10.311 | 10.4719 | 10.6327 | 10.7936 | 10.9545 | 11.1154 | 11.2762 | 11.4371 | 11.598 | 11.7589 | 11.9198 | 12.0806 | 12.2415 | 12.4024 | 12.5633 | 12.7241 | 12.885 | 13.0459 | 13.2067 | 13.3676 | 13.5285 | 13.6894 | 13.8183 | 13.9471 | 14.076 | 14.2049 | 14.3338 | 14.4626 | 14.5915 | 14.7204 | 14.8492 | 14.9781 | 15.107 | 15.2359 | 15.3648 | 15.4936 | 15.6225 | 15.7514 | 15.8803 | 16.0091 | 16.138 | 16.2669 | 16.3957 | 16.5246 | 16.6535 | 16.7824 | 16.9112 | 17.0401 | 17.169 | 17.2979 | 17.4267 | 17.5556 | 17.6495 | 17.7435 | 17.8374 | 17.9313 | 18.0252 | 18.1191 | 18.213 | 18.307 | 18.4009 | 18.4948 | 18.5887 | 18.6826 | 18.7765 | 18.8705 | 18.9644 | 19.0583 | 19.1522 | 19.2461 | 19.34 | 19.434 | 19.5279 | 19.6218 | 19.7157 | 19.8096 | 19.9035 | 19.9975 | 20.0914 | 20.1853 | 20.2792 | 20.3731
6.8 | 0 | 0.253 | 0.506 | 0.759 | 1.012 | 1.265 | 1.518 | 1.771 | 2.024 | 2.277 | 2.53 | 2.504 | 2.478 | 2.452 | 2.426 | 2.4 | 2.3804 | 2.3608 | 2.3412 | 2.3216 | 2.302 | 2.292 | 2.282 | 2.272 | 2.262 | 2.252 | 2.242 | 2.232 | 2.222 | 2.212 | 2.202 | 2.2475 | 2.2929 | 2.3384 | 2.3839 | 2.4293 | 2.4748 | 2.5203 | 2.5657 | 2.6112 | 2.6567 | 2.7021 | 2.7476 | 2.7931 | 2.8385 | 2.884 | 2.9335 | 2.9829 | 3.0324 | 3.0819 | 3.1313 | 3.1808 | 3.2303 | 3.2797 | 3.3292 | 3.3787 | 3.4281 | 3.4776 | 3.5271 | 3.5765 | 3.626 | 3.8058 | 3.9856 | 4.1654 | 4.3452 | 4.525 | 4.7048 | 4.8846 | 5.0644 | 5.2442 | 5.424 | 5.6038 | 5.7836 | 5.9634 | 6.1432 | 6.323 | 6.5028 | 6.6826 | 6.8624 | 7.0422 | 7.222 | 7.4018 | 7.5816 | 7.7614 | 7.9412 | 8.121 | 8.3008 | 8.4806 | 8.6604 | 8.8402 | 9.02 | 9.1835 | 9.3471 | 9.5106 | 9.6741 | 9.8377 | 10.0012 | 10.1647 | 10.3283 | 10.4918 | 10.6553 | 10.8189 | 10.9824 | 11.1459 | 11.3095 | 11.473 | 11.6365 | 11.8001 | 11.9636 | 12.1271 | 12.2907 | 12.4542 | 12.6177 | 12.7813 | 12.9448 | 13.1083 | 13.2719 | 13.4354 | 13.5989 | 13.7625 | 13.926 | 14.057 | 14.188 | 14.319 | 14.45 | 14.581 | 14.712 | 14.843 | 14.974 | 15.105 | 15.236 | 15.367 | 15.498 | 15.629 | 15.76 | 15.891 | 16.022 | 16.153 | 16.284 | 16.415 | 16.546 | 16.677 | 16.808 | 16.939 | 17.07 | 17.201 | 17.332 | 17.463 | 17.594 | 17.725 | 17.856 | 17.9515 | 18.0471 | 18.1426 | 18.2381 | 18.3337 | 18.4292 | 18.5247 | 18.6203 | 18.7158 | 18.8113 | 18.9069 | 19.0024 | 19.0979 | 19.1935 | 19.289 | 19.3845 | 19.4801 | 19.5756 | 19.6711 | 19.7667 | 19.8622 | 19.9577 | 20.0533 | 20.1488 | 20.2443 | 20.3399 | 20.4354 | 20.5309 | 20.6265 | 20.722
6.85 | 0 | 0.257 | 0.514 | 0.771 | 1.028 | 1.285 | 1.542 | 1.799 | 2.056 | 2.313 | 2.57 | 2.5451 | 2.5202 | 2.4954 | 2.4705 | 2.4456 | 2.4258 | 2.406 | 2.3862 | 2.3663 | 2.3465 | 2.3365 | 2.3265 | 2.3165 | 2.3065 | 2.2965 | 2.2865 | 2.2765 | 2.2665 | 2.2565 | 2.2465 | 2.2928 | 2.339 | 2.3853 | 2.4316 | 2.4778 | 2.5241 | 2.5704 | 2.6166 | 2.6629 | 2.7092 | 2.7554 | 2.8017 | 2.848 | 2.8942 | 2.9405 | 2.9908 | 3.0411 | 3.0914 | 3.1417 | 3.192 | 3.2424 | 3.2927 | 3.343 | 3.3933 | 3.4436 | 3.4939 | 3.5442 | 3.5945 | 3.6448 | 3.6951 | 3.8779 | 4.0606 | 4.2433 | 4.426 | 4.6087 | 4.7915 | 4.9742 | 5.1569 | 5.3396 | 5.5224 | 5.7051 | 5.8878 | 6.0705 | 6.2533 | 6.436 | 6.6187 | 6.8014 | 6.9842 | 7.1669 | 7.3496 | 7.5324 | 7.7151 | 7.8978 | 8.0805 | 8.2632 | 8.446 | 8.6287 | 8.8114 | 8.9941 | 9.1769 | 9.3431 | 9.5093 | 9.6754 | 9.8416 | 10.0078 | 10.174 | 10.3402 | 10.5064 | 10.6726 | 10.8388 | 11.005 | 11.1712 | 11.3374 | 11.5036 | 11.6698 | 11.8359 | 12.0021 | 12.1683 | 12.3345 | 12.5007 | 12.6669 | 12.8331 | 12.9993 | 13.1655 | 13.3317 | 13.4979 | 13.664 | 13.8302 | 13.9964 | 14.1626 | 14.2957 | 14.4289 | 14.562 | 14.6951 | 14.8283 | 14.9614 | 15.0945 | 15.2276 | 15.3607 | 15.4939 | 15.627 | 15.7601 | 15.8933 | 16.0264 | 16.1595 | 16.2926 | 16.4258 | 16.5589 | 16.692 | 16.8251 | 16.9582 | 17.0914 | 17.2245 | 17.3576 | 17.4907 | 17.6239 | 17.757 | 17.8901 | 18.0233 | 18.1564 | 18.2535 | 18.3507 | 18.4478 | 18.545 | 18.6421 | 18.7393 | 18.8364 | 18.9336 | 19.0307 | 19.1279 | 19.225 | 19.3222 | 19.4193 | 19.5165 | 19.6136 | 19.7108 | 19.8079 | 19.9051 | 20.0022 | 20.0994 | 20.1965 | 20.2937 | 20.3908 | 20.488 | 20.5851 | 20.6823 | 20.7794 | 20.8766 | 20.9737 | 21.0709
6.9 | 0 | 0.261 | 0.522 | 0.783 | 1.044 | 1.305 | 1.566 | 1.827 | 2.088 | 2.349 | 2.61 | 2.5863 | 2.5625 | 2.5387 | 2.515 | 2.4912 | 2.4712 | 2.4512 | 2.4311 | 2.411 | 2.391 | 2.381 | 2.371 | 2.361 | 2.351 | 2.341 | 2.331 | 2.321 | 2.311 | 2.301 | 2.291 | 2.3381 | 2.3851 | 2.4322 | 2.4793 | 2.5263 | 2.5734 | 2.6205 | 2.6675 | 2.7146 | 2.7617 | 2.8087 | 2.8558 | 2.9029 | 2.9499 | 2.997 | 3.0482 | 3.0993 | 3.1505 | 3.2016 | 3.2527 | 3.3039 | 3.355 | 3.4062 | 3.4573 | 3.5085 | 3.5596 | 3.6108 | 3.662 | 3.7131 | 3.7643 | 3.9499 | 4.1356 | 4.3212 | 4.5069 | 4.6925 | 4.8781 | 5.0638 | 5.2495 | 5.4351 | 5.6208 | 5.8064 | 5.992 | 6.1777 | 6.3633 | 6.549 | 6.7347 | 6.9203 | 7.1059 | 7.2916 | 7.4772 | 7.6629 | 7.8486 | 8.0342 | 8.2198 | 8.4055 | 8.5912 | 8.7768 | 8.9625 | 9.1481 | 9.3338 | 9.5026 | 9.6715 | 9.8403 | 10.0091 | 10.178 | 10.3468 | 10.5157 | 10.6845 | 10.8534 | 11.0222 | 11.1911 | 11.3599 | 11.5288 | 11.6976 | 11.8665 | 12.0353 | 12.2042 | 12.373 | 12.5419 | 12.7108 | 12.8796 | 13.0485 | 13.2173 | 13.3862 | 13.555 | 13.7239 | 13.8927 | 14.0616 | 14.2304 | 14.3993 | 14.5345 | 14.6698 | 14.805 | 14.9403 | 15.0755 | 15.2108 | 15.346 | 15.4812 | 15.6165 | 15.7517 | 15.887 | 16.0222 | 16.1575 | 16.2928 | 16.428 | 16.5633 | 16.6985 | 16.8337 | 16.969 | 17.1043 | 17.2395 | 17.3747 | 17.51 | 17.6453 | 17.7805 | 17.9157 | 18.051 | 18.1863 | 18.3215 | 18.4567 | 18.5555 | 18.6543 | 18.7531 | 18.8518 | 18.9506 | 19.0494 | 19.1481 | 19.2469 | 19.3456 | 19.4444 | 19.5432 | 19.642 | 19.7407 | 19.8395 | 19.9383 | 20.037 | 20.1358 | 20.2345 | 20.3333 | 20.4321 | 20.5309 | 20.6296 | 20.7284 | 20.8271 | 20.9259 | 21.0247 | 21.1234 | 21.2222 | 21.321 | 21.4197
6.95 | 0 | 0.265 | 0.53 | 0.795 | 1.06 | 1.325 | 1.59 | 1.855 | 2.12 | 2.385 | 2.65 | 2.6274 | 2.6048 | 2.5821 | 2.5595 | 2.5369 | 2.5166 | 2.4963 | 2.476 | 2.4558 | 2.4355 | 2.4255 | 2.4155 | 2.4055 | 2.3955 | 2.3855 | 2.3755 | 2.3655 | 2.3555 | 2.3455 | 2.3355 | 2.3834 | 2.4312 | 2.4791 | 2.527 | 2.5748 | 2.6227 | 2.6706 | 2.7184 | 2.7663 | 2.8142 | 2.862 | 2.9099 | 2.9578 | 3.0056 | 3.0535 | 3.1055 | 3.1575 | 3.2095 | 3.2615 | 3.3135 | 3.3655 | 3.4174 | 3.4694 | 3.5214 | 3.5734 | 3.6254 | 3.6774 | 3.7294 | 3.7814 | 3.8334 | 4.022 | 4.2105 | 4.3991 | 4.5877 | 4.7763 | 4.9648 | 5.1534 | 5.342 | 5.5305 | 5.7191 | 5.9077 | 6.0963 | 6.2848 | 6.4734 | 6.662 | 6.8506 | 7.0392 | 7.2277 | 7.4163 | 7.6049 | 7.7934 | 7.982 | 8.1706 | 8.3592 | 8.5478 | 8.7363 | 8.9249 | 9.1135 | 9.302 | 9.4906 | 9.6621 | 9.8336 | 10.0052 | 10.1767 | 10.3482 | 10.5197 | 10.6912 | 10.8627 | 11.0342 | 11.2057 | 11.3772 | 11.5487 | 11.7202 | 11.8917 | 12.0633 | 12.2348 | 12.4063 | 12.5778 | 12.7493 | 12.9208 | 13.0923 | 13.2638 | 13.4353 | 13.6068 | 13.7783 | 13.9498 | 14.1213 | 14.2929 | 14.4644 | 14.6359 | 14.7733 | 14.9106 | 15.048 | 15.1854 | 15.3227 | 15.4601 | 15.5975 | 15.7349 | 15.8722 | 16.0096 | 16.147 | 16.2844 | 16.4217 | 16.5591 | 16.6965 | 16.8339 | 16.9713 | 17.1086 | 17.246 | 17.3834 | 17.5207 | 17.6581 | 17.7955 | 17.9329 | 18.0703 | 18.2076 | 18.345 | 18.4824 | 18.6197 | 18.7571 | 18.8575 | 18.9579 | 19.0583 | 19.1587 | 19.259 | 19.3594 | 19.4598 | 19.5602 | 19.6606 | 19.761 | 19.8613 | 19.9617 | 20.0621 | 20.1625 | 20.2629 | 20.3633 | 20.4636 | 20.564 | 20.6644 | 20.7648 | 20.8652 | 20.9656 | 21.0659 | 21.1663 | 21.2667 | 21.3671 | 21.4675 | 21.5679 | 21.6682 | 21.7686
7 | 0 | 0.269 | 0.538 | 0.807 | 1.076 | 1.345 | 1.614 | 1.883 | 2.152 | 2.421 | 2.69 | 2.6685 | 2.647 | 2.6255 | 2.604 | 2.5825 | 2.562 | 2.5415 | 2.521 | 2.5005 | 2.48 | 2.47 | 2.46 | 2.45 | 2.44 | 2.43 | 2.42 | 2.41 | 2.4 | 2.39 | 2.38 | 2.4287 | 2.4773 | 2.526 | 2.5747 | 2.6233 | 2.672 | 2.7207 | 2.7693 | 2.818 | 2.8667 | 2.9153 | 2.964 | 3.0127 | 3.0613 | 3.11 | 3.1628 | 3.2157 | 3.2685 | 3.3213 | 3.3742 | 3.427 | 3.4798 | 3.5327 | 3.5855 | 3.6383 | 3.6912 | 3.744 | 3.7968 | 3.8497 | 3.9025 | 4.094 | 4.2855 | 4.477 | 4.6685 | 4.86 | 5.0515 | 5.243 | 5.4345 | 5.626 | 5.8175 | 6.009 | 6.2005 | 6.392 | 6.5835 | 6.775 | 6.9665 | 7.158 | 7.3495 | 7.541 | 7.7325 | 7.924 | 8.1155 | 8.307 | 8.4985 | 8.69 | 8.8815 | 9.073 | 9.2645 | 9.456 | 9.6475 | 9.8217 | 9.9958 | 10.17 | 10.3442 | 10.5183 | 10.6925 | 10.8667 | 11.0408 | 11.215 | 11.3892 | 11.5633 | 11.7375 | 11.9117 | 12.0858 | 12.26 | 12.4342 | 12.6083 | 12.7825 | 12.9567 | 13.1308 | 13.305 | 13.4792 | 13.6533 | 13.8275 | 14.0017 | 14.1758 | 14.35 | 14.5242 | 14.6983 | 14.8725 | 15.012 | 15.1515 | 15.291 | 15.4305 | 15.57 | 15.7095 | 15.849 | 15.9885 | 16.128 | 16.2675 | 16.407 | 16.5465 | 16.686 | 16.8255 | 16.965 | 17.1045 | 17.244 | 17.3835 | 17.523 | 17.6625 | 17.802 | 17.9415 | 18.081 | 18.2205 | 18.36 | 18.4995 | 18.639 | 18.7785 | 18.918 | 19.0575 | 19.1595 | 19.2615 | 19.3635 | 19.4655 | 19.5675 | 19.6695 | 19.7715 | 19.8735 | 19.9755 | 20.0775 | 20.1795 | 20.2815 | 20.3835 | 20.4855 | 20.5875 | 20.6895 | 20.7915 | 20.8935 | 20.9955 | 21.0975 | 21.1995 | 21.3015 | 21.4035 | 21.5055 | 21.6075 | 21.7095 | 21.8115 | 21.9135 | 22.0155 | 22.1175
7.05 | 0 | 0.273 | 0.546 | 0.819 | 1.092 | 1.365 | 1.638 | 1.911 | 2.184 | 2.457 | 2.73 | 2.7096 | 2.6892 | 2.6689 | 2.6485 | 2.6281 | 2.6074 | 2.5867 | 2.5659 | 2.5452 | 2.5245 | 2.5145 | 2.5045 | 2.4945 | 2.4845 | 2.4745 | 2.4645 | 2.4545 | 2.4445 | 2.4345 | 2.4245 | 2.474 | 2.5234 | 2.5729 | 2.6224 | 2.6718 | 2.7213 | 2.7708 | 2.8202 | 2.8697 | 2.9192 | 2.9686 | 3.0181 | 3.0676 | 3.117 | 3.1665 | 3.2202 | 3.2738 | 3.3275 | 3.3812 | 3.4349 | 3.4886 | 3.5422 | 3.5959 | 3.6496 | 3.7033 | 3.7569 | 3.8106 | 3.8643 | 3.9179 | 3.9716 | 4.1661 | 4.3605 | 4.5549 | 4.7493 | 4.9437 | 5.1382 | 5.3326 | 5.527 | 5.7214 | 5.9159 | 6.1103 | 6.3047 | 6.4992 | 6.6936 | 6.888 | 7.0824 | 7.2768 | 7.4713 | 7.6657 | 7.8601 | 8.0546 | 8.249 | 8.4434 | 8.6378 | 8.8323 | 9.0267 | 9.2211 | 9.4155 | 9.6099 | 9.8044 | 9.9812 | 10.158 | 10.3348 | 10.5117 | 10.6885 | 10.8653 | 11.0421 | 11.219 | 11.3958 | 11.5726 | 11.7494 | 11.9263 | 12.1031 | 12.2799 | 12.4567 | 12.6336 | 12.8104 | 12.9872 | 13.164 | 13.3409 | 13.5177 | 13.6945 | 13.8713 | 14.0482 | 14.225 | 14.4018 | 14.5786 | 14.7555 | 14.9323 | 15.1091 | 15.2508 | 15.3924 | 15.534 | 15.6756 | 15.8172 | 15.9589 | 16.1005 | 16.2421 | 16.3837 | 16.5254 | 16.667 | 16.8086 | 16.9503 | 17.0919 | 17.2335 | 17.3751 | 17.5167 | 17.6584 | 17.8 | 17.9416 | 18.0832 | 18.2249 | 18.3665 | 18.5081 | 18.6498 | 18.7914 | 18.933 | 19.0746 | 19.2162 | 19.3579 | 19.4615 | 19.5651 | 19.6687 | 19.7723 | 19.876 | 19.9796 | 20.0832 | 20.1868 | 20.2904 | 20.394 | 20.4977 | 20.6013 | 20.7049 | 20.8085 | 20.9121 | 21.0157 | 21.1194 | 21.223 | 21.3266 | 21.4302 | 21.5338 | 21.6374 | 21.7411 | 21.8447 | 21.9483 | 22.0519 | 22.1555 | 22.2591 | 22.3628 | 22.4664
7.1 | 0 | 0.277 | 0.554 | 0.831 | 1.108 | 1.385 | 1.662 | 1.939 | 2.216 | 2.493 | 2.77 | 2.7508 | 2.7315 | 2.7123 | 2.693 | 2.6738 | 2.6528 | 2.6319 | 2.6109 | 2.5899 | 2.569 | 2.559 | 2.549 | 2.539 | 2.529 | 2.519 | 2.509 | 2.499 | 2.489 | 2.479 | 2.469 | 2.5193 | 2.5695 | 2.6198 | 2.6701 | 2.7203 | 2.7706 | 2.8209 | 2.8711 | 2.9214 | 2.9717 | 3.0219 | 3.0722 | 3.1225 | 3.1727 | 3.223 | 3.2775 | 3.332 | 3.3866 | 3.4411 | 3.4956 | 3.5501 | 3.6046 | 3.6591 | 3.7136 | 3.7682 | 3.8227 | 3.8772 | 3.9317 | 3.9862 | 4.0408 | 4.2381 | 4.4355 | 4.6328 | 4.8301 | 5.0275 | 5.2248 | 5.4222 | 5.6196 | 5.8169 | 6.0142 | 6.2116 | 6.4089 | 6.6063 | 6.8037 | 7.001 | 7.1983 | 7.3957 | 7.593 | 7.7904 | 7.9878 | 8.1851 | 8.3825 | 8.5798 | 8.7772 | 8.9745 | 9.1718 | 9.3692 | 9.5665 | 9.7639 | 9.9612 | 10.1407 | 10.3202 | 10.4997 | 10.6792 | 10.8587 | 11.0381 | 11.2176 | 11.3971 | 11.5766 | 11.7561 | 11.9356 | 12.1151 | 12.2945 | 12.474 | 12.6535 | 12.833 | 13.0125 | 13.192 | 13.3714 | 13.5509 | 13.7304 | 13.9099 | 14.0894 | 14.2689 | 14.4483 | 14.6278 | 14.8073 | 14.9868 | 15.1663 | 15.3458 | 15.4895 | 15.6333 | 15.777 | 15.9207 | 16.0645 | 16.2082 | 16.352 | 16.4958 | 16.6395 | 16.7832 | 16.927 | 17.0708 | 17.2145 | 17.3583 | 17.502 | 17.6457 | 17.7895 | 17.9333 | 18.077 | 18.2207 | 18.3645 | 18.5083 | 18.652 | 18.7958 | 18.9395 | 19.0832 | 19.227 | 19.3708 | 19.5145 | 19.6582 | 19.7635 | 19.8687 | 19.9739 | 20.0792 | 20.1844 | 20.2897 | 20.3949 | 20.5001 | 20.6054 | 20.7106 | 20.8158 | 20.9211 | 21.0263 | 21.1315 | 21.2368 | 21.342 | 21.4472 | 21.5525 | 21.6577 | 21.7629 | 21.8681 | 21.9734 | 22.0786 | 22.1838 | 22.2891 | 22.3943 | 22.4995 | 22.6048 | 22.71 | 22.8152
7.15 | 0 | 0.281 | 0.562 | 0.843 | 1.124 | 1.405 | 1.686 | 1.967 | 2.248 | 2.529 | 2.81 | 2.7919 | 2.7738 | 2.7556 | 2.7375 | 2.7194 | 2.6982 | 2.677 | 2.6559 | 2.6347 | 2.6135 | 2.6035 | 2.5935 | 2.5835 | 2.5735 | 2.5635 | 2.5535 | 2.5435 | 2.5335 | 2.5235 | 2.5135 | 2.5646 | 2.6156 | 2.6667 | 2.7178 | 2.7688 | 2.8199 | 2.871 | 2.922 | 2.9731 | 3.0242 | 3.0752 | 3.1263 | 3.1774 | 3.2284 | 3.2795 | 3.3349 | 3.3902 | 3.4456 | 3.5009 | 3.5563 | 3.6117 | 3.667 | 3.7224 | 3.7777 | 3.8331 | 3.8884 | 3.9438 | 3.9992 | 4.0545 | 4.1099 | 4.3102 | 4.5104 | 4.7107 | 4.911 | 5.1113 | 5.3115 | 5.5118 | 5.7121 | 5.9123 | 6.1126 | 6.3129 | 6.5132 | 6.7134 | 6.9137 | 7.114 | 7.3143 | 7.5145 | 7.7148 | 7.9151 | 8.1154 | 8.3157 | 8.5159 | 8.7162 | 8.9165 | 9.1167 | 9.317 | 9.5173 | 9.7176 | 9.9178 | 10.1181 | 10.3003 | 10.4824 | 10.6646 | 10.8467 | 11.0288 | 11.211 | 11.3931 | 11.5753 | 11.7574 | 11.9395 | 12.1217 | 12.3038 | 12.486 | 12.6681 | 12.8503 | 13.0324 | 13.2145 | 13.3967 | 13.5788 | 13.761 | 13.9431 | 14.1252 | 14.3074 | 14.4895 | 14.6717 | 14.8538 | 15.0359 | 15.2181 | 15.4002 | 15.5824 | 15.7282 | 15.8741 | 16.02 | 16.1659 | 16.3117 | 16.4576 | 16.6035 | 16.7494 | 16.8953 | 17.0411 | 17.187 | 17.3329 | 17.4788 | 17.6246 | 17.7705 | 17.9164 | 18.0622 | 18.2081 | 18.354 | 18.4999 | 18.6457 | 18.7916 | 18.9375 | 19.0834 | 19.2293 | 19.3751 | 19.521 | 19.6669 | 19.8128 | 19.9586 | 20.0655 | 20.1723 | 20.2792 | 20.386 | 20.4929 | 20.5997 | 20.7066 | 20.8134 | 20.9203 | 21.0271 | 21.134 | 21.2408 | 21.3477 | 21.4545 | 21.5614 | 21.6682 | 21.7751 | 21.8819 | 21.9888 | 22.0956 | 22.2025 | 22.3093 | 22.4162 | 22.523 | 22.6299 | 22.7367 | 22.8436 | 22.9504 | 23.0573 | 23.1641
7.2 | 0 | 0.285 | 0.57 | 0.855 | 1.14 | 1.425 | 1.71 | 1.995 | 2.28 | 2.565 | 2.85 | 2.833 | 2.816 | 2.799 | 2.782 | 2.765 | 2.7436 | 2.7222 | 2.7008 | 2.6794 | 2.658 | 2.648 | 2.638 | 2.628 | 2.618 | 2.608 | 2.598 | 2.588 | 2.578 | 2.568 | 2.558 | 2.6099 | 2.6617 | 2.7136 | 2.7655 | 2.8173 | 2.8692 | 2.9211 | 2.9729 | 3.0248 | 3.0767 | 3.1285 | 3.1804 | 3.2323 | 3.2841 | 3.336 | 3.3922 | 3.4484 | 3.5046 | 3.5608 | 3.617 | 3.6732 | 3.7294 | 3.7856 | 3.8418 | 3.898 | 3.9542 | 4.0104 | 4.0666 | 4.1228 | 4.179 | 4.3822 | 4.5854 | 4.7886 | 4.9918 | 5.195 | 5.3982 | 5.6014 | 5.8046 | 6.0078 | 6.211 | 6.4142 | 6.6174 | 6.8206 | 7.0238 | 7.227 | 7.4302 | 7.6334 | 7.8366 | 8.0398 | 8.243 | 8.4462 | 8.6494 | 8.8526 | 9.0558 | 9.259 | 9.4622 | 9.6654 | 9.8686 | 10.0718 | 10.275 | 10.4598 | 10.6446 | 10.8294 | 11.0142 | 11.199 | 11.3838 | 11.5686 | 11.7534 | 11.9382 | 12.123 | 12.3078 | 12.4926 | 12.6774 | 12.8622 | 13.047 | 13.2318 | 13.4166 | 13.6014 | 13.7862 | 13.971 | 14.1558 | 14.3406 | 14.5254 | 14.7102 | 14.895 | 15.0798 | 15.2646 | 15.4494 | 15.6342 | 15.819 | 15.967 | 16.115 | 16.263 | 16.411 | 16.559 | 16.707 | 16.855 | 17.003 | 17.151 | 17.299 | 17.447 | 17.595 | 17.743 | 17.891 | 18.039 | 18.187 | 18.335 | 18.483 | 18.631 | 18.779 | 18.927 | 19.075 | 19.223 | 19.371 | 19.519 | 19.667 | 19.815 | 19.963 | 20.111 | 20.259 | 20.3675 | 20.4759 | 20.5844 | 20.6929 | 20.8013 | 20.9098 | 21.0183 | 21.1267 | 21.2352 | 21.3437 | 21.4521 | 21.5606 | 21.6691 | 21.7775 | 21.886 | 21.9945 | 22.1029 | 22.2114 | 22.3199 | 22.4283 | 22.5368 | 22.6453 | 22.7537 | 22.8622 | 22.9707 | 23.0791 | 23.1876 | 23.2961 | 23.4045 | 23.513
7.25 | 0 | 0.289 | 0.578 | 0.867 | 1.156 | 1.445 | 1.734 | 2.023 | 2.312 | 2.601 | 2.89 | 2.8741 | 2.8582 | 2.8424 | 2.8265 | 2.8106 | 2.789 | 2.7674 | 2.7458 | 2.7241 | 2.7025 | 2.6925 | 2.6825 | 2.6725 | 2.6625 | 2.6525 | 2.6425 | 2.6325 | 2.6225 | 2.6125 | 2.6025 | 2.6552 | 2.7078 | 2.7605 | 2.8132 | 2.8658 | 2.9185 | 2.9712 | 3.0238 | 3.0765 | 3.1292 | 3.1818 | 3.2345 | 3.2872 | 3.3398 | 3.3925 | 3.4495 | 3.5066 | 3.5636 | 3.6207 | 3.6777 | 3.7348 | 3.7918 | 3.8488 | 3.9059 | 3.9629 | 4.02 | 4.077 | 4.134 | 4.1911 | 4.2481 | 4.4543 | 4.6604 | 4.8665 | 5.0726 | 5.2787 | 5.4849 | 5.691 | 5.8971 | 6.1033 | 6.3094 | 6.5155 | 6.7216 | 6.9277 | 7.1339 | 7.34 | 7.5461 | 7.7523 | 7.9584 | 8.1645 | 8.3706 | 8.5768 | 8.7829 | 8.989 | 9.1951 | 9.4012 | 9.6074 | 9.8135 | 10.0196 | 10.2257 | 10.4319 | 10.6193 | 10.8068 | 10.9942 | 11.1817 | 11.3692 | 11.5566 | 11.7441 | 11.9315 | 12.119 | 12.3065 | 12.4939 | 12.6814 | 12.8688 | 13.0563 | 13.2438 | 13.4312 | 13.6187 | 13.8061 | 13.9936 | 14.181 | 14.3685 | 14.556 | 14.7434 | 14.9309 | 15.1183 | 15.3058 | 15.4932 | 15.6807 | 15.8682 | 16.0556 | 16.2057 | 16.3559 | 16.506 | 16.6561 | 16.8062 | 16.9564 | 17.1065 | 17.2566 | 17.4067 | 17.5569 | 17.707 | 17.8571 | 18.0072 | 18.1574 | 18.3075 | 18.4576 | 18.6077 | 18.7579 | 18.908 | 19.0581 | 19.2082 | 19.3584 | 19.5085 | 19.6586 | 19.8087 | 19.9589 | 20.109 | 20.2591 | 20.4093 | 20.5594 | 20.6695 | 20.7795 | 20.8896 | 20.9997 | 21.1098 | 21.2199 | 21.33 | 21.44 | 21.5501 | 21.6602 | 21.7703 | 21.8804 | 21.9905 | 22.1005 | 22.2106 | 22.3207 | 22.4308 | 22.5409 | 22.651 | 22.761 | 22.8711 | 22.9812 | 23.0913 | 23.2014 | 23.3115 | 23.4215 | 23.5316 | 23.6417 | 23.7518 | 23.8619
7.3 | 0 | 0.293 | 0.586 | 0.879 | 1.172 | 1.465 | 1.758 | 2.051 | 2.344 | 2.637 | 2.93 | 2.9152 | 2.9005 | 2.8857 | 2.871 | 2.8563 | 2.8344 | 2.8125 | 2.7907 | 2.7689 | 2.747 | 2.737 | 2.727 | 2.717 | 2.707 | 2.697 | 2.687 | 2.677 | 2.667 | 2.657 | 2.647 | 2.7005 | 2.7539 | 2.8074 | 2.8609 | 2.9143 | 2.9678 | 3.0213 | 3.0747 | 3.1282 | 3.1817 | 3.2351 | 3.2886 | 3.3421 | 3.3955 | 3.449 | 3.5069 | 3.5648 | 3.6227 | 3.6805 | 3.7384 | 3.7963 | 3.8542 | 3.9121 | 3.9699 | 4.0278 | 4.0857 | 4.1436 | 4.2015 | 4.2594 | 4.3172 | 4.5263 | 4.7354 | 4.9444 | 5.1535 | 5.3625 | 5.5716 | 5.7806 | 5.9897 | 6.1987 | 6.4078 | 6.6168 | 6.8258 | 7.0349 | 7.2439 | 7.453 | 7.662 | 7.8711 | 8.0801 | 8.2892 | 8.4983 | 8.7073 | 8.9163 | 9.1254 | 9.3345 | 9.5435 | 9.7525 | 9.9616 | 10.1707 | 10.3797 | 10.5887 | 10.7789 | 10.969 | 11.1591 | 11.3492 | 11.5393 | 11.7294 | 11.9196 | 12.1097 | 12.2998 | 12.4899 | 12.68 | 12.8702 | 13.0603 | 13.2504 | 13.4405 | 13.6306 | 13.8207 | 14.0108 | 14.201 | 14.3911 | 14.5812 | 14.7713 | 14.9614 | 15.1516 | 15.3417 | 15.5318 | 15.7219 | 15.912 | 16.1021 | 16.2922 | 16.4445 | 16.5968 | 16.749 | 16.9013 | 17.0535 | 17.2057 | 17.358 | 17.5102 | 17.6625 | 17.8148 | 17.967 | 18.1193 | 18.2715 | 18.4237 | 18.576 | 18.7282 | 18.8805 | 19.0328 | 19.185 | 19.3373 | 19.4895 | 19.6417 | 19.794 | 19.9462 | 20.0985 | 20.2508 | 20.403 | 20.5553 | 20.7075 | 20.8597 | 20.9715 | 21.0831 | 21.1948 | 21.3066 | 21.4183 | 21.5299 | 21.6416 | 21.7534 | 21.8651 | 21.9767 | 22.0885 | 22.2002 | 22.3118 | 22.4235 | 22.5353 | 22.647 | 22.7586 | 22.8703 | 22.9821 | 23.0938 | 23.2054 | 23.3172 | 23.4289 | 23.5405 | 23.6522 | 23.764 | 23.8757 | 23.9873 | 24.099 | 24.2107
7.35 | 0 | 0.297 | 0.594 | 0.891 | 1.188 | 1.485 | 1.782 | 2.079 | 2.376 | 2.673 | 2.97 | 2.9564 | 2.9428 | 2.9291 | 2.9155 | 2.9019 | 2.8798 | 2.8577 | 2.8356 | 2.8136 | 2.7915 | 2.7815 | 2.7715 | 2.7615 | 2.7515 | 2.7415 | 2.7315 | 2.7215 | 2.7115 | 2.7015 | 2.6915 | 2.7458 | 2.8 | 2.8543 | 2.9086 | 2.9628 | 3.0171 | 3.0714 | 3.1256 | 3.1799 | 3.2342 | 3.2884 | 3.3427 | 3.397 | 3.4512 | 3.5055 | 3.5642 | 3.6229 | 3.6817 | 3.7404 | 3.7991 | 3.8579 | 3.9166 | 3.9753 | 4.034 | 4.0927 | 4.1515 | 4.2102 | 4.2689 | 4.3277 | 4.3864 | 4.5983 | 4.8103 | 5.0223 | 5.2343 | 5.4463 | 5.6582 | 5.8702 | 6.0822 | 6.2942 | 6.5061 | 6.7181 | 6.9301 | 7.1421 | 7.354 | 7.566 | 7.778 | 7.99 | 8.2019 | 8.4139 | 8.6259 | 8.8378 | 9.0498 | 9.2618 | 9.4738 | 9.6858 | 9.8977 | 10.1097 | 10.3217 | 10.5336 | 10.7456 | 10.9384 | 11.1312 | 11.3239 | 11.5167 | 11.7095 | 11.9023 | 12.0951 | 12.2878 | 12.4806 | 12.6734 | 12.8661 | 13.0589 | 13.2517 | 13.4445 | 13.6372 | 13.83 | 14.0228 | 14.2156 | 14.4084 | 14.6011 | 14.7939 | 14.9867 | 15.1794 | 15.3722 | 15.565 | 15.7578 | 15.9505 | 16.1433 | 16.3361 | 16.5289 | 16.6833 | 16.8376 | 16.992 | 17.1464 | 17.3008 | 17.4551 | 17.6095 | 17.7639 | 17.9183 | 18.0726 | 18.227 | 18.3814 | 18.5358 | 18.6901 | 18.8445 | 18.9989 | 19.1532 | 19.3076 | 19.462 | 19.6164 | 19.7707 | 19.9251 | 20.0795 | 20.2339 | 20.3882 | 20.5426 | 20.697 | 20.8514 | 21.0057 | 21.1601 | 21.2734 | 21.3868 | 21.5001 | 21.6134 | 21.7267 | 21.84 | 21.9533 | 22.0667 | 22.18 | 22.2933 | 22.4066 | 22.5199 | 22.6332 | 22.7466 | 22.8599 | 22.9732 | 23.0865 | 23.1998 | 23.3131 | 23.4265 | 23.5398 | 23.6531 | 23.7664 | 23.8797 | 23.993 | 24.1064 | 24.2197 | 24.333 | 24.4463 | 24.5596
7.4 | 0 | 0.301 | 0.602 | 0.903 | 1.204 | 1.505 | 1.806 | 2.107 | 2.408 | 2.709 | 3.01 | 2.9975 | 2.985 | 2.9725 | 2.96 | 2.9475 | 2.9252 | 2.9029 | 2.8806 | 2.8583 | 2.836 | 2.826 | 2.816 | 2.806 | 2.796 | 2.786 | 2.776 | 2.766 | 2.756 | 2.746 | 2.736 | 2.7911 | 2.8461 | 2.9012 | 2.9563 | 3.0113 | 3.0664 | 3.1215 | 3.1765 | 3.2316 | 3.2867 | 3.3417 | 3.3968 | 3.4519 | 3.5069 | 3.562 | 3.6216 | 3.6811 | 3.7407 | 3.8003 | 3.8598 | 3.9194 | 3.979 | 4.0385 | 4.0981 | 4.1577 | 4.2172 | 4.2768 | 4.3364 | 4.3959 | 4.4555 | 4.6704 | 4.8853 | 5.1002 | 5.3151 | 5.53 | 5.7449 | 5.9598 | 6.1747 | 6.3896 | 6.6045 | 6.8194 | 7.0343 | 7.2492 | 7.4641 | 7.679 | 7.8939 | 8.1088 | 8.3237 | 8.5386 | 8.7535 | 8.9684 | 9.1833 | 9.3982 | 9.6131 | 9.828 | 10.0429 | 10.2578 | 10.4727 | 10.6876 | 10.9025 | 11.0979 | 11.2934 | 11.4888 | 11.6842 | 11.8797 | 12.0751 | 12.2705 | 12.466 | 12.6614 | 12.8568 | 13.0523 | 13.2477 | 13.4431 | 13.6386 | 13.834 | 14.0294 | 14.2249 | 14.4203 | 14.6157 | 14.8112 | 15.0066 | 15.202 | 15.3975 | 15.5929 | 15.7883 | 15.9838 | 16.1792 | 16.3746 | 16.5701 | 16.7655 | 16.922 | 17.0785 | 17.235 | 17.3915 | 17.548 | 17.7045 | 17.861 | 18.0175 | 18.174 | 18.3305 | 18.487 | 18.6435 | 18.8 | 18.9565 | 19.113 | 19.2695 | 19.426 | 19.5825 | 19.739 | 19.8955 | 20.052 | 20.2085 | 20.365 | 20.5215 | 20.678 | 20.8345 | 20.991 | 21.1475 | 21.304 | 21.4605 | 21.5754 | 21.6904 | 21.8053 | 21.9202 | 22.0352 | 22.1501 | 22.265 | 22.38 | 22.4949 | 22.6098 | 22.7248 | 22.8397 | 22.9546 | 23.0696 | 23.1845 | 23.2994 | 23.4144 | 23.5293 | 23.6442 | 23.7592 | 23.8741 | 23.989 | 24.104 | 24.2189 | 24.3338 | 24.4488 | 24.5637 | 24.6786 | 24.7936 | 24.9085
7.45 | 0 | 0.305 | 0.61 | 0.915 | 1.22 | 1.525 | 1.83 | 2.135 | 2.44 | 2.745 | 3.05 | 3.0386 | 3.0272 | 3.0159 | 3.0045 | 2.9931 | 2.9706 | 2.9481 | 2.9255 | 2.903 | 2.8805 | 2.8705 | 2.8605 | 2.8505 | 2.8405 | 2.8305 | 2.8205 | 2.8105 | 2.8005 | 2.7905 | 2.7805 | 2.8364 | 2.8922 | 2.9481 | 3.004 | 3.0598 | 3.1157 | 3.1716 | 3.2274 | 3.2833 | 3.3392 | 3.395 | 3.4509 | 3.5068 | 3.5626 | 3.6185 | 3.6789 | 3.7393 | 3.7997 | 3.8601 | 3.9205 | 3.9809 | 4.0414 | 4.1018 | 4.1622 | 4.2226 | 4.283 | 4.3434 | 4.4038 | 4.4642 | 4.5246 | 4.7424 | 4.9603 | 5.1781 | 5.3959 | 5.6137 | 5.8316 | 6.0494 | 6.2672 | 6.4851 | 6.7029 | 6.9207 | 7.1385 | 7.3563 | 7.5742 | 7.792 | 8.0098 | 8.2277 | 8.4455 | 8.6633 | 8.8811 | 9.099 | 9.3168 | 9.5346 | 9.7524 | 9.9703 | 10.1881 | 10.4059 | 10.6237 | 10.8415 | 11.0594 | 11.2575 | 11.4556 | 11.6537 | 11.8517 | 12.0498 | 12.2479 | 12.446 | 12.6441 | 12.8422 | 13.0403 | 13.2384 | 13.4365 | 13.6346 | 13.8327 | 14.0307 | 14.2288 | 14.4269 | 14.625 | 14.8231 | 15.0212 | 15.2193 | 15.4174 | 15.6155 | 15.8136 | 16.0117 | 16.2098 | 16.4078 | 16.6059 | 16.804 | 17.0021 | 17.1608 | 17.3194 | 17.478 | 17.6366 | 17.7952 | 17.9539 | 18.1125 | 18.2711 | 18.4297 | 18.5884 | 18.747 | 18.9056 | 19.0643 | 19.2229 | 19.3815 | 19.5401 | 19.6988 | 19.8574 | 20.016 | 20.1746 | 20.3332 | 20.4919 | 20.6505 | 20.8091 | 20.9677 | 21.1264 | 21.285 | 21.4436 | 21.6023 | 21.7609 | 21.8774 | 21.994 | 22.1105 | 22.2271 | 22.3436 | 22.4602 | 22.5767 | 22.6933 | 22.8098 | 22.9264 | 23.0429 | 23.1595 | 23.276 | 23.3926 | 23.5091 | 23.6257 | 23.7422 | 23.8588 | 23.9753 | 24.0919 | 24.2084 | 24.325 | 24.4415 | 24.5581 | 24.6746 | 24.7912 | 24.9077 | 25.0243 | 25.1408 | 25.2574
7.5 | 0 | 0.309 | 0.618 | 0.927 | 1.236 | 1.545 | 1.854 | 2.163 | 2.472 | 2.781 | 3.09 | 3.0798 | 3.0695 | 3.0593 | 3.049 | 3.0387 | 3.016 | 2.9933 | 2.9705 | 2.9478 | 2.925 | 2.915 | 2.905 | 2.895 | 2.885 | 2.875 | 2.865 | 2.855 | 2.845 | 2.835 | 2.825 | 2.8817 | 2.9383 | 2.995 | 3.0517 | 3.1083 | 3.165 | 3.2217 | 3.2783 | 3.335 | 3.3917 | 3.4483 | 3.505 | 3.5617 | 3.6183 | 3.675 | 3.7363 | 3.7975 | 3.8588 | 3.92 | 3.9813 | 4.0425 | 4.1037 | 4.165 | 4.2263 | 4.2875 | 4.3487 | 4.41 | 4.4713 | 4.5325 | 4.5938 | 4.8145 | 5.0352 | 5.256 | 5.4768 | 5.6975 | 5.9182 | 6.139 | 6.3598 | 6.5805 | 6.8012 | 7.022 | 7.2428 | 7.4635 | 7.6842 | 7.905 | 8.1258 | 8.3465 | 8.5672 | 8.788 | 9.0087 | 9.2295 | 9.4503 | 9.671 | 9.8918 | 10.1125 | 10.3332 | 10.554 | 10.7747 | 10.9955 | 11.2163 | 11.417 | 11.6177 | 11.8185 | 12.0192 | 12.22 | 12.4207 | 12.6215 | 12.8223 | 13.023 | 13.2238 | 13.4245 | 13.6252 | 13.826 | 14.0267 | 14.2275 | 14.4283 | 14.629 | 14.8298 | 15.0305 | 15.2312 | 15.432 | 15.6327 | 15.8335 | 16.0343 | 16.235 | 16.4357 | 16.6365 | 16.8373 | 17.038 | 17.2387 | 17.3995 | 17.5602 | 17.721 | 17.8818 | 18.0425 | 18.2033 | 18.364 | 18.5248 | 18.6855 | 18.8463 | 19.007 | 19.1678 | 19.3285 | 19.4892 | 19.65 | 19.8107 | 19.9715 | 20.1322 | 20.293 | 20.4537 | 20.6145 | 20.7752 | 20.936 | 21.0968 | 21.2575 | 21.4183 | 21.579 | 21.7398 | 21.9005 | 22.0613 | 22.1794 | 22.2976 | 22.4157 | 22.5339 | 22.6521 | 22.7703 | 22.8884 | 23.0066 | 23.1247 | 23.2429 | 23.3611 | 23.4793 | 23.5974 | 23.7156 | 23.8337 | 23.9519 | 24.0701 | 24.1883 | 24.3064 | 24.4246 | 24.5428 | 24.6609 | 24.7791 | 24.8972 | 25.0154 | 25.1336 | 25.2518 | 25.3699 | 25.4881 | 25.6062
7.55 | 0 | 0.313 | 0.626 | 0.939 | 1.252 | 1.565 | 1.878 | 2.191 | 2.504 | 2.817 | 3.13 | 3.1209 | 3.1117 | 3.1026 | 3.0935 | 3.0844 | 3.0614 | 3.0384 | 3.0154 | 2.9925 | 2.9695 | 2.9595 | 2.9495 | 2.9395 | 2.9295 | 2.9195 | 2.9095 | 2.8995 | 2.8895 | 2.8795 | 2.8695 | 2.927 | 2.9844 | 3.0419 | 3.0994 | 3.1568 | 3.2143 | 3.2718 | 3.3292 | 3.3867 | 3.4442 | 3.5016 | 3.5591 | 3.6166 | 3.674 | 3.7315 | 3.7936 | 3.8557 | 3.9178 | 3.9799 | 4.042 | 4.104 | 4.1661 | 4.2282 | 4.2903 | 4.3524 | 4.4145 | 4.4766 | 4.5387 | 4.6008 | 4.6629 | 4.8865 | 5.1102 | 5.3339 | 5.5576 | 5.7812 | 6.0049 | 6.2286 | 6.4523 | 6.676 | 6.8996 | 7.1233 | 7.347 | 7.5706 | 7.7943 | 8.018 | 8.2417 | 8.4654 | 8.689 | 8.9127 | 9.1364 | 9.36 | 9.5837 | 9.8074 | 10.0311 | 10.2547 | 10.4784 | 10.7021 | 10.9258 | 11.1494 | 11.3731 | 11.5765 | 11.7799 | 11.9833 | 12.1868 | 12.3902 | 12.5936 | 12.797 | 13.0004 | 13.2038 | 13.4072 | 13.6106 | 13.814 | 14.0174 | 14.2208 | 14.4243 | 14.6277 | 14.8311 | 15.0345 | 15.2379 | 15.4413 | 15.6447 | 15.8481 | 16.0515 | 16.2549 | 16.4583 | 16.6617 | 16.8651 | 17.0686 | 17.272 | 17.4754 | 17.6382 | 17.8011 | 17.964 | 18.1269 | 18.2898 | 18.4526 | 18.6155 | 18.7784 | 18.9413 | 19.1041 | 19.267 | 19.4299 | 19.5927 | 19.7556 | 19.9185 | 20.0814 | 20.2443 | 20.4071 | 20.57 | 20.7329 | 20.8957 | 21.0586 | 21.2215 | 21.3844 | 21.5472 | 21.7101 | 21.873 | 22.0359 | 22.1988 | 22.3616 | 22.4814 | 22.6012 | 22.721 | 22.8408 | 22.9605 | 23.0803 | 23.2001 | 23.3199 | 23.4397 | 23.5595 | 23.6792 | 23.799 | 23.9188 | 24.0386 | 24.1584 | 24.2782 | 24.3979 | 24.5177 | 24.6375 | 24.7573 | 24.8771 | 24.9969 | 25.1166 | 25.2364 | 25.3562 | 25.476 | 25.5958 | 25.7156 | 25.8353 | 25.9551
7.6 | 0 | 0.317 | 0.634 | 0.951 | 1.268 | 1.585 | 1.902 | 2.219 | 2.536 | 2.853 | 3.17 | 3.162 | 3.154 | 3.146 | 3.138 | 3.13 | 3.1068 | 3.0836 | 3.0604 | 3.0372 | 3.014 | 3.004 | 2.994 | 2.984 | 2.974 | 2.964 | 2.954 | 2.944 | 2.934 | 2.924 | 2.914 | 2.9723 | 3.0305 | 3.0888 | 3.1471 | 3.2053 | 3.2636 | 3.3219 | 3.3801 | 3.4384 | 3.4967 | 3.5549 | 3.6132 | 3.6715 | 3.7297 | 3.788 | 3.8509 | 3.9139 | 3.9768 | 4.0397 | 4.1027 | 4.1656 | 4.2285 | 4.2915 | 4.3544 | 4.4173 | 4.4803 | 4.5432 | 4.6061 | 4.6691 | 4.732 | 4.9586 | 5.1852 | 5.4118 | 5.6384 | 5.865 | 6.0916 | 6.3182 | 6.5448 | 6.7714 | 6.998 | 7.2246 | 7.4512 | 7.6778 | 7.9044 | 8.131 | 8.3576 | 8.5842 | 8.8108 | 9.0374 | 9.264 | 9.4906 | 9.7172 | 9.9438 | 10.1704 | 10.397 | 10.6236 | 10.8502 | 11.0768 | 11.3034 | 11.53 | 11.7361 | 11.9421 | 12.1482 | 12.3543 | 12.5603 | 12.7664 | 12.9725 | 13.1785 | 13.3846 | 13.5907 | 13.7967 | 14.0028 | 14.2089 | 14.4149 | 14.621 | 14.8271 | 15.0331 | 15.2392 | 15.4453 | 15.6513 | 15.8574 | 16.0635 | 16.2695 | 16.4756 | 16.6817 | 16.8877 | 17.0938 | 17.2999 | 17.5059 | 17.712 | 17.877 | 18.042 | 18.207 | 18.372 | 18.537 | 18.702 | 18.867 | 19.032 | 19.197 | 19.362 | 19.527 | 19.692 | 19.857 | 20.022 | 20.187 | 20.352 | 20.517 | 20.682 | 20.847 | 21.012 | 21.177 | 21.342 | 21.507 | 21.672 | 21.837 | 22.002 | 22.167 | 22.332 | 22.497 | 22.662 | 22.7834 | 22.9048 | 23.0262 | 23.1476 | 23.269 | 23.3904 | 23.5118 | 23.6332 | 23.7546 | 23.876 | 23.9974 | 24.1188 | 24.2402 | 24.3616 | 24.483 | 24.6044 | 24.7258 | 24.8472 | 24.9686 | 25.09 | 25.2114 | 25.3328 | 25.4542 | 25.5756 | 25.697 | 25.8184 | 25.9398 | 26.0612 | 26.1826 | 26.304
7.65 | 0 | 0.321 | 0.642 | 0.963 | 1.284 | 1.605 | 1.926 | 2.247 | 2.568 | 2.889 | 3.21 | 3.2031 | 3.1963 | 3.1894 | 3.1825 | 3.1756 | 3.1522 | 3.1288 | 3.1054 | 3.0819 | 3.0585 | 3.0485 | 3.0385 | 3.0285 | 3.0185 | 3.0085 | 2.9985 | 2.9885 | 2.9785 | 2.9685 | 2.9585 | 3.0176 | 3.0766 | 3.1357 | 3.1948 | 3.2538 | 3.3129 | 3.372 | 3.431 | 3.4901 | 3.5492 | 3.6082 | 3.6673 | 3.7264 | 3.7854 | 3.8445 | 3.9083 | 3.972 | 4.0358 | 4.0996 | 4.1634 | 4.2271 | 4.2909 | 4.3547 | 4.4185 | 4.4822 | 4.546 | 4.6098 | 4.6736 | 4.7374 | 4.8011 | 5.0306 | 5.2602 | 5.4897 | 5.7192 | 5.9488 | 6.1783 | 6.4078 | 6.6373 | 6.8669 | 7.0964 | 7.3259 | 7.5554 | 7.785 | 8.0145 | 8.244 | 8.4735 | 8.703 | 8.9326 | 9.1621 | 9.3916 | 9.6212 | 9.8507 | 10.0802 | 10.3097 | 10.5392 | 10.7688 | 10.9983 | 11.2278 | 11.4573 | 11.6869 | 11.8956 | 12.1043 | 12.3131 | 12.5218 | 12.7305 | 12.9392 | 13.1479 | 13.3567 | 13.5654 | 13.7741 | 13.9828 | 14.1916 | 14.4003 | 14.609 | 14.8178 | 15.0265 | 15.2352 | 15.4439 | 15.6526 | 15.8614 | 16.0701 | 16.2788 | 16.4875 | 16.6963 | 16.905 | 17.1137 | 17.3224 | 17.5312 | 17.7399 | 17.9486 | 18.1157 | 18.2829 | 18.45 | 18.6171 | 18.7843 | 18.9514 | 19.1185 | 19.2856 | 19.4528 | 19.6199 | 19.787 | 19.9541 | 20.1212 | 20.2884 | 20.4555 | 20.6226 | 20.7898 | 20.9569 | 21.124 | 21.2911 | 21.4582 | 21.6254 | 21.7925 | 21.9596 | 22.1268 | 22.2939 | 22.461 | 22.6281 | 22.7952 | 22.9624 | 23.0854 | 23.2084 | 23.3314 | 23.4544 | 23.5775 | 23.7005 | 23.8235 | 23.9465 | 24.0695 | 24.1925 | 24.3156 | 24.4386 | 24.5616 | 24.6846 | 24.8076 | 24.9306 | 25.0537 | 25.1767 | 25.2997 | 25.4227 | 25.5457 | 25.6687 | 25.7918 | 25.9148 | 26.0378 | 26.1608 | 26.2838 | 26.4068 | 26.5299 | 26.6529
7.7 | 0 | 0.325 | 0.65 | 0.975 | 1.3 | 1.625 | 1.95 | 2.275 | 2.6 | 2.925 | 3.25 | 3.2443 | 3.2385 | 3.2327 | 3.227 | 3.2212 | 3.1976 | 3.174 | 3.1503 | 3.1267 | 3.103 | 3.093 | 3.083 | 3.073 | 3.063 | 3.053 | 3.043 | 3.033 | 3.023 | 3.013 | 3.003 | 3.0629 | 3.1227 | 3.1826 | 3.2425 | 3.3023 | 3.3622 | 3.4221 | 3.4819 | 3.5418 | 3.6017 | 3.6615 | 3.7214 | 3.7813 | 3.8411 | 3.901 | 3.9656 | 4.0302 | 4.0949 | 4.1595 | 4.2241 | 4.2887 | 4.3533 | 4.4179 | 4.4825 | 4.5472 | 4.6118 | 4.6764 | 4.741 | 4.8056 | 4.8703 | 5.1027 | 5.3351 | 5.5676 | 5.8 | 6.0325 | 6.2649 | 6.4974 | 6.7298 | 6.9623 | 7.1947 | 7.4272 | 7.6597 | 7.8921 | 8.1245 | 8.357 | 8.5894 | 8.8219 | 9.0543 | 9.2868 | 9.5192 | 9.7517 | 9.9841 | 10.2166 | 10.449 | 10.6815 | 10.9139 | 11.1464 | 11.3788 | 11.6113 | 11.8438 | 12.0551 | 12.2665 | 12.4779 | 12.6893 | 12.9007 | 13.112 | 13.3234 | 13.5348 | 13.7462 | 13.9576 | 14.169 | 14.3803 | 14.5917 | 14.8031 | 15.0145 | 15.2259 | 15.4373 | 15.6486 | 15.86 | 16.0714 | 16.2828 | 16.4942 | 16.7056 | 16.9169 | 17.1283 | 17.3397 | 17.5511 | 17.7625 | 17.9739 | 18.1852 | 18.3545 | 18.5237 | 18.693 | 18.8622 | 19.0315 | 19.2007 | 19.37 | 19.5392 | 19.7085 | 19.8777 | 20.047 | 20.2162 | 20.3855 | 20.5547 | 20.724 | 20.8932 | 21.0625 | 21.2318 | 21.401 | 21.5703 | 21.7395 | 21.9088 | 22.078 | 22.2473 | 22.4165 | 22.5858 | 22.755 | 22.9243 | 23.0935 | 23.2628 | 23.3874 | 23.512 | 23.6366 | 23.7613 | 23.8859 | 24.0105 | 24.1352 | 24.2598 | 24.3845 | 24.5091 | 24.6337 | 24.7584 | 24.883 | 25.0076 | 25.1322 | 25.2569 | 25.3815 | 25.5062 | 25.6308 | 25.7554 | 25.8801 | 26.0047 | 26.1293 | 26.2539 | 26.3786 | 26.5032 | 26.6278 | 26.7525 | 26.8771 | 27.0017
7.75 | 0 | 0.329 | 0.658 | 0.987 | 1.316 | 1.645 | 1.974 | 2.303 | 2.632 | 2.961 | 3.29 | 3.2854 | 3.2807 | 3.2761 | 3.2715 | 3.2669 | 3.243 | 3.2191 | 3.1953 | 3.1714 | 3.1475 | 3.1375 | 3.1275 | 3.1175 | 3.1075 | 3.0975 | 3.0875 | 3.0775 | 3.0675 | 3.0575 | 3.0475 | 3.1082 | 3.1688 | 3.2295 | 3.2902 | 3.3508 | 3.4115 | 3.4722 | 3.5328 | 3.5935 | 3.6542 | 3.7148 | 3.7755 | 3.8362 | 3.8968 | 3.9575 | 4.023 | 4.0884 | 4.1539 | 4.2193 | 4.2848 | 4.3502 | 4.4157 | 4.4812 | 4.5466 | 4.6121 | 4.6775 | 4.743 | 4.8085 | 4.8739 | 4.9394 | 5.1748 | 5.4101 | 5.6455 | 5.8809 | 6.1162 | 6.3516 | 6.587 | 6.8224 | 7.0578 | 7.2931 | 7.5285 | 7.7639 | 7.9992 | 8.2346 | 8.47 | 8.7054 | 8.9407 | 9.1761 | 9.4115 | 9.6469 | 9.8823 | 10.1176 | 10.353 | 10.5884 | 10.8238 | 11.0591 | 11.2945 | 11.5299 | 11.7652 | 12.0006 | 12.2147 | 12.4287 | 12.6427 | 12.8568 | 13.0708 | 13.2849 | 13.4989 | 13.713 | 13.927 | 14.141 | 14.3551 | 14.5691 | 14.7832 | 14.9972 | 15.2112 | 15.4253 | 15.6393 | 15.8534 | 16.0674 | 16.2815 | 16.4955 | 16.7095 | 16.9236 | 17.1376 | 17.3517 | 17.5657 | 17.7797 | 17.9938 | 18.2078 | 18.4219 | 18.5933 | 18.7646 | 18.936 | 19.1074 | 19.2787 | 19.4501 | 19.6215 | 19.7929 | 19.9642 | 20.1356 | 20.307 | 20.4784 | 20.6498 | 20.8211 | 20.9925 | 21.1639 | 21.3352 | 21.5066 | 21.678 | 21.8494 | 22.0207 | 22.1921 | 22.3635 | 22.5349 | 22.7063 | 22.8776 | 23.049 | 23.2204 | 23.3917 | 23.5631 | 23.6894 | 23.8156 | 23.9419 | 24.0681 | 24.1944 | 24.3206 | 24.4469 | 24.5731 | 24.6994 | 24.8256 | 24.9519 | 25.0781 | 25.2044 | 25.3306 | 25.4569 | 25.5831 | 25.7094 | 25.8356 | 25.9619 | 26.0881 | 26.2144 | 26.3406 | 26.4669 | 26.5931 | 26.7194 | 26.8456 | 26.9719 | 27.0981 | 27.2244 | 27.3506
7.8 | 0 | 0.333 | 0.666 | 0.999 | 1.332 | 1.665 | 1.998 | 2.331 | 2.664 | 2.997 | 3.33 | 3.3265 | 3.323 | 3.3195 | 3.316 | 3.3125 | 3.2884 | 3.2643 | 3.2402 | 3.2161 | 3.192 | 3.182 | 3.172 | 3.162 | 3.152 | 3.142 | 3.132 | 3.122 | 3.112 | 3.102 | 3.092 | 3.1535 | 3.2149 | 3.2764 | 3.3379 | 3.3993 | 3.4608 | 3.5223 | 3.5837 | 3.6452 | 3.7067 | 3.7681 | 3.8296 | 3.8911 | 3.9525 | 4.014 | 4.0803 | 4.1466 | 4.2129 | 4.2792 | 4.3455 | 4.4118 | 4.4781 | 4.5444 | 4.6107 | 4.677 | 4.7433 | 4.8096 | 4.8759 | 4.9422 | 5.0085 | 5.2468 | 5.4851 | 5.7234 | 5.9617 | 6.2 | 6.4383 | 6.6766 | 6.9149 | 7.1532 | 7.3915 | 7.6298 | 7.8681 | 8.1064 | 8.3447 | 8.583 | 8.8213 | 9.0596 | 9.2979 | 9.5362 | 9.7745 | 10.0128 | 10.2511 | 10.4894 | 10.7277 | 10.966 | 11.2043 | 11.4426 | 11.6809 | 11.9192 | 12.1575 | 12.3742 | 12.5909 | 12.8076 | 13.0243 | 13.241 | 13.4577 | 13.6744 | 13.8911 | 14.1078 | 14.3245 | 14.5412 | 14.7579 | 14.9746 | 15.1913 | 15.408 | 15.6247 | 15.8414 | 16.0581 | 16.2748 | 16.4915 | 16.7082 | 16.9249 | 17.1416 | 17.3583 | 17.575 | 17.7917 | 18.0084 | 18.2251 | 18.4418 | 18.6585 | 18.832 | 19.0055 | 19.179 | 19.3525 | 19.526 | 19.6995 | 19.873 | 20.0465 | 20.22 | 20.3935 | 20.567 | 20.7405 | 20.914 | 21.0875 | 21.261 | 21.4345 | 21.608 | 21.7815 | 21.955 | 22.1285 | 22.302 | 22.4755 | 22.649 | 22.8225 | 22.996 | 23.1695 | 23.343 | 23.5165 | 23.69 | 23.8635 | 23.9914 | 24.1192 | 24.2471 | 24.375 | 24.5028 | 24.6307 | 24.7586 | 24.8864 | 25.0143 | 25.1422 | 25.27 | 25.3979 | 25.5258 | 25.6536 | 25.7815 | 25.9094 | 26.0372 | 26.1651 | 26.293 | 26.4208 | 26.5487 | 26.6766 | 26.8044 | 26.9323 | 27.0602 | 27.188 | 27.3159 | 27.4438 | 27.5716 | 27.6995
7.85 | 0 | 0.337 | 0.674 | 1.011 | 1.348 | 1.685 | 2.022 | 2.359 | 2.696 | 3.033 | 3.37 | 3.3676 | 3.3653 | 3.3629 | 3.3605 | 3.3581 | 3.3338 | 3.3095 | 3.2851 | 3.2608 | 3.2365 | 3.2265 | 3.2165 | 3.2065 | 3.1965 | 3.1865 | 3.1765 | 3.1665 | 3.1565 | 3.1465 | 3.1365 | 3.1988 | 3.261 | 3.3233 | 3.3856 | 3.4478 | 3.5101 | 3.5724 | 3.6346 | 3.6969 | 3.7592 | 3.8214 | 3.8837 | 3.946 | 4.0082 | 4.0705 | 4.1376 | 4.2048 | 4.2719 | 4.3391 | 4.4062 | 4.4733 | 4.5405 | 4.6076 | 4.6748 | 4.7419 | 4.8091 | 4.8762 | 4.9433 | 5.0105 | 5.0776 | 5.3189 | 5.5601 | 5.8013 | 6.0425 | 6.2838 | 6.525 | 6.7662 | 7.0074 | 7.2486 | 7.4899 | 7.7311 | 7.9723 | 8.2135 | 8.4548 | 8.696 | 8.9372 | 9.1784 | 9.4197 | 9.6609 | 9.9021 | 10.1433 | 10.3846 | 10.6258 | 10.867 | 11.1082 | 11.3495 | 11.5907 | 11.8319 | 12.0732 | 12.3144 | 12.5337 | 12.7531 | 12.9725 | 13.1918 | 13.4112 | 13.6305 | 13.8499 | 14.0692 | 14.2886 | 14.508 | 14.7273 | 14.9467 | 15.166 | 15.3854 | 15.6047 | 15.8241 | 16.0435 | 16.2628 | 16.4822 | 16.7015 | 16.9209 | 17.1403 | 17.3596 | 17.579 | 17.7983 | 18.0177 | 18.237 | 18.4564 | 18.6758 | 18.8951 | 19.0708 | 19.2464 | 19.422 | 19.5976 | 19.7733 | 19.9489 | 20.1245 | 20.3001 | 20.4758 | 20.6514 | 20.827 | 21.0026 | 21.1782 | 21.3539 | 21.5295 | 21.7051 | 21.8807 | 22.0564 | 22.232 | 22.4076 | 22.5832 | 22.7589 | 22.9345 | 23.1101 | 23.2858 | 23.4614 | 23.637 | 23.8126 | 23.9883 | 24.1639 | 24.2934 | 24.4228 | 24.5523 | 24.6818 | 24.8113 | 24.9408 | 25.0703 | 25.1997 | 25.3292 | 25.4587 | 25.5882 | 25.7177 | 25.8472 | 25.9766 | 26.1061 | 26.2356 | 26.3651 | 26.4946 | 26.6241 | 26.7535 | 26.883 | 27.0125 | 27.142 | 27.2715 | 27.401 | 27.5304 | 27.6599 | 27.7894 | 27.9189 | 28.0484
7.9 | 0 | 0.341 | 0.682 | 1.023 | 1.364 | 1.705 | 2.046 | 2.387 | 2.728 | 3.069 | 3.41 | 3.4088 | 3.4075 | 3.4063 | 3.405 | 3.4038 | 3.3792 | 3.3547 | 3.3301 | 3.3056 | 3.281 | 3.271 | 3.261 | 3.251 | 3.241 | 3.231 | 3.221 | 3.211 | 3.201 | 3.191 | 3.181 | 3.2441 | 3.3071 | 3.3702 | 3.4333 | 3.4963 | 3.5594 | 3.6225 | 3.6855 | 3.7486 | 3.8117 | 3.8747 | 3.9378 | 4.0009 | 4.0639 | 4.127 | 4.195 | 4.263 | 4.331 | 4.3989 | 4.4669 | 4.5349 | 4.6029 | 4.6709 | 4.7389 | 4.8068 | 4.8748 | 4.9428 | 5.0108 | 5.0788 | 5.1468 | 5.3909 | 5.6351 | 5.8792 | 6.1234 | 6.3675 | 6.6117 | 6.8558 | 7.1 | 7.3441 | 7.5883 | 7.8324 | 8.0766 | 8.3207 | 8.5649 | 8.809 | 9.0532 | 9.2973 | 9.5415 | 9.7856 | 10.0297 | 10.2739 | 10.5181 | 10.7622 | 11.0063 | 11.2505 | 11.4947 | 11.7388 | 11.983 | 12.2271 | 12.4712 | 12.6933 | 12.9153 | 13.1373 | 13.3593 | 13.5813 | 13.8034 | 14.0254 | 14.2474 | 14.4694 | 14.6914 | 14.9134 | 15.1355 | 15.3575 | 15.5795 | 15.8015 | 16.0235 | 16.2455 | 16.4675 | 16.6896 | 16.9116 | 17.1336 | 17.3556 | 17.5776 | 17.7996 | 18.0217 | 18.2437 | 18.4657 | 18.6877 | 18.9097 | 19.1318 | 19.3095 | 19.4872 | 19.665 | 19.8427 | 20.0205 | 20.1983 | 20.376 | 20.5538 | 20.7315 | 20.9093 | 21.087 | 21.2648 | 21.4425 | 21.6203 | 21.798 | 21.9758 | 22.1535 | 22.3313 | 22.509 | 22.6868 | 22.8645 | 23.0423 | 23.22 | 23.3978 | 23.5755 | 23.7533 | 23.931 | 24.1088 | 24.2865 | 24.4643 | 24.5954 | 24.7265 | 24.8576 | 24.9887 | 25.1198 | 25.2509 | 25.382 | 25.5131 | 25.6442 | 25.7753 | 25.9064 | 26.0375 | 26.1686 | 26.2997 | 26.4308 | 26.5619 | 26.693 | 26.8241 | 26.9552 | 27.0863 | 27.2174 | 27.3485 | 27.4796 | 27.6107 | 27.7418 | 27.8729 | 28.004 | 28.1351 | 28.2662 | 28.3972
7.95 | 0 | 0.345 | 0.69 | 1.035 | 1.38 | 1.725 | 2.07 | 2.415 | 2.76 | 3.105 | 3.45 | 3.4499 | 3.4498 | 3.4496 | 3.4495 | 3.4494 | 3.4246 | 3.3998 | 3.3751 | 3.3503 | 3.3255 | 3.3155 | 3.3055 | 3.2955 | 3.2855 | 3.2755 | 3.2655 | 3.2555 | 3.2455 | 3.2355 | 3.2255 | 3.2894 | 3.3532 | 3.4171 | 3.481 | 3.5448 | 3.6087 | 3.6726 | 3.7364 | 3.8003 | 3.8642 | 3.928 | 3.9919 | 4.0558 | 4.1196 | 4.1835 | 4.2523 | 4.3212 | 4.39 | 4.4588 | 4.5276 | 4.5965 | 4.6653 | 4.7341 | 4.8029 | 4.8718 | 4.9406 | 5.0094 | 5.0782 | 5.1471 | 5.2159 | 5.463 | 5.71 | 5.9571 | 6.2042 | 6.4513 | 6.6983 | 6.9454 | 7.1925 | 7.4396 | 7.6866 | 7.9337 | 8.1808 | 8.4279 | 8.6749 | 8.922 | 9.1691 | 9.4162 | 9.6632 | 9.9103 | 10.1574 | 10.4045 | 10.6515 | 10.8986 | 11.1457 | 11.3927 | 11.6398 | 11.8869 | 12.134 | 12.3811 | 12.6281 | 12.8528 | 13.0775 | 13.3021 | 13.5268 | 13.7515 | 13.9762 | 14.2009 | 14.4255 | 14.6502 | 14.8749 | 15.0996 | 15.3242 | 15.5489 | 15.7736 | 15.9983 | 16.2229 | 16.4476 | 16.6723 | 16.897 | 17.1216 | 17.3463 | 17.571 | 17.7956 | 18.0203 | 18.245 | 18.4697 | 18.6944 | 18.919 | 19.1437 | 19.3684 | 19.5482 | 19.7281 | 19.908 | 20.0879 | 20.2677 | 20.4476 | 20.6275 | 20.8074 | 20.9872 | 21.1671 | 21.347 | 21.5269 | 21.7068 | 21.8866 | 22.0665 | 22.2464 | 22.4263 | 22.6061 | 22.786 | 22.9659 | 23.1458 | 23.3256 | 23.5055 | 23.6854 | 23.8653 | 24.0451 | 24.225 | 24.4049 | 24.5848 | 24.7646 | 24.8973 | 25.0301 | 25.1628 | 25.2955 | 25.4282 | 25.5609 | 25.6936 | 25.8264 | 25.9591 | 26.0918 | 26.2245 | 26.3572 | 26.4899 | 26.6227 | 26.7554 | 26.8881 | 27.0208 | 27.1535 | 27.2862 | 27.419 | 27.5517 | 27.6844 | 27.8171 | 27.9498 | 28.0825 | 28.2153 | 28.348 | 28.4807 | 28.6134 | 28.7461
8 | 0 | 0.349 | 0.698 | 1.047 | 1.396 | 1.745 | 2.094 | 2.443 | 2.792 | 3.141 | 3.49 | 3.491 | 3.492 | 3.493 | 3.494 | 3.495 | 3.47 | 3.445 | 3.42 | 3.395 | 3.37 | 3.36 | 3.35 | 3.34 | 3.33 | 3.32 | 3.31 | 3.3 | 3.29 | 3.28 | 3.27 | 3.3347 | 3.3993 | 3.464 | 3.5287 | 3.5933 | 3.658 | 3.7227 | 3.7873 | 3.852 | 3.9167 | 3.9813 | 4.046 | 4.1107 | 4.1753 | 4.24 | 4.3097 | 4.3793 | 4.449 | 4.5187 | 4.5883 | 4.658 | 4.7277 | 4.7973 | 4.867 | 4.9367 | 5.0063 | 5.076 | 5.1457 | 5.2153 | 5.285 | 5.535 | 5.785 | 6.035 | 6.285 | 6.535 | 6.785 | 7.035 | 7.285 | 7.535 | 7.785 | 8.035 | 8.285 | 8.535 | 8.785 | 9.035 | 9.285 | 9.535 | 9.785 | 10.035 | 10.285 | 10.535 | 10.785 | 11.035 | 11.285 | 11.535 | 11.785 | 12.035 | 12.285 | 12.535 | 12.785 | 13.0123 | 13.2397 | 13.467 | 13.6943 | 13.9217 | 14.149 | 14.3763 | 14.6037 | 14.831 | 15.0583 | 15.2857 | 15.513 | 15.7403 | 15.9677 | 16.195 | 16.4223 | 16.6497 | 16.877 | 17.1043 | 17.3317 | 17.559 | 17.7863 | 18.0137 | 18.241 | 18.4683 | 18.6957 | 18.923 | 19.1503 | 19.3777 | 19.605 | 19.787 | 19.969 | 20.151 | 20.333 | 20.515 | 20.697 | 20.879 | 21.061 | 21.243 | 21.425 | 21.607 | 21.789 | 21.971 | 22.153 | 22.335 | 22.517 | 22.699 | 22.881 | 23.063 | 23.245 | 23.427 | 23.609 | 23.791 | 23.973 | 24.155 | 24.337 | 24.519 | 24.701 | 24.883 | 25.065 | 25.1993 | 25.3337 | 25.468 | 25.6023 | 25.7367 | 25.871 | 26.0053 | 26.1397 | 26.274 | 26.4083 | 26.5427 | 26.677 | 26.8113 | 26.9457 | 27.08 | 27.2143 | 27.3487 | 27.483 | 27.6173 | 27.7517 | 27.886 | 28.0203 | 28.1547 | 28.289 | 28.4233 | 28.5577 | 28.692 | 28.8263 | 28.9607 | 29.095
8.05 | 0 | 0.353 | 0.706 | 1.059 | 1.412 | 1.765 | 2.118 | 2.471 | 2.824 | 3.177 | 3.53 | 3.5321 | 3.5343 | 3.5364 | 3.5385 | 3.5406 | 3.5154 | 3.4902 | 3.465 | 3.4397 | 3.4145 | 3.4045 | 3.3945 | 3.3845 | 3.3745 | 3.3645 | 3.3545 | 3.3445 | 3.3345 | 3.3245 | 3.3145 | 3.38 | 3.4454 | 3.5109 | 3.5764 | 3.6418 | 3.7073 | 3.7728 | 3.8382 | 3.9037 | 3.9692 | 4.0346 | 4.1001 | 4.1656 | 4.231 | 4.2965 | 4.367 | 4.4375 | 4.508 | 4.5785 | 4.649 | 4.7196 | 4.7901 | 4.8606 | 4.9311 | 5.0016 | 5.0721 | 5.1426 | 5.2131 | 5.2836 | 5.3541 | 5.6071 | 5.86 | 6.1129 | 6.3658 | 6.6188 | 6.8717 | 7.1246 | 7.3775 | 7.6305 | 7.8834 | 8.1363 | 8.3892 | 8.6422 | 8.8951 | 9.148 | 9.4009 | 9.6539 | 9.9068 | 10.1597 | 10.4126 | 10.6655 | 10.9185 | 11.1714 | 11.4243 | 11.6773 | 11.9302 | 12.1831 | 12.436 | 12.689 | 12.9419 | 13.1719 | 13.4019 | 13.6319 | 13.8618 | 14.0918 | 14.3218 | 14.5518 | 14.7818 | 15.0118 | 15.2418 | 15.4718 | 15.7018 | 15.9318 | 16.1618 | 16.3917 | 16.6217 | 16.8517 | 17.0817 | 17.3117 | 17.5417 | 17.7717 | 18.0017 | 18.2317 | 18.4617 | 18.6917 | 18.9217 | 19.1517 | 19.3816 | 19.6116 | 19.8416 | 20.0258 | 20.2099 | 20.394 | 20.5781 | 20.7623 | 20.9464 | 21.1305 | 21.3146 | 21.4988 | 21.6829 | 21.867 | 22.0511 | 22.2353 | 22.4194 | 22.6035 | 22.7876 | 22.9718 | 23.1559 | 23.34 | 23.5241 | 23.7083 | 23.8924 | 24.0765 | 24.2606 | 24.4448 | 24.6289 | 24.813 | 24.9971 | 25.1813 | 25.3654 | 25.5013 | 25.6373 | 25.7732 | 25.9092 | 26.0451 | 26.1811 | 26.317 | 26.453 | 26.5889 | 26.7249 | 26.8608 | 26.9968 | 27.1327 | 27.2687 | 27.4046 | 27.5406 | 27.6765 | 27.8125 | 27.9484 | 28.0844 | 28.2203 | 28.3563 | 28.4922 | 28.6282 | 28.7641 | 28.9001 | 29.036 | 29.172 | 29.3079 | 29.4439
8.1 | 0 | 0.357 | 0.714 | 1.071 | 1.428 | 1.785 | 2.142 | 2.499 | 2.856 | 3.213 | 3.57 | 3.5733 | 3.5765 | 3.5798 | 3.583 | 3.5863 | 3.5608 | 3.5354 | 3.5099 | 3.4845 | 3.459 | 3.449 | 3.439 | 3.429 | 3.419 | 3.409 | 3.399 | 3.389 | 3.379 | 3.369 | 3.359 | 3.4253 | 3.4915 | 3.5578 | 3.6241 | 3.6903 | 3.7566 | 3.8229 | 3.8891 | 3.9554 | 4.0217 | 4.0879 | 4.1542 | 4.2205 | 4.2867 | 4.353 | 4.4244 | 4.4957 | 4.5671 | 4.6384 | 4.7098 | 4.7811 | 4.8525 | 4.9238 | 4.9952 | 5.0665 | 5.1379 | 5.2092 | 5.2806 | 5.3519 | 5.4233 | 5.6791 | 5.935 | 6.1908 | 6.4467 | 6.7025 | 6.9584 | 7.2142 | 7.4701 | 7.7259 | 7.9818 | 8.2376 | 8.4935 | 8.7493 | 9.0052 | 9.261 | 9.5169 | 9.7727 | 10.0285 | 10.2844 | 10.5403 | 10.7961 | 11.0519 | 11.3078 | 11.5637 | 11.8195 | 12.0754 | 12.3312 | 12.587 | 12.8429 | 13.0988 | 13.3314 | 13.564 | 13.7967 | 14.0294 | 14.262 | 14.4947 | 14.7273 | 14.9599 | 15.1926 | 15.4253 | 15.6579 | 15.8905 | 16.1232 | 16.3559 | 16.5885 | 16.8211 | 17.0538 | 17.2864 | 17.5191 | 17.7518 | 17.9844 | 18.2171 | 18.4497 | 18.6823 | 18.915 | 19.1476 | 19.3803 | 19.613 | 19.8456 | 20.0783 | 20.2645 | 20.4508 | 20.637 | 20.8233 | 21.0095 | 21.1958 | 21.382 | 21.5683 | 21.7545 | 21.9408 | 22.127 | 22.3133 | 22.4995 | 22.6858 | 22.872 | 23.0583 | 23.2445 | 23.4308 | 23.617 | 23.8033 | 23.9895 | 24.1758 | 24.362 | 24.5483 | 24.7345 | 24.9208 | 25.107 | 25.2933 | 25.4795 | 25.6658 | 25.8033 | 25.9409 | 26.0785 | 26.216 | 26.3536 | 26.4912 | 26.6287 | 26.7663 | 26.9039 | 27.0414 | 27.179 | 27.3166 | 27.4541 | 27.5917 | 27.7293 | 27.8668 | 28.0044 | 28.142 | 28.2795 | 28.4171 | 28.5547 | 28.6922 | 28.8298 | 28.9674 | 29.1049 | 29.2425 | 29.3801 | 29.5176 | 29.6552 | 29.7927
8.15 | 0 | 0.361 | 0.722 | 1.083 | 1.444 | 1.805 | 2.166 | 2.527 | 2.888 | 3.249 | 3.61 | 3.6144 | 3.6188 | 3.6231 | 3.6275 | 3.6319 | 3.6062 | 3.5805 | 3.5549 | 3.5292 | 3.5035 | 3.4935 | 3.4835 | 3.4735 | 3.4635 | 3.4535 | 3.4435 | 3.4335 | 3.4235 | 3.4135 | 3.4035 | 3.4706 | 3.5376 | 3.6047 | 3.6718 | 3.7388 | 3.8059 | 3.873 | 3.94 | 4.0071 | 4.0742 | 4.1412 | 4.2083 | 4.2754 | 4.3424 | 4.4095 | 4.4817 | 4.5539 | 4.6261 | 4.6983 | 4.7705 | 4.8427 | 4.9148 | 4.987 | 5.0592 | 5.1314 | 5.2036 | 5.2758 | 5.348 | 5.4202 | 5.4924 | 5.7512 | 6.0099 | 6.2687 | 6.5275 | 6.7863 | 7.045 | 7.3038 | 7.5626 | 7.8214 | 8.0801 | 8.3389 | 8.5977 | 8.8565 | 9.1152 | 9.374 | 9.6328 | 9.8916 | 10.1503 | 10.4091 | 10.6679 | 10.9267 | 11.1854 | 11.4442 | 11.703 | 11.9618 | 12.2205 | 12.4793 | 12.7381 | 12.9969 | 13.2556 | 13.4909 | 13.7262 | 13.9616 | 14.1969 | 14.4322 | 14.6675 | 14.9028 | 15.1381 | 15.3734 | 15.6087 | 15.844 | 16.0793 | 16.3146 | 16.5499 | 16.7853 | 17.0206 | 17.2559 | 17.4912 | 17.7265 | 17.9618 | 18.1971 | 18.4324 | 18.6677 | 18.903 | 19.1383 | 19.3736 | 19.609 | 19.8443 | 20.0796 | 20.3149 | 20.5033 | 20.6916 | 20.88 | 21.0684 | 21.2568 | 21.4451 | 21.6335 | 21.8219 | 22.0103 | 22.1986 | 22.387 | 22.5754 | 22.7638 | 22.9521 | 23.1405 | 23.3289 | 23.5173 | 23.7056 | 23.894 | 24.0824 | 24.2708 | 24.4591 | 24.6475 | 24.8359 | 25.0243 | 25.2126 | 25.401 | 25.5894 | 25.7778 | 25.9661 | 26.1053 | 26.2445 | 26.3837 | 26.5229 | 26.662 | 26.8012 | 26.9404 | 27.0796 | 27.2188 | 27.358 | 27.4971 | 27.6363 | 27.7755 | 27.9147 | 28.0539 | 28.1931 | 28.3322 | 28.4714 | 28.6106 | 28.7498 | 28.889 | 29.0282 | 29.1673 | 29.3065 | 29.4457 | 29.5849 | 29.7241 | 29.8633 | 30.0024 | 30.1416
8.2 | 0 | 0.365 | 0.73 | 1.095 | 1.46 | 1.825 | 2.19 | 2.555 | 2.92 | 3.285 | 3.65 | 3.6555 | 3.661 | 3.6665 | 3.672 | 3.6775 | 3.6516 | 3.6257 | 3.5998 | 3.5739 | 3.548 | 3.538 | 3.528 | 3.518 | 3.508 | 3.498 | 3.488 | 3.478 | 3.468 | 3.458 | 3.448 | 3.5159 | 3.5837 | 3.6516 | 3.7195 | 3.7873 | 3.8552 | 3.9231 | 3.9909 | 4.0588 | 4.1267 | 4.1945 | 4.2624 | 4.3303 | 4.3981 | 4.466 | 4.539 | 4.6121 | 4.6851 | 4.7581 | 4.8312 | 4.9042 | 4.9772 | 5.0503 | 5.1233 | 5.1963 | 5.2694 | 5.3424 | 5.4154 | 5.4885 | 5.5615 | 5.8232 | 6.0849 | 6.3466 | 6.6083 | 6.87 | 7.1317 | 7.3934 | 7.6551 | 7.9168 | 8.1785 | 8.4402 | 8.7019 | 8.9636 | 9.2253 | 9.487 | 9.7487 | 10.0104 | 10.2721 | 10.5338 | 10.7955 | 11.0572 | 11.3189 | 11.5806 | 11.8423 | 12.104 | 12.3657 | 12.6274 | 12.8891 | 13.1508 | 13.4125 | 13.6505 | 13.8884 | 14.1264 | 14.3644 | 14.6023 | 14.8403 | 15.0783 | 15.3162 | 15.5542 | 15.7922 | 16.0301 | 16.2681 | 16.5061 | 16.744 | 16.982 | 17.22 | 17.4579 | 17.6959 | 17.9339 | 18.1718 | 18.4098 | 18.6478 | 18.8857 | 19.1237 | 19.3617 | 19.5996 | 19.8376 | 20.0756 | 20.3135 | 20.5515 | 20.742 | 20.9325 | 21.123 | 21.3135 | 21.504 | 21.6945 | 21.885 | 22.0755 | 22.266 | 22.4565 | 22.647 | 22.8375 | 23.028 | 23.2185 | 23.409 | 23.5995 | 23.79 | 23.9805 | 24.171 | 24.3615 | 24.552 | 24.7425 | 24.933 | 25.1235 | 25.314 | 25.5045 | 25.695 | 25.8855 | 26.076 | 26.2665 | 26.4073 | 26.5481 | 26.6889 | 26.8297 | 26.9705 | 27.1113 | 27.2521 | 27.3929 | 27.5337 | 27.6745 | 27.8153 | 27.9561 | 28.0969 | 28.2377 | 28.3785 | 28.5193 | 28.6601 | 28.8009 | 28.9417 | 29.0825 | 29.2233 | 29.3641 | 29.5049 | 29.6457 | 29.7865 | 29.9273 | 30.0681 | 30.2089 | 30.3497 | 30.4905
8.25 | 0 | 0.369 | 0.738 | 1.107 | 1.476 | 1.845 | 2.214 | 2.583 | 2.952 | 3.321 | 3.69 | 3.6966 | 3.7033 | 3.7099 | 3.7165 | 3.7231 | 3.697 | 3.6709 | 3.6448 | 3.6186 | 3.5925 | 3.5825 | 3.5725 | 3.5625 | 3.5525 | 3.5425 | 3.5325 | 3.5225 | 3.5125 | 3.5025 | 3.4925 | 3.5612 | 3.6298 | 3.6985 | 3.7672 | 3.8358 | 3.9045 | 3.9732 | 4.0418 | 4.1105 | 4.1792 | 4.2478 | 4.3165 | 4.3852 | 4.4538 | 4.5225 | 4.5964 | 4.6703 | 4.7441 | 4.818 | 4.8919 | 4.9658 | 5.0396 | 5.1135 | 5.1874 | 5.2613 | 5.3351 | 5.409 | 5.4829 | 5.5568 | 5.6306 | 5.8953 | 6.1599 | 6.4245 | 6.6891 | 6.9538 | 7.2184 | 7.483 | 7.7476 | 8.0123 | 8.2769 | 8.5415 | 8.8061 | 9.0708 | 9.3354 | 9.6 | 9.8646 | 10.1293 | 10.3939 | 10.6585 | 10.9231 | 11.1877 | 11.4524 | 11.717 | 11.9816 | 12.2462 | 12.5109 | 12.7755 | 13.0401 | 13.3048 | 13.5694 | 13.81 | 14.0506 | 14.2912 | 14.5319 | 14.7725 | 15.0131 | 15.2538 | 15.4944 | 15.735 | 15.9756 | 16.2162 | 16.4569 | 16.6975 | 16.9381 | 17.1788 | 17.4194 | 17.66 | 17.9006 | 18.1412 | 18.3819 | 18.6225 | 18.8631 | 19.1038 | 19.3444 | 19.585 | 19.8256 | 20.0663 | 20.3069 | 20.5475 | 20.7881 | 20.9808 | 21.1734 | 21.366 | 21.5586 | 21.7513 | 21.9439 | 22.1365 | 22.3291 | 22.5218 | 22.7144 | 22.907 | 23.0996 | 23.2923 | 23.4849 | 23.6775 | 23.8701 | 24.0628 | 24.2554 | 24.448 | 24.6406 | 24.8333 | 25.0259 | 25.2185 | 25.4111 | 25.6038 | 25.7964 | 25.989 | 26.1816 | 26.3743 | 26.5669 | 26.7093 | 26.8517 | 26.9941 | 27.1365 | 27.279 | 27.4214 | 27.5638 | 27.7062 | 27.8486 | 27.991 | 28.1335 | 28.2759 | 28.4183 | 28.5607 | 28.7031 | 28.8455 | 28.988 | 29.1304 | 29.2728 | 29.4152 | 29.5576 | 29.7 | 29.8425 | 29.9849 | 30.1273 | 30.2697 | 30.4121 | 30.5545 | 30.697 | 30.8394
8.3 | 0 | 0.373 | 0.746 | 1.119 | 1.492 | 1.865 | 2.238 | 2.611 | 2.984 | 3.357 | 3.73 | 3.7378 | 3.7455 | 3.7533 | 3.761 | 3.7688 | 3.7424 | 3.7161 | 3.6897 | 3.6634 | 3.637 | 3.627 | 3.617 | 3.607 | 3.597 | 3.587 | 3.577 | 3.567 | 3.557 | 3.547 | 3.537 | 3.6065 | 3.6759 | 3.7454 | 3.8149 | 3.8843 | 3.9538 | 4.0233 | 4.0927 | 4.1622 | 4.2317 | 4.3011 | 4.3706 | 4.4401 | 4.5095 | 4.579 | 4.6537 | 4.7284 | 4.8032 | 4.8779 | 4.9526 | 5.0273 | 5.102 | 5.1767 | 5.2515 | 5.3262 | 5.4009 | 5.4756 | 5.5503 | 5.625 | 5.6998 | 5.9673 | 6.2349 | 6.5024 | 6.77 | 7.0375 | 7.3051 | 7.5726 | 7.8402 | 8.1077 | 8.3753 | 8.6428 | 8.9104 | 9.1779 | 9.4455 | 9.713 | 9.9806 | 10.2481 | 10.5157 | 10.7832 | 11.0508 | 11.3183 | 11.5859 | 11.8534 | 12.121 | 12.3885 | 12.6561 | 12.9236 | 13.1912 | 13.4587 | 13.7263 | 13.9695 | 14.2128 | 14.4561 | 14.6994 | 14.9427 | 15.186 | 15.4292 | 15.6725 | 15.9158 | 16.1591 | 16.4024 | 16.6456 | 16.8889 | 17.1322 | 17.3755 | 17.6188 | 17.8621 | 18.1054 | 18.3486 | 18.5919 | 18.8352 | 19.0785 | 19.3218 | 19.565 | 19.8083 | 20.0516 | 20.2949 | 20.5382 | 20.7815 | 21.0248 | 21.2195 | 21.4142 | 21.609 | 21.8038 | 21.9985 | 22.1932 | 22.388 | 22.5828 | 22.7775 | 22.9722 | 23.167 | 23.3618 | 23.5565 | 23.7512 | 23.946 | 24.1408 | 24.3355 | 24.5302 | 24.725 | 24.9198 | 25.1145 | 25.3092 | 25.504 | 25.6988 | 25.8935 | 26.0883 | 26.283 | 26.4778 | 26.6725 | 26.8673 | 27.0113 | 27.1553 | 27.2994 | 27.4434 | 27.5874 | 27.7315 | 27.8755 | 28.0195 | 28.1636 | 28.3076 | 28.4516 | 28.5957 | 28.7397 | 28.8837 | 29.0278 | 29.1718 | 29.3158 | 29.4599 | 29.6039 | 29.7479 | 29.892 | 30.036 | 30.18 | 30.3241 | 30.4681 | 30.6121 | 30.7562 | 30.9002 | 31.0442 | 31.1882
8.35 | 0 | 0.377 | 0.754 | 1.131 | 1.508 | 1.885 | 2.262 | 2.639 | 3.016 | 3.393 | 3.77 | 3.7789 | 3.7878 | 3.7966 | 3.8055 | 3.8144 | 3.7878 | 3.7612 | 3.7347 | 3.7081 | 3.6815 | 3.6715 | 3.6615 | 3.6515 | 3.6415 | 3.6315 | 3.6215 | 3.6115 | 3.6015 | 3.5915 | 3.5815 | 3.6518 | 3.722 | 3.7923 | 3.8626 | 3.9328 | 4.0031 | 4.0734 | 4.1436 | 4.2139 | 4.2842 | 4.3544 | 4.4247 | 4.495 | 4.5652 | 4.6355 | 4.7111 | 4.7866 | 4.8622 | 4.9377 | 5.0133 | 5.0889 | 5.1644 | 5.24 | 5.3155 | 5.3911 | 5.4666 | 5.5422 | 5.6178 | 5.6933 | 5.7689 | 6.0394 | 6.3098 | 6.5803 | 6.8508 | 7.1213 | 7.3917 | 7.6622 | 7.9327 | 8.2032 | 8.4736 | 8.7441 | 9.0146 | 9.2851 | 9.5555 | 9.826 | 10.0965 | 10.3669 | 10.6374 | 10.9079 | 11.1784 | 11.4489 | 11.7193 | 11.9898 | 12.2603 | 12.5307 | 12.8012 | 13.0717 | 13.3422 | 13.6127 | 13.8831 | 14.1291 | 14.375 | 14.621 | 14.8669 | 15.1128 | 15.3588 | 15.6047 | 15.8507 | 16.0966 | 16.3425 | 16.5885 | 16.8344 | 17.0804 | 17.3263 | 17.5723 | 17.8182 | 18.0641 | 18.3101 | 18.556 | 18.802 | 19.0479 | 19.2938 | 19.5398 | 19.7857 | 20.0317 | 20.2776 | 20.5236 | 20.7695 | 21.0154 | 21.2614 | 21.4582 | 21.6551 | 21.852 | 22.0489 | 22.2458 | 22.4426 | 22.6395 | 22.8364 | 23.0332 | 23.2301 | 23.427 | 23.6239 | 23.8208 | 24.0176 | 24.2145 | 24.4114 | 24.6083 | 24.8051 | 25.002 | 25.1989 | 25.3958 | 25.5926 | 25.7895 | 25.9864 | 26.1833 | 26.3801 | 26.577 | 26.7739 | 26.9708 | 27.1676 | 27.3133 | 27.4589 | 27.6046 | 27.7502 | 27.8959 | 28.0415 | 28.1872 | 28.3328 | 28.4785 | 28.6241 | 28.7698 | 28.9154 | 29.0611 | 29.2067 | 29.3524 | 29.498 | 29.6437 | 29.7893 | 29.935 | 30.0806 | 30.2263 | 30.3719 | 30.5176 | 30.6632 | 30.8089 | 30.9545 | 31.1002 | 31.2458 | 31.3915 | 31.5371
8.4 | 0 | 0.381 | 0.762 | 1.143 | 1.524 | 1.905 | 2.286 | 2.667 | 3.048 | 3.429 | 3.81 | 3.82 | 3.83 | 3.84 | 3.85 | 3.86 | 3.8332 | 3.8064 | 3.7796 | 3.7528 | 3.726 | 3.716 | 3.706 | 3.696 | 3.686 | 3.676 | 3.666 | 3.656 | 3.646 | 3.636 | 3.626 | 3.6971 | 3.7681 | 3.8392 | 3.9103 | 3.9813 | 4.0524 | 4.1235 | 4.1945 | 4.2656 | 4.3367 | 4.4077 | 4.4788 | 4.5499 | 4.6209 | 4.692 | 4.7684 | 4.8448 | 4.9212 | 4.9976 | 5.074 | 5.1504 | 5.2268 | 5.3032 | 5.3796 | 5.456 | 5.5324 | 5.6088 | 5.6852 | 5.7616 | 5.838 | 6.1114 | 6.3848 | 6.6582 | 6.9316 | 7.205 | 7.4784 | 7.7518 | 8.0252 | 8.2986 | 8.572 | 8.8454 | 9.1188 | 9.3922 | 9.6656 | 9.939 | 10.2124 | 10.4858 | 10.7592 | 11.0326 | 11.306 | 11.5794 | 11.8528 | 12.1262 | 12.3996 | 12.673 | 12.9464 | 13.2198 | 13.4932 | 13.7666 | 14.04 | 14.2886 | 14.5372 | 14.7858 | 15.0344 | 15.283 | 15.5316 | 15.7802 | 16.0288 | 16.2774 | 16.526 | 16.7746 | 17.0232 | 17.2718 | 17.5204 | 17.769 | 18.0176 | 18.2662 | 18.5148 | 18.7634 | 19.012 | 19.2606 | 19.5092 | 19.7578 | 20.0064 | 20.255 | 20.5036 | 20.7522 | 21.0008 | 21.2494 | 21.498 | 21.697 | 21.896 | 22.095 | 22.294 | 22.493 | 22.692 | 22.891 | 23.09 | 23.289 | 23.488 | 23.687 | 23.886 | 24.085 | 24.284 | 24.483 | 24.682 | 24.881 | 25.08 | 25.279 | 25.478 | 25.677 | 25.876 | 26.075 | 26.274 | 26.473 | 26.672 | 26.871 | 27.07 | 27.269 | 27.468 | 27.6153 | 27.7625 | 27.9098 | 28.0571 | 28.2043 | 28.3516 | 28.4989 | 28.6461 | 28.7934 | 28.9407 | 29.0879 | 29.2352 | 29.3825 | 29.5297 | 29.677 | 29.8243 | 29.9715 | 30.1188 | 30.2661 | 30.4133 | 30.5606 | 30.7079 | 30.8551 | 31.0024 | 31.1497 | 31.2969 | 31.4442 | 31.5915 | 31.7387 | 31.886
8.45 | 0 | 0.385 | 0.77 | 1.155 | 1.54 | 1.925 | 2.31 | 2.695 | 3.08 | 3.465 | 3.85 | 3.8611 | 3.8723 | 3.8834 | 3.8945 | 3.9056 | 3.8786 | 3.8516 | 3.8246 | 3.7975 | 3.7705 | 3.7605 | 3.7505 | 3.7405 | 3.7305 | 3.7205 | 3.7105 | 3.7005 | 3.6905 | 3.6805 | 3.6705 | 3.7424 | 3.8142 | 3.8861 | 3.958 | 4.0298 | 4.1017 | 4.1736 | 4.2454 | 4.3173 | 4.3892 | 4.461 | 4.5329 | 4.6048 | 4.6766 | 4.7485 | 4.8257 | 4.903 | 4.9802 | 5.0575 | 5.1347 | 5.212 | 5.2892 | 5.3664 | 5.4437 | 5.5209 | 5.5982 | 5.6754 | 5.7526 | 5.8299 | 5.9071 | 6.1835 | 6.4598 | 6.7361 | 7.0124 | 7.2888 | 7.5651 | 7.8414 | 8.1177 | 8.3941 | 8.6704 | 8.9467 | 9.223 | 9.4994 | 9.7757 | 10.052 | 10.3283 | 10.6046 | 10.881 | 11.1573 | 11.4336 | 11.7099 | 11.9863 | 12.2626 | 12.5389 | 12.8153 | 13.0916 | 13.3679 | 13.6442 | 13.9206 | 14.1969 | 14.4481 | 14.6994 | 14.9506 | 15.2019 | 15.4532 | 15.7044 | 15.9557 | 16.2069 | 16.4582 | 16.7095 | 16.9607 | 17.212 | 17.4632 | 17.7145 | 17.9657 | 18.217 | 18.4683 | 18.7195 | 18.9708 | 19.222 | 19.4733 | 19.7246 | 19.9758 | 20.2271 | 20.4783 | 20.7296 | 20.9809 | 21.2321 | 21.4834 | 21.7346 | 21.9357 | 22.1369 | 22.338 | 22.5391 | 22.7402 | 22.9414 | 23.1425 | 23.3436 | 23.5448 | 23.7459 | 23.947 | 24.1481 | 24.3493 | 24.5504 | 24.7515 | 24.9526 | 25.1538 | 25.3549 | 25.556 | 25.7571 | 25.9583 | 26.1594 | 26.3605 | 26.5616 | 26.7628 | 26.9639 | 27.165 | 27.3661 | 27.5673 | 27.7684 | 27.9173 | 28.0661 | 28.215 | 28.3639 | 28.5128 | 28.6617 | 28.8106 | 28.9594 | 29.1083 | 29.2572 | 29.4061 | 29.555 | 29.7039 | 29.8527 | 30.0016 | 30.1505 | 30.2994 | 30.4483 | 30.5972 | 30.746 | 30.8949 | 31.0438 | 31.1927 | 31.3416 | 31.4905 | 31.6393 | 31.7882 | 31.9371 | 32.086 | 32.2349
8.5 | 0 | 0.389 | 0.778 | 1.167 | 1.556 | 1.945 | 2.334 | 2.723 | 3.112 | 3.501 | 3.89 | 3.9023 | 3.9145 | 3.9268 | 3.939 | 3.9513 | 3.924 | 3.8968 | 3.8695 | 3.8423 | 3.815 | 3.805 | 3.795 | 3.785 | 3.775 | 3.765 | 3.755 | 3.745 | 3.735 | 3.725 | 3.715 | 3.7877 | 3.8603 | 3.933 | 4.0057 | 4.0783 | 4.151 | 4.2237 | 4.2963 | 4.369 | 4.4417 | 4.5143 | 4.587 | 4.6597 | 4.7323 | 4.805 | 4.8831 | 4.9612 | 5.0393 | 5.1173 | 5.1954 | 5.2735 | 5.3516 | 5.4297 | 5.5078 | 5.5858 | 5.6639 | 5.742 | 5.8201 | 5.8982 | 5.9763 | 6.2555 | 6.5348 | 6.814 | 7.0933 | 7.3725 | 7.6518 | 7.931 | 8.2103 | 8.4895 | 8.7688 | 9.048 | 9.3273 | 9.6065 | 9.8858 | 10.165 | 10.4443 | 10.7235 | 11.0028 | 11.282 | 11.5612 | 11.8405 | 12.1197 | 12.399 | 12.6783 | 12.9575 | 13.2368 | 13.516 | 13.7952 | 14.0745 | 14.3537 | 14.6077 | 14.8616 | 15.1155 | 15.3694 | 15.6233 | 15.8773 | 16.1312 | 16.3851 | 16.639 | 16.8929 | 17.1468 | 17.4007 | 17.6547 | 17.9086 | 18.1625 | 18.4164 | 18.6703 | 18.9243 | 19.1782 | 19.4321 | 19.686 | 19.9399 | 20.1938 | 20.4477 | 20.7017 | 20.9556 | 21.2095 | 21.4634 | 21.7173 | 21.9713 | 22.1745 | 22.3778 | 22.581 | 22.7843 | 22.9875 | 23.1908 | 23.394 | 23.5973 | 23.8005 | 24.0038 | 24.207 | 24.4103 | 24.6135 | 24.8168 | 25.02 | 25.2233 | 25.4265 | 25.6298 | 25.833 | 26.0363 | 26.2395 | 26.4428 | 26.646 | 26.8493 | 27.0525 | 27.2558 | 27.459 | 27.6623 | 27.8655 | 28.0688 | 28.2193 | 28.3698 | 28.5203 | 28.6708 | 28.8213 | 28.9718 | 29.1223 | 29.2728 | 29.4233 | 29.5738 | 29.7243 | 29.8748 | 30.0253 | 30.1758 | 30.3263 | 30.4768 | 30.6273 | 30.7778 | 30.9283 | 31.0788 | 31.2293 | 31.3798 | 31.5303 | 31.6808 | 31.8313 | 31.9818 | 32.1323 | 32.2828 | 32.4333 | 32.5837
8.55 | 0 | 0.393 | 0.786 | 1.179 | 1.572 | 1.965 | 2.358 | 2.751 | 3.144 | 3.537 | 3.93 | 3.9434 | 3.9568 | 3.9701 | 3.9835 | 3.9969 | 3.9694 | 3.9419 | 3.9145 | 3.887 | 3.8595 | 3.8495 | 3.8395 | 3.8295 | 3.8195 | 3.8095 | 3.7995 | 3.7895 | 3.7795 | 3.7695 | 3.7595 | 3.833 | 3.9064 | 3.9799 | 4.0534 | 4.1268 | 4.2003 | 4.2738 | 4.3472 | 4.4207 | 4.4942 | 4.5676 | 4.6411 | 4.7146 | 4.788 | 4.8615 | 4.9404 | 5.0194 | 5.0983 | 5.1772 | 5.2561 | 5.3351 | 5.414 | 5.4929 | 5.5718 | 5.6508 | 5.7297 | 5.8086 | 5.8875 | 5.9665 | 6.0454 | 6.3276 | 6.6097 | 6.8919 | 7.1741 | 7.4563 | 7.7384 | 8.0206 | 8.3028 | 8.585 | 8.8671 | 9.1493 | 9.4315 | 9.7137 | 9.9958 | 10.278 | 10.5602 | 10.8423 | 11.1245 | 11.4067 | 11.6889 | 11.971 | 12.2532 | 12.5354 | 12.8176 | 13.0998 | 13.3819 | 13.6641 | 13.9463 | 14.2285 | 14.5106 | 14.7672 | 15.0238 | 15.2804 | 15.5369 | 15.7935 | 16.0501 | 16.3067 | 16.5632 | 16.8198 | 17.0764 | 17.333 | 17.5895 | 17.8461 | 18.1027 | 18.3592 | 18.6158 | 18.8724 | 19.129 | 19.3855 | 19.6421 | 19.8987 | 20.1553 | 20.4119 | 20.6684 | 20.925 | 21.1816 | 21.4382 | 21.6947 | 21.9513 | 22.2079 | 22.4133 | 22.6186 | 22.824 | 23.0294 | 23.2347 | 23.4401 | 23.6455 | 23.8509 | 24.0562 | 24.2616 | 24.467 | 24.6724 | 24.8777 | 25.0831 | 25.2885 | 25.4939 | 25.6992 | 25.9046 | 26.11 | 26.3154 | 26.5208 | 26.7261 | 26.9315 | 27.1369 | 27.3423 | 27.5476 | 27.753 | 27.9584 | 28.1638 | 28.3691 | 28.5212 | 28.6734 | 28.8255 | 28.9776 | 29.1297 | 29.2818 | 29.4339 | 29.5861 | 29.7382 | 29.8903 | 30.0424 | 30.1945 | 30.3466 | 30.4988 | 30.6509 | 30.803 | 30.9551 | 31.1072 | 31.2593 | 31.4115 | 31.5636 | 31.7157 | 31.8678 | 32.0199 | 32.172 | 32.3242 | 32.4763 | 32.6284 | 32.7805 | 32.9326
8.6 | 0 | 0.397 | 0.794 | 1.191 | 1.588 | 1.985 | 2.382 | 2.779 | 3.176 | 3.573 | 3.97 | 3.9845 | 3.999 | 4.0135 | 4.028 | 4.0425 | 4.0148 | 3.9871 | 3.9594 | 3.9317 | 3.904 | 3.894 | 3.884 | 3.874 | 3.864 | 3.854 | 3.844 | 3.834 | 3.824 | 3.814 | 3.804 | 3.8783 | 3.9525 | 4.0268 | 4.1011 | 4.1753 | 4.2496 | 4.3239 | 4.3981 | 4.4724 | 4.5467 | 4.6209 | 4.6952 | 4.7695 | 4.8437 | 4.918 | 4.9978 | 5.0775 | 5.1573 | 5.2371 | 5.3168 | 5.3966 | 5.4764 | 5.5561 | 5.6359 | 5.7157 | 5.7954 | 5.8752 | 5.955 | 6.0347 | 6.1145 | 6.3996 | 6.6847 | 6.9698 | 7.2549 | 7.54 | 7.8251 | 8.1102 | 8.3953 | 8.6804 | 8.9655 | 9.2506 | 9.5357 | 9.8208 | 10.1059 | 10.391 | 10.6761 | 10.9612 | 11.2463 | 11.5314 | 11.8165 | 12.1016 | 12.3867 | 12.6718 | 12.9569 | 13.242 | 13.5271 | 13.8122 | 14.0973 | 14.3824 | 14.6675 | 14.9267 | 15.186 | 15.4452 | 15.7044 | 15.9637 | 16.2229 | 16.4821 | 16.7414 | 17.0006 | 17.2598 | 17.5191 | 17.7783 | 18.0375 | 18.2968 | 18.556 | 18.8152 | 19.0745 | 19.3337 | 19.5929 | 19.8522 | 20.1114 | 20.3706 | 20.6299 | 20.8891 | 21.1483 | 21.4076 | 21.6668 | 21.926 | 22.1853 | 22.4445 | 22.652 | 22.8595 | 23.067 | 23.2745 | 23.482 | 23.6895 | 23.897 | 24.1045 | 24.312 | 24.5195 | 24.727 | 24.9345 | 25.142 | 25.3495 | 25.557 | 25.7645 | 25.972 | 26.1795 | 26.387 | 26.5945 | 26.802 | 27.0095 | 27.217 | 27.4245 | 27.632 | 27.8395 | 28.047 | 28.2545 | 28.462 | 28.6695 | 28.8232 | 28.977 | 29.1307 | 29.2844 | 29.4382 | 29.5919 | 29.7456 | 29.8994 | 30.0531 | 30.2068 | 30.3606 | 30.5143 | 30.668 | 30.8218 | 30.9755 | 31.1292 | 31.283 | 31.4367 | 31.5904 | 31.7442 | 31.8979 | 32.0516 | 32.2054 | 32.3591 | 32.5128 | 32.6666 | 32.8203 | 32.974 | 33.1278 | 33.2815
8.65 | 0 | 0.401 | 0.802 | 1.203 | 1.604 | 2.005 | 2.406 | 2.807 | 3.208 | 3.609 | 4.01 | 4.0256 | 4.0413 | 4.0569 | 4.0725 | 4.0881 | 4.0602 | 4.0323 | 4.0044 | 3.9764 | 3.9485 | 3.9385 | 3.9285 | 3.9185 | 3.9085 | 3.8985 | 3.8885 | 3.8785 | 3.8685 | 3.8585 | 3.8485 | 3.9236 | 3.9986 | 4.0737 | 4.1488 | 4.2238 | 4.2989 | 4.374 | 4.449 | 4.5241 | 4.5992 | 4.6742 | 4.7493 | 4.8244 | 4.8994 | 4.9745 | 5.0551 | 5.1357 | 5.2163 | 5.2969 | 5.3775 | 5.4582 | 5.5388 | 5.6194 | 5.7 | 5.7806 | 5.8612 | 5.9418 | 6.0224 | 6.103 | 6.1836 | 6.4717 | 6.7597 | 7.0477 | 7.3357 | 7.6238 | 7.9118 | 8.1998 | 8.4878 | 8.7759 | 9.0639 | 9.3519 | 9.6399 | 9.928 | 10.216 | 10.504 | 10.792 | 11.08 | 11.3681 | 11.6561 | 11.9441 | 12.2322 | 12.5202 | 12.8082 | 13.0962 | 13.3842 | 13.6723 | 13.9603 | 14.2483 | 14.5364 | 14.8244 | 15.0863 | 15.3482 | 15.61 | 15.8719 | 16.1338 | 16.3957 | 16.6576 | 16.9195 | 17.1814 | 17.4433 | 17.7052 | 17.9671 | 18.229 | 18.4909 | 18.7527 | 19.0146 | 19.2765 | 19.5384 | 19.8003 | 20.0622 | 20.3241 | 20.586 | 20.8479 | 21.1098 | 21.3717 | 21.6336 | 21.8955 | 22.1573 | 22.4192 | 22.6811 | 22.8908 | 23.1004 | 23.31 | 23.5196 | 23.7293 | 23.9389 | 24.1485 | 24.3581 | 24.5678 | 24.7774 | 24.987 | 25.1966 | 25.4062 | 25.6159 | 25.8255 | 26.0351 | 26.2447 | 26.4544 | 26.664 | 26.8736 | 27.0832 | 27.2929 | 27.5025 | 27.7121 | 27.9217 | 28.1314 | 28.341 | 28.5506 | 28.7603 | 28.9699 | 29.1252 | 29.2806 | 29.4359 | 29.5913 | 29.7466 | 29.902 | 30.0573 | 30.2127 | 30.368 | 30.5234 | 30.6787 | 30.8341 | 30.9894 | 31.1448 | 31.3001 | 31.4555 | 31.6108 | 31.7662 | 31.9215 | 32.0769 | 32.2322 | 32.3876 | 32.5429 | 32.6983 | 32.8536 | 33.009 | 33.1643 | 33.3197 | 33.475 | 33.6304
8.7 | 0 | 0.405 | 0.81 | 1.215 | 1.62 | 2.025 | 2.43 | 2.835 | 3.24 | 3.645 | 4.05 | 4.0668 | 4.0835 | 4.1003 | 4.117 | 4.1338 | 4.1056 | 4.0775 | 4.0493 | 4.0212 | 3.993 | 3.983 | 3.973 | 3.963 | 3.953 | 3.943 | 3.933 | 3.923 | 3.913 | 3.903 | 3.893 | 3.9689 | 4.0447 | 4.1206 | 4.1965 | 4.2723 | 4.3482 | 4.4241 | 4.4999 | 4.5758 | 4.6517 | 4.7275 | 4.8034 | 4.8793 | 4.9551 | 5.031 | 5.1125 | 5.1939 | 5.2754 | 5.3568 | 5.4383 | 5.5197 | 5.6012 | 5.6826 | 5.7641 | 5.8455 | 5.927 | 6.0084 | 6.0899 | 6.1713 | 6.2528 | 6.5437 | 6.8347 | 7.1256 | 7.4166 | 7.7075 | 7.9985 | 8.2894 | 8.5804 | 8.8713 | 9.1623 | 9.4532 | 9.7442 | 10.0351 | 10.3261 | 10.617 | 10.9079 | 11.1989 | 11.4899 | 11.7808 | 12.0717 | 12.3627 | 12.6537 | 12.9446 | 13.2355 | 13.5265 | 13.8174 | 14.1084 | 14.3994 | 14.6903 | 14.9812 | 15.2458 | 15.5104 | 15.7749 | 16.0394 | 16.304 | 16.5685 | 16.8331 | 17.0977 | 17.3622 | 17.6268 | 17.8913 | 18.1559 | 18.4204 | 18.685 | 18.9495 | 19.2141 | 19.4786 | 19.7431 | 20.0077 | 20.2722 | 20.5368 | 20.8013 | 21.0659 | 21.3304 | 21.595 | 21.8595 | 22.1241 | 22.3886 | 22.6532 | 22.9178 | 23.1295 | 23.3412 | 23.553 | 23.7647 | 23.9765 | 24.1883 | 24.4 | 24.6118 | 24.8235 | 25.0353 | 25.247 | 25.4588 | 25.6705 | 25.8823 | 26.094 | 26.3058 | 26.5175 | 26.7293 | 26.941 | 27.1528 | 27.3645 | 27.5763 | 27.788 | 27.9998 | 28.2115 | 28.4233 | 28.635 | 28.8468 | 29.0585 | 29.2703 | 29.4272 | 29.5842 | 29.7412 | 29.8981 | 30.0551 | 30.2121 | 30.369 | 30.526 | 30.683 | 30.8399 | 30.9969 | 31.1539 | 31.3108 | 31.4678 | 31.6248 | 31.7817 | 31.9387 | 32.0957 | 32.2526 | 32.4096 | 32.5666 | 32.7235 | 32.8805 | 33.0375 | 33.1944 | 33.3514 | 33.5084 | 33.6653 | 33.8223 | 33.9792
8.75 | 0 | 0.409 | 0.818 | 1.227 | 1.636 | 2.045 | 2.454 | 2.863 | 3.272 | 3.681 | 4.09 | 4.1079 | 4.1258 | 4.1436 | 4.1615 | 4.1794 | 4.151 | 4.1226 | 4.0943 | 4.0659 | 4.0375 | 4.0275 | 4.0175 | 4.0075 | 3.9975 | 3.9875 | 3.9775 | 3.9675 | 3.9575 | 3.9475 | 3.9375 | 4.0142 | 4.0908 | 4.1675 | 4.2442 | 4.3208 | 4.3975 | 4.4742 | 4.5508 | 4.6275 | 4.7042 | 4.7808 | 4.8575 | 4.9342 | 5.0108 | 5.0875 | 5.1698 | 5.2521 | 5.3344 | 5.4167 | 5.499 | 5.5813 | 5.6635 | 5.7458 | 5.8281 | 5.9104 | 5.9927 | 6.075 | 6.1573 | 6.2396 | 6.3219 | 6.6158 | 6.9096 | 7.2035 | 7.4974 | 7.7913 | 8.0851 | 8.379 | 8.6729 | 8.9668 | 9.2606 | 9.5545 | 9.8484 | 10.1423 | 10.4361 | 10.73 | 11.0239 | 11.3178 | 11.6116 | 11.9055 | 12.1994 | 12.4932 | 12.7871 | 13.081 | 13.3749 | 13.6687 | 13.9626 | 14.2565 | 14.5504 | 14.8443 | 15.1381 | 15.4053 | 15.6725 | 15.9398 | 16.207 | 16.4742 | 16.7414 | 17.0086 | 17.2758 | 17.543 | 17.8102 | 18.0774 | 18.3446 | 18.6118 | 18.879 | 19.1462 | 19.4135 | 19.6807 | 19.9479 | 20.2151 | 20.4823 | 20.7495 | 21.0167 | 21.2839 | 21.5511 | 21.8183 | 22.0855 | 22.3528 | 22.62 | 22.8872 | 23.1544 | 23.3682 | 23.5821 | 23.796 | 24.0099 | 24.2237 | 24.4376 | 24.6515 | 24.8654 | 25.0793 | 25.2931 | 25.507 | 25.7209 | 25.9348 | 26.1486 | 26.3625 | 26.5764 | 26.7903 | 27.0041 | 27.218 | 27.4319 | 27.6458 | 27.8596 | 28.0735 | 28.2874 | 28.5013 | 28.7151 | 28.929 | 29.1429 | 29.3568 | 29.5706 | 29.7292 | 29.8878 | 30.0464 | 30.205 | 30.3635 | 30.5221 | 30.6807 | 30.8393 | 30.9979 | 31.1565 | 31.315 | 31.4736 | 31.6322 | 31.7908 | 31.9494 | 32.108 | 32.2665 | 32.4251 | 32.5837 | 32.7423 | 32.9009 | 33.0595 | 33.218 | 33.3766 | 33.5352 | 33.6938 | 33.8524 | 34.011 | 34.1695 | 34.3281
8.8 | 0 | 0.413 | 0.826 | 1.239 | 1.652 | 2.065 | 2.478 | 2.891 | 3.304 | 3.717 | 4.13 | 4.149 | 4.168 | 4.187 | 4.206 | 4.225 | 4.1964 | 4.1678 | 4.1392 | 4.1106 | 4.082 | 4.072 | 4.062 | 4.052 | 4.042 | 4.032 | 4.022 | 4.012 | 4.002 | 3.992 | 3.982 | 4.0595 | 4.1369 | 4.2144 | 4.2919 | 4.3693 | 4.4468 | 4.5243 | 4.6017 | 4.6792 | 4.7567 | 4.8341 | 4.9116 | 4.9891 | 5.0665 | 5.144 | 5.2271 | 5.3103 | 5.3934 | 5.4765 | 5.5597 | 5.6428 | 5.7259 | 5.8091 | 5.8922 | 5.9753 | 6.0585 | 6.1416 | 6.2247 | 6.3079 | 6.391 | 6.6878 | 6.9846 | 7.2814 | 7.5782 | 7.875 | 8.1718 | 8.4686 | 8.7654 | 9.0622 | 9.359 | 9.6558 | 9.9526 | 10.2494 | 10.5462 | 10.843 | 11.1398 | 11.4366 | 11.7334 | 12.0302 | 12.327 | 12.6238 | 12.9206 | 13.2174 | 13.5142 | 13.811 | 14.1078 | 14.4046 | 14.7014 | 14.9982 | 15.295 | 15.5649 | 15.8347 | 16.1046 | 16.3745 | 16.6443 | 16.9142 | 17.1841 | 17.4539 | 17.7238 | 17.9937 | 18.2635 | 18.5334 | 18.8033 | 19.0731 | 19.343 | 19.6129 | 19.8827 | 20.1526 | 20.4225 | 20.6923 | 20.9622 | 21.2321 | 21.5019 | 21.7718 | 22.0417 | 22.3115 | 22.5814 | 22.8513 | 23.1211 | 23.391 | 23.607 | 23.823 | 24.039 | 24.255 | 24.471 | 24.687 | 24.903 | 25.119 | 25.335 | 25.551 | 25.767 | 25.983 | 26.199 | 26.415 | 26.631 | 26.847 | 27.063 | 27.279 | 27.495 | 27.711 | 27.927 | 28.143 | 28.359 | 28.575 | 28.791 | 29.007 | 29.223 | 29.439 | 29.655 | 29.871 | 30.0312 | 30.1914 | 30.3516 | 30.5118 | 30.672 | 30.8322 | 30.9924 | 31.1526 | 31.3128 | 31.473 | 31.6332 | 31.7934 | 31.9536 | 32.1138 | 32.274 | 32.4342 | 32.5944 | 32.7546 | 32.9148 | 33.075 | 33.2352 | 33.3954 | 33.5556 | 33.7158 | 33.876 | 34.0362 | 34.1964 | 34.3566 | 34.5168 | 34.677
8.85 | 0 | 0.417 | 0.834 | 1.251 | 1.668 | 2.085 | 2.502 | 2.919 | 3.336 | 3.753 | 4.17 | 4.1901 | 4.2103 | 4.2304 | 4.2505 | 4.2706 | 4.2418 | 4.213 | 4.1842 | 4.1553 | 4.1265 | 4.1165 | 4.1065 | 4.0965 | 4.0865 | 4.0765 | 4.0665 | 4.0565 | 4.0465 | 4.0365 | 4.0265 | 4.1048 | 4.183 | 4.2613 | 4.3396 | 4.4178 | 4.4961 | 4.5744 | 4.6526 | 4.7309 | 4.8092 | 4.8874 | 4.9657 | 5.044 | 5.1222 | 5.2005 | 5.2845 | 5.3685 | 5.4524 | 5.5364 | 5.6204 | 5.7044 | 5.7883 | 5.8723 | 5.9563 | 6.0403 | 6.1242 | 6.2082 | 6.2922 | 6.3762 | 6.4601 | 6.7599 | 7.0596 | 7.3593 | 7.659 | 7.9588 | 8.2585 | 8.5582 | 8.8579 | 9.1577 | 9.4574 | 9.7571 | 10.0568 | 10.3566 | 10.6563 | 10.956 | 11.2557 | 11.5555 | 11.8552 | 12.1549 | 12.4546 | 12.7544 | 13.0541 | 13.3538 | 13.6535 | 13.9533 | 14.253 | 14.5527 | 14.8524 | 15.1522 | 15.4519 | 15.7244 | 15.9969 | 16.2694 | 16.542 | 16.8145 | 17.087 | 17.3595 | 17.6321 | 17.9046 | 18.1771 | 18.4496 | 18.7222 | 18.9947 | 19.2672 | 19.5398 | 19.8123 | 20.0848 | 20.3573 | 20.6299 | 20.9024 | 21.1749 | 21.4474 | 21.72 | 21.9925 | 22.265 | 22.5375 | 22.8101 | 23.0826 | 23.3551 | 23.6276 | 23.8457 | 24.0639 | 24.282 | 24.5001 | 24.7183 | 24.9364 | 25.1545 | 25.3726 | 25.5907 | 25.8089 | 26.027 | 26.2451 | 26.4633 | 26.6814 | 26.8995 | 27.1176 | 27.3358 | 27.5539 | 27.772 | 27.9901 | 28.2083 | 28.4264 | 28.6445 | 28.8626 | 29.0808 | 29.2989 | 29.517 | 29.7351 | 29.9533 | 30.1714 | 30.3332 | 30.495 | 30.6568 | 30.8186 | 30.9805 | 31.1423 | 31.3041 | 31.4659 | 31.6277 | 31.7895 | 31.9514 | 32.1132 | 32.275 | 32.4368 | 32.5986 | 32.7604 | 32.9223 | 33.0841 | 33.2459 | 33.4077 | 33.5695 | 33.7313 | 33.8932 | 34.055 | 34.2168 | 34.3786 | 34.5404 | 34.7022 | 34.8641 | 35.0259
8.9 | 0 | 0.421 | 0.842 | 1.263 | 1.684 | 2.105 | 2.526 | 2.947 | 3.368 | 3.789 | 4.21 | 4.2313 | 4.2525 | 4.2738 | 4.295 | 4.3163 | 4.2872 | 4.2582 | 4.2291 | 4.2001 | 4.171 | 4.161 | 4.151 | 4.141 | 4.131 | 4.121 | 4.111 | 4.101 | 4.091 | 4.081 | 4.071 | 4.1501 | 4.2291 | 4.3082 | 4.3873 | 4.4663 | 4.5454 | 4.6245 | 4.7035 | 4.7826 | 4.8617 | 4.9407 | 5.0198 | 5.0989 | 5.1779 | 5.257 | 5.3418 | 5.4266 | 5.5115 | 5.5963 | 5.6811 | 5.7659 | 5.8507 | 5.9355 | 6.0204 | 6.1052 | 6.19 | 6.2748 | 6.3596 | 6.4444 | 6.5293 | 6.8319 | 7.1346 | 7.4372 | 7.7399 | 8.0425 | 8.3452 | 8.6478 | 8.9505 | 9.2531 | 9.5558 | 9.8584 | 10.161 | 10.4637 | 10.7663 | 11.069 | 11.3717 | 11.6743 | 11.977 | 12.2796 | 12.5823 | 12.8849 | 13.1875 | 13.4902 | 13.7928 | 14.0955 | 14.3981 | 14.7008 | 15.0035 | 15.3061 | 15.6088 | 15.8839 | 16.1591 | 16.4343 | 16.7095 | 16.9847 | 17.2599 | 17.535 | 17.8102 | 18.0854 | 18.3606 | 18.6358 | 18.9109 | 19.1861 | 19.4613 | 19.7365 | 20.0117 | 20.2869 | 20.562 | 20.8372 | 21.1124 | 21.3876 | 21.6628 | 21.938 | 22.2131 | 22.4883 | 22.7635 | 23.0387 | 23.3139 | 23.5891 | 23.8642 | 24.0845 | 24.3047 | 24.525 | 24.7452 | 24.9655 | 25.1857 | 25.406 | 25.6262 | 25.8465 | 26.0667 | 26.287 | 26.5072 | 26.7275 | 26.9477 | 27.168 | 27.3882 | 27.6085 | 27.8287 | 28.049 | 28.2692 | 28.4895 | 28.7097 | 28.93 | 29.1502 | 29.3705 | 29.5908 | 29.811 | 30.0313 | 30.2515 | 30.4718 | 30.6352 | 30.7986 | 30.9621 | 31.1255 | 31.2889 | 31.4523 | 31.6158 | 31.7792 | 31.9427 | 32.1061 | 32.2695 | 32.4329 | 32.5964 | 32.7598 | 32.9233 | 33.0867 | 33.2501 | 33.4136 | 33.577 | 33.7404 | 33.9039 | 34.0673 | 34.2307 | 34.3942 | 34.5576 | 34.721 | 34.8845 | 35.0479 | 35.2113 | 35.3747
8.95 | 0 | 0.425 | 0.85 | 1.275 | 1.7 | 2.125 | 2.55 | 2.975 | 3.4 | 3.825 | 4.25 | 4.2724 | 4.2948 | 4.3171 | 4.3395 | 4.3619 | 4.3326 | 4.3033 | 4.2741 | 4.2448 | 4.2155 | 4.2055 | 4.1955 | 4.1855 | 4.1755 | 4.1655 | 4.1555 | 4.1455 | 4.1355 | 4.1255 | 4.1155 | 4.1954 | 4.2752 | 4.3551 | 4.435 | 4.5148 | 4.5947 | 4.6746 | 4.7544 | 4.8343 | 4.9142 | 4.994 | 5.0739 | 5.1538 | 5.2336 | 5.3135 | 5.3992 | 5.4848 | 5.5705 | 5.6561 | 5.7418 | 5.8275 | 5.9131 | 5.9988 | 6.0844 | 6.1701 | 6.2557 | 6.3414 | 6.4271 | 6.5127 | 6.5984 | 6.904 | 7.2095 | 7.5151 | 7.8207 | 8.1263 | 8.4318 | 8.7374 | 9.043 | 9.3486 | 9.6541 | 9.9597 | 10.2653 | 10.5709 | 10.8764 | 11.182 | 11.4876 | 11.7932 | 12.0987 | 12.4043 | 12.7099 | 13.0154 | 13.321 | 13.6266 | 13.9322 | 14.2378 | 14.5433 | 14.8489 | 15.1545 | 15.4601 | 15.7656 | 16.0435 | 16.3213 | 16.5992 | 16.877 | 17.1548 | 17.4327 | 17.7105 | 17.9884 | 18.2662 | 18.544 | 18.8219 | 19.0997 | 19.3776 | 19.6554 | 19.9333 | 20.2111 | 20.4889 | 20.7668 | 21.0446 | 21.3225 | 21.6003 | 21.8781 | 22.156 | 22.4338 | 22.7117 | 22.9895 | 23.2674 | 23.5452 | 23.823 | 24.1009 | 24.3233 | 24.5456 | 24.768 | 24.9904 | 25.2127 | 25.4351 | 25.6575 | 25.8799 | 26.1023 | 26.3246 | 26.547 | 26.7694 | 26.9917 | 27.2141 | 27.4365 | 27.6589 | 27.8813 | 28.1036 | 28.326 | 28.5484 | 28.7708 | 28.9931 | 29.2155 | 29.4379 | 29.6603 | 29.8826 | 30.105 | 30.3274 | 30.5498 | 30.7721 | 30.9372 | 31.1022 | 31.2673 | 31.4323 | 31.5974 | 31.7624 | 31.9275 | 32.0925 | 32.2576 | 32.4226 | 32.5877 | 32.7527 | 32.9178 | 33.0828 | 33.2479 | 33.4129 | 33.578 | 33.743 | 33.9081 | 34.0731 | 34.2382 | 34.4032 | 34.5683 | 34.7333 | 34.8984 | 35.0634 | 35.2285 | 35.3935 | 35.5586 | 35.7236
9 | 0 | 0.429 | 0.858 | 1.287 | 1.716 | 2.145 | 2.574 | 3.003 | 3.432 | 3.861 | 4.29 | 4.3135 | 4.337 | 4.3605 | 4.384 | 4.4075 | 4.378 | 4.3485 | 4.319 | 4.2895 | 4.26 | 4.25 | 4.24 | 4.23 | 4.22 | 4.21 | 4.2 | 4.19 | 4.18 | 4.17 | 4.16 | 4.2407 | 4.3213 | 4.402 | 4.4827 | 4.5633 | 4.644 | 4.7247 | 4.8053 | 4.886 | 4.9667 | 5.0473 | 5.128 | 5.2087 | 5.2893 | 5.37 | 5.4565 | 5.543 | 5.6295 | 5.716 | 5.8025 | 5.889 | 5.9755 | 6.062 | 6.1485 | 6.235 | 6.3215 | 6.408 | 6.4945 | 6.581 | 6.6675 | 6.976 | 7.2845 | 7.593 | 7.9015 | 8.21 | 8.5185 | 8.827 | 9.1355 | 9.444 | 9.7525 | 10.061 | 10.3695 | 10.678 | 10.9865 | 11.295 | 11.6035 | 11.912 | 12.2205 | 12.529 | 12.8375 | 13.146 | 13.4545 | 13.763 | 14.0715 | 14.38 | 14.6885 | 14.997 | 15.3055 | 15.614 | 15.9225 | 16.203 | 16.4835 | 16.764 | 17.0445 | 17.325 | 17.6055 | 17.886 | 18.1665 | 18.447 | 18.7275 | 19.008 | 19.2885 | 19.569 | 19.8495 | 20.13 | 20.4105 | 20.691 | 20.9715 | 21.252 | 21.5325 | 21.813 | 22.0935 | 22.374 | 22.6545 | 22.935 | 23.2155 | 23.496 | 23.7765 | 24.057 | 24.3375 | 24.562 | 24.7865 | 25.011 | 25.2355 | 25.46 | 25.6845 | 25.909 | 26.1335 | 26.358 | 26.5825 | 26.807 | 27.0315 | 27.256 | 27.4805 | 27.705 | 27.9295 | 28.154 | 28.3785 | 28.603 | 28.8275 | 29.052 | 29.2765 | 29.501 | 29.7255 | 29.95 | 30.1745 | 30.399 | 30.6235 | 30.848 | 31.0725 | 31.2392 | 31.4058 | 31.5725 | 31.7392 | 31.9058 | 32.0725 | 32.2392 | 32.4058 | 32.5725 | 32.7392 | 32.9058 | 33.0725 | 33.2392 | 33.4058 | 33.5725 | 33.7392 | 33.9058 | 34.0725 | 34.2392 | 34.4058 | 34.5725 | 34.7392 | 34.9058 | 35.0725 | 35.2392 | 35.4058 | 35.5725 | 35.7392 | 35.9058 | 36.0725
9.05 | 0 | 0.433 | 0.866 | 1.299 | 1.732 | 2.165 | 2.598 | 3.031 | 3.464 | 3.897 | 4.33 | 4.3546 | 4.3793 | 4.4039 | 4.4285 | 4.4531 | 4.4234 | 4.3937 | 4.364 | 4.3342 | 4.3045 | 4.2945 | 4.2845 | 4.2745 | 4.2645 | 4.2545 | 4.2445 | 4.2345 | 4.2245 | 4.2145 | 4.2045 | 4.286 | 4.3674 | 4.4489 | 4.5304 | 4.6118 | 4.6933 | 4.7748 | 4.8562 | 4.9377 | 5.0192 | 5.1006 | 5.1821 | 5.2636 | 5.345 | 5.4265 | 5.5138 | 5.6012 | 5.6885 | 5.7759 | 5.8632 | 5.9506 | 6.0379 | 6.1252 | 6.2126 | 6.2999 | 6.3873 | 6.4746 | 6.5619 | 6.6493 | 6.7366 | 7.0481 | 7.3595 | 7.6709 | 7.9823 | 8.2938 | 8.6052 | 8.9166 | 9.228 | 9.5395 | 9.8509 | 10.1623 | 10.4737 | 10.7851 | 11.0966 | 11.408 | 11.7194 | 12.0308 | 12.3423 | 12.6537 | 12.9651 | 13.2766 | 13.588 | 13.8994 | 14.2108 | 14.5222 | 14.8337 | 15.1451 | 15.4565 | 15.768 | 16.0794 | 16.3625 | 16.6457 | 16.9289 | 17.212 | 17.4952 | 17.7783 | 18.0615 | 18.3446 | 18.6278 | 18.911 | 19.1941 | 19.4773 | 19.7604 | 20.0436 | 20.3268 | 20.6099 | 20.8931 | 21.1762 | 21.4594 | 21.7425 | 22.0257 | 22.3089 | 22.592 | 22.8752 | 23.1583 | 23.4415 | 23.7247 | 24.0078 | 24.291 | 24.5741 | 24.8008 | 25.0274 | 25.254 | 25.4806 | 25.7072 | 25.9339 | 26.1605 | 26.3871 | 26.6137 | 26.8404 | 27.067 | 27.2936 | 27.5203 | 27.7469 | 27.9735 | 28.2001 | 28.4267 | 28.6534 | 28.88 | 29.1066 | 29.3332 | 29.5599 | 29.7865 | 30.0131 | 30.2398 | 30.4664 | 30.693 | 30.9196 | 31.1463 | 31.3729 | 31.5412 | 31.7094 | 31.8777 | 32.046 | 32.2143 | 32.3826 | 32.5509 | 32.7191 | 32.8874 | 33.0557 | 33.224 | 33.3923 | 33.5606 | 33.7288 | 33.8971 | 34.0654 | 34.2337 | 34.402 | 34.5703 | 34.7385 | 34.9068 | 35.0751 | 35.2434 | 35.4117 | 35.58 | 35.7482 | 35.9165 | 36.0848 | 36.2531 | 36.4214
9.1 | 0 | 0.437 | 0.874 | 1.311 | 1.748 | 2.185 | 2.622 | 3.059 | 3.496 | 3.933 | 4.37 | 4.3958 | 4.4215 | 4.4473 | 4.473 | 4.4988 | 4.4688 | 4.4389 | 4.4089 | 4.379 | 4.349 | 4.339 | 4.329 | 4.319 | 4.309 | 4.299 | 4.289 | 4.279 | 4.269 | 4.259 | 4.249 | 4.3313 | 4.4135 | 4.4958 | 4.5781 | 4.6603 | 4.7426 | 4.8249 | 4.9071 | 4.9894 | 5.0717 | 5.1539 | 5.2362 | 5.3185 | 5.4007 | 5.483 | 5.5712 | 5.6594 | 5.7476 | 5.8357 | 5.9239 | 6.0121 | 6.1003 | 6.1885 | 6.2767 | 6.3648 | 6.453 | 6.5412 | 6.6294 | 6.7176 | 6.8058 | 7.1201 | 7.4345 | 7.7488 | 8.0632 | 8.3775 | 8.6919 | 9.0062 | 9.3206 | 9.6349 | 9.9493 | 10.2636 | 10.5779 | 10.8923 | 11.2066 | 11.521 | 11.8354 | 12.1497 | 12.4641 | 12.7784 | 13.0928 | 13.4071 | 13.7215 | 14.0358 | 14.3501 | 14.6645 | 14.9788 | 15.2932 | 15.6075 | 15.9219 | 16.2362 | 16.5221 | 16.8079 | 17.0937 | 17.3795 | 17.6653 | 17.9511 | 18.237 | 18.5228 | 18.8086 | 19.0944 | 19.3802 | 19.666 | 19.9519 | 20.2377 | 20.5235 | 20.8093 | 21.0951 | 21.3809 | 21.6668 | 21.9526 | 22.2384 | 22.5242 | 22.81 | 23.0958 | 23.3817 | 23.6675 | 23.9533 | 24.2391 | 24.5249 | 24.8108 | 25.0395 | 25.2683 | 25.497 | 25.7258 | 25.9545 | 26.1833 | 26.412 | 26.6408 | 26.8695 | 27.0983 | 27.327 | 27.5558 | 27.7845 | 28.0133 | 28.242 | 28.4708 | 28.6995 | 28.9283 | 29.157 | 29.3858 | 29.6145 | 29.8433 | 30.072 | 30.3008 | 30.5295 | 30.7583 | 30.987 | 31.2158 | 31.4445 | 31.6733 | 31.8432 | 32.0131 | 32.183 | 32.3529 | 32.5228 | 32.6927 | 32.8626 | 33.0325 | 33.2024 | 33.3723 | 33.5422 | 33.7121 | 33.882 | 34.0519 | 34.2218 | 34.3917 | 34.5616 | 34.7315 | 34.9014 | 35.0713 | 35.2412 | 35.4111 | 35.581 | 35.7509 | 35.9208 | 36.0907 | 36.2606 | 36.4305 | 36.6004 | 36.7702
9.15 | 0 | 0.441 | 0.882 | 1.323 | 1.764 | 2.205 | 2.646 | 3.087 | 3.528 | 3.969 | 4.41 | 4.4369 | 4.4638 | 4.4906 | 4.5175 | 4.5444 | 4.5142 | 4.484 | 4.4539 | 4.4237 | 4.3935 | 4.3835 | 4.3735 | 4.3635 | 4.3535 | 4.3435 | 4.3335 | 4.3235 | 4.3135 | 4.3035 | 4.2935 | 4.3766 | 4.4596 | 4.5427 | 4.6258 | 4.7088 | 4.7919 | 4.875 | 4.958 | 5.0411 | 5.1242 | 5.2072 | 5.2903 | 5.3734 | 5.4564 | 5.5395 | 5.6285 | 5.7176 | 5.8066 | 5.8956 | 5.9846 | 6.0737 | 6.1627 | 6.2517 | 6.3407 | 6.4298 | 6.5188 | 6.6078 | 6.6968 | 6.7859 | 6.8749 | 7.1922 | 7.5094 | 7.8267 | 8.144 | 8.4613 | 8.7785 | 9.0958 | 9.4131 | 9.7304 | 10.0476 | 10.3649 | 10.6822 | 10.9994 | 11.3167 | 11.634 | 11.9513 | 12.2685 | 12.5858 | 12.9031 | 13.2204 | 13.5376 | 13.8549 | 14.1722 | 14.4895 | 14.8067 | 15.124 | 15.4413 | 15.7586 | 16.0758 | 16.3931 | 16.6816 | 16.9701 | 17.2585 | 17.547 | 17.8355 | 18.124 | 18.4124 | 18.7009 | 18.9894 | 19.2779 | 19.5663 | 19.8548 | 20.1433 | 20.4318 | 20.7203 | 21.0087 | 21.2972 | 21.5857 | 21.8742 | 22.1626 | 22.4511 | 22.7396 | 23.0281 | 23.3165 | 23.605 | 23.8935 | 24.182 | 24.4704 | 24.7589 | 25.0474 | 25.2782 | 25.5091 | 25.74 | 25.9709 | 26.2018 | 26.4326 | 26.6635 | 26.8944 | 27.1253 | 27.3561 | 27.587 | 27.8179 | 28.0487 | 28.2796 | 28.5105 | 28.7414 | 28.9723 | 29.2031 | 29.434 | 29.6649 | 29.8958 | 30.1266 | 30.3575 | 30.5884 | 30.8193 | 31.0501 | 31.281 | 31.5119 | 31.7428 | 31.9736 | 32.1451 | 32.3167 | 32.4882 | 32.6597 | 32.8312 | 33.0027 | 33.1742 | 33.3458 | 33.5173 | 33.6888 | 33.8603 | 34.0318 | 34.2033 | 34.3749 | 34.5464 | 34.7179 | 34.8894 | 35.0609 | 35.2324 | 35.404 | 35.5755 | 35.747 | 35.9185 | 36.09 | 36.2615 | 36.4331 | 36.6046 | 36.7761 | 36.9476 | 37.1191
9.2 | 0 | 0.445 | 0.89 | 1.335 | 1.78 | 2.225 | 2.67 | 3.115 | 3.56 | 4.005 | 4.45 | 4.478 | 4.506 | 4.534 | 4.562 | 4.59 | 4.5596 | 4.5292 | 4.4988 | 4.4684 | 4.438 | 4.428 | 4.418 | 4.408 | 4.398 | 4.388 | 4.378 | 4.368 | 4.358 | 4.348 | 4.338 | 4.4219 | 4.5057 | 4.5896 | 4.6735 | 4.7573 | 4.8412 | 4.9251 | 5.0089 | 5.0928 | 5.1767 | 5.2605 | 5.3444 | 5.4283 | 5.5121 | 5.596 | 5.6859 | 5.7757 | 5.8656 | 5.9555 | 6.0453 | 6.1352 | 6.2251 | 6.3149 | 6.4048 | 6.4947 | 6.5845 | 6.6744 | 6.7643 | 6.8541 | 6.944 | 7.2642 | 7.5844 | 7.9046 | 8.2248 | 8.545 | 8.8652 | 9.1854 | 9.5056 | 9.8258 | 10.146 | 10.4662 | 10.7864 | 11.1066 | 11.4268 | 11.747 | 12.0672 | 12.3874 | 12.7076 | 13.0278 | 13.348 | 13.6682 | 13.9884 | 14.3086 | 14.6288 | 14.949 | 15.2692 | 15.5894 | 15.9096 | 16.2298 | 16.55 | 16.8411 | 17.1323 | 17.4234 | 17.7145 | 18.0057 | 18.2968 | 18.5879 | 18.8791 | 19.1702 | 19.4613 | 19.7525 | 20.0436 | 20.3347 | 20.6259 | 20.917 | 21.2081 | 21.4993 | 21.7904 | 22.0815 | 22.3727 | 22.6638 | 22.9549 | 23.2461 | 23.5372 | 23.8283 | 24.1195 | 24.4106 | 24.7017 | 24.9929 | 25.284 | 25.517 | 25.75 | 25.983 | 26.216 | 26.449 | 26.682 | 26.915 | 27.148 | 27.381 | 27.614 | 27.847 | 28.08 | 28.313 | 28.546 | 28.779 | 29.012 | 29.245 | 29.478 | 29.711 | 29.944 | 30.177 | 30.41 | 30.643 | 30.876 | 31.109 | 31.342 | 31.575 | 31.808 | 32.041 | 32.274 | 32.4471 | 32.6203 | 32.7934 | 32.9665 | 33.1397 | 33.3128 | 33.4859 | 33.6591 | 33.8322 | 34.0053 | 34.1785 | 34.3516 | 34.5247 | 34.6979 | 34.871 | 35.0441 | 35.2173 | 35.3904 | 35.5635 | 35.7367 | 35.9098 | 36.0829 | 36.2561 | 36.4292 | 36.6023 | 36.7755 | 36.9486 | 37.1217 | 37.2949 | 37.468
9.25 | 0 | 0.449 | 0.898 | 1.347 | 1.796 | 2.245 | 2.694 | 3.143 | 3.592 | 4.041 | 4.49 | 4.5191 | 4.5483 | 4.5774 | 4.6065 | 4.6356 | 4.605 | 4.5744 | 4.5438 | 4.5131 | 4.4825 | 4.4725 | 4.4625 | 4.4525 | 4.4425 | 4.4325 | 4.4225 | 4.4125 | 4.4025 | 4.3925 | 4.3825 | 4.4672 | 4.5518 | 4.6365 | 4.7212 | 4.8058 | 4.8905 | 4.9752 | 5.0598 | 5.1445 | 5.2292 | 5.3138 | 5.3985 | 5.4832 | 5.5678 | 5.6525 | 5.7432 | 5.8339 | 5.9246 | 6.0153 | 6.106 | 6.1968 | 6.2875 | 6.3782 | 6.4689 | 6.5596 | 6.6503 | 6.741 | 6.8317 | 6.9224 | 7.0131 | 7.3363 | 7.6594 | 7.9825 | 8.3056 | 8.6288 | 8.9519 | 9.275 | 9.5981 | 9.9213 | 10.2444 | 10.5675 | 10.8906 | 11.2137 | 11.5369 | 11.86 | 12.1831 | 12.5062 | 12.8294 | 13.1525 | 13.4756 | 13.7988 | 14.1219 | 14.445 | 14.7681 | 15.0913 | 15.4144 | 15.7375 | 16.0606 | 16.3837 | 16.7069 | 17.0007 | 17.2945 | 17.5882 | 17.882 | 18.1758 | 18.4696 | 18.7634 | 19.0572 | 19.351 | 19.6448 | 19.9386 | 20.2324 | 20.5262 | 20.82 | 21.1137 | 21.4075 | 21.7013 | 21.9951 | 22.2889 | 22.5827 | 22.8765 | 23.1703 | 23.4641 | 23.7579 | 24.0517 | 24.3455 | 24.6393 | 24.933 | 25.2268 | 25.5206 | 25.7557 | 25.9909 | 26.226 | 26.4611 | 26.6963 | 26.9314 | 27.1665 | 27.4016 | 27.6368 | 27.8719 | 28.107 | 28.3421 | 28.5773 | 28.8124 | 29.0475 | 29.2826 | 29.5178 | 29.7529 | 29.988 | 30.2231 | 30.4583 | 30.6934 | 30.9285 | 31.1636 | 31.3988 | 31.6339 | 31.869 | 32.1041 | 32.3393 | 32.5744 | 32.7491 | 32.9239 | 33.0986 | 33.2734 | 33.4481 | 33.6229 | 33.7976 | 33.9724 | 34.1471 | 34.3219 | 34.4966 | 34.6714 | 34.8461 | 35.0209 | 35.1956 | 35.3704 | 35.5451 | 35.7199 | 35.8946 | 36.0694 | 36.2441 | 36.4189 | 36.5936 | 36.7684 | 36.9431 | 37.1179 | 37.2926 | 37.4674 | 37.6421 | 37.8169
9.3 | 0 | 0.453 | 0.906 | 1.359 | 1.812 | 2.265 | 2.718 | 3.171 | 3.624 | 4.077 | 4.53 | 4.5603 | 4.5905 | 4.6208 | 4.651 | 4.6813 | 4.6504 | 4.6196 | 4.5887 | 4.5579 | 4.527 | 4.517 | 4.507 | 4.497 | 4.487 | 4.477 | 4.467 | 4.457 | 4.447 | 4.437 | 4.427 | 4.5125 | 4.5979 | 4.6834 | 4.7689 | 4.8543 | 4.9398 | 5.0253 | 5.1107 | 5.1962 | 5.2817 | 5.3671 | 5.4526 | 5.5381 | 5.6235 | 5.709 | 5.8006 | 5.8921 | 5.9837 | 6.0752 | 6.1668 | 6.2583 | 6.3499 | 6.4414 | 6.533 | 6.6245 | 6.7161 | 6.8076 | 6.8992 | 6.9907 | 7.0823 | 7.4083 | 7.7344 | 8.0604 | 8.3865 | 8.7125 | 9.0386 | 9.3646 | 9.6907 | 10.0167 | 10.3428 | 10.6688 | 10.9948 | 11.3209 | 11.647 | 11.973 | 12.299 | 12.6251 | 12.9512 | 13.2772 | 13.6032 | 13.9293 | 14.2553 | 14.5814 | 14.9075 | 15.2335 | 15.5595 | 15.8856 | 16.2116 | 16.5377 | 16.8637 | 17.1602 | 17.4566 | 17.7531 | 18.0495 | 18.346 | 18.6425 | 18.9389 | 19.2354 | 19.5318 | 19.8283 | 20.1247 | 20.4212 | 20.7176 | 21.0141 | 21.3105 | 21.607 | 21.9034 | 22.1999 | 22.4963 | 22.7928 | 23.0892 | 23.3856 | 23.6821 | 23.9785 | 24.275 | 24.5714 | 24.8679 | 25.1643 | 25.4608 | 25.7572 | 25.9945 | 26.2318 | 26.469 | 26.7063 | 26.9435 | 27.1808 | 27.418 | 27.6553 | 27.8925 | 28.1298 | 28.367 | 28.6043 | 28.8415 | 29.0788 | 29.316 | 29.5533 | 29.7905 | 30.0278 | 30.265 | 30.5023 | 30.7395 | 30.9768 | 31.214 | 31.4513 | 31.6885 | 31.9258 | 32.163 | 32.4003 | 32.6375 | 32.8748 | 33.0511 | 33.2275 | 33.4039 | 33.5802 | 33.7566 | 33.933 | 34.1093 | 34.2857 | 34.4621 | 34.6384 | 34.8148 | 34.9912 | 35.1675 | 35.3439 | 35.5203 | 35.6966 | 35.873 | 36.0494 | 36.2257 | 36.4021 | 36.5785 | 36.7548 | 36.9312 | 37.1076 | 37.2839 | 37.4603 | 37.6367 | 37.813 | 37.9894 | 38.1657
9.35 | 0 | 0.457 | 0.914 | 1.371 | 1.828 | 2.285 | 2.742 | 3.199 | 3.656 | 4.113 | 4.57 | 4.6014 | 4.6328 | 4.6641 | 4.6955 | 4.7269 | 4.6958 | 4.6647 | 4.6337 | 4.6026 | 4.5715 | 4.5615 | 4.5515 | 4.5415 | 4.5315 | 4.5215 | 4.5115 | 4.5015 | 4.4915 | 4.4815 | 4.4715 | 4.5578 | 4.644 | 4.7303 | 4.8166 | 4.9028 | 4.9891 | 5.0754 | 5.1616 | 5.2479 | 5.3342 | 5.4204 | 5.5067 | 5.593 | 5.6792 | 5.7655 | 5.8579 | 5.9503 | 6.0427 | 6.1351 | 6.2275 | 6.3199 | 6.4122 | 6.5046 | 6.597 | 6.6894 | 6.7818 | 6.8742 | 6.9666 | 7.059 | 7.1514 | 7.4804 | 7.8093 | 8.1383 | 8.4673 | 8.7963 | 9.1252 | 9.4542 | 9.7832 | 10.1121 | 10.4411 | 10.7701 | 11.0991 | 11.4281 | 11.757 | 12.086 | 12.415 | 12.7439 | 13.0729 | 13.4019 | 13.7309 | 14.0599 | 14.3888 | 14.7178 | 15.0468 | 15.3758 | 15.7047 | 16.0337 | 16.3627 | 16.6916 | 17.0206 | 17.3197 | 17.6188 | 17.918 | 18.2171 | 18.5162 | 18.8153 | 19.1144 | 19.4135 | 19.7126 | 20.0117 | 20.3108 | 20.6099 | 20.909 | 21.2081 | 21.5072 | 21.8064 | 22.1055 | 22.4046 | 22.7037 | 23.0028 | 23.3019 | 23.601 | 23.9001 | 24.1992 | 24.4983 | 24.7974 | 25.0966 | 25.3957 | 25.6948 | 25.9939 | 26.2333 | 26.4726 | 26.712 | 26.9514 | 27.1908 | 27.4301 | 27.6695 | 27.9089 | 28.1483 | 28.3876 | 28.627 | 28.8664 | 29.1058 | 29.3451 | 29.5845 | 29.8239 | 30.0633 | 30.3026 | 30.542 | 30.7814 | 31.0208 | 31.2601 | 31.4995 | 31.7389 | 31.9783 | 32.2176 | 32.457 | 32.6964 | 32.9358 | 33.1751 | 33.3531 | 33.5311 | 33.7091 | 33.8871 | 34.065 | 34.243 | 34.421 | 34.599 | 34.777 | 34.955 | 35.1329 | 35.3109 | 35.4889 | 35.6669 | 35.8449 | 36.0229 | 36.2008 | 36.3788 | 36.5568 | 36.7348 | 36.9128 | 37.0908 | 37.2687 | 37.4467 | 37.6247 | 37.8027 | 37.9807 | 38.1587 | 38.3366 | 38.5146
9.4 | 0 | 0.461 | 0.922 | 1.383 | 1.844 | 2.305 | 2.766 | 3.227 | 3.688 | 4.149 | 4.61 | 4.6425 | 4.675 | 4.7075 | 4.74 | 4.7725 | 4.7412 | 4.7099 | 4.6786 | 4.6473 | 4.616 | 4.606 | 4.596 | 4.586 | 4.576 | 4.566 | 4.556 | 4.546 | 4.536 | 4.526 | 4.516 | 4.6031 | 4.6901 | 4.7772 | 4.8643 | 4.9513 | 5.0384 | 5.1255 | 5.2125 | 5.2996 | 5.3867 | 5.4737 | 5.5608 | 5.6479 | 5.7349 | 5.822 | 5.9152 | 6.0085 | 6.1017 | 6.1949 | 6.2882 | 6.3814 | 6.4746 | 6.5679 | 6.6611 | 6.7543 | 6.8476 | 6.9408 | 7.034 | 7.1273 | 7.2205 | 7.5524 | 7.8843 | 8.2162 | 8.5481 | 8.88 | 9.2119 | 9.5438 | 9.8757 | 10.2076 | 10.5395 | 10.8714 | 11.2033 | 11.5352 | 11.8671 | 12.199 | 12.5309 | 12.8628 | 13.1947 | 13.5266 | 13.8585 | 14.1904 | 14.5223 | 14.8542 | 15.1861 | 15.518 | 15.8499 | 16.1818 | 16.5137 | 16.8456 | 17.1775 | 17.4793 | 17.781 | 18.0828 | 18.3846 | 18.6863 | 18.9881 | 19.2899 | 19.5916 | 19.8934 | 20.1952 | 20.4969 | 20.7987 | 21.1005 | 21.4022 | 21.704 | 22.0058 | 22.3075 | 22.6093 | 22.9111 | 23.2128 | 23.5146 | 23.8164 | 24.1181 | 24.4199 | 24.7217 | 25.0234 | 25.3252 | 25.627 | 25.9287 | 26.2305 | 26.472 | 26.7135 | 26.955 | 27.1965 | 27.438 | 27.6795 | 27.921 | 28.1625 | 28.404 | 28.6455 | 28.887 | 29.1285 | 29.37 | 29.6115 | 29.853 | 30.0945 | 30.336 | 30.5775 | 30.819 | 31.0605 | 31.302 | 31.5435 | 31.785 | 32.0265 | 32.268 | 32.5095 | 32.751 | 32.9925 | 33.234 | 33.4755 | 33.6551 | 33.8347 | 34.0143 | 34.1939 | 34.3735 | 34.5531 | 34.7327 | 34.9123 | 35.0919 | 35.2715 | 35.4511 | 35.6307 | 35.8103 | 35.9899 | 36.1695 | 36.3491 | 36.5287 | 36.7083 | 36.8879 | 37.0675 | 37.2471 | 37.4267 | 37.6063 | 37.7859 | 37.9655 | 38.1451 | 38.3247 | 38.5043 | 38.6839 | 38.8635
9.45 | 0 | 0.465 | 0.93 | 1.395 | 1.86 | 2.325 | 2.79 | 3.255 | 3.72 | 4.185 | 4.65 | 4.6836 | 4.7173 | 4.7509 | 4.7845 | 4.8181 | 4.7866 | 4.7551 | 4.7236 | 4.692 | 4.6605 | 4.6505 | 4.6405 | 4.6305 | 4.6205 | 4.6105 | 4.6005 | 4.5905 | 4.5805 | 4.5705 | 4.5605 | 4.6484 | 4.7362 | 4.8241 | 4.912 | 4.9998 | 5.0877 | 5.1756 | 5.2634 | 5.3513 | 5.4392 | 5.527 | 5.6149 | 5.7028 | 5.7906 | 5.8785 | 5.9726 | 6.0667 | 6.1607 | 6.2548 | 6.3489 | 6.443 | 6.537 | 6.6311 | 6.7252 | 6.8193 | 6.9133 | 7.0074 | 7.1015 | 7.1956 | 7.2896 | 7.6245 | 7.9593 | 8.2941 | 8.6289 | 8.9638 | 9.2986 | 9.6334 | 9.9682 | 10.3031 | 10.6379 | 10.9727 | 11.3075 | 11.6424 | 11.9772 | 12.312 | 12.6468 | 12.9817 | 13.3165 | 13.6513 | 13.9861 | 14.3209 | 14.6558 | 14.9906 | 15.3254 | 15.6602 | 15.9951 | 16.3299 | 16.6647 | 16.9995 | 17.3344 | 17.6388 | 17.9432 | 18.2477 | 18.5521 | 18.8565 | 19.1609 | 19.4654 | 19.7698 | 20.0742 | 20.3786 | 20.6831 | 20.9875 | 21.2919 | 21.5963 | 21.9007 | 22.2052 | 22.5096 | 22.814 | 23.1184 | 23.4229 | 23.7273 | 24.0317 | 24.3361 | 24.6406 | 24.945 | 25.2494 | 25.5539 | 25.8583 | 26.1627 | 26.4671 | 26.7108 | 26.9544 | 27.198 | 27.4416 | 27.6853 | 27.9289 | 28.1725 | 28.4161 | 28.6598 | 28.9034 | 29.147 | 29.3906 | 29.6343 | 29.8779 | 30.1215 | 30.3651 | 30.6088 | 30.8524 | 31.096 | 31.3396 | 31.5833 | 31.8269 | 32.0705 | 32.3141 | 32.5578 | 32.8014 | 33.045 | 33.2886 | 33.5323 | 33.7759 | 33.9571 | 34.1383 | 34.3195 | 34.5007 | 34.682 | 34.8632 | 35.0444 | 35.2256 | 35.4068 | 35.588 | 35.7693 | 35.9505 | 36.1317 | 36.3129 | 36.4941 | 36.6753 | 36.8566 | 37.0378 | 37.219 | 37.4002 | 37.5814 | 37.7626 | 37.9439 | 38.1251 | 38.3063 | 38.4875 | 38.6687 | 38.8499 | 39.0312 | 39.2124
9.5 | 0 | 0.469 | 0.938 | 1.407 | 1.876 | 2.345 | 2.814 | 3.283 | 3.752 | 4.221 | 4.69 | 4.7248 | 4.7595 | 4.7943 | 4.829 | 4.8638 | 4.832 | 4.8003 | 4.7685 | 4.7368 | 4.705 | 4.695 | 4.685 | 4.675 | 4.665 | 4.655 | 4.645 | 4.635 | 4.625 | 4.615 | 4.605 | 4.6937 | 4.7823 | 4.871 | 4.9597 | 5.0483 | 5.137 | 5.2257 | 5.3143 | 5.403 | 5.4917 | 5.5803 | 5.669 | 5.7577 | 5.8463 | 5.935 | 6.0299 | 6.1248 | 6.2198 | 6.3147 | 6.4096 | 6.5045 | 6.5994 | 6.6943 | 6.7893 | 6.8842 | 6.9791 | 7.074 | 7.1689 | 7.2638 | 7.3588 | 7.6965 | 8.0343 | 8.372 | 8.7098 | 9.0475 | 9.3853 | 9.723 | 10.0608 | 10.3985 | 10.7363 | 11.074 | 11.4117 | 11.7495 | 12.0872 | 12.425 | 12.7628 | 13.1005 | 13.4383 | 13.776 | 14.1137 | 14.4515 | 14.7892 | 15.127 | 15.4648 | 15.8025 | 16.1403 | 16.478 | 16.8158 | 17.1535 | 17.4913 | 17.7983 | 18.1054 | 18.4125 | 18.7196 | 19.0267 | 19.3337 | 19.6408 | 19.9479 | 20.255 | 20.5621 | 20.8692 | 21.1762 | 21.4833 | 21.7904 | 22.0975 | 22.4046 | 22.7117 | 23.0188 | 23.3258 | 23.6329 | 23.94 | 24.2471 | 24.5542 | 24.8612 | 25.1683 | 25.4754 | 25.7825 | 26.0896 | 26.3967 | 26.7038 | 26.9495 | 27.1953 | 27.441 | 27.6868 | 27.9325 | 28.1783 | 28.424 | 28.6698 | 28.9155 | 29.1613 | 29.407 | 29.6528 | 29.8985 | 30.1443 | 30.39 | 30.6358 | 30.8815 | 31.1273 | 31.373 | 31.6188 | 31.8645 | 32.1103 | 32.356 | 32.6018 | 32.8475 | 33.0933 | 33.339 | 33.5848 | 33.8305 | 34.0763 | 34.2591 | 34.4419 | 34.6248 | 34.8076 | 34.9904 | 35.1733 | 35.3561 | 35.5389 | 35.7218 | 35.9046 | 36.0874 | 36.2703 | 36.4531 | 36.6359 | 36.8188 | 37.0016 | 37.1844 | 37.3673 | 37.5501 | 37.7329 | 37.9158 | 38.0986 | 38.2814 | 38.4643 | 38.6471 | 38.8299 | 39.0128 | 39.1956 | 39.3784 | 39.5612
9.55 | 0 | 0.473 | 0.946 | 1.419 | 1.892 | 2.365 | 2.838 | 3.311 | 3.784 | 4.257 | 4.73 | 4.7659 | 4.8018 | 4.8376 | 4.8735 | 4.9094 | 4.8774 | 4.8454 | 4.8135 | 4.7815 | 4.7495 | 4.7395 | 4.7295 | 4.7195 | 4.7095 | 4.6995 | 4.6895 | 4.6795 | 4.6695 | 4.6595 | 4.6495 | 4.739 | 4.8284 | 4.9179 | 5.0074 | 5.0968 | 5.1863 | 5.2758 | 5.3652 | 5.4547 | 5.5442 | 5.6336 | 5.7231 | 5.8126 | 5.902 | 5.9915 | 6.0873 | 6.183 | 6.2788 | 6.3745 | 6.4703 | 6.5661 | 6.6618 | 6.7576 | 6.8533 | 6.9491 | 7.0448 | 7.1406 | 7.2364 | 7.3321 | 7.4279 | 7.7686 | 8.1092 | 8.4499 | 8.7906 | 9.1313 | 9.4719 | 9.8126 | 10.1533 | 10.4939 | 10.8346 | 11.1753 | 11.516 | 11.8567 | 12.1973 | 12.538 | 12.8787 | 13.2194 | 13.56 | 13.9007 | 14.2414 | 14.5821 | 14.9227 | 15.2634 | 15.6041 | 15.9448 | 16.2854 | 16.6261 | 16.9668 | 17.3074 | 17.6481 | 17.9579 | 18.2676 | 18.5773 | 18.8871 | 19.1968 | 19.5066 | 19.8163 | 20.1261 | 20.4358 | 20.7455 | 21.0553 | 21.365 | 21.6748 | 21.9845 | 22.2943 | 22.604 | 22.9137 | 23.2235 | 23.5332 | 23.843 | 24.1527 | 24.4624 | 24.7722 | 25.0819 | 25.3917 | 25.7014 | 26.0112 | 26.3209 | 26.6306 | 26.9404 | 27.1883 | 27.4361 | 27.684 | 27.9319 | 28.1798 | 28.4276 | 28.6755 | 28.9234 | 29.1713 | 29.4191 | 29.667 | 29.9149 | 30.1628 | 30.4106 | 30.6585 | 30.9064 | 31.1543 | 31.4021 | 31.65 | 31.8979 | 32.1458 | 32.3936 | 32.6415 | 32.8894 | 33.1373 | 33.3851 | 33.633 | 33.8809 | 34.1288 | 34.3766 | 34.5611 | 34.7455 | 34.93 | 35.1144 | 35.2989 | 35.4833 | 35.6678 | 35.8522 | 36.0367 | 36.2211 | 36.4056 | 36.59 | 36.7745 | 36.9589 | 37.1434 | 37.3278 | 37.5123 | 37.6967 | 37.8812 | 38.0656 | 38.2501 | 38.4345 | 38.619 | 38.8034 | 38.9879 | 39.1723 | 39.3568 | 39.5412 | 39.7257 | 39.9101
9.6 | 0 | 0.477 | 0.954 | 1.431 | 1.908 | 2.385 | 2.862 | 3.339 | 3.816 | 4.293 | 4.77 | 4.807 | 4.844 | 4.881 | 4.918 | 4.955 | 4.9228 | 4.8906 | 4.8584 | 4.8262 | 4.794 | 4.784 | 4.774 | 4.764 | 4.754 | 4.744 | 4.734 | 4.724 | 4.714 | 4.704 | 4.694 | 4.7843 | 4.8745 | 4.9648 | 5.0551 | 5.1453 | 5.2356 | 5.3259 | 5.4161 | 5.5064 | 5.5967 | 5.6869 | 5.7772 | 5.8675 | 5.9577 | 6.048 | 6.1446 | 6.2412 | 6.3378 | 6.4344 | 6.531 | 6.6276 | 6.7242 | 6.8208 | 6.9174 | 7.014 | 7.1106 | 7.2072 | 7.3038 | 7.4004 | 7.497 | 7.8406 | 8.1842 | 8.5278 | 8.8714 | 9.215 | 9.5586 | 9.9022 | 10.2458 | 10.5894 | 10.933 | 11.2766 | 11.6202 | 11.9638 | 12.3074 | 12.651 | 12.9946 | 13.3382 | 13.6818 | 14.0254 | 14.369 | 14.7126 | 15.0562 | 15.3998 | 15.7434 | 16.087 | 16.4306 | 16.7742 | 17.1178 | 17.4614 | 17.805 | 18.1174 | 18.4298 | 18.7422 | 19.0546 | 19.367 | 19.6794 | 19.9918 | 20.3042 | 20.6166 | 20.929 | 21.2414 | 21.5538 | 21.8662 | 22.1786 | 22.491 | 22.8034 | 23.1158 | 23.4282 | 23.7406 | 24.053 | 24.3654 | 24.6778 | 24.9902 | 25.3026 | 25.615 | 25.9274 | 26.2398 | 26.5522 | 26.8646 | 27.177 | 27.427 | 27.677 | 27.927 | 28.177 | 28.427 | 28.677 | 28.927 | 29.177 | 29.427 | 29.677 | 29.927 | 30.177 | 30.427 | 30.677 | 30.927 | 31.177 | 31.427 | 31.677 | 31.927 | 32.177 | 32.427 | 32.677 | 32.927 | 33.177 | 33.427 | 33.677 | 33.927 | 34.177 | 34.427 | 34.677 | 34.8631 | 35.0491 | 35.2352 | 35.4213 | 35.6073 | 35.7934 | 35.9795 | 36.1655 | 36.3516 | 36.5377 | 36.7237 | 36.9098 | 37.0959 | 37.2819 | 37.468 | 37.6541 | 37.8401 | 38.0262 | 38.2123 | 38.3983 | 38.5844 | 38.7705 | 38.9565 | 39.1426 | 39.3287 | 39.5147 | 39.7008 | 39.8869 | 40.0729 | 40.259
9.65 | 0 | 0.481 | 0.962 | 1.443 | 1.924 | 2.405 | 2.886 | 3.367 | 3.848 | 4.329 | 4.81 | 4.8481 | 4.8863 | 4.9244 | 4.9625 | 5.0006 | 4.9682 | 4.9358 | 4.9034 | 4.8709 | 4.8385 | 4.8285 | 4.8185 | 4.8085 | 4.7985 | 4.7885 | 4.7785 | 4.7685 | 4.7585 | 4.7485 | 4.7385 | 4.8296 | 4.9206 | 5.0117 | 5.1028 | 5.1938 | 5.2849 | 5.376 | 5.467 | 5.5581 | 5.6492 | 5.7402 | 5.8313 | 5.9224 | 6.0134 | 6.1045 | 6.2019 | 6.2994 | 6.3968 | 6.4943 | 6.5917 | 6.6892 | 6.7866 | 6.884 | 6.9815 | 7.0789 | 7.1764 | 7.2738 | 7.3712 | 7.4687 | 7.5661 | 7.9127 | 8.2592 | 8.6057 | 8.9522 | 9.2988 | 9.6453 | 9.9918 | 10.3383 | 10.6849 | 11.0314 | 11.3779 | 11.7244 | 12.0709 | 12.4175 | 12.764 | 13.1105 | 13.4571 | 13.8036 | 14.1501 | 14.4966 | 14.8431 | 15.1897 | 15.5362 | 15.8827 | 16.2293 | 16.5758 | 16.9223 | 17.2688 | 17.6153 | 17.9619 | 18.2769 | 18.592 | 18.9071 | 19.2221 | 19.5372 | 19.8522 | 20.1673 | 20.4823 | 20.7974 | 21.1125 | 21.4275 | 21.7426 | 22.0576 | 22.3727 | 22.6878 | 23.0028 | 23.3179 | 23.6329 | 23.948 | 24.263 | 24.5781 | 24.8932 | 25.2082 | 25.5233 | 25.8383 | 26.1534 | 26.4685 | 26.7835 | 27.0986 | 27.4136 | 27.6657 | 27.9179 | 28.17 | 28.4221 | 28.6743 | 28.9264 | 29.1785 | 29.4306 | 29.6827 | 29.9349 | 30.187 | 30.4391 | 30.6913 | 30.9434 | 31.1955 | 31.4476 | 31.6998 | 31.9519 | 32.204 | 32.4561 | 32.7082 | 32.9604 | 33.2125 | 33.4646 | 33.7167 | 33.9689 | 34.221 | 34.4731 | 34.7253 | 34.9774 | 35.1651 | 35.3527 | 35.5404 | 35.7281 | 35.9158 | 36.1035 | 36.2912 | 36.4788 | 36.6665 | 36.8542 | 37.0419 | 37.2296 | 37.4173 | 37.6049 | 37.7926 | 37.9803 | 38.168 | 38.3557 | 38.5434 | 38.731 | 38.9187 | 39.1064 | 39.2941 | 39.4818 | 39.6695 | 39.8571 | 40.0448 | 40.2325 | 40.4202 | 40.6079
9.7 | 0 | 0.485 | 0.97 | 1.455 | 1.94 | 2.425 | 2.91 | 3.395 | 3.88 | 4.365 | 4.85 | 4.8893 | 4.9285 | 4.9678 | 5.007 | 5.0463 | 5.0136 | 4.981 | 4.9483 | 4.9157 | 4.883 | 4.873 | 4.863 | 4.853 | 4.843 | 4.833 | 4.823 | 4.813 | 4.803 | 4.793 | 4.783 | 4.8749 | 4.9667 | 5.0586 | 5.1505 | 5.2423 | 5.3342 | 5.4261 | 5.5179 | 5.6098 | 5.7017 | 5.7935 | 5.8854 | 5.9773 | 6.0691 | 6.161 | 6.2593 | 6.3576 | 6.4559 | 6.5541 | 6.6524 | 6.7507 | 6.849 | 6.9473 | 7.0456 | 7.1438 | 7.2421 | 7.3404 | 7.4387 | 7.537 | 7.6353 | 7.9847 | 8.3342 | 8.6836 | 9.0331 | 9.3825 | 9.732 | 10.0814 | 10.4308 | 10.7803 | 11.1297 | 11.4792 | 11.8286 | 12.1781 | 12.5275 | 12.877 | 13.2264 | 13.5759 | 13.9254 | 14.2748 | 14.6243 | 14.9737 | 15.3232 | 15.6726 | 16.0221 | 16.3715 | 16.721 | 17.0704 | 17.4199 | 17.7693 | 18.1188 | 18.4365 | 18.7542 | 19.0719 | 19.3896 | 19.7073 | 20.0251 | 20.3428 | 20.6605 | 20.9782 | 21.2959 | 21.6136 | 21.9314 | 22.2491 | 22.5668 | 22.8845 | 23.2022 | 23.5199 | 23.8377 | 24.1554 | 24.4731 | 24.7908 | 25.1085 | 25.4262 | 25.744 | 26.0617 | 26.3794 | 26.6971 | 27.0148 | 27.3325 | 27.6503 | 27.9045 | 28.1588 | 28.413 | 28.6673 | 28.9215 | 29.1758 | 29.43 | 29.6843 | 29.9385 | 30.1928 | 30.447 | 30.7013 | 30.9555 | 31.2098 | 31.464 | 31.7183 | 31.9725 | 32.2268 | 32.481 | 32.7353 | 32.9895 | 33.2438 | 33.498 | 33.7523 | 34.0065 | 34.2608 | 34.515 | 34.7693 | 35.0235 | 35.2778 | 35.4671 | 35.6564 | 35.8457 | 36.035 | 36.2243 | 36.4136 | 36.6029 | 36.7922 | 36.9815 | 37.1708 | 37.3601 | 37.5494 | 37.7387 | 37.928 | 38.1173 | 38.3066 | 38.4959 | 38.6852 | 38.8745 | 39.0638 | 39.2531 | 39.4424 | 39.6317 | 39.821 | 40.0103 | 40.1996 | 40.3889 | 40.5782 | 40.7675 | 40.9567
9.75 | 0 | 0.489 | 0.978 | 1.467 | 1.956 | 2.445 | 2.934 | 3.423 | 3.912 | 4.401 | 4.89 | 4.9304 | 4.9708 | 5.0111 | 5.0515 | 5.0919 | 5.059 | 5.0261 | 4.9933 | 4.9604 | 4.9275 | 4.9175 | 4.9075 | 4.8975 | 4.8875 | 4.8775 | 4.8675 | 4.8575 | 4.8475 | 4.8375 | 4.8275 | 4.9202 | 5.0128 | 5.1055 | 5.1982 | 5.2908 | 5.3835 | 5.4762 | 5.5688 | 5.6615 | 5.7542 | 5.8468 | 5.9395 | 6.0322 | 6.1248 | 6.2175 | 6.3166 | 6.4158 | 6.5149 | 6.614 | 6.7131 | 6.8123 | 6.9114 | 7.0105 | 7.1096 | 7.2088 | 7.3079 | 7.407 | 7.5061 | 7.6053 | 7.7044 | 8.0568 | 8.4091 | 8.7615 | 9.1139 | 9.4663 | 9.8186 | 10.171 | 10.5234 | 10.8758 | 11.2281 | 11.5805 | 11.9329 | 12.2852 | 12.6376 | 12.99 | 13.3424 | 13.6948 | 14.0471 | 14.3995 | 14.7519 | 15.1043 | 15.4566 | 15.809 | 16.1614 | 16.5138 | 16.8661 | 17.2185 | 17.5709 | 17.9232 | 18.2756 | 18.596 | 18.9164 | 19.2368 | 19.5571 | 19.8775 | 20.1979 | 20.5182 | 20.8386 | 21.159 | 21.4794 | 21.7997 | 22.1201 | 22.4405 | 22.7609 | 23.0813 | 23.4016 | 23.722 | 24.0424 | 24.3627 | 24.6831 | 25.0035 | 25.3239 | 25.6442 | 25.9646 | 26.285 | 26.6054 | 26.9258 | 27.2461 | 27.5665 | 27.8869 | 28.1433 | 28.3996 | 28.656 | 28.9124 | 29.1688 | 29.4251 | 29.6815 | 29.9379 | 30.1943 | 30.4506 | 30.707 | 30.9634 | 31.2198 | 31.4761 | 31.7325 | 31.9889 | 32.2453 | 32.5016 | 32.758 | 33.0144 | 33.2708 | 33.5271 | 33.7835 | 34.0399 | 34.2963 | 34.5526 | 34.809 | 35.0654 | 35.3218 | 35.5781 | 35.769 | 35.96 | 36.1509 | 36.3418 | 36.5327 | 36.7236 | 36.9145 | 37.1055 | 37.2964 | 37.4873 | 37.6782 | 37.8691 | 38.06 | 38.251 | 38.4419 | 38.6328 | 38.8237 | 39.0146 | 39.2055 | 39.3965 | 39.5874 | 39.7783 | 39.9692 | 40.1601 | 40.351 | 40.542 | 40.7329 | 40.9238 | 41.1147 | 41.3056
9.8 | 0 | 0.493 | 0.986 | 1.479 | 1.972 | 2.465 | 2.958 | 3.451 | 3.944 | 4.437 | 4.93 | 4.9715 | 5.013 | 5.0545 | 5.096 | 5.1375 | 5.1044 | 5.0713 | 5.0382 | 5.0051 | 4.972 | 4.962 | 4.952 | 4.942 | 4.932 | 4.922 | 4.912 | 4.902 | 4.892 | 4.882 | 4.872 | 4.9655 | 5.0589 | 5.1524 | 5.2459 | 5.3393 | 5.4328 | 5.5263 | 5.6197 | 5.7132 | 5.8067 | 5.9001 | 5.9936 | 6.0871 | 6.1805 | 6.274 | 6.374 | 6.4739 | 6.5739 | 6.6739 | 6.7738 | 6.8738 | 6.9738 | 7.0737 | 7.1737 | 7.2737 | 7.3736 | 7.4736 | 7.5736 | 7.6735 | 7.7735 | 8.1288 | 8.4841 | 8.8394 | 9.1947 | 9.55 | 9.9053 | 10.2606 | 10.6159 | 10.9712 | 11.3265 | 11.6818 | 12.0371 | 12.3924 | 12.7477 | 13.103 | 13.4583 | 13.8136 | 14.1689 | 14.5242 | 14.8795 | 15.2348 | 15.5901 | 15.9454 | 16.3007 | 16.656 | 17.0113 | 17.3666 | 17.7219 | 18.0772 | 18.4325 | 18.7555 | 19.0786 | 19.4016 | 19.7246 | 20.0477 | 20.3707 | 20.6937 | 21.0168 | 21.3398 | 21.6628 | 21.9859 | 22.3089 | 22.6319 | 22.955 | 23.278 | 23.601 | 23.9241 | 24.2471 | 24.5701 | 24.8932 | 25.2162 | 25.5392 | 25.8623 | 26.1853 | 26.5083 | 26.8314 | 27.1544 | 27.4774 | 27.8005 | 28.1235 | 28.382 | 28.6405 | 28.899 | 29.1575 | 29.416 | 29.6745 | 29.933 | 30.1915 | 30.45 | 30.7085 | 30.967 | 31.2255 | 31.484 | 31.7425 | 32.001 | 32.2595 | 32.518 | 32.7765 | 33.035 | 33.2935 | 33.552 | 33.8105 | 34.069 | 34.3275 | 34.586 | 34.8445 | 35.103 | 35.3615 | 35.62 | 35.8785 | 36.071 | 36.2636 | 36.4561 | 36.6486 | 36.8412 | 37.0337 | 37.2262 | 37.4188 | 37.6113 | 37.8038 | 37.9964 | 38.1889 | 38.3814 | 38.574 | 38.7665 | 38.959 | 39.1516 | 39.3441 | 39.5366 | 39.7292 | 39.9217 | 40.1142 | 40.3068 | 40.4993 | 40.6918 | 40.8844 | 41.0769 | 41.2694 | 41.462 | 41.6545
9.85 | 0 | 0.497 | 0.994 | 1.491 | 1.988 | 2.485 | 2.982 | 3.479 | 3.976 | 4.473 | 4.97 | 5.0126 | 5.0553 | 5.0979 | 5.1405 | 5.1831 | 5.1498 | 5.1165 | 5.0832 | 5.0498 | 5.0165 | 5.0065 | 4.9965 | 4.9865 | 4.9765 | 4.9665 | 4.9565 | 4.9465 | 4.9365 | 4.9265 | 4.9165 | 5.0108 | 5.105 | 5.1993 | 5.2936 | 5.3878 | 5.4821 | 5.5764 | 5.6706 | 5.7649 | 5.8592 | 5.9534 | 6.0477 | 6.142 | 6.2362 | 6.3305 | 6.4313 | 6.5321 | 6.6329 | 6.7337 | 6.8345 | 6.9354 | 7.0362 | 7.137 | 7.2378 | 7.3386 | 7.4394 | 7.5402 | 7.641 | 7.7418 | 7.8426 | 8.2009 | 8.5591 | 8.9173 | 9.2755 | 9.6338 | 9.992 | 10.3502 | 10.7084 | 11.0666 | 11.4249 | 11.7831 | 12.1413 | 12.4995 | 12.8578 | 13.216 | 13.5742 | 13.9324 | 14.2907 | 14.6489 | 15.0071 | 15.3653 | 15.7236 | 16.0818 | 16.44 | 16.7983 | 17.1565 | 17.5147 | 17.8729 | 18.2312 | 18.5894 | 18.9151 | 19.2408 | 19.5665 | 19.8921 | 20.2178 | 20.5435 | 20.8692 | 21.1949 | 21.5206 | 21.8463 | 22.172 | 22.4977 | 22.8234 | 23.1491 | 23.4748 | 23.8004 | 24.1261 | 24.4518 | 24.7775 | 25.1032 | 25.4289 | 25.7546 | 26.0803 | 26.406 | 26.7317 | 27.0574 | 27.3831 | 27.7087 | 28.0344 | 28.3601 | 28.6208 | 28.8814 | 29.142 | 29.4026 | 29.6633 | 29.9239 | 30.1845 | 30.4451 | 30.7058 | 30.9664 | 31.227 | 31.4876 | 31.7483 | 32.0089 | 32.2695 | 32.5301 | 32.7908 | 33.0514 | 33.312 | 33.5726 | 33.8333 | 34.0939 | 34.3545 | 34.6151 | 34.8758 | 35.1364 | 35.397 | 35.6576 | 35.9183 | 36.1789 | 36.373 | 36.5672 | 36.7613 | 36.9555 | 37.1496 | 37.3438 | 37.5379 | 37.7321 | 37.9262 | 38.1204 | 38.3145 | 38.5087 | 38.7028 | 38.897 | 39.0911 | 39.2853 | 39.4794 | 39.6736 | 39.8677 | 40.0619 | 40.256 | 40.4502 | 40.6443 | 40.8385 | 41.0326 | 41.2268 | 41.4209 | 41.6151 | 41.8092 | 42.0034
9.9 | 0 | 0.501 | 1.002 | 1.503 | 2.004 | 2.505 | 3.006 | 3.507 | 4.008 | 4.509 | 5.01 | 5.0538 | 5.0975 | 5.1413 | 5.185 | 5.2288 | 5.1952 | 5.1617 | 5.1281 | 5.0946 | 5.061 | 5.051 | 5.041 | 5.031 | 5.021 | 5.011 | 5.001 | 4.991 | 4.981 | 4.971 | 4.961 | 5.0561 | 5.1511 | 5.2462 | 5.3413 | 5.4363 | 5.5314 | 5.6265 | 5.7215 | 5.8166 | 5.9117 | 6.0067 | 6.1018 | 6.1969 | 6.2919 | 6.387 | 6.4887 | 6.5903 | 6.692 | 6.7936 | 6.8953 | 6.9969 | 7.0986 | 7.2002 | 7.3019 | 7.4035 | 7.5052 | 7.6068 | 7.7085 | 7.8101 | 7.9118 | 8.2729 | 8.6341 | 8.9952 | 9.3564 | 9.7175 | 10.0786 | 10.4398 | 10.801 | 11.1621 | 11.5233 | 11.8844 | 12.2455 | 12.6067 | 12.9679 | 13.329 | 13.6901 | 14.0513 | 14.4124 | 14.7736 | 15.1348 | 15.4959 | 15.8571 | 16.2182 | 16.5794 | 16.9405 | 17.3017 | 17.6628 | 18.024 | 18.3851 | 18.7463 | 19.0746 | 19.403 | 19.7313 | 20.0597 | 20.388 | 20.7164 | 21.0447 | 21.3731 | 21.7014 | 22.0298 | 22.3581 | 22.6865 | 23.0148 | 23.3432 | 23.6715 | 23.9999 | 24.3282 | 24.6566 | 24.9849 | 25.3133 | 25.6416 | 25.97 | 26.2983 | 26.6267 | 26.955 | 27.2834 | 27.6117 | 27.9401 | 28.2684 | 28.5968 | 28.8595 | 29.1223 | 29.385 | 29.6478 | 29.9105 | 30.1733 | 30.436 | 30.6988 | 30.9615 | 31.2243 | 31.487 | 31.7498 | 32.0125 | 32.2753 | 32.538 | 32.8008 | 33.0635 | 33.3263 | 33.589 | 33.8518 | 34.1145 | 34.3773 | 34.64 | 34.9028 | 35.1655 | 35.4283 | 35.691 | 35.9538 | 36.2165 | 36.4793 | 36.675 | 36.8708 | 37.0666 | 37.2623 | 37.4581 | 37.6539 | 37.8496 | 38.0454 | 38.2412 | 38.4369 | 38.6327 | 38.8285 | 39.0242 | 39.22 | 39.4158 | 39.6115 | 39.8073 | 40.0031 | 40.1988 | 40.3946 | 40.5904 | 40.7861 | 40.9819 | 41.1777 | 41.3734 | 41.5692 | 41.765 | 41.9607 | 42.1565 | 42.3522
9.95 | 0 | 0.505 | 1.01 | 1.515 | 2.02 | 2.525 | 3.03 | 3.535 | 4.04 | 4.545 | 5.05 | 5.0949 | 5.1398 | 5.1846 | 5.2295 | 5.2744 | 5.2406 | 5.2068 | 5.1731 | 5.1393 | 5.1055 | 5.0955 | 5.0855 | 5.0755 | 5.0655 | 5.0555 | 5.0455 | 5.0355 | 5.0255 | 5.0155 | 5.0055 | 5.1014 | 5.1972 | 5.2931 | 5.389 | 5.4848 | 5.5807 | 5.6766 | 5.7724 | 5.8683 | 5.9642 | 6.06 | 6.1559 | 6.2518 | 6.3476 | 6.4435 | 6.546 | 6.6485 | 6.751 | 6.8535 | 6.956 | 7.0585 | 7.1609 | 7.2634 | 7.3659 | 7.4684 | 7.5709 | 7.6734 | 7.7759 | 7.8784 | 7.9809 | 8.345 | 8.709 | 9.0731 | 9.4372 | 9.8013 | 10.1653 | 10.5294 | 10.8935 | 11.2576 | 11.6216 | 11.9857 | 12.3498 | 12.7139 | 13.0779 | 13.442 | 13.8061 | 14.1701 | 14.5342 | 14.8983 | 15.2624 | 15.6265 | 15.9905 | 16.3546 | 16.7187 | 17.0828 | 17.4468 | 17.8109 | 18.175 | 18.5391 | 18.9031 | 19.2341 | 19.5651 | 19.8962 | 20.2272 | 20.5582 | 20.8892 | 21.2202 | 21.5512 | 21.8822 | 22.2132 | 22.5442 | 22.8752 | 23.2062 | 23.5372 | 23.8683 | 24.1993 | 24.5303 | 24.8613 | 25.1923 | 25.5233 | 25.8543 | 26.1853 | 26.5163 | 26.8473 | 27.1783 | 27.5093 | 27.8404 | 28.1714 | 28.5024 | 28.8334 | 29.0983 | 29.3631 | 29.628 | 29.8929 | 30.1578 | 30.4226 | 30.6875 | 30.9524 | 31.2173 | 31.4821 | 31.747 | 32.0119 | 32.2768 | 32.5416 | 32.8065 | 33.0714 | 33.3363 | 33.6011 | 33.866 | 34.1309 | 34.3958 | 34.6606 | 34.9255 | 35.1904 | 35.4553 | 35.7201 | 35.985 | 36.2499 | 36.5148 | 36.7796 | 36.977 | 37.1744 | 37.3718 | 37.5692 | 37.7665 | 37.9639 | 38.1613 | 38.3587 | 38.5561 | 38.7535 | 38.9508 | 39.1482 | 39.3456 | 39.543 | 39.7404 | 39.9378 | 40.1351 | 40.3325 | 40.5299 | 40.7273 | 40.9247 | 41.1221 | 41.3194 | 41.5168 | 41.7142 | 41.9116 | 42.109 | 42.3064 | 42.5037 | 42.7011
10 | 0 | 0.509 | 1.018 | 1.527 | 2.036 | 2.545 | 3.054 | 3.563 | 4.072 | 4.581 | 5.09 | 5.136 | 5.182 | 5.228 | 5.274 | 5.32 | 5.286 | 5.252 | 5.218 | 5.184 | 5.15 | 5.14 | 5.13 | 5.12 | 5.11 | 5.1 | 5.09 | 5.08 | 5.07 | 5.06 | 5.05 | 5.1467 | 5.2433 | 5.34 | 5.4367 | 5.5333 | 5.63 | 5.7267 | 5.8233 | 5.92 | 6.0167 | 6.1133 | 6.21 | 6.3067 | 6.4033 | 6.5 | 6.6033 | 6.7067 | 6.81 | 6.9133 | 7.0167 | 7.12 | 7.2233 | 7.3267 | 7.43 | 7.5333 | 7.6367 | 7.74 | 7.8433 | 7.9467 | 8.05 | 8.417 | 8.784 | 9.151 | 9.518 | 9.885 | 10.252 | 10.619 | 10.986 | 11.353 | 11.72 | 12.087 | 12.454 | 12.821 | 13.188 | 13.555 | 13.922 | 14.289 | 14.656 | 15.023 | 15.39 | 15.757 | 16.124 | 16.491 | 16.858 | 17.225 | 17.592 | 17.959 | 18.326 | 18.693 | 19.06 | 19.3937 | 19.7273 | 20.061 | 20.3947 | 20.7283 | 21.062 | 21.3957 | 21.7293 | 22.063 | 22.3967 | 22.7303 | 23.064 | 23.3977 | 23.7313 | 24.065 | 24.3987 | 24.7323 | 25.066 | 25.3997 | 25.7333 | 26.067 | 26.4007 | 26.7343 | 27.068 | 27.4017 | 27.7353 | 28.069 | 28.4027 | 28.7363 | 29.07 | 29.337 | 29.604 | 29.871 | 30.138 | 30.405 | 30.672 | 30.939 | 31.206 | 31.473 | 31.74 | 32.007 | 32.274 | 32.541 | 32.808 | 33.075 | 33.342 | 33.609 | 33.876 | 34.143 | 34.41 | 34.677 | 34.944 | 35.211 | 35.478 | 35.745 | 36.012 | 36.279 | 36.546 | 36.813 | 37.08 | 37.279 | 37.478 | 37.677 | 37.876 | 38.075 | 38.274 | 38.473 | 38.672 | 38.871 | 39.07 | 39.269 | 39.468 | 39.667 | 39.866 | 40.065 | 40.264 | 40.463 | 40.662 | 40.861 | 41.06 | 41.259 | 41.458 | 41.657 | 41.856 | 42.055 | 42.254 | 42.453 | 42.652 | 42.851 | 43.05